## Hydraulic Demand Comparison
Demand Included in Various Models (MMcfd)
| CPUC Simulations |  |  | Phase 3 Simulations (Shortfall Analysis)
| SIM 01 - 2020 | SIM 03 - 2025 | SIM 05 - 2030 | Phase 3 -2027 | Phase 3 -2035
Core | 3285 | 3170.7 | 3034 | 3101 | 2987
Non-Elec Gen Non-Core | 654 | 689.2 | 664.6 | 670 | 653
Elec Gen | 1048 | 900 | 1122.6 | 744.9896 | 804.0105
Total | 4987 | 4759.9 | 4821.2 | 4515.9896 | 4444.0105
Electric Generation Demand Breakout
FTI-Plexos |  |  |  | 620.9896 | 683.0105
EOR Electric |  |  |  | 52 | 50
Refinery Electric |  |  |  | 72 | 71
Total |  |  |  | 744.9896 | 804.0105
EG Demand Reduction Required to Balance Model
Base Requirements (above) |  |  |  | 4515.9896 | 4444.0105
(Demand Reduction (EG)) |  |  |  | -394.8384 | -322.9299
Total Served in Hydraulic Model |  |  |  | 4121.1512 | 4121.0806

## Total Demand Sourcing
Projected Natural Gas Demand on SoCal Gas System for Hydraulic Modeling
Year | SoCalGas Core 1/ | SDG&E Core 2/ | Other Core 3/ | Noncore Non-EG 4/ | EG 5/ | Total "1-in-10" Demand
2020 | 2752 | 400 | 103 | 661 | 1068 | 4984
2021 | 2732 | 399 | 104 | 659 | 1072 | 4966
2022 | 2718 | 400 | 105 | 664 | 1105 | 4992
2023 | 2698 | 398 | 105 | 668 | 1106 | 4975
2024 | 2676 | 397 | 106 | 671 | 1089 | 4939
2025 | 2652 | 395 | 107 | 674 | 1119 | 4947
2026 | 2626 | 394 | 108 | 674 | 1101 | 4903
2027 | 2601 | 392.8 | 107.3214 | 669.7653 | 964 | 4734.8867
2030 | 2529.9 | 389.9 | 105.4584 | 658.1387 |  | 3683.3971
2035 | 2493 | 389.6 | 104.6488 | 653.0858 | 961 | 4601.3346
Notes
1/ SoCal Gas Core Demand Forecast as detailed on Page 303 of SoCal Gas' 2020 California Gas Report REDACTED Workpapers.
2/ SDG&E Gas Core Demand Forecast as detailed on Page 303 of SoCal Gas' 2020 California Gas Report REDACTED Workpapers.
3/ 1-in-10 peak temperature cold day core demand of SWG, City of Long Beach, and City of Vernon. Demand thru 2026 as per
2020 California Gas Report. Demand after 2026 assumed to change at the average of SoCal Gas and SDG&E Core annual
rate of change.
4/ 1-in-10 peak temperature cold day non-core demand per 2020 California Gas Report for years 2020-2026. Demand after
2026 assumed to change each year based upon the average of the SoCal Gsa and SDG&E Core annual rate of change.
5/ EG Demand in years 2027 and 2035 as projected by FTI using PLEXOS modeling software. FTI demand in MMBtu/day.
Converted to MMcfd using SoCal Gas Dth/Mcf conversion factor of 1.0336 as described in footnote 4 on Page 303 of
SoCalGas 2020 California Gas Report REDACTED Workpapers.

## EG on SoCal Gas System
Electric Generation Demand in FTI/GSC Models of SoCal Gas System --- Modeled Demand Curtailments Required Absent Aliso Canyon (MMcfd)
|  |  | 2027 Analysis |  |  |  | 2035 Analysis
|  |  | Requirements per PLEXOS Model |  | Supported per Hydraulic Model |  | Requirements per PLEXOS Model |  | Supported per Hydraulic Model
Region | Facility Name | EIA Plant Code | Generation NG Demand Per FTI - PLEXOS Model (MMBtu/day) | Generation NG Demand Per FTI - PLEXOS Model (MMcf/day) | Generation NG Demand Supported - Hydraulic Model (MMBtu/day) | Generation NG Demand Supported - Hydraulic Model (MMcf/day) | Generation NG Demand Per FTI - PLEXOS Model (MMBtu/day) | Generation NG Demand Per FTI - PLEXOS Model (MMcf/day) | Generation NG Demand Per FTI - PLEXOS Model (MMBtu/day) | Generation NG Demand Per FTI - PLEXOS Model (MMcf/day) | Physical Location on SoCal Gas System
SCE | Att Van Nuys | 62574 | 83.92 | 0.081192 | 0 | 0 | 125.88 | 0.12179 | 0 | 0 | LA Basin
SCE | St. Johns Health Center | 50610 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | LA Basin
SCE | CES Placerita | 10677 | 1782.77 | 1.7248 | 0 | 0 | 3204.16 | 3.1 | 3204.16 | 3.1 | Coastal Zone
LDWP | LADWP Valley | 408 | 12007.83 | 11.6175 | 0 | 0 | 16891.72 | 16.3426 | 16891.72 | 16.3426 | LA Basin
LDWP | Lake One | 7987 | 409.36 | 0.39605 | 0 | 0 | 1637.44 | 1.5842 | 0 | 0 | LA Basin
LDWP | SCPPA - Magnolia | 56046 | 7759.25 | 7.507 | 7759.25 | 7.507 | 10205.37 | 9.8736 | 10205.37 | 9.8736 | LA Basin
LDWP | Olive | 6013 | 0 | 0 | 0 | 0 | 4893.17 | 4.7341 | 0 | 0 | LA Basin
LDWP | Grayson | 377 | 5839.96 | 5.6501 | 0 | 0 | 13516.68 | 13.0773 | 0 | 0 | LA Basin
LDWP | Scattergood | 404 | 37036.52 | 35.8325 | 37036.52 | 35.8325 | 41343.09 | 39.9991 | 41343.09 | 39.9991 | LA Basin
SCE | Walnut Creek Energy Park | 57515 | 4338.06 | 4.197 | 0 | 0 | 17352.24 | 16.7882 | 0 | 0 | LA Basin
SCE | CSUCI Site Authority | 50851 | 4060.56 | 3.9286 | 0 | 0 | 3389.53 | 3.2793 | 3389.53 | 3.2793 | Southern Zone (San Diego)
SCE | Glenarm | 422 | 12985.52 | 12.5634 | 0 | 0 | 13096.99 | 12.6712 | 0 | 0 | LA Basin
SCE | Ratkovich Alhambra | 62458 | 83.92 | 0.081192 | 0 | 0 | 125.88 | 0.12179 | 0 | 0 | LA Basin
SCE | SCE Center Peaker | 56475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | LA Basin
SCE | Harbor Cogen | 50541 | 2892.46 | 2.7984 | 0 | 0 | 5839.44 | 5.6496 | 0 | 0 | LA Basin
LDWP | LADWP Harbor Generation | 399 | 4088.95 | 3.956 | 0 | 0 | 7964.79 | 7.7059 | 0 | 0 | LA Basin
SCE | Long Beach Generation, LLC | 341 | 1707.5 | 1.652 | 0 | 0 | 10910.94 | 10.5563 | 0 | 0 | LA Basin
SCE | El Segundo Energy Center | 57901 | 12120.73 | 11.7267 | 0 | 0 | 24183.92 | 23.3978 | 0 | 0 | LA Basin
SCE | Oxnard Paper Mill | 57585 | 2324.78 | 2.2492 | 0 | 0 | 3336.8 | 3.2283 | 0 | 0 | Coastal Zone (East of La Goleta)
SCE | AES Alamitos Energy Center | 62115 | 80805.36 | 78.1786 | 80805.36 | 78.1786 | 60604.02 | 58.6339 | 60604.02 | 58.6339 | LA Basin
LDWP | LADWP Haynes Gen | 400 | 15016.36 | 14.5282 | 0 | 0 | 26868.72 | 25.9953 | 0 | 0 | LA Basin
SCE | Canyon Power | 57027 | 853.88 | 0.82612 | 0 | 0 | 3415.52 | 3.3045 | 0 | 0 | LA Basin
SCE | Mountainview Generation Station | 358 | 26338.93 | 25.4827 | 26339.2288 | 25.483 | 43006.96 | 41.6089 | 43006.96 | 41.6089 | Northern Zone / Southern Zone
SCE | Grapeland Hybrid | 56472 | 3543.44 | 3.4283 | 0 | 0 | 5315.16 | 5.1424 | 0 | 0 | Northern Zone / Southern Zone
SCE | Mira Loma Peaker | 56473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Northern Zone
SCE | AES Huntington Beach Energy Project | 62116 | 81809.52 | 79.1501 | 81809.52 | 79.1501 | 59449.49 | 57.5169 | 59449.49 | 57.5169 | LA Basin
IID | El Centro Hybrid | 389 | 37515 | 36.2955 | 0 | 0 | 39879.36 | 38.583 | 0 | 0 | Southern Zone (5000, 2000, 2001)
IID | Coachella | 6060 | 269.07 | 0.26032 | 0 | 0 | 1067.18 | 1.0325 | 0 | 0 | Southern Zone (5000, 2000, 2001)
IID | Rockwood | 7824 | 309.42 | 0.29936 | 0 | 0 | 928.26 | 0.89808 | 0 | 0 | Southern Zone (5000, 2000, 2001)
SDGE | Grossmont Hospital | 10115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Southern Zone (San Diego)
PGAE | Fresno Cogen Partners | 10156 | 10965.96 | 10.6095 | 0 | 0 | 8070.2 | 7.8079 | 0 | 0 | Line 85 Zone
SDGE | Childrens Hospital | 10175 | 26.22 | 0.025368 | 0 | 0 | 78.66 | 0.076103 | 0 | 0 | Southern Zone (San Diego)
SCE | Loma Linda University Cogen | 10206 | 214.01 | 0.20705 | 0 | 0 | 297.75 | 0.28807 | 0 | 0 | Northern Zone (Line 4002)
SCE | California Institute of Technology | 10262 | 359.04 | 0.34737 | 0 | 0 | 254.32 | 0.24605 | 0 | 0 | LA Basin
SDGE | Kyocera America Project | 10720 | 153.36 | 0.14837 | 0 | 0 | 178.56 | 0.17276 | 0 | 0 | Southern Zone (San Diego)
SCE | E F Oxnard Energy Facility | 10776 | 2066.06 | 1.9989 | 0 | 0 | 3474.9 | 3.3619 | 0 | 0 | Southern Zone (San Diego)
SCE | San Antonion Regional Hospital | 50234 | 62.34 | 0.060313 | 0 | 0 | 80.02 | 0.077419 | 0 | 0 | Northern Zone / Southern Zone
SCE | Oxnard | 50464 | 7363.95 | 7.1246 | 0 | 0 | 9353.6 | 9.0495 | 0 | 0 | Southern Zone (San Diego)
SCE | Municipal Cogen Plant | 50674 | 100.72 | 0.097446 | 0 | 0 | 151.08 | 0.14617 | 0 | 0 | Southern Zone (5000, 2000, 2001)
SCE | OLS Energy - Chino | 50850 | 1861.47 | 1.801 | 0 | 0 | 2459.36 | 2.3794 | 2459.36 | 2.3794 | Southern Zone (5000, 2000, 2001)
SDGE | Naval Hospital Medical Center | 50963 | 13 | 0.012577 | 0 | 0 | 17.69 | 0.017115 | 0 | 0 | Southern Zone (San Diego)
SDGE | CP Kelco San Diego Plant | 52147 | 1688.34 | 1.6335 | 0 | 0 | 2121.84 | 2.0529 | 0 | 0 | Southern Zone (San Diego)
SCE | Biola University Hybrid | 54296 | 30.72 | 0.029721 | 0 | 0 | 35.76 | 0.034598 | 0 | 0 | LA Basin
SDGE | NRG Energy San Diego | 54337 | 92.46 | 0.089454 | 0 | 0 | 130.38 | 0.12614 | 0 | 0 | Southern Zone (San Diego)
SDGE | Goal Line LP | 54749 | 7352.4 | 7.1134 | 0 | 0 | 6079.57 | 5.8819 | 0 | 0 | Southern Zone (San Diego)
SDGE | Richard J Donavan Correctional Facility | 54936 | 397.38 | 0.38446 | 0 | 0 | 499.68 | 0.48344 | 0 | 0 | Southern Zone (San Diego)
SCE | Blythe Energy Inc. | 55295 | 63675.6 | 61.6057 | 0 | 0 | 45103.55 | 43.6373 | 45103.55 | 43.6373 | Southern Zone (5000, 2000, 2001)
SDGE | Otay Mesa Generating Project | 55345 | 60501.84 | 58.5351 | 0 | 0 | 43965.81 | 42.5366 | 43965.81 | 42.5366 | Southern Zone
SDGE | CalPeak Power Border Peaker Plant | 55510 | 3847.76 | 3.7227 | 0 | 0 | 5771.64 | 5.584 | 0 | 0 | Southern Zone (San Diego)
SDGE | Cuyamaca Peak Energy Plant | 55512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Southern Zone (San Diego)
SDGE | CalPeak Power Enterprise Peaker Plant | 55513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | LA Basin
SDGE | Escondido Energy Center | 55538 | 3803.04 | 3.6794 | 0 | 0 | 5704.56 | 5.5191 | 0 | 0 | Southern Zone (San Diego)
SDGE | Chula Vista Energy Center | 55540 | 2036 | 1.9698 | 0 | 0 | 3563 | 3.4472 | 0 | 0 | Southern Zone (San Diego)
SCE | Indigo Energy Center | 55541 | 853.16 | 0.82543 | 0 | 0 | 4686.23 | 4.5339 | 0 | 0 | Southern Zone (5000, 2000, 2001)
SDGE | Larkspur Energy Facility | 55542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Southern Zone (San Diego)
PGAE | Hanford Energy Park Peaker | 55698 | 5220.36 | 5.0507 | 0 | 0 | 3480.24 | 3.3671 | 0 | 0 | San Joaquiin Valley
PGAE | Henrietta Peaker | 55807 | 10460.4 | 10.1204 | 0 | 0 | 6973.6 | 6.7469 | 0 | 0 | San Joaquiin Valley
SCE | Century Generating Facility | 55934 | 241.04 | 0.2332 | 0 | 0 | 723.12 | 0.69961 | 0 | 0 | Southern Zone (5000, 2000, 2001)
SCE | Drews Generating Facility | 55935 | 361.56 | 0.34981 | 0 | 0 | 1446.24 | 1.3992 | 0 | 0 | Northern Zone / Southern Zone
SCE | Agua Mansa Power Plant | 55951 | 373.72 | 0.36157 | 0 | 0 | 1494.88 | 1.4463 | 0 | 0 | Southern Zone (5000, 2000, 2001)
SDGE | Palomar Energy | 55985 | 52089.84 | 50.3965 | 0 | 0 | 36896.97 | 35.6975 | 36896.97 | 35.6975 | Southern Zone (San Diego)
SCE | H. Gonzalez | 56039 | 80.8 | 0.078173 | 0 | 0 | 242.4 | 0.23452 | 0 | 0 | LA Basin
SCE | Malburg | 56041 | 3307.03 | 3.1995 | 0 | 0 | 5659.28 | 5.4753 | 5659.28 | 5.4753 | LA Basin
SCE | Riverside Energy Resource Center | 56143 | 425.47 | 0.41164 | 0 | 0 | 1701.88 | 1.6466 | 0 | 0 | Southern Zone (5000, 2000, 2001)
SCE | Springs Generating Station | 56144 | 328.68 | 0.318 | 0 | 0 | 1314.72 | 1.272 | 0 | 0 | Southern Zone (5000, 2000, 2001)
SDGE | Miramar Energy Facility | 56232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Southern Zone (San Diego)
SCE | Bear Valley Power Plant | 56346 | 503.6 | 0.48723 | 0 | 0 | 755.4 | 0.73084 | 0 | 0 | Northern Zone
SCE | Clearwater Power Plant | 56356 | 2034.82 | 1.9687 | 0 | 0 | 2696.08 | 2.6084 | 0 | 0 | Southern Zone (5000, 2000, 2001)
SCE | McGrath Peaker | 56471 | 488.17 | 0.4723 | 0 | 0 | 1952.68 | 1.8892 | 0 | 0 | Southern Zone (San Diego)
SCE | Barre Peaker | 56474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | LA Basin
IID | Niland Gas Turbine Plant | 56569 | 4110.3 | 3.9767 | 0 | 0 | 16836.27 | 16.289 | 0 | 0 | Southern Zone (5000, 2000, 2001)
SDGE | Orange Grove Peaking Facility | 56914 | 3440.64 | 3.3288 | 0 | 0 | 7741.44 | 7.4898 | 0 | 0 | Southern Zone (San Diego)
SDGE | El Cajon Energy Center | 57001 | 3292.32 | 3.1853 | 0 | 0 | 4938.48 | 4.7779 | 0 | 0 | Southern Zone (San Diego)
SCE | UCI Facilities Management Central Plant | 57122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | LA Basin
SCE | Sentinel Energy Center, LLC | 57482 | 3193.68 | 3.0899 | 0 | 0 | 12774.72 | 12.3594 | 0 | 0 | Southern Zone (5000, 2000, 2001)
SCE | Cal State University San Bernadino FCO1 | 57544 | 172 | 0.16641 | 0 | 0 | 258 | 0.24961 | 0 | 0 | Northern Zone / Southern Zone
SDGE | Pio Pico Energy Center | 57555 | 16549.92 | 16.0119 | 0 | 0 | 20700.36 | 20.0274 | 0 | 0 | Southern Zone
SDGE | Watkins Manufacturing Co. | 57715 | 122.64 | 0.11865 | 0 | 0 | 142.8 | 0.13816 | 0 | 0 | Southern Zone (San Diego)
| UCSD Fuel Cell Plant | 57735 | 234.96 | 0.22732 | 0 | 0 | 352.44 | 0.34098 | 0 | 0 | Southern Zone (San Diego)
SCE | MolsonCoors Irwindale Brewery | 58056 | 434.96 | 0.42082 | 0 | 0 | 533.56 | 0.51622 | 0 | 0 | LA Basin
SCE | Energy Center | 58168 | 75.6 | 0.073142 | 0 | 0 | 113.4 | 0.10971 | 0 | 0 | Southern Zone (5000, 2000, 2001)
SCE | Honda Torrance | 58300 | 61.44 | 0.059443 | 0 | 0 | 71.52 | 0.069195 | 0 | 0 | LA Basin
SDGE | Life Technologies Carlsbad | 58302 | 30.72 | 0.029721 | 0 | 0 | 35.76 | 0.034598 | 0 | 0 | Southern Zone (San Diego)
SCE | Houweling Nurseries | 58432 | 1109.12 | 1.0731 | 0 | 0 | 1290.48 | 1.2485 | 0 | 0 | Coastal Zone (East of La Goleta)
SCE | MCAGCC Cogen Plant | 58914 | 527.6 | 0.51045 | 0 | 0 | 680.62 | 0.65849 | 0 | 0 | Southern Zone (5000, 2000, 2001)
SDGE | Carlsbad Energy Center | 59002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Southern Zone
SDGE | P Plant | 59456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Southern Zone (San Diego)
SCE | Amazon San Bernadino | 59800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Northern Zone (Line 4002)
SCE | Starbucks - Evolution Fresh | 59804 | 76.72 | 0.074226 | 0 | 0 | 89.28 | 0.086378 | 0 | 0 | Northern Zone / Southern Zone
SCE | UCI Fuel Cell | 60120 | 214.72 | 0.20774 | 0 | 0 | 249.96 | 0.24183 | 0 | 0 | LA Basin
SCE | Stanton Energy Reliability Center Hybrid | 60698 | 7560.32 | 7.3146 | 0 | 0 | 11340.48 | 10.9718 | 0 | 0 | LA Basin
SCE | SunSelect1 | 61754 | 276.88 | 0.26788 | 0 | 0 | 415.32 | 0.40182 | 0 | 0 | Coastal Zone
SCE | Bolthouse Farms Fuel Cell | 61845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Wheeler Ridge Zone
SCE | Disney Prospect | 62571 | 83.92 | 0.081192 | 0 | 0 | 125.88 | 0.12179 | 0 | 0 | LA Basin
SCE | ATT Kelvin | 62573 | 83.92 | 0.081192 | 0 | 0 | 125.88 | 0.12179 | 0 | 0 | LA Basin
SCE | Kaiser East La Palma Ave. Fuel Cell | 62698 | 125.84 | 0.12175 | 0 | 0 | 188.76 | 0.18262 | 0 | 0 | LA Basin
SCE | Equinix Douglas St. Fuel Cell | 62704 | 125.84 | 0.12175 | 0 | 0 | 188.76 | 0.18262 | 0 | 0 | LA Basin
SCE | Equinix Maple Ave. Fuel Cell | 62705 | 167.84 | 0.16238 | 0 | 0 | 167.84 | 0.16238 | 0 | 0 | LA Basin
SCE | Valero Wilmington Cogeneration Plant | 63285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | LA Basin
SCE | Gaviota Oil Plant | 50623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Coastal Zone (West of La Goleta)
SCE | Berry Placerita Cogen | 52096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | LA Basin
SCE | Berry NMW Cogens | 62176 | 419.52 | 0.40588 | 0 | 0 | 629.28 | 0.60882 | 0 | 0 | Line 85 Zone
| Total - Generation (MMcfd) - Excluding EOR Cogen and Refinery Cogen |  | 620.9896 | 620.9896 | 226.1512 | 226.1512 | 683.0105 | 683.0105 | 360.0806 | 360.0806
| Total - Generation (MMBtu/day) - Excluding EOR Cogen and Refinery Cogen |  | 641854.81 |  | 233749.8788 |  | 705959.65 |  | 372179.31
Total - Generation (MWh) - Excluding EOR Cogen and Refinery Cogen
|  |  | 2027 Analysis |  |  |  | 2035 Analysis
| Plants in PLEXOS that are not on SoCal Gas System | EIA Plant Code | Generation NG Demand Per PLEXOS Model (MMcfd) |  |  |  | Generation NG Demand Per PLEXOS Model (MMcfd) | Generation NG Demand Per PLEXOS Model (MMcfd) |  |  | Pipeline Delivering to Site
SCE | High Desert Power Plant | 55518 | 101581.44 |  |  |  | 83312.04 | 83312.04 |  |  | Kern River Pipeline
SCE | Pastoria Energy Facility, LLC | 55656 | 94884.48 |  |  |  | 77748.24 | 77748.24 |  |  | Kern River Pipeline
SCE | Kern River Cogeneration | 10496 | 35382.72 |  |  |  | 47480.64 | 47480.64 |  |  | Kern River Pipeline
SCE | Sycamore Cogeneration | 50134 | 43341.32 |  |  |  | 62295.56 | 62295.56 |  |  | Kern River Pipeline
SCE | Dome Project | 54449 | 118.72 |  |  |  | 158.96 | 158.96 |  |  | Kern River Pipeline
SCE | US Borax | 50115 | 3918.88 |  |  |  | 5255.12 | 5255.12 |  |  | Kern River Pipeline
|  |  | 279227.56 |  |  |  | 276250.56 | 276250.56
Note: EG Demand (MMBtu/day) in years 2027 and 2035 as projected by FTI using PLEXOS modeling software.
Converted to MMcfd using SoCal Gas Dth/Mcf conversion factor of 1.0336 as described in footnote 4 on Page 303 of SoCal Gas' 2020 California Gas Report REDACTED Workpapers.