## Slide 1: Rule 20 Phase II Workshop
November 8, 2022

## Slide 2: WebEx and Call-In Information
Join by Computer:
https://cpuc.webex.com/cpuc/onstage/g.php?MTID=ec1de21171c00afb828287a262d6c2f3f
Event Password: Underground1 (case sensitive)
Meeting Number: 2485 839 5545
Join by Phone:
Please register using the WebEx link to view phone number.
(Staff recommends using your computer’s audio if possible.)
Notes:
Today’s presentations will be available at https://www.cpuc.ca.gov/industries-and-topics/electrical-energy/infrastructure/electric-reliability/undergrounding-program-description/cpuc-rule-20-undergrounding-programs--current-proceeding-r1705010 under the “Rule 20 Workshops” link.
This meeting will be recorded.

## Slide 3: WebEx Logistics
All attendees are muted on entry by default.
Please write your questions in the Q & A box, and addressed to the host and presenters. Some questions will be addressed at the end of each section while others will be answered at the end of the workshop.
Comments can be provided verbally during the feedback session using the “raise hand” function.
  The host will unmute you and you will have a maximum of 2 minutes to speak.
  Please lower your hand after you’ve asked your question by clicking on the “raise hand” again.
  If you have another question, please “re-raise your hand” by clicking on the “raise hand” button twice.
2. Raise your hand by clicking the hand icon.
3. Lower it by clicking again.
1. Click here to access the attendee list to raise and lower your hand.
WebEx Tip
Access the written Q&A panel here
Access your meeting audio settings here
Notes: objectives.

## Slide 4: Workshop Objectives
Attendees understand Rule 20
Attendees are aware of challenges to Rule 20
Attendees are aware of Rule 20 Adjacent Programs
Attendees may provide and offer actionable feedback on necessary changes to Rule 20 in Phase II

## Slide 5: Workshop Objectives
Answer and explore solutions related to the Scoping Memo Issue Questions
  Whether to add Rule 20A project eligibility criteria for wildfire safety and emergency-related undergrounding or otherwise modify Rule 20A project eligibility criteria;
  Whether to modify the Rule 20 program to support future projects in underserved, tribal, and/or disadvantaged communities or otherwise advance the goals of the Commission’s Environmental and Social Justice Action Plan;
  Whether the Commission or utilities should enhance engagement with local governments to inform utility investments in undergrounding for safety, resilience, or emergency-related purposes.

## Slide 6: Workshop Agenda
Section | Section Title | Duration
I | Logistics & Opening Remarks | 9 AM – 9:15 AM
II | Introduction to Rule 20 | 9:15 AM – 9:35 AM
III | Stakeholder presentations- Wildfire Undergrounding & Local Engagement | 9:40 AM – 10:40 AM
IV | Stakeholder presentations- Equity | 10:45 AM- 11:45 AM
V | Equity Panel | 11:50 AM -12:30 PM
VI | Questions & Comments from the Public | 12:30 PM – 12:50PM

## Slide 7: Opening Remarks
President Reynolds Office

## Slide 8: Introduce Key Participants
San Diego Gas & Electric (SDG&E), Pacific Gas and Electric (PG&E), Southern California Edison (SCE)
The Utility Reform Network (TURN), Public Advocates Office (Cal Advocates)
Rural Counties Representatives of California (RCRC) / Lake County
California League of Cities

## Slide 9: II. Rule 20 Presentation
Energy Division Staff

## Slide 10: Electric Tariff Rule 20
CPUC Energy Division
Julian Enis and Messay Betru
Grid Resiliency and Microgrids
Credit: Messay Betru

## Slide 11: Agenda
  Introduction to Rule 20
  Issues and Observations
  Current Activities
  Next Steps
Credit: Messay Betru

## Slide 12: Introduction to Rule 20
Program Overview

## Slide 13: Rule 20 Overview
Rule 20 is a program and tariff that undergrounds powerlines and facilities at the request of third parties (e.g., local governments, developers, and other non-utility parties). The scope is aesthetic only, and factors such as wildfire mitigation are not considered (with exception for Rule 20D).
Utility Rule 20 Program expenditures are approved through the through the General Rate Case process.
4 subprograms (A – D) covering different levels of cost allocation between the requestor and the utility. Each project request slots into specific subprogram, dependent upon on who has requested the work and how they wish to fund the work.

## Slide 14: Rule 20 Subprograms
Rule 20 is split into four distinct subprograms, A – D:
¹Requires requestor to have sufficient work credit balance. In effect, work credits are vouchers that local governments can redeem to perform undergrounding work and were allocated annually until 2022.
²SDG&E region-based subprogram only.
Subprogram | Project Requestor | Funding Description
Rule 20A¹ | Local Governments | 100% ratepayer-funded
Rule 20B | Applicant | 20-40% rate payer funded
Rule 20C | Applicant | Majority funded by municipality/individual property owner/developer
Rule 20D¹,² | Local governments identified in high fire risk areas | 100% ratepayer-funded

## Slide 15: Rule 20 Project Criteria
Rule 20A:
  Projects are funded solely by ratepayers.
  The local government agency must adopt an ordinance to create an underground district. Districts created via the public process must demonstrate that the project is in the general public interest through key criteria (including, not limited to):
    Elimination of unusually heavy concentration of overhead electric facilities/heavy volume of pedestrian or vehicular traffic;
    The street has limited/impeded wheelchair access that is not compliant with the Americans with Disabilities Act (ADA); and,
    The street is deemed to be an arterial street or major collector as defined by the California Department of Transportation (CalDOT).

## Slide 16: Rule 20 Project Criteria (Continued)
Rule 20B:
  Affected property owners agree in writing that service will be from an underground source and that the utility can discontinue overhead service; and,
  Applicant renders payment to the utility for completion of undergrounding work.
Rule 20C:
  Applicant renders advanced payment for cost of undergrounding distribution facilities to the utility.
Rule 20D (SDG&E Territory Only):
  The local government has found that undergrounding work is in the public interest because it will occur within an SDG&E Fire Threat Zone and is the utility preferred method to reduce ignition risk;
  The local government has adopted an ordinance creating an undergrounding district; and,
  Sufficient Rule 20D work credits are available to perform the work.

## Slide 17: Issues and Observations
What Is At Issue And Being Addressed In Phase II

## Slide 18: Rule 20 Current Issues
The following are some issues that the existing Rule 20 program as written faces, which will need to be addressed:
Inequity in the program;
Lack of transparency into IOU methods;
No program mechanisms to incentivize timely, cost-efficient project completion; and,
Public interest criteria are no longer aligned with goals of undergrounding and CPUC directives of reliability and safety.

## Slide 19: Rule 20 Issues with Work Credits
The following are some issues that the existing Rule 20 program as written faces, which will need to be addressed:
Large unused work credit balances in some communities;
Inequitable allocation formula that requires smaller communities to save for much longer before being able to undertake projects; and,
Inflation-adjusted project costs have risen since 2005, while work credit allocations have remained static.

## Slide 20: Rule 20 Program Observations & Questions
Project expenditures have primarily occurred in economically core areas like the Bay Area and coastal San Diego County.
  The work credit allocation formulas give larger jurisdictions proportionally more work credits and thus undergrounding tends to be done in more urban areas.
Small communities do not receive enough work credit allocations to fund projects unless they save for long periods of time.
  Work credit allocation formulas for more rural communities are proportionally small and utilities will generally only pursue a project if work credits are available.
82 communities (16 percent) state-wide did not complete any Rule 20A projects from 2005 – 2019.
  Is this an issue of poor outreach, low visibility, or local governments not having enough resources to take advantage of this program?

## Slide 21: Current Activities
Current Procedural Activities & Requirements

## Slide 22: Rule 20 Annual Report
D.21-06-013 created an updated annual reporting requirement for utility data on their Rule 20 A – D programs. This annual report template, which can be found here, asks for, among other things:
  Data on completed and in-flight projects, including cost and trench lengths;
  Data on active and inactive communities, including work credit balances and debt; and,
  GIS data of project locations and trench paths.
Since this was a new requirement, the utilities have filed for and received an extension on providing some of the data until August 2022.
  The IOUs have submitted partial reports with data they were able to provide on April 1st.

## Slide 23: Next Steps
Phase II Initial Framework Layout

## Slide 24: Phase II of R.17-05-010
D.21-06-013 proposes the following set of issues to be considered in Phase II of the Proceeding- whether to:
  Add Rule 20A project eligibility criteria for wildfire safety and emergency-related undergrounding or otherwise modify Rule 20A project eligibility criteria;
  Modify the Rule 20A program to support projects in underserved and disadvantaged communities;
  Take additional steps to support the completion of active Rule 20A projects; and,
  Modify or discontinue the Rule 20D program.
Notes: For Phase II of the proceeding, staff will consider the following measures:
Is it feasible to expand the existing 20 A criteria to include wildfire and emergency –related UG
What modifications can be added to increase penetration into disadvantaged communities
What considerations can support the completion of 20A projects, and
Is it effective to sunset the SDGE 20D program

## Slide 26: III. Stakeholder Presentations
Wildfire Undergrounding & Local Engagement

## Slide 27: Stakeholder Presentations
SDG&E

## Slide 28
Rule 20 Phase II Workshop
SDG&E Strategic Undergrounding Program
November 8, 2022

## Slide 29
Customer Accounts
Weather Stations
Miles of Overhead Lines
Underground Infrastructure
3,500
64%
2
221
Trees Inventoried
183k
42%
Of Service Territory
High Fire Threat
District (HFTD)
Tier 2
Tier 3
53%
Wildfire Risk in SDG&E’s
Service Area
High Fire Threat District (HFTD)

## Slide 30
By the end of 2023, 100% of SDG&E’s transmission system in Tier 3 of the HFTD will be hardened
84% risk event reduction
Falling conductor protection will be implemented on transmission
> 900 / 3,500 miles (25%) of overhead distribution lines in the HFTD have been hardened with bare wire and begun transition to covered wire
65% risk event reduction
20 miles completed in 2021
60 miles planned in 2022
Continued falling conductor protection
SDG&E is the first IOU to apply wildfire mitigation undergrounding of overhead lines inclusive of secondaries & services in the HFTD
98% risk event reduction
25+ miles completed in 2021
65 miles planned in 2022
Grid & Infrastructure Hardening
30
Transmission
Strategic Undergrounding
Covered Conductor

## Slide 31
Electric System Hardening
Chart: Undergrounding and Covered Conductor SCOPE
| 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
UG miles | 60 | 80 | 125 | 150 | 160 | 170 | 170 | 170 | 170 | 170 | 100
CC miles | 60 | 60 | 60 | 40 | 40 | 40 | 40 | 30
1500 miles UG
Total Portfolio
370 miles CC
Industry-leading Strategic Undergrounding
2020-2022 YTD Completed 80 miles of distribution underground in HFTD.
Undergrounding helps to reduce wildfire risk at a greater rate
Undergrounding supports reduction of PSPS impacts and risks to customers.
All 2000 miles of transmission will be hardened by 2026
Modernizing Strategic Undergrounding
Only utility to include the service lines up to meter panels.
As climate change continues to increase the potential for wildfires, undergrounding will help better address future climate challenges.

## Slide 32
Risk Assessment
Wildfire Next Generation System (WiNGS)
6​
Optimal Mitigation
32

## Slide 33
Construction Photos
6​
33
C440 – Sunrise Highway
Trencher C1090 – Valley Center
C1090 – Valley Center

## Slide 34
Tim Knowd – Program Manager, Major Projects
858-637-7930 Office
Tknowd@sdge.com

## Slide 35: Stakeholder Presentations
SCE

## Slide 36
SCE’s Targeted Undergrounding Program for Wildfire Mitigation
California Public Utility Commission Rule 20 Phase 2 Workshop 11/08/2022

## Slide 37: SCE SERVICE AREA & HIGH FIRE RISK AREAS
SCE Service Area County Lines
Tier 2 – Elevated Fire Threat
Tier 3 – Extreme Fire Threat
50,000 SQ. MI.
of SCE service area across southern, central and coastal California
14,000 SQ. MI.
of high fire risk areas
5M
customer accounts or 15M residents in SCE’s service area
1.3M
customer accounts or 3.9M residents served by circuits in high fire risk areas
52,000 MI.
of SCE overhead distribution and transmission lines
14,000 MI.
in high fire risk areas
1.4M
power poles
300,000
in high fire risk areas
Counties with high fire risk area served by SCE | Fresno Inyo Kern Los Angeles Mono Orange Riverside San Bernardino Santa Barbara Tulare Ventura | Counties with no or limited high fire risk areas served by SCE | Imperial Kings Madera Tuolumne 27% servi high f
of SCE's ce area is in
ire risk areas

## Slide 38: A COMPREHENSIVE STRATEGY TO PREVENT, COMBAT AND RESPOND
3
A COMPREHENSIVE STRATEGY to prevent, combat and respond
ENHANCING OPERATIONAL PRACTICES
BOLSTERING SITUATIONAL AWARENESS CAPABILITIES
HARDENING THE ELECTRIC GRID

## Slide 39: HARDENING ELECTRIC GRID & INFRASTRUCTURE
4
Replacing bare wire with covered conductor to reduce wildfire risk as well as safely raise windspeed thresholds for PSPS in targeted areas.
Over 4,050 miles of covered conductor installed since 2018
Installing mix of composite poles and wooden poles with fire-resistant wrap to reduce risk of damaged poles during an emergency
FIRE- RESISTANT POLES
MICROGRIDS
UNDERGROUNDING
COVERED CONDUCTOR
PROTECTIVE DEVICES
Installing fast-acting fuses to interrupt electric current more quickly when there’s an electrical fault and remote- controlled sectionalizing devices to segment and isolate portions of circuits during PSPS events
Complete 17 miles of undergrounding in 2021-22 in targeted high fire risk areas based on risk and feasibility. Potential for significant increase in subsequent years.
Partnered with San Jacinto High School for a microgrid resiliency pilot.
Targeting a second pilot site at a school in the Rialto Unified School District.
Data as of 9/30/22

## Slide 40: COVERED CONDUCTOR IS ONE OF THE MOST EFFECTIVE MEASURES TO REDUCE WILDFIRE & PSPS RISKS IN SCE’S SERVICE AREA
Execution Speed
Covered conductor can be deployed within 16–24+ months, and sometimes faster
Undergrounding generally takes 25–48+ months
Unique Factors
Undergrounding is considered where there is:
High burn frequency
Limited egress
Wind speeds exceeding covered conductor PSPS thresholds
Exceptionally high potential consequence (>10,000 acres)
Operational feasibility
Several hundred miles currently under evaluation
for additional enhanced mitigation, including undergrounding
Cost to Implement
Covered conductor installation costs significantly lower than undergrounding
Undergrounding costs vary depending on construction methods, locational, and operational factors
Cost per mile1
$ in Millions
~5.5
~1.5
~0.6
Under- ground
Covered Conductor
Covered conductor is a very valuable tool to expeditiously and cost-effectively reduce wildfire risk specific to SCE
Undergrounding pursued for certain locations based on risk profile
~65–90%
lower
https://library.sce.com/conten t/dam/eix/documents/investo rs/wildfires-document- library/Wildfire_CaliforniaBiom es.pdf
Geography
Contact from vegetation and other objects is a key risk factor in much of SCE’s area
Covered conductor is very
effective in mitigating these
risks
Chaparral (brushland) presents different primary risk factors than heavily forested areas
Click to view
larger image
Vegetation Type Evergreen Forest Deciduous Forest Broadleaved Forest Chaparral Grassland
Desert Scrub
5
Covered Cond. |  | Under- ground
Initiate | ~2–3 | ~2–3
Plan | ~6–9 | ~9–15
Schedule2 | ~6–9 | ~9–15
Execute | ~2–3 | ~5–15
Total | 16–24+ | 25–48+
Avg. Implementation Time
In Months
Based on data provided in SCE’s 2022 WMP Update
The Schedule phase includes verifying permits, obtaining easements, scoping and bundling work, and scheduling construction

## Slide 41: ASSESSMENT OF RISK FACTORS & POTENTIAL MITIGATIONS IN SEVERE RISK AREAS
Locations which are likely to exceed de-energization thresholds even with CC fully deployed
Highest Ranked Egress Constrained/ Fire Frequency Locations
Burn in Buffers using WRRM risk factors (acres and wind speed)
Egress Constrained Locations
Locations with High Historical Fire Frequency
Risk factors considered include:
Wildfire Risk Reduction Model (WRRM) scores
̶ Fuel & weather
̶ Probability
̶ Standard consequence1
Egress constrained locations
Locations with high historical fire frequency
Locations which are likely to exceed de-energization thresholds
Community specific egress concerns
Overhead hardening does not have sufficient risk buydown
̶ Heavy tree proximity
̶ Full complement
of mitigations (CC++) residual risk too high
Potential mitigations may include:
Undergrounding
Aerial bundle cable
Spacer cable
Steel poles
REFCL & CC++
CC++
Mitigation selection criteria include:
Existing wildfire mitigation deployment
Electrical topology
Terrain
Geology
Environmental factors
Tree canopy height and density
Asset proximity to egress
Assess
Develop
Implement
1“Standard” consequence represents raw output from Technosylva showing acres burned, and buildings impacted within a fire scar, unadjusted for non-modeled dimensions like egress and other factors
High Standard Consequence Areas
6

## Slide 42: INTEGRATED GRID HARDENING STRATEGY
SCE’s refined integrated grid hardening strategy considers wildfire risk drivers and PSPS risk at circuit segments and mitigations that cost effectively addresses those risk drivers. We continue to prioritize hardening our riskiest areas first.
7
1Based on initial feasibility analysis of circuit miles in severe risk areas, several hundred miles currently under consideration for additional enhanced mitigation, including undergrounding
 | Risk Designation | Risk Criteria | Mitigation Selection
Total High Fire Risk Area (HFRA) Overhead Distribution Segments (Total of ~9,700 circuit miles, of which 37% is already hardened) | Severe Risk Areas (~2,275 circuit miles)1 | Fire risk egress constrained locations, extreme high wind areas, and extreme consequence areas | Pursue undergrounding unless covered conductor already installed or specific terrain not practical for undergrounding and necessitates feasible alternative mitigations
 | High Consequence Segments (~4,675 circuit miles) | Locations that meet 300-acre consequence threshold at 8 hours or at risk of Public Safety Power Shutoff (PSPS) | Pursue covered conductor plus other mitigations such as asset inspections, vegetation management, and fast curve settings
 | Other HFRA Segments (~2,750 circuit miles) | Locations that are not in a Severe Risk Area and do not meet High Consequence criteria | Naturally replace retired or damaged bare wire with covered conductor per high fire risk area standard; continue mitigations such as asset inspections, vegetation management, and fast-curve settings

## Slide 43: COVERED CONDUCTOR & UNDERGROUNDING
8
Determine scope based on risk
Finalize project timelines
Initiate early permit application (city/county/Cal Trans)
Initiate government lands and environmental requirements
Perform standard permitting and easement processes
Perform environmental clearance process
Obtain additional agency permits
Construct overhead assets and conductors, using helicopters as necessary
Determine scope based on risk
Finalize project timelines
Initiate early permit application (city/county/Cal Trans)
Initiate government lands and environmental requirements
Perform standard permitting and easement processes
Perform environmental clearance process
Obtain additional agency permits
Excavation, trenching and paving
Installation/removal of equipment
Note: Underground construction requires disturbance along entire route, which could require approval from multiple agencies and jurisdictions and more extensive environmental reviews and approval, whereas overhead conductor construction primarily disturbs locations where poles are installed.

## Slide 44: THANK YOU

## Slide 45: Stakeholder Presentations
PG&E

## Slide 46: 10,000-Mile Undergrounding Program California Public Utilities Commission Rule 20 Phase II Workshop
November 8, 2022

## Slide 47: 95%
Drought-Intensified Wildfire Risk in Our Service Area
2020 | 2021 | 2022
47%
of acreage
burned by wildfires ignited
on non-Red Flag
Warning days
of acreage burned by wildfires ignited on non-Red Flag Warning days
Driest year to date
over the last
128 years
U.S. drought monitor Map as of 12/29/2020
U.S. drought monitor Map as of 11/2/2021
U.S. drought monitor Map as of 8/9/2022
D0: Abnormally dry | D1: Moderate drought | D2: Severe drought | D3: Extreme drought | D4: Exceptional drought
MAP LEGEND

## Slide 48: Underground 10,000 Miles of Our Electric System
PG&E has taken a stand that catastrophic wildfires shall stop.
Last year PG&E announced a major new initiative to underground 10,000 miles of power lines in high fire-risk areas.
10,000 miles is nearly 40% of the miles
PG&E has in high fire-threat areas.
This commitment represents the largest effort in the U.S. to underground power lines as a wildfire risk reduction measure.
CPUC High Fire-Threat District (HFTD) Map
More than 25,000 miles of our electric lines are now located in HFTD.
Source: California Public Utilities Commission
High Fire-Threat
Tier 2 - Elevated
Tier 3 - Extreme
PG&E service area

## Slide 49: Benefits of Undergrounding
Our undergrounding plans will help build the system for the future and will benefit our customers by:
Reducing powerline ignition risk by approximately 99% in that location
Limiting future safety power outages
Improving system reliability
Decreasing future tree work
Beautifying our hometowns
A SAFER SYSTEM FOR THE FUTURE
Reduce Wildfire
Risk
Improve System Reliability
Reduce Ongoing Expenses
Protect the Environment

## Slide 50: Identifying Underground Miles
Constructability and
Community Impact
Balance impact to customers, communities and agencies
Deploy diverse construction means and methods
Execute
Improve Efficiency
and Lower Cost
Optimize wildfire risk
reduction per dollar spent
Bundling miles in nearby areas to maximize efficiency and reduce the length of construction impact
Sequence
Reduce Wildfire Risk
and Safety Outages
Risk model identified miles
PSPS miles
Public safety risk identified
miles
Fire rebuild miles
Identify

## Slide 51: Focusing on Primary Lines to Reduce Wildfire Risk
Higher voltage distribution lines (or primary lines) pose the greatest
wildfire risk, therefore, to maximize safety for our customers we
are prioritizing undergrounding those lines.
In most cases, lower voltage secondary powerlines (including those connecting to individual homes or businesses) as well as telecommunication lines and poles, will remain in place as they represent a lower wildfire risk.
Transformer
Service Wires
Higher Voltage Distribution Lines
Secondary Lines
Telecommunication

## Slide 52: Partnering with Customers and External Stakeholders
Stakeholders | Outreach Methods | 
Customers | CWSP Webinars Website Updates Media Call Center/Email Correspondence | Construction Outreach (Phone Calls, Letters, 1-on-1 Meetings)
Local Agencies (Cities/Counties/Tribes) | Public Presentations 1-on-1 Meetings Site Visits Undergrounding Advisory Group (UAG) Meetings | Local Government Forums Regional Working Groups Permitting Discussions
State and Federal Agencies | Public Presentations 1-on-1 Meetings Site Visits UAG Meetings | Regional Working Groups Regulatory Filings Permitting Discussions
Other Key Stakeholders (Telecom Providers/Etc.) | UAG Meetings 1-on-1 Meetings | Site Visits
We know that we cannot do this alone – we need help. We are engaging and partnering with our customers and communities.

## Slide 53
2022 Progress to Date
We are on track to underground at least 175 miles this year, more than doubling the mileage that we completed in 2021.
57+
MILES IN
CONSTRUCTION
(to meet our 175-mile goal)
118*
MILES
COMPLETE
(67% of the 2022 goal)
*Includes 1.5 miles of Rule 20A Undergrounding in HFTD areas.
100%
80%
60%
40%
20%
0%
Data is approximate and as of 10/24/22. Note the miles identified for 2022 exceed the 175-mile target to account for potential delays or changes due to scheduling, permitting, weather and other factors.

## Slide 54: Undergrounding Work Plans by County
Note: This map is for illustrative purposes only. Work plans are subject to change due to weather, access, and permitting, among other constraints.
COUNTY | 2022 PLANNED/ COMPLETED MILES | 2023 PLANNED MILES | 2024-2026 PLANNED MILES
Alameda | - | 2 | -
Amador | 2 | 21 | 377
Butte | 112 | 148 | 285
Calaveras | <1 | 33 | 199
Contra Costa | 6 | 3 | 59
El Dorado | 35 | 11 | 393
Fresno | <1 | 1 | -
Glenn | - | 20 | -
Humboldt | <1 | - | -
Kern | - | 49 | -
Lake | 23 | 84 | 269
Marin | 3 | - | -
Mariposa | - | 5 | 70
Mendocino | <1 | 3 | -
*Data is as of 09/01/2022. Planned miles reflect undergrounding projects that are in any stage of the planning process. Planned miles exceed annual targets, and mileage in your community may increase or decrease due to access, weather, permitting or other constraints. If planned work is not completed during the year originally identified, it will continue through planning/construction phases during subsequent years.
High Fire-Risk Area
PG&E Electric Service Area
2022 Planned/
Completed Project
2023 Planned Project
COUNTY | 2022 PLANNED/ COMPLETED MILES | 2023 PLANNED MILES | 2024-2026 PLANNED MILES
Napa | 5 | 53 | 302
Nevada | <1 | 92 | 172
Placer | 3 | 49 | 362
Plumas | 16 | 55 | 39
San Luis Obispo | - | 7 | -
San Mateo | 6 | 5 | -
Santa Barbara | - | 18 | -
Santa Cruz | 2 | 7 | -
Shasta | 17 | 100 | 114
Solano | 7 | 81 | 9
Sonoma | 2 | 6 | 59
Tehama | 2 | 18 | 46
Trinity | - | 11 | 10
Tuolumne | - | 3 | 55

## Slide 55: Thank You

## Slide 56: Stakeholder Presentations
Energy Division Staff

## Slide 57: Senate Bill 884
Bill Overview

## Slide 58: Senate Bill 884 Overview
Senate Bill (SB) 884 was introduced by Senator McGuire and signed into law by Governor Newsom on September 29, 2022.
SB 884 directs the CPUC to establish an expedited utility distribution undergrounding program for large electrical utilities (> 250,000 customer count). An application containing the following will first be submitted to the Office of Energy Infrastructure Safety (OEIS):
  A 10-year plan for undergrounding distribution lines in Tier 2 and 3 high fire threat districts, including identification of the projects to be constructed in this program with timeline for completion, unit costs, and yearly mileage targets
  A comparison of undergrounding versus aboveground hardening of electrical lines and wildfire mitigation
  A plan for utility and contractor workforce development and cost containment assumptions for the program
OEIS will then put the plan up for public comment and has nine (9) months to approve or deny the plan. If approved, the utility will then file an Application with the CPUC requesting review and conditional approval of the plan’s costs.

## Slide 59: Senate Bill 884 Overview
The Application to the CPUC should include the following items:
  Improvements in safety risk and reduced costs compared to other hardening measures
  Cost targets that result in attainable cost reductions compared to historical undergrounding costs.
  How cost targets are expected to decline over time and a strategy for achieving the targets
CPUC will have nine (9) months to approve or deny the application and must hold a public workshop and take public comment
If the plan is approved by OEIS and CPUC, the utility will be required to:
  Hire an independent monitor (selected by OEIS) to assess compliance with the plan and file a report annually
  File a progress report every six (6) months to both agencies.
If deficiencies are found by the independent monitor’s report, the utilities have 180 days to correct them. Based on this report and utility compliance, OEIS may recommend penalties to CPUC which CPUC will then be charged with enforcing.

## Slide 60: PG&E’s Enhanced Powerline Safety Settings (EPSS)
Program Description as an Alternative Wildfire Mitigation Strategy

## Slide 61: Enhanced Powerline Safety Settings (EPSS)
Enhanced Powerline Safety Settings (EPSS, commonly referred to as “Fast Trip”) is a PG&E wildfire mitigation program that programs and coordinates distribution reclosers and fuses to be more sensitive to faults, interrupting power before a fault can become a spark and a potential wildfire ignition. Restoration of service occurs after a patrol has taken place to ensure the line can be re-energized safely.
For 2022, PG&E has activated EPSS for all 44,000+ miles of distribution infrastructure in high fire threat districts.
EPSS-type wildfire mitigations exists for other utilities. SCE’s Fast Curve program and SDG&E’s Sensitive Relay Profiles program use the same principles.
EPSS-type programs are low-cost alternatives to other wildfire mitigations (e.g., covered conductor and undergrounding) that can significantly reduce potential ignitions. However, these programs include the trade-off of increased outage frequency.

## Slide 62: Enhanced Powerline Safety Settings (EPSS)
EPSS type outages are unplanned and if the trip happens at night or in inaccessible terrain, outages can be long as crews patrol the line to restore power.
PG&E’s program will cost around $151 Million in 2023, driven mostly by costs of patrolling lines and to some degree by new and expanded customer support programs.
  PG&E asserts that undergrounding line will reduce the need for EPSS and Public Safety Power Shutoff outage types and forecast decreasing costs for subsequent years in the GRC.
While program costs for EPSS are not insignificant, undergrounding all 44,000+ miles of distribution infrastructure in high fire threat districts would be extremely cost-prohibitive by comparison.

## Slide 63: Rule 20 and California Tribes
Applicability, Eligibility, and Participation

## Slide 64: Tribal Participation in Rule 20
Tribal governments can initiate and participate in Rule 20 projects insofar as they are served by a utility with a Rule 20 tariff.
However, as the rule is currently written, Tribal governments receive no work credit allocations of their own and thus would need to work with the county government of where the Tribe resides to initiate or execute projects.
  The relationship between governments can sometimes be non-existent or antagonistic, which represents a steep barrier to Tribal participation in Rule 20.
Additionally, it has ben observed that there is little to no Tribal government awareness of what Rule 20 is and what it offers.
Further Tribal government participation will be needed in Phase II of R.17-05-010 to assess how this program can best serve Tribal needs for undergrounding of utility lines.

## Slide 65
Julian.Enis@cpuc.ca.gov

## Slide 66: Q&A and Feedback from Attendees

## Slide 67: Break

## Slide 68: IV. Stakeholder Presentations- Equity
Cal Advocates, The Utility Reform Network, Rural Counties Representatives of California, & California State Association of Counties

## Slide 69: Stakeholder Presentations- Equity
Public Advocates Office (California Advocates)

## Slide 70
Equity Considerations for Rule 20 Programs
CPUC Order Instituting Rulemaking 17-05-010
Danielle Dooley| November 8, 2022

## Slide 71: Cal Advocates’ Positions
The Rule 20 program exists in a time of escalating electric rates.
  Lowering these costs will help to decrease ratepayer burdens.
Rule 20A projects historically led to little undergrounding statewide and occurred primarily in coastal, wealthier areas.
The Commission should consider sunsetting the entire Rule 20A
program.
If the Commission should decide to reallocate unused work credits, it should prioritize reallocation to underserved communities as defined by the Commission’s Environmental Social Justice plan.

## Slide 72: Electric Rates are Escalating

## Slide 73: Lowering T&D Costs will help to lower Ratepayer Burdens
Utility Costs And Affordability Of The Grid Of The Future, CPUC, 2021

## Slide 74: Rule 20A has led to Little Undergrounding Statewide
The CPUC’s Decision sunsets new work credit allocations after December 31, 2022, and allows communities to spend any previously-accumulated credits.
In Phase 2 of this proceeding, the Commission should consider sunsetting the entire Rule 20A program.
  Over 52 years, Rule 20A projects converted only 2,500 miles of overhead lines, while nearly 147,000 miles of overhead remain.
  Other programs could more effectively underground with a lower ratepayer burden.
Staff Proposal for Rule 20 Program Reform and Enhancements, CPUC, 2020

## Slide 75: The Benefits of Rule 20A Projects are not Evenly Distributed
The largest work credit expenditures are primarily in wealthier, more populous coastal areas.
Rural areas may see limited to no benefits from the
Rule 20 programs.
82 communities statewide have not completed a single project since 2005.
Staff Proposal for Rule 20 Program Reform and Enhancements, CPUC, 2020

## Slide 76: Incorporate the ESJ Community Definition for Underserved Communities
The CPUC intended the Environmental Social Justice (ESJ) Community definition to be used in CPUC proceedings, as defined in the ESJ Action Plan.
The ESJ Community is broad, encompassing:
  Tribal Lands,
  Disadvantaged Communities (DACs),
  Low-income households and census tracts.
The ESJ Definition aligns with other legislative underserved criteria, such as AB 841.
Environmental & Social Justice Action Plan Version 2.0, CPUC, 2022

## Slide 77: Community Eligibility for One-time Credit Reallocation
An underserved community that:
  Is eligible under the ESJ Community definition.
  Is an Active community:
    Identified a project in the public interest,
    Formed a utility undergrounding district,
  Has not historically benefited from the
program.

## Slide 78: Stakeholder Presentations- Equity
Rural County Representatives of California (RCRC)

## Slide 79: Stakeholder Presentations- Equity
California State Association of Counties (CSAC)

## Slide 80: Stakeholder Presentations- Equity
The Utility Reform Network (TURN)

## Slide 81: Possible Changes to the Work Credit Trading System to Address Equity and Other Concerns
David Cheng Staff Attorney

## Slide 82: Equity Concern
Some smaller cities will either never accumulate enough credits for a project or need to wait for a long, long time
Residents of these cities have paid their portion of Rule 20A projects in rates
Without trading these credits with other cities that are in a position to use the credits, these smaller cities are unable to extract value of their work credits for residents of those cities

## Slide 83: Issues with the Previous Trading System
No Commission oversight
No standardized pricing
No restrictions on how the selling city will use the proceeds from the trade/sale

## Slide 84: Ideas for Improved “Trading” System (Idea #1)
Purchasing city pays 80 cents (or some standardized amount) for each dollar of credit it wishes to purchase
Payment is made to the Utility and held in a trust account
Payments are distributed to the customers of the selling city as a bill credit
Pros: - Commission oversight
  Standardized pricing
  Funds go toward benefiting utility customers

## Slide 85: Ideas for Improved “Trading” System (Idea #2)
Each time a city redeems work credits toward a project, 5-10% is deposited into a lottery pool
Each year, cities that have never completed a project are entered into the lottery
Winning city can redeem the work credits in the lottery pool. Any leftover stays in the pool.
Pros: - Commission oversight
  No negotiations between cities necessary
  Funds go toward undergrounding projects

## Slide 86: Thank You!

## Slide 87: Q&A and Feedback from Attendees

## Slide 88: Break

## Slide 89: V. Equity Panel
The Utility Reform Network (TURN), California State Association of Counties (CSAC), Lake County Supervisors, & Public Advocates Office (Cal Advocates). Moderated by California League of Cities

## Slide 90: Panel Questions for Consideration
What are some solutions to enhancing coordination between local communities and utilities?
What changes could be implemented to the Annual Update requirement to increase equity in the Rule 20 Program?
How can we increase participation within Tribal communities for the Rule 20 Program?

## Slide 91: Q&A and Feedback from Attendees

## Slide 92: VI. Q&A and Feedback from Attendees

## Slide 93
https://www.cpuc.ca.gov/rule-20-workshops