## All Outage Details
| HFTD WIRE-DOWN OUTAGE DETAILS (2013 - Jun 2023) | [5 empty] | Source: Tom Hyunh's Team extracted from Outage Database on 7/6/2023.
DISTRIBUTION CIRCUIT & TRANSFORMER-ONLY OUTAGES
(2.5b ME Days Only)
http | ILIS Link | Division | Field Ops Center | Tier | Feeder Name | Feeder # | Device | Oper # | Date | FNL | OIS # | Duration | Outage Level | Basic Cause | Supplemental Cause | CESO | C Min | Open Point Latitude | Open Point Longitude | Fault Location | Weather | Failed/Involved Equipment | Equipment Condition | ILIS # | Const Type | Sus/Mom | PM # | Weather Day | Year | Month | Wire Down | Outage Fault Type | Misc | EquipTypeID | OH/UG | MEDay | Column1
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0022141&numberofmonths=24&showchangehistorylog=1 | 13-0022141 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | RECLOSER | B1101 | 20130408 | 302 | 768524 | 651 | Distribution Circuit | Equipment Failure/Involved | Other | 450 | 0 | 37.1248 | -122.125 | BRANDT28512122088BenlomondsubbrokenDE | Strong winds-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 13-0022141 | OH | Sus | 41877870 | yes | 2013 | APR | Yes |  | 99292344 | CSO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0022232&numberofmonths=24&showchangehistorylog=1 | 13-0022232 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 9181 | 20130408 | 218 | 768978 | 698 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 9772 | 37.2286 | -122.1483 | 2SPLSOF9181 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0022232 | OH | Sus | 41877941 | yes | 2013 | APR | Yes | Line to Ground | 99292299 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0022293&numberofmonths=24&showchangehistorylog=1 | 13-0022293 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 5465 | 20130408 | 503 | 769114 | 1137 | Distribution Circuit | Vegetation | Tree - branch fell on line | 55 | 53911 | 37.1393 | -122.1483 | 500BLOCKOFACORN | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0022293 | OH | Sus | 30988000 | yes | 2013 | APR | Yes |  | 99292246 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0022442&numberofmonths=24&showchangehistorylog=1 | 13-0022442 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 10025 | 20130408 | 428 | 769770 | 1122 | Distribution Circuit | Equipment Failure/Involved | Other | 36 | 40392 | 37.1401 | -122.1526 | CORNEROFACORNEBONY | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0022442 | OH | Sus | 0 | yes | 2013 | APR | Yes | Line to Ground | 99292128 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0022451&numberofmonths=24&showchangehistorylog=1 | 13-0022451 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 9741 | 20130408 | 620 | 768938 | 405 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 17010 | 37.1571 | -122.1288 | 900MEADOWLANE | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0022451 | OH | Sus | 0 | yes | 2013 | APR | Yes | Line to Ground | 99292119 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0022792&numberofmonths=24&showchangehistorylog=1 | 13-0022792 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | OTHER |  | 20130408 | 1628 | 771123 | 1135 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 4136 | 37.0302 | -122.0138 | 1480REDWOODDR | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0022792 | OH | Sus | 0 | yes | 2013 | APR | Yes | Line to Ground | 99291768 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0022445&numberofmonths=24&showchangehistorylog=1 | 13-0022445 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 2229 | 20130408 | 344 | 768597 | 1006 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 14084 | 37.0479 | -121.9943 | 825GRANITERIDGEDR | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0022445 | OH | Sus | 0 | yes | 2013 | APR | Yes | Line to Ground | 99292125 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0022528&numberofmonths=24&showchangehistorylog=1 | 13-0022528 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 1909 | 20130408 | 134 | 768275 | 926 | Distribution Circuit | Equipment Failure/Involved | Other | 5 | 4630 | 37.0981 | -121.9772 | 3SPLSOF1909 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 13-0022528 | OH | Sus | 0 | yes | 2013 | APR | Yes | Line to Ground | 99292071 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0022729&numberofmonths=24&showchangehistorylog=1 | 13-0022729 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE | 2835 | 20130408 | 1641 | 770758 | 47 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 3885 | 36.5861 | -121.875 | 1SPLSOF2775 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 13-0022729 | OH | Sus | 0 | yes | 2013 | APR | Yes | Line to Ground | 99291921 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0022766&numberofmonths=24&showchangehistorylog=1 | 13-0022766 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE | 2871 | 20130408 | 1652 | 770780 | 1356 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 4068 | 36.5705 | -121.8885 | 1SPLSOF2871 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0022766 | OH | Sus | 0 | yes | 2013 | APR | Yes | Line to Line | 99291772 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0022423&numberofmonths=24&showchangehistorylog=1 | 13-0022423 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | OTTER-1101 | 182941101 | FUSE | 1275 | 20130408 | 652 | 769007 | 450 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 4050 | 36.3992 | -121.8777 | 2spansLDsideof1275 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0022423 | OH | Sus | 0 | yes | 2013 | APR | Yes |  | 99292143 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0022130&numberofmonths=24&showchangehistorylog=1 | 13-0022130 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | RECLOSER | 10722 | 20130408 | 156 | 768329 | 941 | Distribution Circuit | Vegetation | Tree - branch fell on line | 798 | 371844 | 37.078 | -122.1331 | STORMENT284668218098540EmpireGradeRdSC | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0022130 | OH | Sus | 41877861 | yes | 2013 | APR | Yes | Line to Ground | 99292353 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0022550&numberofmonths=24&showchangehistorylog=1 | 13-0022550 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 7799 | 20130408 | 441 | 768950 | 1265 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 38703 | 37.0908 | -122.1397 | 468VICK | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0022550 | OH | Sus | 0 | yes | 2013 | APR | Yes | Line to Ground | 99292050 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0022672&numberofmonths=24&showchangehistorylog=1 | 13-0022672 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | OTHER |  | 20130408 | 850 | 769390 | 860 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 860 | 37.0594 | -122.139 | HardtapTWDTRANSFORMERMTR1009262114 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0022672 | OH | Sus | 0 | yes | 2013 | APR | Yes | Line to Ground | 99291963 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0022825&numberofmonths=24&showchangehistorylog=1 | 13-0022825 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | SEACLIFF-0401 | 83500401 | OTHER |  | 20130408 | 1951 | 771132 | 1089 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 7255 | 37.0021 | -121.9068 | 1682APTOSCREEKRD | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0022825 | OH | Sus | 0 | yes | 2013 | APR | Yes | Open Circuit | 99291761 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0041878&numberofmonths=24&showchangehistorylog=1 | 13-0041878 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5421 | 20130623 | 1650 | 815162 | 653 | Distribution Circuit | Equipment Failure/Involved | Other | 112 | 15520 | 37.1253 | -122.1278 | 365MADRONEDRBOULDERCREEK | Overcast-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0041878 | OH | Sus | 31004714 | yes | 2013 | JUN | Yes | Line to Line | 99278401 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0073443&numberofmonths=24&showchangehistorylog=1 | 14-0073443 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | OTHER |  | 20141203 | 758 | 1123048 | 1173 | Distribution Circuit | Vegetation | Tree - fell into line | 120 | 78210 | 37.0983 | -122.0858 | MTR1009615568 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073443 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99196575 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0073235&numberofmonths=24&showchangehistorylog=1 | 14-0073235 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE | 5183 | 20141203 | 808 | 1121957 | 696 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 15224 | 37.1078 | -122.1098 | 9SPLDSIDEOF5183 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073235 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99196934 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0073506&numberofmonths=24&showchangehistorylog=1 | 14-0073506 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE | 5439 | 20141203 | 1352 | 1123312 | 586 | Distribution Circuit | Vegetation | Tree - fell into line | 228 | 33987 | 37.1126 | -122.1142 | MTR1007591647 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073506 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99196749 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0073650&numberofmonths=24&showchangehistorylog=1 | 14-0073650 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE | 6215 | 20141203 | 939 | 1122157 | 1141 | Distribution Circuit | Vegetation | Tree - branch fell on line | 31 | 35371 | 37.1128 | -122.1156 | 12182ALTAVIA | Heavy rain-32 - 90 F | Conductor, Overhead | On Ground | 14-0073650 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99196644 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0073666&numberofmonths=24&showchangehistorylog=1 | 14-0073666 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE | 9307 | 20141203 | 2144 | 1123979 | 626 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 2504 | 37.1165 | -122.1142 | 1POLELOADSIDEOF9307 | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073666 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99196550 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0073302&numberofmonths=24&showchangehistorylog=1 | 14-0073302 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | RECLOSER | 10296 | 20141203 | 1031 | 1122359 | 793 | Distribution Circuit | Vegetation | Tree - fell into line | 629 | 360852 | 37.1332 | -122.1258 | HWY9SEQUOIARD | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073302 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99196886 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0073586&numberofmonths=24&showchangehistorylog=1 | 14-0073586 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5485 | 20141203 | 1047 | 1122408 | 1050 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 34650 | 37.1322 | -122.109 | MTR1007590393 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073586 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Multi-Fault | 99196685 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0073596&numberofmonths=24&showchangehistorylog=1 | 14-0073596 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5487 | 20141203 | 1024 | 1122372 | 991 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 54505 | 37.1375 | -122.1006 | 1POLEWEST781615 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073596 | OH | Sus | 0 | yes | 2014 | DEC | Yes |  | 99196677 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0073610&numberofmonths=24&showchangehistorylog=1 | 14-0073610 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 7219 | 20141203 | 1706 | 1123757 | 1040 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 4478 | 37.1413 | -122.091 | 1STTAPFEEDINGNORTHMTR1007590875 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073610 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99196564 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0073622&numberofmonths=24&showchangehistorylog=1 | 14-0073622 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 12069 | 20141203 | 1115 | 1122605 | 945 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 31185 | 37.1239 | -122.1195 | MTR1007592564 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073622 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Three Phase Fault | 99196662 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0073126&numberofmonths=24&showchangehistorylog=1 | 14-0073126 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 9763 | 20141203 | 134 | 1121585 | 436 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 6540 | 37.1766 | -122.1625 | 640MEMORYLANE | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073126 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99197012 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0073169&numberofmonths=24&showchangehistorylog=1 | 14-0073169 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 4259 | 20141203 | 204 | 1121602 | 1240 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 7440 | 37.167 | -122.1874 | 1SPLSOF20141BIGBASINWAY | Heavy rain-32 - 90 F | Conductor, Overhead | On Ground | 14-0073169 | OH | Sus | 0 | yes | 2014 | DEC | Yes |  | 99196982 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0073551&numberofmonths=24&showchangehistorylog=1 | 14-0073551 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | OTHER |  | 20141203 | 1029 | 1122328 | 735 | Distribution Circuit | Vegetation | Tree - branch fell on line | 94 | 64075 | 37.172 | -122.1779 | MTR1007591511 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073551 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Open Circuit | 99196714 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0073692&numberofmonths=24&showchangehistorylog=1 | 14-0073692 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | OTHER |  | 20141203 | 1202 | 1122943 | 1258 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1258 | 37.1596 | -122.1734 | 2SP22OF1440BLOOMGRADEROAD | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073692 | OH | Sus | 0 | yes | 2014 | DEC | Yes |  | 99196532 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0073393&numberofmonths=24&showchangehistorylog=1 | 14-0073393 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG TREES-0402 | 83050402 | FUSE | 11965 | 20141203 | 708 | 1121833 | 1102 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 8816 | 37.0305 | -122.0807 | 1740FERRARIDR | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073393 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99196579 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0073228&numberofmonths=24&showchangehistorylog=1 | 14-0073228 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 5335 | 20141203 | 630 | 1121772 | 761 | Distribution Circuit | Vegetation | Tree - branch fell on line | 74 | 56314 | 37.0281 | -121.9871 | 2SPLDSIDEOF4517 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073228 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99196940 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0073187&numberofmonths=24&showchangehistorylog=1 | 14-0073187 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER | 10786 | 20141203 | 728 | 1121846 | 1361 | Distribution Circuit | Vegetation | Tree - fell into line | 124 | 97551 | 37.0925 | -122.0969 | SSOF7101SB | Heavy rain-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0073187 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99196583 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0073441&numberofmonths=24&showchangehistorylog=1 | 14-0073441 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | CAMP EVERS-2105 | 83622105 | FUSE | 5239 | 20141203 | 1155 | 1122911 | 680 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 27880 | 37.0683 | -122.0826 | MTR1007590393 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073441 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99196799 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0073570&numberofmonths=24&showchangehistorylog=1 | 14-0073570 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 9071 | 20141203 | 1055 | 1122594 | 996 | Distribution Circuit | Vegetation | Tree - branch fell on line | 122 | 121512 | 37.0596 | -122.0589 | 1POLENOF7193 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073570 | OH | Sus | 42283952 | yes | 2014 | DEC | Yes | Line to Line | 99196568 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0073639&numberofmonths=24&showchangehistorylog=1 | 14-0073639 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 10717 | 20141203 | 852 | 1122321 | 1973 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 45815 | 37.0912 | -122.1047 | UNKNOWNLOCATION | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073639 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99196558 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0073680&numberofmonths=24&showchangehistorylog=1 | 14-0073680 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 9701 | 20141203 | 2322 | 1124051 | 536 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 536 | 37.0965 | -122.1267 | 3PLSOF9701 | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073680 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99196540 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0073131&numberofmonths=24&showchangehistorylog=1 | 14-0073131 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER | 37210 | 20141203 | 141 | 1121592 | 679 | Distribution Circuit | Vegetation | Tree - branch fell on line | 141 | 57808 | 37.0808 | -122.0045 | WIREDOWN1SPSSOF6037ONMAINLINE | Rain-32 - 90 F | Conductor, Overhead | On Ground | 14-0073131 | OH | Sus | 0 | yes | 2014 | DEC | Yes |  | 99197011 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0073258&numberofmonths=24&showchangehistorylog=1 | 14-0073258 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 2821 | 20141203 | 700 | 1121807 | 907 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2721 | 37.0599 | -121.9816 | 445VINEHILLRD | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073258 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99196914 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0073593&numberofmonths=24&showchangehistorylog=1 | 14-0073593 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 12055 | 20141203 | 1156 | 1122918 | 939 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 4695 | 37.0943 | -122.0048 | 3SPLOADSIDEOF12055 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073593 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99196679 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0073661&numberofmonths=24&showchangehistorylog=1 | 14-0073661 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 8961 | 20141203 | 2353 | 1124060 | 362 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 724 | 37.043 | -122.0513 | 2SPFROMEOL | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073661 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99196554 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0073476&numberofmonths=24&showchangehistorylog=1 | 14-0073476 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | PACIFIC GROVE-0422 | 182440422 | SWITCH | 99040 | 20141203 | 1428 | 1123261 | 682 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 402 | 10854 | 36.6003 | -121.938 | ONTAPFEEDINGMTR1008349010 | Drizzle-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0073476 | OH | Sus | 0 | yes | 2014 | DEC | Yes |  | 99196770 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0073642&numberofmonths=24&showchangehistorylog=1 | 14-0073642 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2104 | 83252104 | OTHER |  | 20141203 | 1906 | 1123961 | 634 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 5072 | 37.0385 | -121.9664 | CRIVELLO417683168219124100NRODEOGULCHRD | Fog-32 - 90 F | Conductor, Overhead | On Ground | 14-0073642 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99196649 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0073514&numberofmonths=24&showchangehistorylog=1 | 14-0073514 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 5401 | 20141203 | 841 | 1123613 | 849 | Distribution Circuit | Vegetation | Tree - branch fell on line | 70 | 39732 | 37.0647 | -122.1232 | 1PHASEDOWNLDSIDEOF11737 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073514 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Open Circuit | 99196743 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0073517&numberofmonths=24&showchangehistorylog=1 | 14-0073517 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 8359 | 20141203 | 728 | 1122195 | 752 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 11280 | 37.0778 | -122.1333 | 4SPANSLDSIDEOF8359 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073517 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99196573 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0073601&numberofmonths=24&showchangehistorylog=1 | 14-0073601 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 7371 | 20141203 | 1229 | 1123053 | 931 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 4655 | 37.0585 | -122.1419 | 4SPLOADSIDEOFMETER1009262114 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 14-0073601 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99196674 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0073618&numberofmonths=24&showchangehistorylog=1 | 14-0073618 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 9005 | 20141203 | 1353 | 1123315 | 913 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 19173 | 37.0322 | -122.137 | 8SPLS9005 | Heavy rain-32 - 90 F | Conductor, Overhead | On Ground | 14-0073618 | OH | Sus | 0 | yes | 2014 | DEC | Yes |  | 99196664 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0073151&numberofmonths=24&showchangehistorylog=1 | 14-0073151 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | RECLOSER | 9698 | 20141203 | 514 | 1121721 | 796 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 17469 | 36.5725 | -121.9435 | GALLEGOS17MileDrAlvaradoLn | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073151 | OH | Sus | 31117940 | yes | 2014 | DEC | Yes | Line to Ground | 99196998 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0073390&numberofmonths=24&showchangehistorylog=1 | 14-0073390 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 40285 | 20141203 | 1058 | 1122509 | 392 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 17248 | 36.5853 | -121.921 | 1SPANLDSIDEOF40285 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073390 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99196831 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075254&numberofmonths=24&showchangehistorylog=1 | 14-0075254 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | RECLOSER | 16010 | 20141211 | 921 | 1132222 | 1016 | Distribution Circuit | Vegetation | Tree - fell into line | 138 | 140208 | 37.0886 | -122.0872 | 299riversidedrbenlomond | Heavy rain-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 14-0075254 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99195022 | CAW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076289&numberofmonths=24&showchangehistorylog=1 | 14-0076289 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE | 5143 | 20141211 | 948 | 1132445 | 2592 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 67392 | 37.0994 | -122.0868 | 5POLENOF5143 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076289 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Multi-Fault | 99194030 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075698&numberofmonths=24&showchangehistorylog=1 | 14-0075698 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE | 9309 | 20141211 | 1035 | 1133007 | 2453 | Distribution Circuit | Vegetation | Tree - fell into line | 137 | 209809 | 37.1186 | -122.1154 | 2SPLDSIDEOFMTR1007590350 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075698 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99193556 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076333&numberofmonths=24&showchangehistorylog=1 | 14-0076333 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE | 7279 | 20141211 | 923 | 1132204 | 2997 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 17982 | 37.0995 | -122.101 | 415PIKERD | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076333 | OH | Sus | 0 | yes | 2014 | DEC | Yes |  | 99193485 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076034&numberofmonths=24&showchangehistorylog=1 | 14-0076034 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5485 | 20141211 | 1352 | 1134064 | 743 | Distribution Circuit | Vegetation | Tree - branch fell on line | 33 | 24519 | 37.1322 | -122.109 | 298LOVERSLANE | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076034 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194491 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076059&numberofmonths=24&showchangehistorylog=1 | 14-0076059 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5487 | 20141211 | 1259 | 1133756 | 1271 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 69905 | 37.1375 | -122.1006 | 895HOPKINSGULCH | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0076059 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99194190 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076118&numberofmonths=24&showchangehistorylog=1 | 14-0076118 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | OTHER |  | 20141211 | 1417 | 1136990 | 1761 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 7044 | 37.1534 | -122.1421 | 540SUNSET | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076118 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Open Circuit | 99194165 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075017&numberofmonths=24&showchangehistorylog=1 | 14-0075017 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER | 5066 | 20141211 | 654 | 1130234 | 813 | Distribution Circuit | Equipment Failure/Involved | Other | 108 | 78098 | 37.1705 | -122.1654 | 6SPANSLOADSIDE12383 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 14-0075017 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99195206 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075065&numberofmonths=24&showchangehistorylog=1 | 14-0075065 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 12779 | 20141211 | 540 | 1129530 | 740 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 11840 | 37.1598 | -122.1554 | 656KINGSHWY | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075065 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99195172 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075256&numberofmonths=24&showchangehistorylog=1 | 14-0075256 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG TREES-0402 | 83050402 | RECLOSER | 5300 | 20141211 | 940 | 1132406 | 935 | Distribution Circuit | Vegetation | Tree - branch fell on line | 347 | 235865 | 37.0382 | -122.0705 | MAINLINEATCOUTS7293 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075256 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99193212 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075829&numberofmonths=24&showchangehistorylog=1 | 14-0075829 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG TREES-0402 | 83050402 | FUSE | 5219 | 20141211 | 852 | 1135792 | 849 | Distribution Circuit | Equipment Failure/Involved | Other | 21 | 17829 | 37.037 | -122.0657 | LOADSIDE1SPANFROM5219 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 14-0075829 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194616 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075833&numberofmonths=24&showchangehistorylog=1 | 14-0075833 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG TREES-0402 | 83050402 | FUSE | 12887 | 20141211 | 817 | 1131784 | 735 | Distribution Circuit | Vegetation | Tree - fell into line | 124 | 89661 | 37.0384 | -122.0679 | PAST5219 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075833 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Multi-Fault | 99194614 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075973&numberofmonths=24&showchangehistorylog=1 | 14-0075973 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG TREES-0402 | 83050402 | FUSE | 5217 | 20141211 | 2044 | 1135994 | 151 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 2265 | 37.0371 | -122.0662 | 1SPANLOADSIDE5217 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075973 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99194520 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075683&numberofmonths=24&showchangehistorylog=1 | 14-0075683 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 6103 | 20141211 | 903 | 1131963 | 2085 | Distribution Circuit | Equipment Failure/Involved | Other | 54 | 112590 | 37.0116 | -122.012 | 2SPANSLOADSIDE6103 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075683 | OH | Sus | 0 | yes | 2014 | DEC | Yes | None | 99193557 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076002&numberofmonths=24&showchangehistorylog=1 | 14-0076002 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | RECLOSER | 11056 | 20141211 | 2328 | 1136631 | 905 | Distribution Circuit | Vegetation | Tree - fell into line | 452 | 409060 | 36.9938 | -122.0298 | MULITABLELOCATIONS | Rain-32 - 90 F | Conductor, Overhead | On Ground | 14-0076002 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99193531 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076600&numberofmonths=24&showchangehistorylog=1 | 14-0076600 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 9499 | 20141211 | 1115 | 1139312 | 2730 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 5460 | 37.0275 | -122.0241 | 400LOADSIDEOF9499 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076600 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99193439 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075401&numberofmonths=24&showchangehistorylog=1 | 14-0075401 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 6085 | 20141211 | 907 | 1133339 | 2020 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 20200 | 37.0637 | -122.0347 | RYDERLOCKHARTGULCH | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075401 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194353 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075409&numberofmonths=24&showchangehistorylog=1 | 14-0075409 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2104 | 83622104 | OTHER |  | 20141211 | 853 | 1133361 | 1749 | Distribution Circuit | Vegetation | Tree - fell into line | 514 | 188980 | 37.0663 | -122.0335 | SSOF6087 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075409 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99192465 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076015&numberofmonths=24&showchangehistorylog=1 | 14-0076015 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 11929 | 20141211 | 2132 | 1136251 | 1636 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 81800 | 37.1003 | -122.0345 | 1SPLDSIDEOFFUCO11929 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076015 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99193528 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076307&numberofmonths=24&showchangehistorylog=1 | 14-0076307 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 8883 | 20141211 | 954 | 1132524 | 2003 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 34336 | 37.0833 | -122.0958 | 1SPLDSIDEOF1007586455 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076307 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194019 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076559&numberofmonths=24&showchangehistorylog=1 | 14-0076559 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 9435 | 20141211 | 1734 | 1135169 | 1845 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 25830 | 37.074 | -122.0803 | LOADSIDE | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076559 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99193840 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075138&numberofmonths=24&showchangehistorylog=1 | 14-0075138 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | CAMP EVERS-2106 | 83622106 | RECLOSER | 5302 | 20141211 | 816 | 1131504 | 737 | Distribution Circuit | Vegetation | Tree - fell into line | 442 | 192760 | 37.0438 | -122.0755 | 14SPANSSOURCESIDEOF10718 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075138 | OH | Sus | 0 | yes | 2014 | DEC | Yes |  | 99192869 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075286&numberofmonths=24&showchangehistorylog=1 | 14-0075286 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE | 7683 | 20141211 | 836 | 1131681 | 334 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 5344 | 36.5828 | -121.8644 | EOL | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075286 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194995 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075642&numberofmonths=24&showchangehistorylog=1 | 14-0075642 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE | 8553 | 20141211 | 1316 | 1133871 | 2332 | Distribution Circuit | Equipment Failure/Involved | Other | 7 | 16324 | 36.5682 | -121.8964 | 3SPOFWIREDOWNSTARTINGATFUCO8553 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075642 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99193561 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075926&numberofmonths=24&showchangehistorylog=1 | 14-0075926 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HATTON-1102 | 182291102 | FUSE | 8047 | 20141211 | 916 | 1135461 | 2354 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 21114 | 36.5027 | -121.9336 | 4SPANSLOADSIDEOF8047ONSINGLEPHASE | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075926 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99193538 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076240&numberofmonths=24&showchangehistorylog=1 | 14-0076240 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | LAURELES-1111 | 182371111 | FUSE | 8407 | 20141211 | 721 | 1130936 | 3484 | Distribution Circuit | Equipment Failure/Involved | Other | 8 | 27872 | 36.4209 | -121.7378 | MTR1008577856 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076240 | OH | Sus | 0 | yes | 2014 | DEC | Yes |  | 99193500 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075102&numberofmonths=24&showchangehistorylog=1 | 14-0075102 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | LOMPICO-0401 | 88880401 | RECLOSER | 11010 | 20141211 | 802 | 1131296 | 1100 | Distribution Circuit | Equipment Failure/Involved | Other | 106 | 113123 | 37.1052 | -122.0517 | UNKNOWN | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 14-0075102 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Multi-Fault | 99193581 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076115&numberofmonths=24&showchangehistorylog=1 | 14-0076115 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | LOMPICO-0401 | 88880401 | FUSE | 5629 | 20141211 | 959 | 1132325 | 1925 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 38500 | 37.1129 | -122.0479 | MTR1009701742 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076115 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194167 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075102&numberofmonths=24&showchangehistorylog=1 | 14-0075102 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | LOMPICO-0401 | 88880401 | FUSE | BXD7 | 20141211 | 802 | 1136351 | 2016 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2016 | 37.1078 | -122.0578 | 1SPSSOFMTR1006210966 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075102 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194162 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075424&numberofmonths=24&showchangehistorylog=1 | 14-0075424 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | OTTER-1101 | 182941101 | FUSE | 8833 | 20141211 | 838 | 1131698 | 2363 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 7089 | 36.3824 | -121.8638 | 2SPANSLDSIDEOF8833 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075424 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Multi-Fault | 99194349 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075812&numberofmonths=24&showchangehistorylog=1 | 14-0075812 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1101 | 182941101 | FUSE | 2181 | 20141211 | 917 | 1132240 | 1717 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 112429 | 36.4893 | -121.9362 | MTR1008580352 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075812 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194266 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075208&numberofmonths=24&showchangehistorylog=1 | 14-0075208 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | PACIFIC GROVE-0422 | 182440422 | FUSE | 2581 | 20141211 | 811 | 1131962 | 1310 | Distribution Circuit | Vegetation | Tree - fell into line | 98 | 36586 | 36.5917 | -121.9453 | RodriguezLou580923303612spansloadside2217 | Partly cloudy-32 - 90 F | Conductor, Overhead | On Ground | 14-0075208 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194369 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0074992&numberofmonths=24&showchangehistorylog=1 | 14-0074992 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | RECLOSER | 36516 | 20141211 | 642 | 1129620 | 1063 | Distribution Circuit | Vegetation | Tree - branch fell on line | 883 | 322996 | 37.0786 | -122.1335 | BET107715200310349EMPIREGRADE | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074992 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99193583 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075060&numberofmonths=24&showchangehistorylog=1 | 14-0075060 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | POINT MORETTI-1101 | 82931101 | RECLOSER | 83716 | 20141211 | 659 | 1130272 | 2059 | Distribution Circuit | Equipment Failure/Involved | Other | 30 | 54203 | 37.0863 | -122.2602 | SALESCHRISTOPHER3spansloadsideof8033 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075060 | OH | Sus | 0 | yes | 2014 | DEC | Yes |  | 99192870 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075619&numberofmonths=24&showchangehistorylog=1 | 14-0075619 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 7371 | 20141211 | 702 | 1134590 | 1628 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 8140 | 37.0585 | -122.1419 | WinterCreekIcecreamGrade | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075619 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194317 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075772&numberofmonths=24&showchangehistorylog=1 | 14-0075772 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 8515 | 20141211 | 1227 | 1133578 | 1106 | Distribution Circuit | Vegetation | Tree - fell into line | 103 | 92438 | 37.0482 | -122.1606 | 200THAYERRD | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075772 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194283 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075834&numberofmonths=24&showchangehistorylog=1 | 14-0075834 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 2979 | 20141211 | 1412 | 1135808 | 1068 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 4272 | 37.0366 | -122.1466 | 1SPLOADSIDEOF2979 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075834 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99194259 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076138&numberofmonths=24&showchangehistorylog=1 | 14-0076138 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 5401 | 20141211 | 1814 | 1135597 | 1088 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 76160 | 37.0647 | -122.1232 | BOYNTON345983133166201SPANSOURCESIDECO11739 | Heavy rain-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0076138 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99193511 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075650&numberofmonths=24&showchangehistorylog=1 | 14-0075650 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | FUSE | 1957 | 20141211 | 1407 | 1134196 | 1423 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 5692 | 36.9695 | -121.8174 | LOADSIDE1957 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075650 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194310 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075916&numberofmonths=24&showchangehistorylog=1 | 14-0075916 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | FUSE | 2199 | 20141211 | 2031 | 1135947 | 1100 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 31900 | 36.9517 | -121.8337 | 6SPLDSIDEOF2199 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075916 | OH | Sus | 0 | yes | 2014 | DEC | Yes |  | 99194240 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075594&numberofmonths=24&showchangehistorylog=1 | 14-0075594 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 11835 | 20141211 | 1255 | 1133738 | 883 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 10864 | 36.9832 | -121.8841 | MTR500003818 | Heavy rain-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0075594 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194323 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075054&numberofmonths=24&showchangehistorylog=1 | 14-0075054 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | RECLOSER | 9698 | 20141211 | 730 | 1130893 | 3418 | Distribution Circuit | Vegetation | Tree - branch fell on line | 39 | 32886 | 36.5725 | -121.9435 | GALLEGOSRiataRdVenadero | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075054 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99193582 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075329&numberofmonths=24&showchangehistorylog=1 | 14-0075329 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | RECLOSER | 9114 | 20141211 | 1005 | 1132798 | 2934 | Distribution Circuit | Vegetation | Tree - fell into line | 866 | 342914 | 36.5784 | -121.9279 | 9704 | Overcast-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0075329 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Multi-Fault | 99193570 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075820&numberofmonths=24&showchangehistorylog=1 | 14-0075820 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 7873 | 20141211 | 1242 | 1133648 | 3196 | Distribution Circuit | Vegetation | Tree - branch fell on line | 30 | 43320 | 36.5772 | -121.9451 | MTR1008579889 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075820 | OH | Sus | 31120494 | yes | 2014 | DEC | Yes | Line to Ground | 99193546 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076664&numberofmonths=24&showchangehistorylog=1 | 14-0076664 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 7879 | 20141211 | 1219 | 1133503 | 2860 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 42900 | 36.5783 | -121.9442 | LSOF7879 | Rain-32 - 90 F | Conductor, Overhead | On Ground | 14-0076664 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99193413 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075194&numberofmonths=24&showchangehistorylog=1 | 14-0075194 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2202 | 182852202 | RECLOSER | 92792 | 20141211 | 751 | 1131212 | 2272 | Distribution Circuit | Vegetation | Tree - fell into line | 141 | 320352 | 36.5898 | -121.9457 | STEVENSONSLOAT | Drizzle-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0075194 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99193577 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075217&numberofmonths=24&showchangehistorylog=1 | 14-0075217 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2202 | 182852202 | RECLOSER | 9118 | 20141211 | 900 | 1131664 | 1083 | Distribution Circuit | Vegetation | Tree - fell into line | 617 | 188759 | 36.6036 | -121.9357 | 2SPANSSSOF8267 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075217 | OH | Sus | 0 | yes | 2014 | DEC | Yes |  | 99193575 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075309&numberofmonths=24&showchangehistorylog=1 | 14-0075309 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2202 | 182852202 | RECLOSER | 9488 | 20141211 | 1004 | 1132789 | 3193 | Distribution Circuit | Vegetation | Tree - fell into line | 223 | 225105 | 36.5902 | -121.9442 | CORIMARKrlstevensonschool | Drizzle-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0075309 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99193572 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076380&numberofmonths=24&showchangehistorylog=1 | 14-0076380 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2203 | 182852203 | FUSE | 7537 | 20141211 | 837 | 1131693 | 1873 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 9365 | 36.5718 | -121.9053 | LDSIDEOF7537 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076380 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99193967 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076474&numberofmonths=24&showchangehistorylog=1 | 14-0076474 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE | 9125 | 20141212 | 631 | 1137634 | 599 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 25158 | 37.1006 | -122.086 | 12MILDSIDEOFFUCO9125 | Strong winds-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 14-0076474 | OH | Sus | 0 | yes | 2014 | DEC | Yes |  | 99193898 | CAW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076347&numberofmonths=24&showchangehistorylog=1 | 14-0076347 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG TREES-0402 | 83050402 | FUSE | 7299 | 20141212 | 648 | 1137234 | 647 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 7764 | 37.0308 | -122.0937 | 2PNORTHOF3PHASEONSINGLEPHASE | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076347 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99193986 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076227&numberofmonths=24&showchangehistorylog=1 | 14-0076227 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 10717 | 20141212 | 448 | 1137063 | 552 | Distribution Circuit | Equipment Failure/Involved | Other | 25 | 13800 | 37.0912 | -122.1047 | SOF10717 | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076227 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194078 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076035&numberofmonths=24&showchangehistorylog=1 | 14-0076035 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER | 5020 | 20141212 | 43 | 1136771 | 1262 | Distribution Circuit | Vegetation | Tree - fell into line | 1183 | 307760 | 37.1024 | -121.9845 | 8SPANSNOF1895 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076035 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99189468 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076649&numberofmonths=24&showchangehistorylog=1 | 14-0076649 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 8329 | 20141212 | 816 | 1137521 | 2002 | Distribution Circuit | Equipment Failure/Involved | Other | 7 | 14014 | 37.0575 | -121.9746 | 4205VINEHILL | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076649 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99193419 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076392&numberofmonths=24&showchangehistorylog=1 | 14-0076392 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | GREEN VALLEY-2101 | 83192101 | FUSE | 921 | 20141212 | 1326 | 1138416 | 1329 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2658 | 36.8837 | -121.6205 | 1800COLERD | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076392 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99193473 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076389&numberofmonths=24&showchangehistorylog=1 | 14-0076389 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 12129 | 20141212 | 1038 | 1138006 | 782 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 782 | 37.0848 | -122.1418 | 2SPLDSIDEOFFUCO12129 | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076389 | OH | Sus | 0 | yes | 2014 | DEC | Yes |  | 99193959 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076574&numberofmonths=24&showchangehistorylog=1 | 14-0076574 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | OTHER |  | 20141212 | 1423 | 1139224 | 1302 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1302 | 37.0717 | -122.1344 | 795SUNLITLN | Fog-32 - 90 F | Conductor, Underground | Broken, wire on ground | 14-0076574 | OH | Sus | 0 | yes | 2014 | DEC | Yes | None | 99193443 | CU | UG | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076271&numberofmonths=24&showchangehistorylog=1 | 14-0076271 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | RECLOSER | 10960 | 20141212 | 951 | 1137851 | 293 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2378 | 424771 | 36.9866 | -121.8582 | MAINLINEFUCO9569 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076271 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99193493 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076314&numberofmonths=24&showchangehistorylog=1 | 14-0076314 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 40285 | 20141212 | 140 | 1138068 | 1310 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 39760 | 36.5853 | -121.921 | MTR1008066381 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076314 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Multi-Fault | 99194013 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076571&numberofmonths=24&showchangehistorylog=1 | 14-0076571 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2203 | 182852203 | FUSE | 7537 | 20141212 | 1643 | 1138907 | 582 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 1956 | 36.5718 | -121.9053 | 1SPANLDSIDEOF7537NORTHTAP | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076571 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99193833 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079660&numberofmonths=24&showchangehistorylog=1 | 14-0079660 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE | 9125 | 20141230 | 2045 | 1156256 | 1245 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 52290 | 37.1006 | -122.086 | 5POLESLOADSIDEOF9125 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079660 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99190050 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079594&numberofmonths=24&showchangehistorylog=1 | 14-0079594 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5501 | 20141230 | 2013 | 1155425 | 1588 | Distribution Circuit | Vegetation | Tree - fell into line | 141 | 192492 | 37.1431 | -122.1317 | MULTIPLELOCATIONS | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079594 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Multi-Fault | 99190091 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079613&numberofmonths=24&showchangehistorylog=1 | 14-0079613 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | OTHER |  | 20141230 | 2216 | 1155999 | 1404 | Distribution Circuit | Vegetation | Tree - branch fell on line | 279 | 81266 | 37.1588 | -122.0815 | 17220BearCreekRdBC | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079613 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99190082 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079773&numberofmonths=24&showchangehistorylog=1 | 14-0079773 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 8471 | 20141230 | 2216 | 1157480 | 1454 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 8724 | 37.1595 | -122.0822 | 1123PILGER | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079773 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99189697 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079775&numberofmonths=24&showchangehistorylog=1 | 14-0079775 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5435 | 20141230 | 2118 | 1155651 | 1327 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 9289 | 37.1175 | -122.1213 | 2POLESLOADSIDEOF5435 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on object | 14-0079775 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99189944 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079669&numberofmonths=24&showchangehistorylog=1 | 14-0079669 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 8403 | 20141230 | 2011 | 1155514 | 1594 | Distribution Circuit | Vegetation | Tree - fell into line | 141 | 138379 | 37.1549 | -122.1332 | JUSTLOADSIDEOF9741 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079669 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99190040 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079385&numberofmonths=24&showchangehistorylog=1 | 14-0079385 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG TREES-0402 | 83050402 | FUSE | 7295 | 20141230 | 1544 | 1153547 | 1546 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 37227 | 37.0326 | -122.0879 | 1640MCCLELLAN | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079385 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99190150 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079516&numberofmonths=24&showchangehistorylog=1 | 14-0079516 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG TREES-0402 | 83050402 | FUSE | 12887 | 20141230 | 1926 | 1155809 | 2123 | Distribution Circuit | Vegetation | Tree - fell into line | 108 | 197757 | 37.0384 | -122.0679 | 5SPANSLDOF12887 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079516 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99189720 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079565&numberofmonths=24&showchangehistorylog=1 | 14-0079565 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG TREES-0402 | 83050402 | FUSE | 7301 | 20141230 | 1831 | 1155994 | 795 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 13515 | 37.0328 | -122.0745 | 845RedwoodRdFelton | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079565 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99190104 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079726&numberofmonths=24&showchangehistorylog=1 | 14-0079726 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG TREES-0402 | 83050402 | FUSE | 3233 | 20141230 | 2036 | 1157188 | 1714 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 63418 | 37.0325 | -122.0627 | 251STEINMEYER | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079726 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99189703 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079212&numberofmonths=24&showchangehistorylog=1 | 14-0079212 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 6103 | 20141230 | 1214 | 1151785 | 1786 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 13234 | 37.0116 | -122.012 | MTR1009257465 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079212 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99190184 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079593&numberofmonths=24&showchangehistorylog=1 | 14-0079593 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 5335 | 20141230 | 1916 | 1155163 | 875 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 64750 | 37.0281 | -121.9871 | 2SPANSSSOF517 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079593 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99190092 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079560&numberofmonths=24&showchangehistorylog=1 | 14-0079560 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 9247 | 20141230 | 1832 | 1154816 | 1933 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 71521 | 37.0897 | -122.0446 | 2SPSSOFCGC315495021810 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079560 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99189715 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079598&numberofmonths=24&showchangehistorylog=1 | 14-0079598 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 7959 | 20141230 | 2011 | 1155388 | 2197 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 39546 | 37.0696 | -122.0915 | 1236SOLYOHEIGHTSDRMTR1007042732 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079598 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99189714 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079607&numberofmonths=24&showchangehistorylog=1 | 14-0079607 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 1427 | 20141230 | 2001 | 1154731 | 1820 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 101920 | 37.0823 | -122.0914 | 646MOUNTAINVIEW | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079607 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99190086 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079736&numberofmonths=24&showchangehistorylog=1 | 14-0079736 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 9033 | 20141230 | 1856 | 1157284 | 1804 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 41168 | 37.0721 | -122.0754 | MULTIPLELOCATIONSLSOFMTR1009700733 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079736 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99189702 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079465&numberofmonths=24&showchangehistorylog=1 | 14-0079465 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER | 10718 | 20141230 | 2019 | 1155441 | 596 | Distribution Circuit | Vegetation | Tree - fell into line | 230 | 104984 | 37.0358 | -122.1063 | TXR315294320364 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079465 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99190132 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079779&numberofmonths=24&showchangehistorylog=1 | 14-0079779 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 1633 | 20141230 | 2206 | 1155751 | 1430 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 12870 | 37.0362 | -122.0837 | 1SPLSOF1633 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079779 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99189694 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079403&numberofmonths=24&showchangehistorylog=1 | 14-0079403 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 11737 | 20141230 | 1342 | 1152371 | 1984 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 15936 | 37.0697 | -122.1302 | MTR1008411636 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079403 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99190146 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0002021&numberofmonths=24&showchangehistorylog=1 | 14-0002021 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | FUSE | 1939 | 20141230 | 2057 | 1155593 | 1895 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 11370 | 36.9839 | -121.8311 | 4675FREEDOMBLVD | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0002021 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99189915 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0009860&numberofmonths=24&showchangehistorylog=1 | 15-0009860 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER | 10728 | 20150206 | 753 | 1173502 | 621 | Distribution Circuit | Vegetation | Tree - fell into line | 3019 | 259134 | 37.0665 | -122.0796 | LSSSOFSCADASW11081 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0009860 | OH | Sus | 31132982 | yes | 2015 | FEB | Yes | Line to Line | 99185312 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010646&numberofmonths=24&showchangehistorylog=1 | 15-0010646 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HATTON-1102 | 182291102 | FUSE | 1491 | 20150206 | 1621 | 1176829 | 548 | Distribution Circuit | Vegetation | Tree - branch fell on line | 40 | 14621 | 36.5056 | -121.9351 | 1SPLSOF1491 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010646 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99184839 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0009879&numberofmonths=24&showchangehistorylog=1 | 15-0009879 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | LAURELES-1111 | 182371111 | FUSE | 6625 | 20150206 | 218 | 1173086 | 672 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 10080 | 36.3757 | -121.5911 | KINCANNONRDCARMEL | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0009879 | OH | Sus | 42329112 | yes | 2015 | FEB | Yes | Line to Line | 99185299 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011372&numberofmonths=24&showchangehistorylog=1 | 15-0011372 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | LOMPICO-0401 | 88880401 | FUSE | 10457 | 20150206 | 1730 | 1176990 | 1610 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 25760 | 37.1086 | -122.0457 | 10457 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011372 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99184243 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010398&numberofmonths=24&showchangehistorylog=1 | 15-0010398 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1101 | 182941101 | RECLOSER | 440 | 20150206 | 1510 | 1176124 | 694 | Distribution Circuit | Vegetation | Tree - fell into line | 368 | 79208 | 36.4379 | -121.9196 | 2SPSSOF40411 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 15-0010398 | OH | Sus | 31132865 | yes | 2015 | FEB | Yes | Line to Line | 99184991 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010872&numberofmonths=24&showchangehistorylog=1 | 15-0010872 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 3459 | 20150206 | 2123 | 1178684 | 1275 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 67575 | 37.0246 | -121.8835 | 2SPWO12677 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010872 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99184522 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011297&numberofmonths=24&showchangehistorylog=1 | 15-0011297 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 11305 | 20150207 | 1549 | 1181473 | 569 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 7397 | 37.0301 | -121.7861 | MTR5000038053 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011297 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99184281 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011056&numberofmonths=24&showchangehistorylog=1 | 15-0011056 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 2453 | 20150207 | 653 | 1180209 | 387 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 2283 | 36.5723 | -121.9397 | MTR1008580646 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011056 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99184429 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011130&numberofmonths=24&showchangehistorylog=1 | 15-0011130 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 6185 | 20150207 | 652 | 1180206 | 432 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2160 | 36.5688 | -121.9288 | 2SPLSOF9185 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011130 | OH | Sus | 0 | yes | 2015 | FEB | Yes | None | 99184385 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011779&numberofmonths=24&showchangehistorylog=1 | 15-0011779 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5421 | 20150208 | 1741 | 1183927 | 679 | Distribution Circuit | Vegetation | Tree - fell into line | 114 | 41006 | 37.1253 | -122.1278 | MTR1007592899 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011779 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183580 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011919&numberofmonths=24&showchangehistorylog=1 | 15-0011919 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | BIG BASIN-1102 | 82841102 | FUSE | 11817 | 20150208 | 1751 | 1185409 | 1918 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 13963 | 37.1701 | -122.2198 | MTR009128531 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011919 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182802 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011654&numberofmonths=24&showchangehistorylog=1 | 15-0011654 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | OTHER |  | 20150208 | 1056 | 1182430 | 851 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 851 | 37.0183 | -122.0121 | 1SPSSOFMTR1007850535 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011654 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183656 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011651&numberofmonths=24&showchangehistorylog=1 | 15-0011651 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 7605 | 20150208 | 1506 | 1183040 | 431 | Distribution Circuit | Equipment Failure/Involved | Other | 16 | 6896 | 37.0866 | -122.0057 | 1881GLENWOODDR | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011651 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183658 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011726&numberofmonths=24&showchangehistorylog=1 | 15-0011726 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | LOMPICO-0401 | 88880401 | FUSE | 5619 | 20150208 | 1829 | 1183478 | 760 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 60040 | 37.1095 | -122.0494 | SSOF7199 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011726 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183325 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011768&numberofmonths=24&showchangehistorylog=1 | 15-0011768 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | LOMPICO-0401 | 88880401 | FUSE | 5629 | 20150208 | 1738 | 1183996 | 848 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 16960 | 37.1129 | -122.0479 | 12865LOMPICORD | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011768 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182827 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011669&numberofmonths=24&showchangehistorylog=1 | 15-0011669 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2102 | 83252102 | FUSE | 11105 | 20150208 | 1125 | 1182507 | 1040 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 6240 | 37.0112 | -122.075 | NR2519EMPIREGRADESANTACRUZ | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011669 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183646 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011638&numberofmonths=24&showchangehistorylog=1 | 15-0011638 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 2453 | 20150208 | 1227 | 1182688 | 548 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 7672 | 36.5723 | -121.9397 | MTR1009260665 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011638 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183666 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0071472&numberofmonths=24&showchangehistorylog=1 | 15-0071472 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | JUMPER | OPENJUMPERS1SPANSSMTR | 20151018 | 49 | 1324491 | 508 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 3048 | 37.087 | -122.0932 | 1379GREENBANKDRBENLOMAND | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 15-0071472 | OH | Sus | 0 | yes | 2015 | OCT | Yes | None | 1163163 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0084792&numberofmonths=24&showchangehistorylog=1 | 15-0084792 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5507 | 20151213 | 1005 | 1361151 | 405 | Distribution Circuit | Vegetation | Tree - branch fell on line | 34 | 13770 | 37.1418 | -122.1321 | NA | Strong Winds-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084792 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1174458 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0084839&numberofmonths=24&showchangehistorylog=1 | 15-0084839 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 7219 | 20151213 | 1005 | 1361152 | 578 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 10982 | 37.1412 | -122.0914 | 3SPANSLDSIDEOF7219 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084839 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Line | 1174506 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0084876&numberofmonths=24&showchangehistorylog=1 | 15-0084876 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | JUMPER | OJSTOMTR1007590064 | 20151213 | 1010 | 1362302 | 673 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 2019 | 37.1408 | -122.0904 | 1SPLSOFOJSONHARDTAP | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084876 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1174543 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0085039&numberofmonths=24&showchangehistorylog=1 | 15-0085039 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 8259 | 20151213 | 1731 | 1362822 | 334 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 6012 | 37.1593 | -122.1271 | 5SPMAINLINESSOF10641 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0085039 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1174712 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0084859&numberofmonths=24&showchangehistorylog=1 | 15-0084859 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG TREES-0402 | 83050402 | FUSE | 3233 | 20151213 | 957 | 1361120 | 758 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 21142 | 37.0325 | -122.0629 | CAPWELL39158312061280BEHIND276TOLLHOUSEGULCH | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084859 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1174526 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0084823&numberofmonths=24&showchangehistorylog=1 | 15-0084823 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 5577 | 20151213 | 1011 | 1361207 | 483 | Distribution Circuit | Equipment Failure/Involved | Overhead | 98 | 20928 | 37.0487 | -122.0616 | DARBYSHIRE41778312122089AT6SUMMITXSTTERRACEWAY | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084823 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1174491 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0084752&numberofmonths=24&showchangehistorylog=1 | 15-0084752 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 8427 | 20151213 | 944 | 1361640 | 101 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 4343 | 37.0825 | -121.9717 | 767CHARLESHILLRD | Clear-32-90 F | Conductor, Overhead | On Ground | 15-0084752 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1174420 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0084936&numberofmonths=24&showchangehistorylog=1 | 15-0084936 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 6601 | 20151213 | 1044 | 1361445 | 1635 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 39921 | 36.9941 | -121.7172 | WELSH130BELLAVISTALN | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084936 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Open Circuit | 1174609 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0084858&numberofmonths=24&showchangehistorylog=1 | 15-0084858 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | FUSE | 1945 | 20151213 | 1032 | 1361363 | 969 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 4845 | 36.9865 | -121.8546 | 2SPLSOF1945 | Partly Cloudy-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084858 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1174525 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0013271&numberofmonths=24&showchangehistorylog=1 | 16-0013271 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG TREES-0402 | 83050402 | JUMPER | OPENJPRS1SPANSSSOFMTR50001225809 | 20160217 | 1427 | 1405459 | 545 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1635 | 37.0407 | -122.0658 | 1SPANSSSOFMTR5000122580 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013271 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Open Circuit | 1186359 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0013302&numberofmonths=24&showchangehistorylog=1 | 16-0013302 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 9545 | 20160217 | 1638 | 1405933 | 737 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1474 | 37.0423 | -121.984 | 1SPLDSIDEOFFUCO9545 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013302 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Line to Ground | 1186386 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0013489&numberofmonths=24&showchangehistorylog=1 | 16-0013489 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | POINT MORETTI-1101 | 82931101 | JUMPER | OJHIGHSIDEOF2293 | 20160217 | 1942 | 1407599 | 828 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 828 | 37.0638 | -122.2269 | LDSIDEOF2293 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013489 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Line to Line | 1186577 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0013773&numberofmonths=24&showchangehistorylog=1 | 16-0013773 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | POINT MORETTI-1101 | 82931101 | FUSE | 8033 | 20160217 | 1950 | 1406650 | 1327 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 9289 | 37.1035 | -122.2775 | 3SPLS8033 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013773 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Line to Line | 1186813 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017628&numberofmonths=24&showchangehistorylog=1 | 16-0017628 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5487 | 20160305 | 1556 | 1417015 | 322 | Distribution Circuit | Vegetation | Tree - branch fell on line | 56 | 15080 | 37.1371 | -122.1006 | MTR100969039 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017628 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1189482 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017965&numberofmonths=24&showchangehistorylog=1 | 16-0017965 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5473 | 20160305 | 1930 | 1418526 | 250 | Distribution Circuit | Vegetation | Tree - branch fell on line | 90 | 22500 | 37.1287 | -122.1204 | MTR1004491106 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017965 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1189834 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0018051&numberofmonths=24&showchangehistorylog=1 | 16-0018051 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5519 | 20160305 | 1933 | 1418557 | 1172 | Distribution Circuit | Vegetation | Tree - fell into line | 174 | 188631 | 37.1515 | -122.1362 | 2SPANSFROMMTR1007590487TREEDOWNWIRE | Overcast-Heavy Rain-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 16-0018051 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1189923 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017976&numberofmonths=24&showchangehistorylog=1 | 16-0017976 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 7773 | 20160305 | 1644 | 1417445 | 850 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 20206 | 37.1882 | -122.1579 | 301STELARWAY | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017976 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1189847 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0018033&numberofmonths=24&showchangehistorylog=1 | 16-0018033 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 8501 | 20160305 | 1641 | 1417392 | 903 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 18060 | 37.1653 | -122.201 | 25SPANSLOADSIDEONBIGBASINWAY | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018033 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Multi-Fault | 1189904 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0018246&numberofmonths=24&showchangehistorylog=1 | 16-0018246 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 7289 | 20160305 | 2246 | 1421125 | 1055 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 14770 | 37.1709 | -122.1805 | MTR1007592577 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018246 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1190113 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017498&numberofmonths=24&showchangehistorylog=1 | 16-0017498 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | RECLOSER | 10946 | 20160305 | 1420 | 1416774 | 734 | Distribution Circuit | Vegetation | Tree - fell into line | 156 | 50664 | 37.0156 | -122.0254 | WELSH1504ELRANCHODR | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017498 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1189376 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017987&numberofmonths=24&showchangehistorylog=1 | 16-0017987 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 6087 | 20160305 | 2049 | 1419389 | 1468 | Distribution Circuit | Vegetation | Tree - branch fell on line | 184 | 172095 | 37.0669 | -122.0336 | MULTIPLEDMGLOCATIONS | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | On Ground | 16-0017987 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1189858 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017465&numberofmonths=24&showchangehistorylog=1 | 16-0017465 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 287 | 20160305 | 1157 | 1416594 | 339 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 5424 | 37.0905 | -122.0855 | ATMTR1007586416 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017465 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1189348 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017537&numberofmonths=24&showchangehistorylog=1 | 16-0017537 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER | 10728 | 20160305 | 1544 | 1416983 | 666 | Distribution Circuit | Vegetation | Tree - fell into line | 3432 | 251938 | 37.0665 | -122.0797 | STORMENT41788312780287Hwy9Felton | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017537 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1189396 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017695&numberofmonths=24&showchangehistorylog=1 | 16-0017695 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 11929 | 20160305 | 1632 | 1418034 | 705 | Distribution Circuit | Vegetation | Tree - fell into line | 100 | 60572 | 37.0999 | -122.0343 | 1SPANSOUTHOF9479 | Clear-32-90 F | Conductor, Overhead | On Ground | 16-0017695 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Multi-Fault | 1189550 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0018037&numberofmonths=24&showchangehistorylog=1 | 16-0018037 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 9251 | 20160305 | 1830 | 1418135 | 436 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 3052 | 37.0934 | -122.0428 | BEYOND9251 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | On Ground | 16-0018037 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Force Out | 1189908 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0018345&numberofmonths=24&showchangehistorylog=1 | 16-0018345 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | JUMPER | OJS1SPSS1BROOKESLN | 20160305 | 1721 | 1421565 | 1374 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 5496 | 37.0864 | -122.1043 | OJS1SPSS1BROOKESLN | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018345 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Force Out | 1190198 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017396&numberofmonths=24&showchangehistorylog=1 | 16-0017396 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 7457 | 20160305 | 731 | 1416317 | 714 | Distribution Circuit | Equipment Failure/Involved | Overhead | 317 | 42327 | 37.037 | -122.0421 | 700SUGARPINERD | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 16-0017396 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1189294 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017496&numberofmonths=24&showchangehistorylog=1 | 16-0017496 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 11323 | 20160305 | 1313 | 1416660 | 426 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 2130 | 37.0568 | -122.0191 | 1SPANSOUTHOFCOUT11323 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017496 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1189375 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0018413&numberofmonths=24&showchangehistorylog=1 | 16-0018413 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 1117 | 20160305 | 1740 | 1421282 | 2843 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 56860 | 37.1155 | -121.9708 | bet11178161 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018413 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190258 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0018197&numberofmonths=24&showchangehistorylog=1 | 16-0018197 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HATTON-1102 | 182291102 | FUSE | 2875 | 20160305 | 2157 | 1419887 | 973 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 8757 | 36.4996 | -121.9312 | 2SPANSSOUTH40335 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018197 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190066 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0018103&numberofmonths=24&showchangehistorylog=1 | 16-0018103 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1101 | 182941101 | FUSE | 8245 | 20160305 | 1753 | 1420877 | 1174 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 18886 | 36.4938 | -121.9342 | ATMTR1007265863 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | On Ground | 16-0018103 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1189974 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017828&numberofmonths=24&showchangehistorylog=1 | 16-0017828 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | POINT MORETTI-1101 | 82931101 | RECLOSER | 5074 | 20160305 | 2045 | 1419193 | 1521 | Distribution Circuit | Vegetation | Tree - fell into line | 136 | 173554 | 37.0208 | -122.2072 | 12POLESLOADSIDE5074 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017828 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1189682 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017955&numberofmonths=24&showchangehistorylog=1 | 16-0017955 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | POINT MORETTI-1101 | 82931101 | RECLOSER | 5078 | 20160305 | 2049 | s1189817 | 246 | Distribution Circuit | Equipment Failure/Involved | Overhead | 808 | 138399 | 37.0315 | -122.1867 | 4PSS8759 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 16-0017955 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1189817 | CSO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0018853&numberofmonths=24&showchangehistorylog=1 | 16-0018853 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | POINT MORETTI-1101 | 82931101 | FUSE | 5539 | 20160305 | 2106 | 1423823 | 2609 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 5218 | 37.0722 | -122.2234 | LDSIDEOF5539640SWANTONVIEWRD | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018853 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190659 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0018136&numberofmonths=24&showchangehistorylog=1 | 16-0018136 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 6641 | 20160305 | 2058 | 1420902 | 1900 | Distribution Circuit | Vegetation | Tree - fell into line | 265 | 370817 | 37.0161 | -121.8161 | LS9949 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018136 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1190007 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017557&numberofmonths=24&showchangehistorylog=1 | 16-0017557 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | RECLOSER | 5090 | 20160305 | 1616 | 1417182 | 805 | Distribution Circuit | Vegetation | Tree - fell into line | 429 | 71579 | 36.9802 | -121.8922 | NYSTROM105840879987991984TroutGulch | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017557 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1189415 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017667&numberofmonths=24&showchangehistorylog=1 | 16-0017667 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 10421 | 20160305 | 1646 | 1417459 | 1329 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 19935 | 36.5659 | -121.9347 | BET8159ANDMTR1008699036 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0017667 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Multi-Fault | 1189523 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017873&numberofmonths=24&showchangehistorylog=1 | 16-0017873 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | OCB | 22012 | 20160305 | 2102 | 1419375 | 1071 | Distribution Circuit | Vegetation | Tree - fell into line | 6887 | 631240 | 36.5786 | -121.9085 | BRANSONJeff4132crestrd | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017873 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1189727 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0018040&numberofmonths=24&showchangehistorylog=1 | 16-0018040 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2203 | 182852203 | FUSE | 9623 | 20160305 | 2142 | 1417491 | 548 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 21920 | 36.5722 | -121.9058 | ATCOUT8559 | Overcast-Rain-32-90 F | Conductor, Overhead | On Ground | 16-0018040 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Multi-Fault | 1189911 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017602&numberofmonths=24&showchangehistorylog=1 | 16-0017602 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2204 | 182852204 | FUSE | 2371 | 20160305 | 1628 | 1417245 | 552 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 21176 | 36.5818 | -121.9091 | ATMTR1008231067 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017602 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1189456 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0072262&numberofmonths=24&showchangehistorylog=1 | 16-0072262 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 2667 | 20161014 | 1515 | 1559890 | 195 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 975 | 37.0261 | -121.775 | 1SPANLOADSIDE2667 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0072262 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Ground | 1229333 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0072307&numberofmonths=24&showchangehistorylog=1 | 16-0072307 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 5397 | 20161014 | 1805 | 1560193 | 680 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 15640 | 37.0762 | -122.1431 | 4NO5397 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0072307 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Ground | 1229367 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0003363&numberofmonths=24&showchangehistorylog=1 | 17-0003363 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 6103 | 20170103 | 2303 | 1617210 | 2395 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 15274 | 37.0115 | -122.0121 | 401REDWOODDR | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003363 | OH | Sus | 31292865 | yes | 2017 | JAN | Yes | Line to Ground | 1243539 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0002955&numberofmonths=24&showchangehistorylog=1 | 17-0002955 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 3307 | 20170103 | 1012 | 1615612 | 96 | Distribution Circuit | Vegetation | Tree - fell into line | 2034 | 147983 | 37.0485 | -122.0645 | 1spanPAST3307 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0002955 | OH | Sus | 42908763 | yes | 2017 | JAN | Yes | Three Phase Fault | 1243250 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0003151&numberofmonths=24&showchangehistorylog=1 | 17-0003151 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | OTTER-1101 | 182941101 | OTHER | WIREDOWNSW461 | 20170103 | 1536 | 1615941 | 764 | Distribution Circuit | Equipment Failure/Involved | Overhead | 579 | 235871 | 36.3952 | -121.9022 | NORTHSIDEOFPOLESW461 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0003151 | OH | Sus | 42909923 | yes | 2017 | JAN | Yes | Open Circuit | 1243325 | CSO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0003318&numberofmonths=24&showchangehistorylog=1 | 17-0003318 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE | 5985 | 20170103 | 2141 | 1616979 | 379 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 9310 | 37.045 | -121.9384 | 4SPLDSIDEFUSE11905 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003318 | OH | Sus | 42909935 | yes | 2017 | JAN | Yes | Line to Ground | 1243491 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0003317&numberofmonths=24&showchangehistorylog=1 | 17-0003317 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | POINT MORETTI-1101 | 82931101 | RECLOSER | 12122 | 20170103 | 2247 | 1617172 | 1153 | Distribution Circuit | Vegetation | Tree - fell into line | 78 | 61170 | 37.0664 | -122.2286 | IFO3546HWY1 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003317 | OH | Sus | 31292865 | yes | 2017 | JAN | Yes | Line to Line | 1243490 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0004942&numberofmonths=24&showchangehistorylog=1 | 17-0004942 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN SUB | 8284 | OCB | 11012 | 20170108 | 650 | 1622844 | 3315 | Distribution Circuit | Vegetation | Tree - fell into line | 2942 | 3680039 | 37.1312 | -122.1724 | CAPWELL3915831206128011303EMPIREGRADEAND11SPANSSSOFRCO10649 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004942 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1244743 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005147&numberofmonths=24&showchangehistorylog=1 | 17-0005147 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 8469 | 20170108 | 650 | 1625134 | 4839 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 4839 | 37.1544 | -122.0824 | 2LDSIDEOF8469 | Overcast-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0005147 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Force Out | 1244943 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005095&numberofmonths=24&showchangehistorylog=1 | 17-0005095 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER | 12758 | 20170108 | 956 | 1624575 | 1730 | Distribution Circuit | Vegetation | Tree - fell into line | 240 | 195317 | 37.1487 | -122.1748 | BET6896595719 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005095 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1244893 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005852&numberofmonths=24&showchangehistorylog=1 | 17-0005852 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | JUMPER | WIREDOWN3SPANSSSIDEOF4367 | 20170108 | 811 | 1629928 | 4768 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 16784 | 37.1919 | -122.163 | 3SPANSSOURCESIDEOF4367 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005852 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Force Out | 1245635 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0004890&numberofmonths=24&showchangehistorylog=1 | 17-0004890 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BURNS-2101 | 183582101 | JUMPER | WIREDOWN1SPANSOURCESIDE374675 | 20170108 | 10 | 1622372 | 585 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 7308 | 37.095 | -122.0857 | 1SPANSOURCESIDE374675 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004890 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Open Circuit | 1244690 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0004994&numberofmonths=24&showchangehistorylog=1 | 17-0004994 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BURNS-2101 | 183582101 | FUSE | 3307 | 20170108 | 709 | 1622950 | 444 | Distribution Circuit | Equipment Failure/Involved | Overhead | 617 | 57692 | 37.066 | -122.0797 | 3307 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004994 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1244794 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0004989&numberofmonths=24&showchangehistorylog=1 | 17-0004989 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BURNS-2101 | 183582101 | RECLOSER | 10728 | 20170108 | 1205 | 1626008 | 148 | Distribution Circuit | Vegetation | Tree - fell into line | 534 | 78536 | 37.0665 | -122.0797 | FUSE3307 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004989 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Force Out | 1245039 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005411&numberofmonths=24&showchangehistorylog=1 | 17-0005411 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BURNS-2101 | 183582101 | JUMPER | OJMTR1007590761 | 20170108 | 935 | 1627443 | 1530 | Distribution Circuit | Vegetation | Tree - branch fell on line | 137 | 47202 | 37.1191 | -122.1037 | ROGERSDON21016613405640REBECCAANDDAISYPL | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005411 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245194 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005772&numberofmonths=24&showchangehistorylog=1 | 17-0005772 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BURNS-2101 | 183582101 | RECLOSER | 10912 | 20170108 | 2249 | 1629739 | 2528 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 86560 | 37.0913 | -122.096 | 4SPANSWO4745 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005772 | OH | Sus | 31294181 | yes | 2017 | JAN | Yes | Line to Ground | 1245559 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005163&numberofmonths=24&showchangehistorylog=1 | 17-0005163 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 1143 | 20170108 | 940 | 1624286 | 361 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 5054 | 37.0041 | -122.0202 | 3SPANDLOADSIDE | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005163 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1244958 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005274&numberofmonths=24&showchangehistorylog=1 | 17-0005274 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 12525 | 20170108 | 1003 | 1624565 | 7247 | Distribution Circuit | Environmental/External | Flood/Erosion | 64 | 474176 | 37.094 | -122.0241 | CRIVELLO417683168219123polesfromsw835 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0005274 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245064 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005600&numberofmonths=24&showchangehistorylog=1 | 17-0005600 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 4355 | 20170108 | 1504 | 1627581 | 2485 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 57155 | 37.0602 | -122.064 | 7550mCADAMAVE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005600 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245378 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005828&numberofmonths=24&showchangehistorylog=1 | 17-0005828 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | JUMPER | OJSSOFMTR1008750940 | 20170108 | 1625 | 1629940 | 3075 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 12300 | 37.0836 | -122.0855 | OJ1SSSATLINEBUCKOFMTR1008750940 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005828 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Open Circuit | 1245613 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005912&numberofmonths=24&showchangehistorylog=1 | 17-0005912 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | OTHER | WIREDOWN1SPSSOF839 | 20170108 | 1603 | 1630335 | 2962 | Distribution Circuit | Equipment Failure/Involved | Overhead | 67 | 167071 | 37.1295 | -122.0184 | 1SPSSOF839 | Overcast-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0005912 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245693 | PW | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005943&numberofmonths=24&showchangehistorylog=1 | 17-0005943 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | OTHER | WIREDWN2SPLDSIDEOF11929 | 20170108 | 1600 | 1630333 | 2925 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 90675 | 37.1002 | -122.0342 | 2SPLDSIDEOF11929 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005943 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245715 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0004900&numberofmonths=24&showchangehistorylog=1 | 17-0004900 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 6037 | 20170108 | 200 | 1622468 | 870 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 14370 | 37.0729 | -122.0159 | MCKELLJAMESEndofMackenziecreekRd | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0004900 | OH | Sus | 31294181 | yes | 2017 | JAN | Yes | Line to Ground | 1244701 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005068&numberofmonths=24&showchangehistorylog=1 | 17-0005068 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER | 11006 | 20170108 | 902 | 1623885 | 2465 | Distribution Circuit | Vegetation | Tree - fell into line | 1634 | 308579 | 37.05 | -122.0657 | NYSTROM10584087998799ZayanteRedwoodCampjustNOGrahamHill | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005068 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1244867 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005622&numberofmonths=24&showchangehistorylog=1 | 17-0005622 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 6043 | 20170108 | 1732 | 1628395 | 1588 | Distribution Circuit | Vegetation | Tree - fell into line | 134 | 25556 | 37.0696 | -121.995 | BEYONDMETER1008947480 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005622 | OH | Sus | 31294181 | yes | 2017 | JAN | Yes | Line to Ground | 1245400 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005736&numberofmonths=24&showchangehistorylog=1 | 17-0005736 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 11919 | 20170108 | 1851 | 1629523 | 1228 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 23332 | 37.0701 | -122.0162 | 1SPANLDSIDE11919 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005736 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245520 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0004936&numberofmonths=24&showchangehistorylog=1 | 17-0004936 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | OTHER | WIREDOWN1SPSSFUCO5725 | 20170108 | 635 | 1622784 | 524 | Distribution Circuit | Vegetation | Tree - fell into line | 292 | 78433 | 36.9902 | -121.7368 | 1SPSSFUSE5725 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004936 | OH | Sus | 42912765 | yes | 2017 | JAN | Yes | Line to Ground | 1244737 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005039&numberofmonths=24&showchangehistorylog=1 | 17-0005039 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HATTON-1102 | 182291102 | FUSE | 10189 | 20170108 | 748 | 1623241 | 372 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 1488 | 36.5057 | -121.9364 | 2SPANSLOADSIDE | Overcast-Fog-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005039 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Force Out | 1244837 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005379&numberofmonths=24&showchangehistorylog=1 | 17-0005379 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1101 | 182941101 | FUSE | 40417 | 20170108 | 1248 | 1626423 | 212 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 636 | 36.491 | -121.9361 | 2PLOADSIDE40417 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005379 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1245165 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005484&numberofmonths=24&showchangehistorylog=1 | 17-0005484 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | OTTER-1101 | 182941101 | FUSE | 633 | 20170108 | 1213 | 1626055 | 610 | Distribution Circuit | Vegetation | Tree - branch fell on line | 22 | 13420 | 36.4171 | -121.9132 | HWY1NEARGARAPATABRIDGEBIGSUR | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005484 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Multi-Fault | 1245267 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005511&numberofmonths=24&showchangehistorylog=1 | 17-0005511 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1101 | 182941101 | FUSE | 457 | 20170108 | 1427 | 1628029 | 884 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 16796 | 36.4928 | -121.9334 | 5POLESLOADSIDE | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005511 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Multi-Fault | 1245294 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005021&numberofmonths=24&showchangehistorylog=1 | 17-0005021 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | RECLOSER | 39126 | 20170108 | 834 | 1623735 | 1721 | Distribution Circuit | Vegetation | Tree - fell into line | 136 | 168352 | 37.0778 | -122.1326 | ATFUSE5403 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005021 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1244819 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005269&numberofmonths=24&showchangehistorylog=1 | 17-0005269 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 10139 | 20170108 | 1100 | 1626288 | 1648 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 6592 | 37.044 | -122.1552 | LOADSIDEOF10139 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005269 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245059 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005428&numberofmonths=24&showchangehistorylog=1 | 17-0005428 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | OTHER | WIREDOWN1SPANLSOFMETER1008412331 | 20170108 | 941 | 1624296 | 1887 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 18523 | 37.0524 | -122.1508 | 1SPANBEYONDMETER1008412331 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005428 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245212 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005569&numberofmonths=24&showchangehistorylog=1 | 17-0005569 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 5409 | 20170108 | 1635 | 1628065 | 1828 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 10968 | 37.0658 | -122.1519 | 2SPANLOADSIDE5409 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005569 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1245352 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006347&numberofmonths=24&showchangehistorylog=1 | 17-0006347 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | POINT MORETTI-1101 | 82931101 | FUSE | 8033 | 20170108 | 1807 | 1628522 | 2033 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 14231 | 37.1035 | -122.2775 | 2SPANSLDSIDEOF8033 | Overcast-Rain-32-90 F | Conductor, Overhead | On Ground | 17-0006347 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1246053 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005192&numberofmonths=24&showchangehistorylog=1 | 17-0005192 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | FUSE | 7989 | 20170108 | 942 | 1624468 | 4458 | Distribution Circuit | Vegetation | Tree - fell into line | 262 | 726569 | 36.9817 | -121.8645 | TURNIPSEEDPAULValeciaCoxDayValley | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0005192 | OH | Sus | 31294181 | yes | 2017 | JAN | Yes | Line to Line | 1244984 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005628&numberofmonths=24&showchangehistorylog=1 | 17-0005628 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | OTHER | WIREDOWN2SPANSLDSOMTR409498 | 20170108 | 1919 | 1628824 | 2888 | Distribution Circuit | Vegetation | Tree - fell into line | 335 | 98368 | 37.0277 | -121.8781 | 2SPANSLDSOFMETER409498 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005628 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Force Out | 1245410 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005768&numberofmonths=24&showchangehistorylog=1 | 17-0005768 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 2705 | 20170108 | 1850 | 1628154 | 1782 | Distribution Circuit | Vegetation | Tree - fell into line | 144 | 255358 | 37.0005 | -121.7405 | BET2705AND12349 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005768 | OH | Sus | 31294181 | yes | 2017 | JAN | Yes | Multi-Fault | 1245554 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005774&numberofmonths=24&showchangehistorylog=1 | 17-0005774 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 11305 | 20170108 | 2027 | 1629067 | 2493 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 32409 | 37.0307 | -121.7864 | FIRSTTWOSPANSLDSIDEOF11305 | Clear-32-90 F | Conductor, Overhead | On Ground | 17-0005774 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245561 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005642&numberofmonths=24&showchangehistorylog=1 | 17-0005642 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | SAN BENITO-2104 | 182742104 | FUSE | 6523 | 20170108 | 1508 | 1627637 | 1707 | Distribution Circuit | Equipment Failure/Involved | Overhead | 163 | 54934 | 36.8749 | -121.6417 | 1SPANLDSIDEOF945LABELED645INFIELD | Overcast-Rain-32-90 F | Conductor, Overhead | On Ground | 17-0005642 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245421 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005644&numberofmonths=24&showchangehistorylog=1 | 17-0005644 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 7259 | 20170108 | 1523 | 1628439 | 1481 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 62202 | 36.5752 | -121.9365 | WIREDOWNMTR1009437331 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005644 | OH | Sus | 31293495 | yes | 2017 | JAN | Yes | Line to Line | 1245424 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006443&numberofmonths=24&showchangehistorylog=1 | 17-0006443 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5485 | 20170109 | 1852 | 1632090 | 923 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 30459 | 37.1322 | -122.1091 | 1LDSIDEOF5485 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006443 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246132 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006517&numberofmonths=24&showchangehistorylog=1 | 17-0006517 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 9773 | 20170109 | 1609 | 1631724 | 1294 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 37526 | 37.1288 | -122.1141 | 2SO9773 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006517 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1246176 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005975&numberofmonths=24&showchangehistorylog=1 | 17-0005975 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 12125 | 20170109 | 915 | 1630649 | 1845 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 5535 | 37.2253 | -122.1487 | 2SPANLOASIDEFUSE12125 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005975 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1245740 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005875&numberofmonths=24&showchangehistorylog=1 | 17-0005875 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BURNS-2101 | 183582101 | SECTIONALIZER | 95394 | 20170109 | 524 | 1630158 | 1935 | Distribution Circuit | Vegetation | Tree - fell into line | 1896 | 163482 | 37.0743 | -122.083 | MTR1009786993 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005875 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245659 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006226&numberofmonths=24&showchangehistorylog=1 | 17-0006226 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | JUMPER | OJLDSIDEOFTX315371522847 | 20170109 | 1211 | 1631729 | 4651 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 13953 | 37.117 | -122.0861 | LSOFTX315371522847 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006226 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245926 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005966&numberofmonths=24&showchangehistorylog=1 | 17-0005966 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1102 | 182941102 | RECLOSER | 63868 | 20170109 | 901 | 1630615 | 1406 | Distribution Circuit | Environmental/External | Flood/Erosion | 416 | 579980 | 36.2641 | -121.7954 | 6SP8SPLDSIDEOF10441 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005966 | OH | Sus | 31293495 | yes | 2017 | JAN | Yes | Three Phase Fault | 1245733 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006272&numberofmonths=24&showchangehistorylog=1 | 17-0006272 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | POINT MORETTI-1101 | 82931101 | FUSE | 5043 | 20170109 | 1833 | 1632070 | 1122 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 3366 | 37.0607 | -122.226 | 3SPANSSOURCESIDEOF310SWANTON | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006272 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1245969 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005898&numberofmonths=24&showchangehistorylog=1 | 17-0005898 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | FUSE | 737 | 20170109 | 332 | 1630264 | 2518 | Distribution Circuit | Vegetation | Tree - branch fell on line | 59 | 148562 | 37.0046 | -121.8552 | 1LDSIDEOF2429 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005898 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Three Phase Fault | 1245682 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006258&numberofmonths=24&showchangehistorylog=1 | 17-0006258 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 1861 | 20170109 | 1240 | 1631241 | 460 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 460 | 37.0267 | -121.777 | LDSIDEOF1881 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006258 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245951 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007048&numberofmonths=24&showchangehistorylog=1 | 17-0007048 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | RECLOSER | 5028 | 20170110 | 2046 | 1637013 | 985 | Distribution Circuit | Vegetation | Tree - fell into line | 636 | 565128 | 37.1284 | -122.1222 | 2SPLDSD696141LDSD9771 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0007048 | OH | Sus | 31294181 | yes | 2017 | JAN | Yes | Line to Ground | 1246633 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007046&numberofmonths=24&showchangehistorylog=1 | 17-0007046 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER | 12992 | 20170110 | 2047 | 1636280 | 1242 | Distribution Circuit | Vegetation | Tree - fell into line | 687 | 261630 | 37.1987 | -122.1536 | BRANDT41798312122088nearscadamatecheckwithCapwell | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007046 | OH | Sus | 31294181 | yes | 2017 | JAN | Yes | Line to Line | 1246631 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007363&numberofmonths=24&showchangehistorylog=1 | 17-0007363 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG TREES-0402 | 83050402 | FUSE | 7301 | 20170110 | 1822 | 1635359 | 1278 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 21726 | 37.0329 | -122.0745 | 4LDSIDEOF7301 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007363 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1246948 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007608&numberofmonths=24&showchangehistorylog=1 | 17-0007608 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BURNS-2101 | 183582101 | FUSE | 7199 | 20170110 | 1646 | 1634493 | 1485 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 7425 | 37.1116 | -122.0478 | LompicoRoadAndOldMillRoadLOMPICO | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007608 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247123 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006906&numberofmonths=24&showchangehistorylog=1 | 17-0006906 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 6105 | 20170110 | 1731 | 1634710 | 2944 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 11776 | 37.0099 | -122.0107 | CAPWELL39158312061280756GLENCANYONRD | Overcast-Heavy Rain-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0006906 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246487 | CSO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007254&numberofmonths=24&showchangehistorylog=1 | 17-0007254 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER | 33542 | 20170110 | 2325 | 1638064 | 2315 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 57579 | 37.0905 | -122.0456 | CRIVELLO41768316821912nearco | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007254 | OH | Sus | 31294181 | yes | 2017 | JAN | Yes | Line to Ground | 1246834 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007433&numberofmonths=24&showchangehistorylog=1 | 17-0007433 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 11929 | 20170110 | 1939 | 1638919 | 1301 | Distribution Circuit | Vegetation | Tree - fell into line | 382 | 164745 | 37.0999 | -122.0343 | PASTFUSE11929PASTFUSE6161SS9241 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007433 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247016 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007445&numberofmonths=24&showchangehistorylog=1 | 17-0007445 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | TRIP-SAVER | 5577 | 20170110 | 1442 | 1633788 | 1300 | Distribution Circuit | Vegetation | Tree - branch fell on line | 98 | 119344 | 37.0487 | -122.0616 | SPANSLOADSIDE1623 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007445 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247022 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007701&numberofmonths=24&showchangehistorylog=1 | 17-0007701 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 5587 | 20170110 | 2355 | 1638151 | 2160 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 17280 | 37.0672 | -122.0586 | 2SPANSLSOF5587 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007701 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247194 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006659&numberofmonths=24&showchangehistorylog=1 | 17-0006659 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | JUMPER | OJSATTAKEOFFPOWERTOEOL | 20170110 | 837 | 1632698 | 578 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 578 | 37.092 | -121.9636 | OJSATTAKEOFFPOLE | Strong Winds-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006659 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246287 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007266&numberofmonths=24&showchangehistorylog=1 | 17-0007266 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | CAMP EVERS-2106 | 83622106 | FUSE | 1613 | 20170110 | 2105 | 1637179 | 1155 | Distribution Circuit | Vegetation | Tree - fell into line | 154 | 60500 | 37.0467 | -122.0757 | CRIVELLO41768316821912485orchard | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0007266 | OH | Sus | 31294181 | yes | 2017 | JAN | Yes | Line to Line | 1246846 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007737&numberofmonths=24&showchangehistorylog=1 | 17-0007737 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 10619 | 20170110 | 1909 | 1635973 | 2555 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 7665 | 37.0765 | -122.0114 | 2LDSIDEOF10619 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007737 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Multi-Fault | 1247216 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007742&numberofmonths=24&showchangehistorylog=1 | 17-0007742 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | OTHER | WIREDOWN17230LAURELRD | 20170110 | 1933 | 1640082 | 2731 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 140889 | 37.1104 | -121.9729 | 17230LAURELRD | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007742 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247219 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007411&numberofmonths=24&showchangehistorylog=1 | 17-0007411 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 6647 | 20170110 | 1956 | 1638665 | 1174 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 24654 | 37.0265 | -121.7798 | 1SS11305 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007411 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1246998 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006711&numberofmonths=24&showchangehistorylog=1 | 17-0006711 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HATTON-1102 | 182291102 | FUSE | 1491 | 20170110 | 1428 | 1633754 | 982 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 16798 | 36.5058 | -121.9351 | BRANSONJefftreefell | Overcast-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0006711 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246323 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007302&numberofmonths=24&showchangehistorylog=1 | 17-0007302 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE | 5985 | 20170110 | 1926 | 1636215 | 1194 | Distribution Circuit | Vegetation | Tree - fell into line | 91 | 108654 | 37.045 | -121.9384 | METER1007852655 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007302 | OH | Sus | 42912765 | yes | 2017 | JAN | Yes | Line to Ground | 1246883 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006697&numberofmonths=24&showchangehistorylog=1 | 17-0006697 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | RECLOSER | 10954 | 20170110 | 1442 | 1633797 | 1708 | Distribution Circuit | Vegetation | Tree - fell into line | 430 | 223903 | 36.9873 | -121.86 | FUCO4233FUCO1111 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006697 | OH | Sus | 31294181 | yes | 2017 | JAN | Yes | Line to Ground | 1246314 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006910&numberofmonths=24&showchangehistorylog=1 | 17-0006910 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | SAN JUSTO-1101 | 183181101 | FUSE | 4245 | 20170110 | 1628 | 1634348 | 1077 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 4535 | 36.8938 | -121.5973 | MTR1007757307 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006910 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246491 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007359&numberofmonths=24&showchangehistorylog=1 | 17-0007359 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 7805 | 20170111 | 233 | 1638504 | 512 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1024 | 37.2145 | -122.1489 | MTR1007347607 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007359 | OH | Sus | 31294181 | yes | 2017 | JAN | Yes | Line to Ground | 1246944 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007937&numberofmonths=24&showchangehistorylog=1 | 17-0007937 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 1827 | 20170111 | 1933 | 1640692 | 1182 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 14736 | 37.2132 | -122.1553 | BOYNTON345983133166204SPANSLOADSIDECO1827 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007937 | OH | Sus | 31294181 | yes | 2017 | JAN | Yes | Multi-Fault | 1247382 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007828&numberofmonths=24&showchangehistorylog=1 | 17-0007828 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | JUMPER | WIREDOWN1LDSIDEOF5151 | 20170111 | 656 | 1639979 | 2086 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 6258 | 37.1115 | -122.0895 | 1LDSIDEOF5151 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007828 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247288 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007938&numberofmonths=24&showchangehistorylog=1 | 17-0007938 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 6593 | 20170111 | 1627 | 1640341 | 1394 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 16728 | 37.0163 | -121.7201 | MCKELLJAMES6spanssouthof6593 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007938 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247383 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007507&numberofmonths=24&showchangehistorylog=1 | 17-0007507 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | FUSE | 1939 | 20170111 | 254 | 1638817 | 2081 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 12486 | 36.9838 | -121.8311 | METER100969942 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007507 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247054 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0008264&numberofmonths=24&showchangehistorylog=1 | 17-0008264 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 11305 | 20170111 | 2357 | 1640886 | 2305 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 15995 | 37.0307 | -121.7864 | 2SPANSSOURCESIDEMTR1008517303 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0008264 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247702 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007431&numberofmonths=24&showchangehistorylog=1 | 17-0007431 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | SAN BENITO-2104 | 182742104 | FUSE | 6773 | 20170111 | 333 | 1638560 | 625 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 54375 | 36.88 | -121.6403 | RANGELRUFINO719SEELYAVE | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007431 | OH | Sus | 42912765 | yes | 2017 | JAN | Yes | Line to Ground | 1247013 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0010460&numberofmonths=24&showchangehistorylog=1 | 17-0010460 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 10621 | 20170118 | 1814 | 1649117 | 1202 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 8414 | 37.0652 | -122.0175 | 2LDSIDE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010460 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Force Out | 1249478 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0010554&numberofmonths=24&showchangehistorylog=1 | 17-0010554 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 11179 | 20170118 | 2030 | 1648889 | 1284 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 33384 | 37.0016 | -122.0278 | 2933PASATIEMPODR | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010554 | OH | Sus | 31297127 | yes | 2017 | JAN | Yes | Line to Ground | 1249571 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0010486&numberofmonths=24&showchangehistorylog=1 | 17-0010486 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | POINT MORETTI-1101 | 82931101 | FUSE | 5995 | 20170118 | 1951 | 1648711 | 989 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 6923 | 37.078 | -122.244 | 2SPANSSSOFMETER1008918857 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010486 | OH | Sus | 31297127 | yes | 2017 | JAN | Yes | Line to Ground | 1249504 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0010455&numberofmonths=24&showchangehistorylog=1 | 17-0010455 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 5819 | 20170118 | 1922 | 1648649 | 1103 | Distribution Circuit | Vegetation | Tree - branch fell on line | 59 | 58322 | 37.0447 | -121.8131 | METER28P214 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010455 | OH | Sus | 31297127 | yes | 2017 | JAN | Yes | Line to Ground | 1249473 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0010572&numberofmonths=24&showchangehistorylog=1 | 17-0010572 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2202 | 182852202 | FUSE | 55781 | 20170118 | 2047 | 1648948 | 244 | Distribution Circuit | Vegetation | Tree - branch fell on line | 47 | 11468 | 36.6018 | -121.9374 | 2SPANSLDSIDEOF55781 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010572 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1249589 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0010494&numberofmonths=24&showchangehistorylog=1 | 17-0010494 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2204 | 182852204 | FUSE | 2371 | 20170118 | 1959 | 1648748 | 899 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 32442 | 36.5818 | -121.9091 | MTR1008233773 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010494 | OH | Sus | 42928578 | yes | 2017 | JAN | Yes | Line to Ground | 1249512 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0010570&numberofmonths=24&showchangehistorylog=1 | 17-0010570 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2204 | 182852204 | FUSE | 7567 | 20170118 | 2047 | 1648956 | 1089 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 21780 | 36.5783 | -121.9039 | 3SPANSLSOF7567 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010570 | OH | Sus | 31297011 | yes | 2017 | JAN | Yes | Line to Ground | 1249587 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011077&numberofmonths=24&showchangehistorylog=1 | 17-0011077 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1102 | 182941102 | JUMPER | WIREDOWN1SPSSIDEOF6133 | 20170119 | 1830 | 1651782 | 8395 | Distribution Circuit | Environmental/External | Flood/Erosion | 52 | 16696 | 36.1078 | -121.6246 | 1SPANSSOF6133 | Clear-32-90 F | Conductor, Overhead | On Ground | 17-0011077 | OH | Sus | 31297011 | yes | 2017 | JAN | Yes | Force Out | 1249986 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011441&numberofmonths=24&showchangehistorylog=1 | 17-0011441 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 8461 | 20170120 | 805 | 1653163 | 1688 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 13504 | 37.1333 | -122.1028 | 1SPANSLDSIDEOF8461 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011441 | OH | Sus | 31297127 | yes | 2017 | JAN | Yes | Line to Ground | 1250324 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011739&numberofmonths=24&showchangehistorylog=1 | 17-0011739 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 2945 | 20170120 | 1513 | 1654540 | 1287 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 64350 | 37.1733 | -122.1442 | WELSH755CREEKDR | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0011739 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1250572 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011405&numberofmonths=24&showchangehistorylog=1 | 17-0011405 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2104 | 83622104 | JUMPER | JUMPERSIFOMTR100845729 | 20170120 | 724 | 1652973 | 3450 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 7912 | 37.0405 | -121.9976 | 1SPANLDSIDEMTR100845729 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011405 | OH | Sus | 31297127 | yes | 2017 | JAN | Yes | Open Circuit | 1250293 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011563&numberofmonths=24&showchangehistorylog=1 | 17-0011563 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 4169 | 20170120 | 1115 | 1653882 | 1405 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1405 | 37.0915 | -122.0472 | WELSH9609ZAYANTEDR6SPNOEZAYANTEDR | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 17-0011563 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1250426 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011631&numberofmonths=24&showchangehistorylog=1 | 17-0011631 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 3603 | 20170120 | 1035 | 1653756 | 1747 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 15723 | 37.1149 | -122.1138 | 5200TINKERSTRAIL | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011631 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1250483 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011650&numberofmonths=24&showchangehistorylog=1 | 17-0011650 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 5151 | 20170120 | 941 | 1653546 | 1715 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 10290 | 37.1109 | -122.0898 | MTR1009698877 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011650 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1250500 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011668&numberofmonths=24&showchangehistorylog=1 | 17-0011668 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER | 5400 | 20170120 | 1531 | 1654594 | 439 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 6062 | 37.08 | -122.0838 | 1SPANNOF7231 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011668 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1250517 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011711&numberofmonths=24&showchangehistorylog=1 | 17-0011711 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | JUMPER | WIREDOWN | 20170120 | 1124 | 1653992 | 476 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 2380 | 37.092 | -121.9769 | 9000HWY17 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011711 | OH | Sus | 0 | yes | 2017 | JAN | Yes | None | 1250553 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011627&numberofmonths=24&showchangehistorylog=1 | 17-0011627 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE | 7681 | 20170120 | 544 | 1652565 | 1830 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 18300 | 36.5832 | -121.865 | 2SPANSSSOF702085 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011627 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1250480 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011510&numberofmonths=24&showchangehistorylog=1 | 17-0011510 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | GREEN VALLEY-2101 | 83192101 | JUMPER | WIREDOWN2SPEO766683 | 20170120 | 1053 | 1653789 | 439 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 3386 | 36.9777 | -121.7244 | 2SPEO766683 | Partly Cloudy-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011510 | OH | Sus | 31297127 | yes | 2017 | JAN | Yes | Open Circuit | 1250384 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011575&numberofmonths=24&showchangehistorylog=1 | 17-0011575 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HATTON-1101 | 182291101 | FUSE | 627 | 20170120 | 1319 | 1653046 | 598 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 13156 | 36.5489 | -121.8966 | 1SWO627 | Partly Cloudy-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011575 | OH | Sus | 31297011 | yes | 2017 | JAN | Yes | Force Out | 1250434 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011712&numberofmonths=24&showchangehistorylog=1 | 17-0011712 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HATTON-1101 | 182291101 | FUSE | 8171 | 20170120 | 1407 | 1654407 | 1553 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 3106 | 36.5448 | -121.8847 | 3SPANSLDSIDEOF8171 | Partly Cloudy-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011712 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1250554 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011629&numberofmonths=24&showchangehistorylog=1 | 17-0011629 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE | 5985 | 20170120 | 1315 | 1654294 | 1455 | Distribution Circuit | Equipment Failure/Involved | Overhead | 91 | 15651 | 37.045 | -121.9384 | 10073 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011629 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1250481 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011558&numberofmonths=24&showchangehistorylog=1 | 17-0011558 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | POINT MORETTI-1101 | 82931101 | FUSE | 5995 | 20170120 | 553 | 1652605 | 1984 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 13888 | 37.078 | -122.244 | IFOMTR10702J | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011558 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1250421 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013129&numberofmonths=24&showchangehistorylog=1 | 17-0013129 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 6605 | 20170120 | 1855 | 1655040 | 2745 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 19215 | 37.013 | -121.7519 | UNKNOWN | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013129 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1251947 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011658&numberofmonths=24&showchangehistorylog=1 | 17-0011658 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | RECLOSER | 5090 | 20170120 | 1507 | 1654535 | 853 | Distribution Circuit | Vegetation | Tree - fell into line | 431 | 75682 | 36.9802 | -121.8922 | 10SPANSLDSIDEOF153489MTR1006278514 | Overcast-Drizzle-32-90 F | Conductor, Overhead | On Ground | 17-0011658 | OH | Sus | 31297127 | yes | 2017 | JAN | Yes | Multi-Fault | 1250507 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011721&numberofmonths=24&showchangehistorylog=1 | 17-0011721 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | SAN BENITO-2104 | 182742104 | FUSE | 775 | 20170120 | 1521 | 1654559 | 1849 | Distribution Circuit | Vegetation | Tree - fell into line | 103 | 35761 | 36.8875 | -121.6273 | 1SNO775 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011721 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1250562 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011593&numberofmonths=24&showchangehistorylog=1 | 17-0011593 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 6975 | 20170120 | 528 | 1652469 | 725 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 36250 | 36.5797 | -121.9203 | WIREDOWNFROM4135SUNSETLNTO4144SUNSETLN | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011593 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1250450 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012016&numberofmonths=24&showchangehistorylog=1 | 17-0012016 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2202 | 182852202 | FUSE | 9123 | 20170120 | 1219 | 1654154 | 1545 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 21630 | 36.6056 | -121.9368 | 27992803ForestLodgeRd | Overcast-Rain-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0012016 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Force Out | 1250833 | CSO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012315&numberofmonths=24&showchangehistorylog=1 | 17-0012315 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE | 5141 | 20170121 | 2020 | 1657228 | 1061 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 12732 | 37.0946 | -122.0864 | 5141FUCO | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012315 | OH | Sus | 31297127 | yes | 2017 | JAN | Yes | Line to Ground | 1251133 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012506&numberofmonths=24&showchangehistorylog=1 | 17-0012506 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5487 | 20170121 | 1959 | 1657227 | 4016 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 156718 | 37.1371 | -122.1006 | 3SPANSOUTHOF4183 | Strong Winds-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012506 | OH | Sus | 42928924 | yes | 2017 | JAN | Yes | Line to Ground | 1251325 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012093&numberofmonths=24&showchangehistorylog=1 | 17-0012093 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | OTHER | WIREDOWNMETER1007348651 | 20170121 | 1035 | 1656282 | 440 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 1640 | 37.1952 | -122.1554 | METER1007348651 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012093 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1250908 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012166&numberofmonths=24&showchangehistorylog=1 | 17-0012166 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 12525 | 20170121 | 1644 | 1656979 | 1189 | Distribution Circuit | Vegetation | Tree - fell into line | 64 | 14482 | 37.094 | -122.0241 | 2WO835 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012166 | OH | Sus | 31297127 | yes | 2017 | JAN | Yes | Line to Line | 1250983 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011921&numberofmonths=24&showchangehistorylog=1 | 17-0011921 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | PAUL SWEET-2106 | 83252106 | FUSE | 7749 | 20170121 | 640 | 1655700 | 607 | Distribution Circuit | Vegetation | Tree - fell into line | 102 | 38296 | 36.9978 | -121.9506 | TREEDOWN5SPANNOF5951 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011921 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1250748 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011931&numberofmonths=24&showchangehistorylog=1 | 17-0011931 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 6641 | 20170121 | 912 | 1656099 | 3274 | Distribution Circuit | Vegetation | Tree - fell into line | 266 | 105470 | 37.0161 | -121.8161 | 5EO11321 | Overcast-Fog-32-90 F | Pole-Wood | Broken, wire on ground | 17-0011931 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Three Phase Fault | 1250758 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011934&numberofmonths=24&showchangehistorylog=1 | 17-0011934 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2202 | 182852202 | OCB | 22022 | 20170121 | 900 | 1656047 | 278 | Distribution Circuit | 3rd Party | Vehicle | 6011 | 190342 | 36.5786 | -121.9085 | ADORNIJUSTINc09091 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011934 | OH | Sus | 31297517 | yes | 2017 | JAN | Yes | Line to Ground | 1250762 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013047&numberofmonths=24&showchangehistorylog=1 | 17-0013047 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 9597 | 20170122 | 1057 | 1660473 | 193 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 965 | 37.1439 | -122.0899 | 7SPANSLOADSIDEOF9597 | Overcast-Drizzle-32-90 F | Conductor, Overhead | On Ground | 17-0013047 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1251867 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013142&numberofmonths=24&showchangehistorylog=1 | 17-0013142 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG TREES-0402 | 83050402 | FUSE | 12887 | 20170122 | 1222 | 1660882 | 1392 | Distribution Circuit | Vegetation | Tree - fell into line | 145 | 76914 | 37.0385 | -122.068 | TREETHROUGHLINE1SPANSOUTHOF3233 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013142 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1251955 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013194&numberofmonths=24&showchangehistorylog=1 | 17-0013194 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 11939 | 20170122 | 511 | 1658973 | 790 | Distribution Circuit | Vegetation | Tree - fell into line | 71 | 56090 | 37.0107 | -122.0443 | LDSD11939 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013194 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1252006 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013280&numberofmonths=24&showchangehistorylog=1 | 17-0013280 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 11943 | 20170122 | 533 | 1659036 | 708 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 21471 | 37.0113 | -122.0443 | 452YORKAVE | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013280 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1252094 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012713&numberofmonths=24&showchangehistorylog=1 | 17-0012713 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER | 10294 | 20170122 | 317 | 1658375 | 4998 | Distribution Circuit | Environmental/External | Flood/Erosion | 522 | 970726 | 37.0992 | -122.0531 | 1SPANLDSIDEOF102943SPANSLDSIDEOF10294 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | On Ground | 17-0012713 | OH | Sus | 42928924 | yes | 2017 | JAN | Yes | Line to Ground | 1251535 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012789&numberofmonths=24&showchangehistorylog=1 | 17-0012789 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER | 5146 | 20170122 | 511 | 1658985 | 2074 | Distribution Circuit | Vegetation | Tree - fell into line | 178 | 42876 | 37.0577 | -122.0595 | HOLLANDDONAVON55990328067701ZANANTERD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0012789 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Multi-Fault | 1251611 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012819&numberofmonths=24&showchangehistorylog=1 | 17-0012819 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER | 5020 | 20170122 | 546 | 1659127 | 1765 | Distribution Circuit | Vegetation | Tree - fell into line | 1079 | 87210 | 37.1024 | -121.9848 | NYSTROM10584087998799GlenwoodSOGlenwoodCutoff | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012819 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Multi-Fault | 1251641 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013302&numberofmonths=24&showchangehistorylog=1 | 17-0013302 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 10619 | 20170122 | 538 | 1659120 | 1942 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 5826 | 37.0765 | -122.0114 | 4SPLDSIDEOF10619 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013302 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1252114 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013343&numberofmonths=24&showchangehistorylog=1 | 17-0013343 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 11237 | 20170122 | 1100 | 1660485 | 3015 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 12060 | 37.0911 | -121.9633 | 4SPANSLOADSIDEOF11237 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013343 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1252158 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013656&numberofmonths=24&showchangehistorylog=1 | 17-0013656 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 335 | 20170122 | 546 | 1659121 | 1904 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3808 | 37.0558 | -121.9555 | 1SPANLDSIDEOF335 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | On Ground | 17-0013656 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1252466 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012600&numberofmonths=24&showchangehistorylog=1 | 17-0012600 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HATTON-1102 | 182291102 | RECLOSER | 2010 | 20170122 | 150 | 1658095 | 2376 | Distribution Circuit | Vegetation | Tree - fell into line | 123 | 195633 | 36.5061 | -121.9358 | HACUONGSONNYtreefellintoline8945 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012600 | OH | Sus | 31297011 | yes | 2017 | JAN | Yes | Line to Line | 1251422 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012709&numberofmonths=24&showchangehistorylog=1 | 17-0012709 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1101 | 182941101 | RECLOSER | 9640 | 20170122 | 346 | s1251532 | 747 | Distribution Circuit | Vegetation | Tree - branch fell on line | 292 | 41531 | 36.496 | -121.9369 | LDSIDESW473 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012709 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1251532 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013124&numberofmonths=24&showchangehistorylog=1 | 17-0013124 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1101 | 182941101 | FUSE | 2181 | 20170122 | 220 | 1660916 | 2155 | Distribution Circuit | Vegetation | Tree - fell into line | 83 | 175985 | 36.4895 | -121.9363 | 7SPANSLDSIDEOF2181 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013124 | OH | Sus | 31297011 | yes | 2017 | JAN | Yes | Line to Ground | 1251943 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013144&numberofmonths=24&showchangehistorylog=1 | 17-0013144 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | OTTER-1101 | 182941101 | TRIP-SAVER | 7611 | 20170122 | 248 | 1660992 | 2099 | Distribution Circuit | Vegetation | Tree - branch fell on line | 42 | 15055 | 36.3864 | -121.8708 | PALOCOLORADONEARMURRAYGRADEVICINITYOF38042PALOCOLORADO | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013144 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1251957 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013103&numberofmonths=24&showchangehistorylog=1 | 17-0013103 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1102 | 182941102 | FUSE | 40253 | 20170122 | 717 | 1660839 | 1807 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 7228 | 36.2418 | -121.7915 | 3SPANSLDSIDE40253 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013103 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1251922 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013162&numberofmonths=24&showchangehistorylog=1 | 17-0013162 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1102 | 182941102 | OTHER | 49899 | 20170122 | 1305 | 1660483 | 1673 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 6692 | 36.2305 | -121.757 | 4SPANSLOADSIDEOF49899 | Overcast-Drizzle-32-90 F | Connector or Splice (OH) | Broken, wire on object | 17-0013162 | OH | Sus | 31297011 | yes | 2017 | JAN | Yes | Line to Ground | 1251972 | CSO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013271&numberofmonths=24&showchangehistorylog=1 | 17-0013271 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE | 8353 | 20170122 | 557 | 1659272 | 1748 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 7052 | 37.0582 | -121.9417 | 2SOF5591 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013271 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1252085 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013395&numberofmonths=24&showchangehistorylog=1 | 17-0013395 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | PAUL SWEET-2109 | 83252109 | RECLOSER | 12946 | 20170122 | 1957 | 1662249 | 853 | Distribution Circuit | Vegetation | Tree - fell into line | 212 | 172388 | 36.9876 | -121.9185 | 1SPANLSOF7533 | Overcast-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on object | 17-0013395 | OH | Sus | 31297127 | yes | 2017 | JAN | Yes | Line to Line | 1252210 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012721&numberofmonths=24&showchangehistorylog=1 | 17-0012721 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | JUMPER | WIREDOWN3SEO5411 | 20170122 | 204 | 1658252 | 609 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 10353 | 37.0549 | -122.1615 | 3SEO5411 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012721 | OH | Sus | 31297127 | yes | 2017 | JAN | Yes | Force Out | 1251543 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012952&numberofmonths=24&showchangehistorylog=1 | 17-0012952 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | OTHER | WIREDOWN843CALABASAS | 20170122 | 626 | 1659254 | 2069 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 41425 | 36.9662 | -121.8285 | Klein5594766880843calabasasrd | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012952 | OH | Sus | 31297427 | yes | 2017 | JAN | Yes | Line to Ground | 1251772 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013074&numberofmonths=24&showchangehistorylog=1 | 17-0013074 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 5819 | 20170122 | 732 | 1660089 | 1693 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 93087 | 37.0447 | -121.8131 | 6SPANSLDSIDEOF5819 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013074 | OH | Sus | 42928924 | yes | 2017 | JAN | Yes | Line to Ground | 1251892 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013543&numberofmonths=24&showchangehistorylog=1 | 17-0013543 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 11835 | 20170122 | 1935 | 1662215 | 1865 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 26655 | 36.9832 | -121.8842 | 531HAYWARDRD | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013543 | OH | Sus | 31297127 | yes | 2017 | JAN | Yes | Line to Ground | 1252361 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012824&numberofmonths=24&showchangehistorylog=1 | 17-0012824 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 1489 | 20170122 | 554 | 1659143 | 429 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 4719 | 36.5665 | -121.9355 | 338017MILEDR | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012824 | OH | Sus | 42928578 | yes | 2017 | JAN | Yes | Line to Ground | 1251646 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013005&numberofmonths=24&showchangehistorylog=1 | 17-0013005 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 6071 | 20170122 | 657 | 1659369 | 256 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 4864 | 36.5797 | -121.9312 | RodriguezLou58092330361same | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | On Ground | 17-0013005 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1251826 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013085&numberofmonths=24&showchangehistorylog=1 | 17-0013085 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 6809 | 20170122 | 325 | 1658396 | 1805 | Distribution Circuit | Vegetation | Tree - branch fell on line | 180 | 148122 | 36.573 | -121.9271 | LOADSIDEOF7529 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0013085 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1251904 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013721&numberofmonths=24&showchangehistorylog=1 | 17-0013721 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 2309 | 20170122 | 654 | 1659355 | 1711 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 32509 | 36.5821 | -121.9201 | 5SPANSLDSIDEOF2309 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0013721 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1252516 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013021&numberofmonths=24&showchangehistorylog=1 | 17-0013021 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2203 | 182852203 | FUSE | 8559 | 20170122 | 343 | 1660358 | 978 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 10758 | 36.5693 | -121.9071 | RODRIQUEZELILoadsideofCO8559 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013021 | OH | Sus | 42928578 | yes | 2017 | JAN | Yes | Line to Line | 1251842 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013809&numberofmonths=24&showchangehistorylog=1 | 17-0013809 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | JUMPER | WIREDWN487ONMAINLINE | 20170123 | 1011 | 1663596 | 1866 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 77148 | 37.1051 | -122.0857 | WIREDWN487ONMAINLINE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013809 | OH | Sus | 31297127 | yes | 2017 | JAN | Yes | Line to Ground | 1252586 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013748&numberofmonths=24&showchangehistorylog=1 | 17-0013748 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 8241 | 20170123 | 1108 | 1663734 | 202 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 1616 | 37.1179 | -121.9647 | TURNIPSEEDPAULtapto16805Laurel | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0013748 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1252534 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0014213&numberofmonths=24&showchangehistorylog=1 | 17-0014213 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER | 5020 | 20170123 | 2215 | 1665069 | 1019 | Distribution Circuit | Environmental/External | Flood/Erosion | 1009 | 151850 | 37.1024 | -121.9848 | 6051FUCO | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0014213 | OH | Sus | 31297127 | yes | 2017 | JAN | Yes | Line to Ground | 1252962 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013627&numberofmonths=24&showchangehistorylog=1 | 17-0013627 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | LOS OSITOS-2103 | 182082103 | FUSE | 7697 | 20170123 | 751 | 1663095 | 575 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 8050 | 36.2095 | -121.2796 | TREETHROUGHLINE1SPANLDSIDEOFCUTOUTS | Clear-32-90 F | Conductor, Overhead | On Ground | 17-0013627 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Multi-Fault | 1252448 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013857&numberofmonths=24&showchangehistorylog=1 | 17-0013857 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | POINT MORETTI-1101 | 82931101 | FUSE | 5539 | 20170123 | 930 | 1663437 | 1720 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 3440 | 37.0722 | -122.2234 | 5539 | Clear-32-90 F | Footings, Tower or Pole | Broken, wire on object | 17-0013857 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1252628 | FP | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013798&numberofmonths=24&showchangehistorylog=1 | 17-0013798 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 125 | 20170123 | 1109 | 1663741 | 3156 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 80508 | 37.0114 | -121.9009 | 1LDSIDEOFMTR1K7583 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013798 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1252575 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013596&numberofmonths=24&showchangehistorylog=1 | 17-0013596 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2203 | 182852203 | FUSE | 7537 | 20170123 | 302 | 1662909 | 583 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 3010 | 36.572 | -121.9054 | 1LDSIDEOF7537 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013596 | OH | Sus | 42928578 | yes | 2017 | JAN | Yes | Line to Ground | 1252420 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018659&numberofmonths=24&showchangehistorylog=1 | 17-0018659 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5501 | 20170207 | 830 | 1678971 | 1827 | Distribution Circuit | Vegetation | Tree - fell into line | 142 | 92872 | 37.1432 | -122.1317 | MTR1008735802 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018659 | OH | Sus | 42939797 | yes | 2017 | FEB | Yes | Line to Ground | 1256427 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018045&numberofmonths=24&showchangehistorylog=1 | 17-0018045 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 5335 | 20170207 | 107 | 1677325 | 778 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 57572 | 37.0281 | -121.9871 | 710HAPPYVALLEYRD | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018045 | OH | Sus | 31304293 | yes | 2017 | FEB | Yes | Line to Ground | 1255898 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018264&numberofmonths=24&showchangehistorylog=1 | 17-0018264 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER | 33542 | 20170207 | 747 | 1678755 | 1646 | Distribution Circuit | Vegetation | Tree - fell into line | 522 | 194099 | 37.0905 | -122.0456 | SOLOMPICOSTEPDOWNFUCO5621 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018264 | OH | Sus | 31304215 | yes | 2017 | FEB | Yes | Line to Ground | 1256110 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018500&numberofmonths=24&showchangehistorylog=1 | 17-0018500 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER | B1101 | 20170207 | 1123 | 1679930 | 4520 | Distribution Circuit | Environmental/External | Flood/Erosion | 289 | 192265 | 37.0926 | -122.0966 | 4SPANSNOFREGSR60 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0018500 | OH | Sus | 31304215 | yes | 2017 | FEB | Yes | Line to Ground | 1256308 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018693&numberofmonths=24&showchangehistorylog=1 | 17-0018693 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 5151 | 20170207 | 1639 | 1680684 | 1410 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 8460 | 37.1109 | -122.0898 | 1LDSIDEOF5151 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018693 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1256448 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018748&numberofmonths=24&showchangehistorylog=1 | 17-0018748 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 6161 | 20170207 | 730 | 1679363 | 2071 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 41420 | 37.1182 | -122.0198 | 2SPANSONLDSIDEOF6161 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | On Ground | 17-0018748 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1256496 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018812&numberofmonths=24&showchangehistorylog=1 | 17-0018812 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 11929 | 20170207 | 1128 | 1680927 | 1657 | Distribution Circuit | Vegetation | Tree - fell into line | 78 | 128686 | 37.0999 | -122.0343 | MCKELLJAMES5spansloadsideof11929 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018812 | OH | Sus | 31304215 | yes | 2017 | FEB | Yes | Multi-Fault | 1256558 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018325&numberofmonths=24&showchangehistorylog=1 | 17-0018325 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 5901 | 20170207 | 130 | 1677332 | 1569 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 26673 | 37.0945 | -121.9715 | NYSTROM105840879987991005Tucker | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018325 | OH | Sus | 42939797 | yes | 2017 | FEB | Yes | Line to Ground | 1256160 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018388&numberofmonths=24&showchangehistorylog=1 | 17-0018388 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 7593 | 20170207 | 756 | 1679056 | 6047 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 57290 | 37.1058 | -121.9724 | 3SPANLDSIDEOF8239ATLINEANDBUCK | Overcast-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0018388 | OH | Sus | 31304215 | yes | 2017 | FEB | Yes | Line to Ground | 1256217 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018633&numberofmonths=24&showchangehistorylog=1 | 17-0018633 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | LAURELES-1111 | 182371111 | JUMPER | OJ1LDSIDEOF10705 | 20170207 | 1205 | 1680125 | 1662 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3324 | 36.3914 | -121.6287 | MTR1008448172 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018633 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1256403 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018675&numberofmonths=24&showchangehistorylog=1 | 17-0018675 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | LAURELES-1111 | 182371111 | JUMPER | WIREDOWNLDSIDEOF7521 | 20170207 | 849 | 1680627 | 1811 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1811 | 36.39 | -121.6317 | Sissom580820626173spansloadsideof7521 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018675 | OH | Sus | 31304264 | yes | 2017 | FEB | Yes | Line to Ground | 1256441 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018054&numberofmonths=24&showchangehistorylog=1 | 17-0018054 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | PAUL SWEET-2106 | 83252106 | FUSE | 7749 | 20170207 | 135 | 1677342 | 757 | Distribution Circuit | Environmental/External | Flood/Erosion | 102 | 52137 | 36.9978 | -121.9506 | 5951SS | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0018054 | OH | Sus | 42939835 | yes | 2017 | FEB | Yes | Line to Line | 1255908 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018120&numberofmonths=24&showchangehistorylog=1 | 17-0018120 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE | 10073 | 20170207 | 452 | 1677830 | 2748 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 10992 | 37.0602 | -121.9262 | 2SPANSLSOF10073 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018120 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1255982 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018699&numberofmonths=24&showchangehistorylog=1 | 17-0018699 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE | 8353 | 20170207 | 1043 | 1680242 | 1497 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 13473 | 37.0582 | -121.9417 | BRANDT417983121220885733OldSanJoseRd2ndspanpastCO8353 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018699 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1256453 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018795&numberofmonths=24&showchangehistorylog=1 | 17-0018795 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | POINT MORETTI-1101 | 82931101 | FUSE | 5995 | 20170207 | 1001 | 1679617 | 3185 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 22295 | 37.078 | -122.244 | 3TXFROMEOL | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018795 | OH | Sus | 31304215 | yes | 2017 | FEB | Yes | Line to Line | 1256539 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018273&numberofmonths=24&showchangehistorylog=1 | 17-0018273 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 5819 | 20170207 | 104 | 1678178 | 2380 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 140420 | 37.0447 | -121.8131 | MTR1007330338 | Overcast-Rain-32-90 F | Conductor, Overhead | On Ground | 17-0018273 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Multi-Fault | 1256116 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018528&numberofmonths=24&showchangehistorylog=1 | 17-0018528 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | FUSE | 3029 | 20170207 | 901 | 1679387 | 1849 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 83205 | 36.9644 | -121.8173 | MULTIPLELOCATIONS | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | On Ground | 17-0018528 | OH | Sus | 42939797 | yes | 2017 | FEB | Yes | Line to Ground | 1256323 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018743&numberofmonths=24&showchangehistorylog=1 | 17-0018743 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 6647 | 20170207 | 1428 | 1680508 | 3073 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 64533 | 37.0265 | -121.7798 | 2SPANSLDSIDEOF6647 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 17-0018743 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1256490 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018823&numberofmonths=24&showchangehistorylog=1 | 17-0018823 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | OTHER | WIREDOWNTWDMTR1006211444 | 20170207 | 2134 | 1681093 | 1162 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 16565 | 36.9996 | -121.8637 | 4SPANSONSINGLEPHASETAPLOADSIDE1003 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018823 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1256569 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018915&numberofmonths=24&showchangehistorylog=1 | 17-0018915 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 5781 | 20170207 | 1735 | 1680782 | 2450 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 24500 | 37.0448 | -121.8145 | 4SPANSLDSIDEOFCUTOUTWIREDOWNHOTTREEWIRE | Overcast-Drizzle-32-90 F | Conductor, Overhead | On Ground | 17-0018915 | OH | Sus | 42939797 | yes | 2017 | FEB | Yes | Force Out | 1256634 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0019368&numberofmonths=24&showchangehistorylog=1 | 17-0019368 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 6651 | 20170207 | 345 | 1682634 | 3613 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 18065 | 37.0219 | -121.7848 | WIREDOWN5SPANSLDSIDEOF6651 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019368 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1256924 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0019711&numberofmonths=24&showchangehistorylog=1 | 17-0019711 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE | 487 | 20170209 | 2123 | 1684190 | 2263 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 77561 | 37.1053 | -122.0857 | 1SPANLOADSIDE48710605LOVECREEK | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019711 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1257182 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0019614&numberofmonths=24&showchangehistorylog=1 | 17-0019614 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 8501 | 20170209 | 1557 | 1683829 | 1343 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 26860 | 37.1653 | -122.201 | 3SPANSSSOF8503TREETHROUGHLINEONMAINLINE | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | On Ground | 17-0019614 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Multi-Fault | 1257084 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0019521&numberofmonths=24&showchangehistorylog=1 | 17-0019521 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG TREES-0402 | 83050402 | OTHER | WIREDOWNLDSIDEMETER1008728481 | 20170209 | 1433 | 1683708 | 1580 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 12640 | 37.039 | -122.0639 | LDSIDEMETER1008728481 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019521 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1257019 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0019736&numberofmonths=24&showchangehistorylog=1 | 17-0019736 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 5587 | 20170209 | 2316 | 1684351 | 1116 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 8928 | 37.0672 | -122.0586 | 329ELALAMEIN | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019736 | OH | Sus | 42939797 | yes | 2017 | FEB | Yes | Line to Ground | 1257207 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0019626&numberofmonths=24&showchangehistorylog=1 | 17-0019626 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 7351 | 20170209 | 1351 | 1684110 | 1539 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3078 | 37.0557 | -121.978 | TREETHROUGHLINEFIRST3SPANSLDSIDEOF7351ONGROUND | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | On Ground | 17-0019626 | OH | Sus | 31304215 | yes | 2017 | FEB | Yes | Line to Ground | 1257097 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0019497&numberofmonths=24&showchangehistorylog=1 | 17-0019497 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 2705 | 20170209 | 1243 | 1683403 | 1457 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 6410 | 37.0005 | -121.7405 | TREETHROUGHLINEONHARDTAPFEEDING1898GREENVALLEYRD | Clear-32-90 F | Conductor, Overhead | On Ground | 17-0019497 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Multi-Fault | 1257005 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0019333&numberofmonths=24&showchangehistorylog=1 | 17-0019333 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 11739 | 20170209 | 824 | 1682868 | 1869 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 13083 | 37.0654 | -122.1258 | CAPWELL39158312061280355WILDIRISLN | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0019333 | OH | Sus | 31304215 | yes | 2017 | FEB | Yes | Line to Ground | 1256906 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0019710&numberofmonths=24&showchangehistorylog=1 | 17-0019710 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 6647 | 20170209 | 1953 | 1684134 | 4087 | Distribution Circuit | Environmental/External | Flood/Erosion | 21 | 60427 | 37.0265 | -121.7798 | RedwoodRdBrownSValleyRd | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019710 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1257181 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0019491&numberofmonths=24&showchangehistorylog=1 | 17-0019491 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2105 | 83692105 | RECLOSER | 71630 | 20170209 | 1751 | 1684021 | 41 | Distribution Circuit | Vegetation | Tree - fell into line | 582 | 20334 | 36.976 | -121.8947 | LDSIDEOF1181 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019491 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1257077 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0019632&numberofmonths=24&showchangehistorylog=1 | 17-0019632 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | RECLOSER | 5166 | 20170209 | 1957 | 1684137 | 1361 | Distribution Circuit | Vegetation | Tree - fell into line | 262 | 356582 | 36.9818 | -121.901 | CORDEIROM20326613368324626cathedraldr | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019632 | OH | Sus | 31304215 | yes | 2017 | FEB | Yes | Line to Line | 1257103 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0019718&numberofmonths=24&showchangehistorylog=1 | 17-0019718 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | RECLOSER | 5090 | 20170209 | 2345 | 1684103 | 1067 | Distribution Circuit | Vegetation | Tree - fell into line | 393 | 133534 | 36.9802 | -121.8922 | ATMTR1008989844ANDATFUSE11313 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019718 | OH | Sus | 42939797 | yes | 2017 | FEB | Yes | Line to Ground | 1257190 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0019731&numberofmonths=24&showchangehistorylog=1 | 17-0019731 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 1301 | 20170209 | 2345 | 1684396 | 655 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1965 | 36.9968 | -121.8858 | LOADSIDE1301 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019731 | OH | Sus | 31304215 | yes | 2017 | FEB | Yes | Line to Ground | 1257202 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0022158&numberofmonths=24&showchangehistorylog=1 | 17-0022158 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5435 | 20170217 | 959 | 1693717 | 3159 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 22113 | 37.1175 | -122.1214 | 12565BOULDERST | Partly Cloudy-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022158 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1259237 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0022552&numberofmonths=24&showchangehistorylog=1 | 17-0022552 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | OTHER | WIREDOWN5SPLDSD4533 | 20170217 | 1556 | 1697014 | 1540 | Distribution Circuit | Equipment Failure/Involved | Overhead | 270 | 38337 | 37.1773 | -122.0626 | STEVENSROBERT6POLESLOADSIDELCO453320215BEARCREEK | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022552 | OH | Sus | 31306421 | yes | 2017 | FEB | Yes | Open Circuit | 1259574 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023434&numberofmonths=24&showchangehistorylog=1 | 17-0023434 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG TREES-0402 | 83050402 | FUSE | 11967 | 20170217 | 1108 | 1694745 | 3135 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 97185 | 37.0289 | -122.0724 | LOADSIDE11967 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023434 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1260418 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0022411&numberofmonths=24&showchangehistorylog=1 | 17-0022411 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | SECTIONALIZER | 12013 | 20170217 | 955 | 1694253 | 815 | Distribution Circuit | Vegetation | Tree - fell into line | 1368 | 1114746 | 37.0177 | -122.0269 | DARBYSHIRE417783121220891600ELRANCHODRIVE | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022411 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1259453 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0022601&numberofmonths=24&showchangehistorylog=1 | 17-0022601 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | OTHER | WIREDOWNMTR1008453916 | 20170217 | 1319 | 1698177 | 5865 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 17251 | 37.0353 | -121.9998 | BRANDT41798312122088200BachelorRanchRdRedwoodfellthroughthelastspan | Heavy Rain-Strong Winds-Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022601 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Force Out | 1259623 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0022713&numberofmonths=24&showchangehistorylog=1 | 17-0022713 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | TRANSFORMER | 315479222480 | 20170217 | 1656 | 1697533 | 8145 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 8145 | 37.1068 | -122.0516 | STORMENT41788312780287340LenoreWayFelton | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022713 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1259729 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0022832&numberofmonths=24&showchangehistorylog=1 | 17-0022832 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER | 11010 | 20170217 | 848 | 1692567 | 4449 | Distribution Circuit | Vegetation | Tree - branch fell on line | 169 | 220685 | 37.1053 | -122.0518 | STORMENT4178831278028711101SequoiaAveFelton | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022832 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Multi-Fault | 1259850 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0021846&numberofmonths=24&showchangehistorylog=1 | 17-0021846 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER | 10718 | 20170217 | 717 | 1691347 | 6542 | Distribution Circuit | Vegetation | Tree - fell into line | 745 | 156896 | 37.0361 | -122.107 | CAPWELL391583120612807258EMPIREGRADE | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0021846 | OH | Sus | 42949498 | yes | 2017 | FEB | Yes | Line to Ground | 1258961 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0022966&numberofmonths=24&showchangehistorylog=1 | 17-0022966 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 3753 | 20170217 | 1711 | 1697612 | 7089 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 19017 | 37.0539 | -121.9528 | 2SPANSFROMEOL | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022966 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1259981 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0021790&numberofmonths=24&showchangehistorylog=1 | 17-0021790 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2104 | 182222104 | RECLOSER | 2624 | 20170217 | 500 | 1690890 | 9340 | Distribution Circuit | Vegetation | Tree - fell into line | 3187 | 5555655 | 36.569 | -121.7951 | FUSE3933281LAURELESGRADE25415HIDDENMESA3060CORRALDETIERRA | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0021790 | OH | Sus | 31306180 | yes | 2017 | FEB | Yes | Multi-Fault | 1258907 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023064&numberofmonths=24&showchangehistorylog=1 | 17-0023064 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HATTON-1102 | 182291102 | FUSE | 8937 | 20170217 | 1836 | 1699433 | 1171 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 57379 | 36.5031 | -121.9341 | 3SPANSSSOF8945 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023064 | OH | Sus | 31306180 | yes | 2017 | FEB | Yes | Line to Ground | 1260070 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023467&numberofmonths=24&showchangehistorylog=1 | 17-0023467 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HATTON-1102 | 182291102 | FUSE | 8245 | 20170217 | 804 | 1701693 | 3647 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 51902 | 36.4938 | -121.9342 | 2SPANSLOADSIDEOFOPENJUMPERS | Heavy Rain-Strong Winds-Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 17-0023467 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1260455 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023154&numberofmonths=24&showchangehistorylog=1 | 17-0023154 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | LAURELES-1111 | 182371111 | FUSE | 2943 | 20170217 | 631 | 1699372 | 4802 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 196882 | 36.4759 | -121.7193 | NEAR57CARMELVALLEYRDCARMELVLY | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0023154 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1260159 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0022220&numberofmonths=24&showchangehistorylog=1 | 17-0022220 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | LAURELES-1112 | 182371112 | FUSE | 435 | 20170217 | 552 | 1691210 | 1653 | Distribution Circuit | Vegetation | Tree - fell into line | 104 | 171912 | 36.5049 | -121.7621 | 1SPANLDOFSIDEOF435 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022220 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1259295 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0022660&numberofmonths=24&showchangehistorylog=1 | 17-0022660 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | LAURELES-1112 | 182371112 | FUSE | 7091 | 20170217 | 527 | 1692398 | 4754 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 57048 | 36.5107 | -121.7676 | 2SPANSSSOF6825 | Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022660 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1259684 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023841&numberofmonths=24&showchangehistorylog=1 | 17-0023841 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | LAURELES-1112 | 182371112 | FUSE | 6703 | 20170217 | 529 | 1691021 | 6099 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 36594 | 36.512 | -121.7692 | 2SPANSLDSIDEOF6703 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023841 | OH | Sus | 42949491 | yes | 2017 | FEB | Yes | Line to Ground | 1260823 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0022386&numberofmonths=24&showchangehistorylog=1 | 17-0022386 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1101 | 182941101 | FUSE | 2181 | 20170217 | 823 | 1696697 | 4788 | Distribution Circuit | Vegetation | Tree - fell into line | 83 | 309033 | 36.4895 | -121.9363 | 17MENTONERD | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0022386 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1259431 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0022705&numberofmonths=24&showchangehistorylog=1 | 17-0022705 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | OTTER-1101 | 182941101 | FUSE | 633 | 20170217 | 1548 | 1698474 | 2836 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 62392 | 36.4171 | -121.9132 | WIREDOWN8SPANLDSIDE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022705 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1259721 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0021827&numberofmonths=24&showchangehistorylog=1 | 17-0021827 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1102 | 182941102 | RECLOSER | 2002 | 20170217 | 649 | 1691384 | 2004 | Distribution Circuit | Vegetation | Tree - fell into line | 124 | 248406 | 36.2249 | -121.7589 | MFHIGHWAY1NONEPENTHES | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0021827 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1258941 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0021997&numberofmonths=24&showchangehistorylog=1 | 17-0021997 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1102 | 182941102 | SWITCH | 467 | 20170217 | 716 | 1691491 | 1924 | Distribution Circuit | Vegetation | Tree - fell into line | 364 | 684593 | 36.2958 | -121.8627 | 6SPSSOF2166TREEINTHELINEWIREDWN | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0021997 | OH | Sus | 31306180 | yes | 2017 | FEB | Yes | Line to Ground | 1259098 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023155&numberofmonths=24&showchangehistorylog=1 | 17-0023155 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2102 | 83252102 | FUSE | 11105 | 20170217 | 1306 | 1695836 | 5844 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 35064 | 37.0112 | -122.0751 | 2548EMPIREGRADE | Overcast-Rain-32-90 F | Conductor, Overhead | On Ground | 17-0023155 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1260160 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0021973&numberofmonths=24&showchangehistorylog=1 | 17-0021973 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | PAUL SWEET-2109 | 83252109 | FUSE | 6137 | 20170217 | 750 | 1691606 | 3621 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 155703 | 36.9729 | -121.9032 | 6137 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0021973 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1259076 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0021809&numberofmonths=24&showchangehistorylog=1 | 17-0021809 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | OTHER | WIREDOWNBETWEEN5413823 | 20170217 | 501 | 1691237 | 1896 | Distribution Circuit | Vegetation | Tree - fell into line | 296 | 149623 | 37.0442 | -122.1497 | STORMENT41788312780287Acrossfrom85PineFlatRdSC |  | Conductor, Overhead | On Ground | 17-0021809 | OH | Sus | 31306188 | yes | 2017 | FEB | Yes | Open Circuit | 1258925 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0022263&numberofmonths=24&showchangehistorylog=1 | 17-0022263 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 8511 | 20170217 | 1231 | 1695769 | 3506 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 49084 | 37.0618 | -122.1474 | CAPWELL39158312061280558WESTDALEDR | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0022263 | OH | Sus | 31306188 | yes | 2017 | FEB | Yes | Line to Ground | 1259336 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0022361&numberofmonths=24&showchangehistorylog=1 | 17-0022361 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 9827 | 20170217 | 1330 | 1696022 | 4272 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 136704 | 37.0799 | -122.1387 | CAPWELL39158312061280BEHIND64NICHOLSDR | Strong Winds-Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022361 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1259410 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0022567&numberofmonths=24&showchangehistorylog=1 | 17-0022567 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 7371 | 20170217 | 1633 | 1697398 | 102 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 510 | 37.0586 | -122.142 | 2SPLSOF7371 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022567 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1259589 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0021789&numberofmonths=24&showchangehistorylog=1 | 17-0021789 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | RESERVATION ROAD-1101 | 182731101 | RECLOSER | 3026 | 20170217 | 505 | 1690928 | 9195 | Distribution Circuit | Vegetation | Tree - fell into line | 706 | 2064974 | 36.5787 | -121.7199 | CALENDARKEN8316821739ManywiredownlocationsLSof3026 | Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0021789 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1258906 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0022014&numberofmonths=24&showchangehistorylog=1 | 17-0022014 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | FUSE | 3889 | 20170217 | 843 | 1692466 | 5929 | Distribution Circuit | Vegetation | Tree - bark fell into line | 70 | 25157 | 36.9487 | -121.8523 | MTR1008737010 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022014 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1259112 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0022724&numberofmonths=24&showchangehistorylog=1 | 17-0022724 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | RECLOSER | 10954 | 20170217 | 2147 | 1698528 | 1347 | Distribution Circuit | Vegetation | Tree - fell into line | 430 | 392418 | 36.9873 | -121.86 | FUCO3719ONMAINLINEMTR1010194710 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022724 | OH | Sus | 31306188 | yes | 2017 | FEB | Yes | Line to Ground | 1259740 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0022903&numberofmonths=24&showchangehistorylog=1 | 17-0022903 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | FUSE | 2199 | 20170217 | 825 | 1698735 | 4665 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 139950 | 36.9517 | -121.8341 | 2SPANSLSOF2199 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022903 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1259916 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023847&numberofmonths=24&showchangehistorylog=1 | 17-0023847 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 6647 | 20170217 | 901 | 1703506 | 5084 | Distribution Circuit | Environmental/External | Flood/Erosion | 8 | 40672 | 37.0265 | -121.7798 | 3SPANSLOADSIDEOF6647 | Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023847 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1260829 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024741&numberofmonths=24&showchangehistorylog=1 | 17-0024741 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 11305 | 20170217 | 901 | 1706770 | 5914 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 76882 | 37.0307 | -121.7864 | EOLFROM11305 | Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024741 | OH | Sus | 0 | yes | 2017 | FEB | Yes | None | 1261709 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023363&numberofmonths=24&showchangehistorylog=1 | 17-0023363 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2105 | 83692105 | FUSE | 8595 | 20170217 | 824 | 1692151 | 3174 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 136482 | 36.9661 | -121.8692 | 825LOMAPRIETADRBROKENPOLETOP | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0023363 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1260350 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023367&numberofmonths=24&showchangehistorylog=1 | 17-0023367 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 6121 | 20170217 | 828 | 1694719 | 3043 | Distribution Circuit | Vegetation | Tree - fell into line | 109 | 331687 | 36.9836 | -121.8848 | 750VALENCIARDAPTOS | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023367 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1260353 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023299&numberofmonths=24&showchangehistorylog=1 | 17-0023299 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | SAN BENITO-2104 | 182742104 | FUSE | 6773 | 20170217 | 1837 | 1698283 | 2659 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 231333 | 36.88 | -121.6403 | 714SEELY | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023299 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1260301 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0022126&numberofmonths=24&showchangehistorylog=1 | 17-0022126 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | SAN JUSTO-1101 | 183181101 | FUSE | 4245 | 20170217 | 938 | 1693433 | 4621 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 90909 | 36.8938 | -121.5973 | 1SPLDSIDEOF4263 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022126 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1259207 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023463&numberofmonths=24&showchangehistorylog=1 | 17-0023463 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | SAN JUSTO-1101 | 183181101 | FUSE | 4097 | 20170217 | 606 | 1701681 | 4834 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 19336 | 36.8008 | -121.4957 | AT4097TREEBROUGHTWIRESDOWNCUTOUTSDAMAGED | Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023463 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1260452 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023008&numberofmonths=24&showchangehistorylog=1 | 17-0023008 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 10717 | 20170218 | 1009 | 1699415 | 5988 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 50478 | 37.0914 | -122.1045 | CAPWELL39158312061280297HUBBARDGULCH | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023008 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1260024 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023150&numberofmonths=24&showchangehistorylog=1 | 17-0023150 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 11935 | 20170218 | 1613 | 1694376 | 1653 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 8265 | 37.056 | -121.9627 | 2SPANSLDSIDE11935 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023150 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1260156 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023082&numberofmonths=24&showchangehistorylog=1 | 17-0023082 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE | 2235 | 20170218 | 341 | 1698824 | 4932 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 83040 | 36.5753 | -121.8741 | 1SPANLDSIDEOF40299 | Heavy Rain-Strong Winds-Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023082 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1260087 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023210&numberofmonths=24&showchangehistorylog=1 | 17-0023210 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HOLLISTER-2106 | 182492106 | JUMPER | 50689 | 20170218 | 1853 | 1699622 | 2715 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 46155 | 36.7601 | -121.399 | WIREDOWNMTR172770 | Heavy Rain-Strong Winds-Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023210 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Open Circuit | 1260212 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023212&numberofmonths=24&showchangehistorylog=1 | 17-0023212 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | LAURELES-1112 | 182371112 | FUSE | 6899 | 20170218 | 1421 | 1700097 | 1248 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 12587 | 36.489 | -121.7223 | ONFIRSTHARDTAPLINELOADSIDE6899 | Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023212 | OH | Sus | 42949491 | yes | 2017 | FEB | Yes | Line to Ground | 1260214 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023391&numberofmonths=24&showchangehistorylog=1 | 17-0023391 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1102 | 182941102 | FUSE | 7791 | 20170218 | 1644 | 1701282 | 1492 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 20792 | 36.2641 | -121.7982 | 3SPANSLOADSIDEOF641 | Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023391 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1260375 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025083&numberofmonths=24&showchangehistorylog=1 | 17-0025083 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | FUSE | 2155 | 20170218 | 536 | 1698931 | 6401 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 25604 | 36.9518 | -121.841 | 4SPANSLOADSIDEOF2155 | Strong Winds-Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025083 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1262018 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0022988&numberofmonths=24&showchangehistorylog=1 | 17-0022988 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2204 | 182852204 | FUSE | 7567 | 20170218 | 620 | 1698967 | 720 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 13808 | 36.5783 | -121.9039 | 7567 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022988 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1260004 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023956&numberofmonths=24&showchangehistorylog=1 | 17-0023956 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | RECLOSER | 16010 | 20170220 | 1706 | 1704473 | 2784 | Distribution Circuit | Vegetation | Tree - fell into line | 137 | 343328 | 37.0886 | -122.0874 | METER1007009983 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023956 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1260928 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023976&numberofmonths=24&showchangehistorylog=1 | 17-0023976 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | SECTIONALIZER | 8655 | 20170220 | 1738 | 1704199 | 2788 | Distribution Circuit | Vegetation | Tree - fell into line | 178 | 262858 | 37.1402 | -122.0938 | SCADASw86554SPANSLSOF7219BET29538473 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023976 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1260948 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024742&numberofmonths=24&showchangehistorylog=1 | 17-0024742 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 9725 | 20170220 | 1732 | 1704944 | 2812 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 41414 | 37.1522 | -122.1366 | MTR1007328258 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024742 | OH | Sus | 42949498 | yes | 2017 | FEB | Yes | Line to Ground | 1261710 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025020&numberofmonths=24&showchangehistorylog=1 | 17-0025020 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 12069 | 20170220 | 1730 | 1704907 | 1581 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 52173 | 37.1239 | -122.1196 | LDSIDEOF12069 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | On Ground | 17-0025020 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1261971 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023764&numberofmonths=24&showchangehistorylog=1 | 17-0023764 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 8365 | 20170220 | 930 | 1703085 | 3162 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 91698 | 37.1667 | -122.2007 | 4SPANSLDSIDEOF8365 | Overcast-Heavy Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0023764 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1260755 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024995&numberofmonths=24&showchangehistorylog=1 | 17-0024995 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 9181 | 20170220 | 1651 | 1705811 | 3915 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 58725 | 37.2286 | -122.1481 | 13SPANSLOADSIDEOF9181 | Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024995 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1261952 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025057&numberofmonths=24&showchangehistorylog=1 | 17-0025057 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | TRIP-SAVER | 6219 | 20170220 | 1636 | 1704194 | 4137 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 91014 | 37.184 | -122.1409 | 1SPANLOADSIDEOF6219 | Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025057 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1261996 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025275&numberofmonths=24&showchangehistorylog=1 | 17-0025275 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 11995 | 20170220 | 1721 | 1704700 | 4164 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 33312 | 37.1783 | -122.1821 | BENTLEYSTEVE55947096822seperatelocationsBlakecompletingtags | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | On Ground | 17-0025275 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1262179 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023669&numberofmonths=24&showchangehistorylog=1 | 17-0023669 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG TREES-0402 | 83050402 | FUSE | 7299 | 20170220 | 602 | 1702505 | 603 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 7236 | 37.031 | -122.0941 | 1STSPANLSOF7299 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023669 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1260670 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024753&numberofmonths=24&showchangehistorylog=1 | 17-0024753 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 4567 | 20170220 | 1622 | 1704031 | 2808 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 16848 | 37.033 | -121.9869 | LOADSIDE4567 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024753 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1261721 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025235&numberofmonths=24&showchangehistorylog=1 | 17-0025235 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 4295 | 20170220 | 1658 | 1704416 | 3004 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 75100 | 37.033 | -122.0109 | ONTIVEROSR18832PNWOMTR1007854674 | Overcast-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0025235 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1262133 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023913&numberofmonths=24&showchangehistorylog=1 | 17-0023913 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 6087 | 20170220 | 1458 | 1703624 | 4146 | Distribution Circuit | Environmental/External | Flood/Erosion | 525 | 514596 | 37.0669 | -122.0336 | ATMETER1008515667 | Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023913 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1260889 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023930&numberofmonths=24&showchangehistorylog=1 | 17-0023930 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2104 | 83622104 | RECLOSER | 5096 | 20170220 | 1637 | 1704223 | 2476 | Distribution Circuit | Vegetation | Tree - fell into line | 340 | 318650 | 37.0511 | -122.037 | 5POLESLSOF151139 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023930 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1260903 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023885&numberofmonths=24&showchangehistorylog=1 | 17-0023885 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 5155 | 20170220 | 1450 | 1703589 | 1665 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 123210 | 37.0868 | -122.0887 | 2SPANLOADSIDE | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023885 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1260864 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023910&numberofmonths=24&showchangehistorylog=1 | 17-0023910 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER | 10912 | 20170220 | 1607 | 1703838 | 2903 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 84526 | 37.0913 | -122.096 | LSOF107174745 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023910 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1260886 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023971&numberofmonths=24&showchangehistorylog=1 | 17-0023971 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 8929 | 20170220 | 1603 | 1703886 | 2725 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 155325 | 37.0661 | -122.0844 | BENTLEYSTEVE5594709682Meter1008738989 | Overcast-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0023971 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1260943 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024011&numberofmonths=24&showchangehistorylog=1 | 17-0024011 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 5173 | 20170220 | 1550 | 1703807 | 3310 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 18440 | 37.1011 | -122.1017 | METER1008717339 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024011 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1260980 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024020&numberofmonths=24&showchangehistorylog=1 | 17-0024020 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | CAMP EVERS-2105 | 83622105 | FUSE | 2943 | 20170220 | 1526 | 1704440 | 1599 | Distribution Circuit | Vegetation | Tree - fell into line | 193 | 118579 | 37.0575 | -122.0764 | 2SPANSLSOF8805 | Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024020 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1260988 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024059&numberofmonths=24&showchangehistorylog=1 | 17-0024059 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 5185 | 20170220 | 1831 | 1705173 | 2709 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 56889 | 37.1075 | -122.1095 | 3SPANSLOADSIDEOF5185 | Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024059 | OH | Sus | 42949498 | yes | 2017 | FEB | Yes | Line to Ground | 1261025 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024073&numberofmonths=24&showchangehistorylog=1 | 17-0024073 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 5183 | 20170220 | 1631 | 1705165 | 2837 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 139013 | 37.108 | -122.1098 | 3SPANSLOADSIDEOF5183METER1008750394 | Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024073 | OH | Sus | 31306188 | yes | 2017 | FEB | Yes | Line to Line | 1261038 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024404&numberofmonths=24&showchangehistorylog=1 | 17-0024404 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | SECTIONALIZER | 10231 | 20170220 | 1651 | 1704367 | 1414 | Distribution Circuit | Equipment Failure/Involved | Overhead | 368 | 293972 | 37.0526 | -122.0575 | 5579 | Overcast-Heavy Rain-Strong Winds-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0024404 | OH | Sus | 42949498 | yes | 2017 | FEB | Yes | Line to Ground | 1261369 | CSO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024891&numberofmonths=24&showchangehistorylog=1 | 17-0024891 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 11929 | 20170220 | 1515 | 1707553 | 3113 | Distribution Circuit | Vegetation | Tree - fell into line | 98 | 305074 | 37.0999 | -122.0343 | 2spansNOEastCreekRdFelton | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024891 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1261865 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024894&numberofmonths=24&showchangehistorylog=1 | 17-0024894 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 5609 | 20170220 | 1515 | 1707556 | 3986 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 25557 | 37.0916 | -122.0438 | 3SPANSLSOF5609 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024894 | OH | Sus | 42949498 | yes | 2017 | FEB | Yes | Line to Ground | 1261867 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024935&numberofmonths=24&showchangehistorylog=1 | 17-0024935 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | CAMP EVERS-2105 | 83622105 | FUSE | 5233 | 20170220 | 1716 | 1704611 | 2739 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 65736 | 37.0577 | -122.0762 | NYSTROM105840879987996869SanLorenzoWay | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0024935 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1261909 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025037&numberofmonths=24&showchangehistorylog=1 | 17-0025037 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 5443 | 20170220 | 1804 | 1705171 | 2951 | Distribution Circuit | Environmental/External | Flood/Erosion | 6 | 17706 | 37.1106 | -122.1143 | ENDOF5443TAPLINE | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025037 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1261982 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023922&numberofmonths=24&showchangehistorylog=1 | 17-0023922 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER | 10718 | 20170220 | 1621 | 1704077 | 3174 | Distribution Circuit | Vegetation | Tree - fell into line | 486 | 783560 | 37.0361 | -122.107 | PASQUAMARK55956711461poleno4735sb660WILDIRISLN | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0023922 | OH | Sus | 42949498 | yes | 2017 | FEB | Yes | Line to Ground | 1260896 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025224&numberofmonths=24&showchangehistorylog=1 | 17-0025224 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 12895 | 20170220 | 2044 | 1706188 | 2716 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 13312 | 37.0888 | -121.9716 | 2SPANSLSOF12895 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025224 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1262123 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025282&numberofmonths=24&showchangehistorylog=1 | 17-0025282 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 6033 | 20170220 | 2020 | 1707804 | 2489 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 199120 | 37.081 | -122.0046 | 2SPANSLOADSIDE6033 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025282 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Open Circuit | 1262189 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025754&numberofmonths=24&showchangehistorylog=1 | 17-0025754 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE | 8555 | 20170220 | 1545 | 1703785 | 3021 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 12084 | 36.5673 | -121.8923 | PAST8555 | Overcast-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025754 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1262541 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024683&numberofmonths=24&showchangehistorylog=1 | 17-0024683 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2104 | 182222104 | OTHER | WIREDWN9213 | 20170220 | 1725 | 1704787 | 2901 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 54295 | 36.5746 | -121.8028 | WIREDWN9213 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024683 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1261649 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023864&numberofmonths=24&showchangehistorylog=1 | 17-0023864 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 2705 | 20170220 | 1319 | 1703355 | 115 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 2875 | 37.0005 | -121.7405 | 2EOF12349 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023864 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Three Phase Fault | 1260845 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025065&numberofmonths=24&showchangehistorylog=1 | 17-0025065 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 2667 | 20170220 | 1826 | 1705272 | 1613 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 9678 | 37.0261 | -121.775 | 2SPANSLSOF2667 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025065 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1262003 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025079&numberofmonths=24&showchangehistorylog=1 | 17-0025079 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 6483 | 20170220 | 1844 | 1705338 | 2589 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 28479 | 36.9898 | -121.7354 | 2SPANSLOADSIDEOF6483 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025079 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1262015 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023852&numberofmonths=24&showchangehistorylog=1 | 17-0023852 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HATTON-1102 | 182291102 | FUSE | 40419 | 20170220 | 1116 | 1703538 | 2012 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 74444 | 36.4908 | -121.9357 | BROKENPOLEAT457 | Partly Cloudy-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0023852 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1260834 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023853&numberofmonths=24&showchangehistorylog=1 | 17-0023853 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HATTON-1102 | 182291102 | FUSE | 8245 | 20170220 | 1115 | 1703542 | 2013 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 38247 | 36.4938 | -121.9342 | 2SPANSLDSIDEOFFUCO | Partly Cloudy-Heavy Rain-32-90 F | Conductor, Overhead | On Ground | 17-0023853 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Multi-Fault | 1260835 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024003&numberofmonths=24&showchangehistorylog=1 | 17-0024003 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HATTON-1102 | 182291102 | OCB | 2654 | 20170220 | 1748 | 1705142 | 1620 | Distribution Circuit | Vegetation | Tree - fell into line | 2752 | 2776086 | 36.5569 | -121.8976 | Sissom580820626173polesloadsideswitch475 | Overcast-Rain-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0024003 | OH | Sus | 31306180 | yes | 2017 | FEB | Yes | Line to Ground | 1260972 | CAW | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024074&numberofmonths=24&showchangehistorylog=1 | 17-0024074 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | LAURELES-1111 | 182371111 | RECLOSER | 2020 | 20170220 | 1900 | 1705434 | 1843 | Distribution Circuit | Vegetation | Tree - bark fell into line | 638 | 780630 | 36.4633 | -121.712 | GALLEGOSHENRY18181CachaguaRd | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0024074 | OH | Sus | 31306180 | yes | 2017 | FEB | Yes | Line to Ground | 1261039 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023933&numberofmonths=24&showchangehistorylog=1 | 17-0023933 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | LAURELES-1112 | 182371112 | FUSE | 407 | 20170220 | 1524 | 1703915 | 1259 | Distribution Circuit | Vegetation | Tree - branch fell on line | 170 | 214030 | 36.4868 | -121.7394 | 2SPANSLDSIDE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023933 | OH | Sus | 42949491 | yes | 2017 | FEB | Yes | Line to Line | 1260906 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024044&numberofmonths=24&showchangehistorylog=1 | 17-0024044 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | LAURELES-1112 | 182371112 | FUSE | 6891 | 20170220 | 1740 | 1705093 | 1334 | Distribution Circuit | Equipment Failure/Involved | Overhead | 133 | 177422 | 36.4832 | -121.7276 | SOURCESIDE9229 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024044 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1261011 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023801&numberofmonths=24&showchangehistorylog=1 | 17-0023801 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | OTTER-1101 | 182941101 | OCB | 11012 | 20170220 | 1237 | 1703213 | 6129 | Distribution Circuit | Equipment Failure/Involved | Overhead | 191 | 375767 | 36.3803 | -121.8988 | 2SPANSPAST6939ONMAINLINE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023801 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Force Out | 1260791 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025671&numberofmonths=24&showchangehistorylog=1 | 17-0025671 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | OTTER-1101 | 182941101 | FUSE | 8081 | 20170220 | 1953 | 1705762 | 5447 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 141622 | 36.3951 | -121.8792 | FUCO1279 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0025671 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1262484 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023848&numberofmonths=24&showchangehistorylog=1 | 17-0023848 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1102 | 182941102 | RECLOSER | 2166 | 20170220 | 728 | 1703510 | 4938 | Distribution Circuit | Vegetation | Tree - fell into line | 423 | 2085732 | 36.2769 | -121.8264 | 13SPANLOADSIDE2166 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023848 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1260830 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024820&numberofmonths=24&showchangehistorylog=1 | 17-0024820 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2102 | 83252102 | FUSE | 11103 | 20170220 | 2320 | 1706735 | 1251 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 40032 | 36.9936 | -122.0698 | 2SPLDSIDEOFFUCO8585 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0024820 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1261789 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023819&numberofmonths=24&showchangehistorylog=1 | 17-0023819 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | JUMPER | OJS4SPANSLOADSIDEOF5411 | 20170220 | 1320 | 1703353 | 118 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 118 | 37.0549 | -122.1631 | ENDOFTAPLINE4SPANSLOADSIDEOF5411 | Strong Winds-Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023819 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1260804 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023886&numberofmonths=24&showchangehistorylog=1 | 17-0023886 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | POINT MORETTI-1101 | 82931101 | RECLOSER | 12122 | 20170220 | 1523 | 1703714 | 3180 | Distribution Circuit | Vegetation | Tree - fell into line | 78 | 248040 | 37.0664 | -122.2286 | TREEWIRESDOWNNEARSWITCH5995 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023886 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1260865 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024598&numberofmonths=24&showchangehistorylog=1 | 17-0024598 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | POINT MORETTI-1101 | 82931101 | RECLOSER | 5078 | 20170220 | 1620 | 1704033 | 4109 | Distribution Circuit | Vegetation | Tree - fell into line | 296 | 444914 | 37.0315 | -122.1867 | NOF8527 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024598 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1261564 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024949&numberofmonths=24&showchangehistorylog=1 | 17-0024949 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | FUSE | 2751 | 20170220 | 1928 | 1705546 | 1308 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 24852 | 36.9691 | -121.8315 | GONZALES28108316821831EUCTOOKOUT2PHASESTHISADDRESS | Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024949 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1261920 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025305&numberofmonths=24&showchangehistorylog=1 | 17-0025305 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | FUSE | 9975 | 20170220 | 1800 | 1705140 | 4280 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 9698 | 36.9821 | -121.8291 | 2spansloadsideof9975 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025305 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1262213 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023808&numberofmonths=24&showchangehistorylog=1 | 17-0023808 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | RECLOSER | 5166 | 20170220 | 1243 | 1703277 | 2350 | Distribution Circuit | Vegetation | Tree - fell into line | 269 | 631989 | 36.9818 | -121.901 | BENTLEYSTEVE55947096825PLoadsideofLR5166 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0023808 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1260798 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025405&numberofmonths=24&showchangehistorylog=1 | 17-0025405 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 11327 | 20170220 | 2019 | 1708286 | 4106 | Distribution Circuit | Environmental/External | Flood/Erosion | 1 | 4106 | 36.9867 | -121.8847 | EOLPOLE | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0025405 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1262315 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023664&numberofmonths=24&showchangehistorylog=1 | 17-0023664 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | SAN BENITO-2104 | 182742104 | FUSE | 6773 | 20170220 | 506 | 1702455 | 679 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 7215 | 36.88 | -121.6403 | LINEFEEDINGMETER1008747807 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023664 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1260667 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023693&numberofmonths=24&showchangehistorylog=1 | 17-0023693 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | SAN BENITO-2104 | 182742104 | FUSE | 6773 | 20170220 | 713 | 1702729 | 776 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 8301 | 36.88 | -121.6403 | ATMETER1008751766 | Strong Winds-Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023693 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1260692 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024104&numberofmonths=24&showchangehistorylog=1 | 17-0024104 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | SAN BENITO-2104 | 182742104 | RECLOSER | 88772 | 20170220 | 2045 | 1705987 | 1412 | Distribution Circuit | Environmental/External | Flood/Erosion | 1237 | 428435 | 36.904 | -121.6087 | 1SPANWESTOFC336 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 17-0024104 | OH | Sus | 42949498 | yes | 2017 | FEB | Yes | Three Phase Fault | 1261068 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023796&numberofmonths=24&showchangehistorylog=1 | 17-0023796 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | SAN JUSTO-1101 | 183181101 | JUMPER | WIREDWN4SOF4091 | 20170220 | 836 | 1703223 | 1677 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 57018 | 36.7896 | -121.4718 | WIREDWN4SOF4091 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023796 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1260786 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023850&numberofmonths=24&showchangehistorylog=1 | 17-0023850 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | RECLOSER | 9698 | 20170220 | 1429 | 1703515 | 2925 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 65946 | 36.5726 | -121.9437 | MULTIPLESPANSWIREDOWNANDBROKENPOLEDUETOTREESSOF2799 | Overcast-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0023850 | OH | Sus | 31306180 | yes | 2017 | FEB | Yes | Line to Ground | 1260832 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023965&numberofmonths=24&showchangehistorylog=1 | 17-0023965 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | SECTIONALIZER | 40017 | 20170220 | 1719 | 1704739 | 2973 | Distribution Circuit | Vegetation | Tree - fell into line | 73 | 115808 | 36.5815 | -121.9256 | RAPADASANTHONY3200LOPEZRD5NO912709 | Overcast-Drizzle-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0023965 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1260937 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024025&numberofmonths=24&showchangehistorylog=1 | 17-0024025 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2202 | 182852202 | FUSE | 8021 | 20170220 | 1615 | 1703988 | 2895 | Distribution Circuit | Vegetation | Tree - fell into line | 84 | 168930 | 36.5868 | -121.9096 | ATMETER1008229979 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024025 | OH | Sus | 31306180 | yes | 2017 | FEB | Yes | Line to Ground | 1260994 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024037&numberofmonths=24&showchangehistorylog=1 | 17-0024037 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2202 | 182852202 | OCB | 22022 | 20170220 | 1905 | 1705431 | 492 | Distribution Circuit | Vegetation | Tree - fell into line | 2283 | 1090928 | 36.5786 | -121.9085 | 4SPANSSOURCE85904TWD40743 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024037 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1261005 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025423&numberofmonths=24&showchangehistorylog=1 | 17-0025423 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2202 | 182852202 | FUSE | 9127 | 20170220 | 1949 | 1705735 | 3160 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 37920 | 36.604 | -121.9361 | 1SPANSOURCESIDEOFENDOFLINE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025423 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1262333 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024024&numberofmonths=24&showchangehistorylog=1 | 17-0024024 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2203 | 182852203 | FUSE | 1445 | 20170220 | 1808 | 1705198 | 2947 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 29470 | 36.5735 | -121.9107 | ifomtr1009279225 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024024 | OH | Sus | 31306180 | yes | 2017 | FEB | Yes | Three Phase Fault | 1260993 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025453&numberofmonths=24&showchangehistorylog=1 | 17-0025453 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2203 | 182852203 | FUSE | 10421 | 20170220 | 2023 | 1708955 | 3127 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 34165 | 36.5659 | -121.9347 | TREEDOWNONHARDTAPFEEDINGMTR1009436722 | Overcast-Strong Winds-32-90 F | Conductor, Overhead | On Ground | 17-0025453 | OH | Sus | 31306180 | yes | 2017 | FEB | Yes | Multi-Fault | 1262353 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024868&numberofmonths=24&showchangehistorylog=1 | 17-0024868 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2204 | 182852204 | FUSE | 55781 | 20170220 | 1915 | 1706204 | 2561 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 120367 | 36.6018 | -121.9374 | 4SPANLOADSIDE | Overcast-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024868 | OH | Sus | 31306180 | yes | 2017 | FEB | Yes | Line to Ground | 1261840 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025477&numberofmonths=24&showchangehistorylog=1 | 17-0025477 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2204 | 182852204 | JUMPER | OJONHARDTAPFEEDINGMTR1008554001 | 20170220 | 1607 | 1710290 | 3106 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 3106 | 36.5763 | -121.8976 | MTR1008554001 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | On Ground | 17-0025477 | OH | Sus | 42949491 | yes | 2017 | FEB | Yes | Line to Ground | 1262374 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025481&numberofmonths=24&showchangehistorylog=1 | 17-0025481 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2204 | 182852204 | OTHER | WIREDOWNSSOF9559 | 20170220 | 1607 | 1710298 | 2978 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 3942 | 36.5758 | -121.8954 | 1SPANSS9559 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025481 | OH | Sus | 42949491 | yes | 2017 | FEB | Yes | Line to Line | 1262376 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025257&numberofmonths=24&showchangehistorylog=1 | 17-0025257 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE | 6295 | 20170221 | 325 | 1709172 | 2387 | Distribution Circuit | Vegetation | Tree - branch fell on line | 115 | 75425 | 37.0992 | -122.0867 | 6295 | Overcast-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0025257 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1262158 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025105&numberofmonths=24&showchangehistorylog=1 | 17-0025105 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5487 | 20170221 | 28 | 1707470 | 765 | Distribution Circuit | Equipment Failure/Involved | Overhead | 56 | 42840 | 37.1371 | -122.1006 | ATMETER1009696039 | Heavy Rain-Strong Winds-32-90 F | Insulator | Broken, wire on object | 17-0025105 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1262031 | INS | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025377&numberofmonths=24&showchangehistorylog=1 | 17-0025377 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 2323 | 20170221 | 1240 | 1704677 | 3053 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 4141 | 37.1746 | -122.1383 | BLAKEGREG55924600743PLDSIDEOF2323 | Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025377 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1262286 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024911&numberofmonths=24&showchangehistorylog=1 | 17-0024911 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 5329 | 20170221 | 744 | 1704296 | 440 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 27720 | 37.0179 | -121.9973 | 5SPANSLOADSIDEOF5329 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024911 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Three Phase Fault | 1261886 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025313&numberofmonths=24&showchangehistorylog=1 | 17-0025313 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 3979 | 20170221 | 1936 | 1709418 | 1193 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 25053 | 37.021 | -122.0097 | Whitney20345970961nearmtr1007588486 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025313 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1262222 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025221&numberofmonths=24&showchangehistorylog=1 | 17-0025221 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | JUMPER | WIREDOWN2SPEOF7199 | 20170221 | 737 | 1709006 | 3473 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 14867 | 37.1116 | -122.0476 | 2SPANSEOF7199 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025221 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1262120 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025274&numberofmonths=24&showchangehistorylog=1 | 17-0025274 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 9247 | 20170221 | 323 | 1709254 | 2257 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 41975 | 37.0897 | -122.0448 | METER350696 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025274 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1262178 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025283&numberofmonths=24&showchangehistorylog=1 | 17-0025283 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 9259 | 20170221 | 319 | 1709351 | 3731 | Distribution Circuit | Vegetation | Tree - fell into line | 412 | 1345108 | 37.099 | -122.053 | BOYNTON34598313316620LOMPICORDSTEPDOWN | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025283 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1262190 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025570&numberofmonths=24&showchangehistorylog=1 | 17-0025570 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | OTHER | WIREDOWN1SPLDSIDEOFMTR1008739291 | 20170221 | 319 | 1710608 | 3336 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 32764 | 37.1018 | -122.0557 | 1SPANLDSIDEOFMTR1008739291 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025570 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1262423 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025114&numberofmonths=24&showchangehistorylog=1 | 17-0025114 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | CAMP EVERS-2106 | 83622106 | RECLOSER | 12760 | 20170221 | 1256 | 1708585 | 1837 | Distribution Circuit | Vegetation | Tree - fell into line | 546 | 156387 | 37.0676 | -121.9966 | TURNIPSEEDPAULloc115211581VineHillloc2465QuailRidgeRd | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025114 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1262036 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024835&numberofmonths=24&showchangehistorylog=1 | 17-0024835 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2104 | 182222104 | FUSE | 54071 | 20170221 | 245 | 1704578 | 2293 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2293 | 36.5676 | -121.7769 | 2LDSIDEOF54071 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024835 | OH | Sus | 31306180 | yes | 2017 | FEB | Yes | Line to Line | 1261804 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025137&numberofmonths=24&showchangehistorylog=1 | 17-0025137 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 7807 | 20170221 | 29 | 1706890 | 3602 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 61234 | 36.9884 | -121.7395 | WIRE5SPANSLDSIDEOF7807 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025137 | OH | Sus | 31306188 | yes | 2017 | FEB | Yes | Line to Line | 1262056 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025243&numberofmonths=24&showchangehistorylog=1 | 17-0025243 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | LAURELES-1111 | 182371111 | FUSE | 8643 | 20170221 | 1652 | 1709104 | 1464 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 19032 | 36.4803 | -121.7131 | 3SPANSLOADSIDEOF8643 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025243 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1262142 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025248&numberofmonths=24&showchangehistorylog=1 | 17-0025248 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | LAURELES-1111 | 182371111 | TRIP-SAVER | 6421 | 20170221 | 1657 | 1709110 | 1077 | Distribution Circuit | Vegetation | Tree - branch fell on line | 30 | 32310 | 36.4545 | -121.6954 | SPANLOADSIDE6421 | Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025248 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1262147 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025218&numberofmonths=24&showchangehistorylog=1 | 17-0025218 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2104 | 83252104 | SWITCH | 1867 | 20170221 | 1617 | 1708985 | 1406 | Distribution Circuit | Vegetation | Tree - branch fell on line | 142 | 199652 | 37.01 | -121.9647 | BETWEEN15338203 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025218 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1262118 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025965&numberofmonths=24&showchangehistorylog=1 | 17-0025965 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | POINT MORETTI-1101 | 82931101 | FUSE | 5043 | 20170221 | 930 | 1711917 | 3345 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 10035 | 37.0607 | -122.226 | 2SPANSLSOF5043 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025965 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1262733 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025073&numberofmonths=24&showchangehistorylog=1 | 17-0025073 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 4431 | 20170221 | 1140 | 1707685 | 1907 | Distribution Circuit | Environmental/External | Flood/Erosion | 109 | 207863 | 37.0195 | -121.8182 | 5871 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025073 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Force Out | 1262010 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025238&numberofmonths=24&showchangehistorylog=1 | 17-0025238 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | SAN JUSTO-1101 | 183181101 | SWITCH | 9975 | 20170221 | 1628 | 1708878 | 1478 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 32516 | 36.764 | -121.4796 | VALLEJOCRAIG5polesloadsdieof9975 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025238 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1262136 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025061&numberofmonths=24&showchangehistorylog=1 | 17-0025061 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2203 | 182852203 | JUMPER | WIREDOWN1SPANLDSIDEOF2143 | 20170221 | 1121 | 1708345 | 1818 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 5454 | 36.5677 | -121.9294 | WIREDOWN1SPANLDSIDEOF2143 | Partly Cloudy-32-90 F | Conductor, Overhead | On Ground | 17-0025061 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Multi-Fault | 1262000 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025446&numberofmonths=24&showchangehistorylog=1 | 17-0025446 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 5151 | 20170222 | 828 | 1710127 | 598 | Distribution Circuit | Environmental/External | Flood/Erosion | 6 | 3588 | 37.1109 | -122.0898 | LDSIDEOF5151 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025446 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1262347 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025704&numberofmonths=24&showchangehistorylog=1 | 17-0025704 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 4731 | 20170222 | 1536 | 1710998 | 204 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 816 | 37.0923 | -122.0759 | BLAKEGREG559246007410228NEWELLCREEKRD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025704 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1262507 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025876&numberofmonths=24&showchangehistorylog=1 | 17-0025876 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 11929 | 20170222 | 2308 | 1711488 | 1002 | Distribution Circuit | Vegetation | Tree - fell into line | 98 | 98196 | 37.0999 | -122.0343 | 7spannof11929 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025876 | OH | Sus | 42949498 | yes | 2017 | FEB | Yes | Line to Line | 1262675 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025575&numberofmonths=24&showchangehistorylog=1 | 17-0025575 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 8361 | 20170222 | 1148 | 1710593 | 581 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 7553 | 37.0764 | -122.1319 | 2NDTXFROMEOL | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025575 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1262425 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025936&numberofmonths=24&showchangehistorylog=1 | 17-0025936 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | JUMPER | OJMTR1008725926 | 20170222 | 1638 | 1711090 | 1377 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 13770 | 37.0807 | -122.144 | 750COMSTOCKRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025936 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1262715 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025769&numberofmonths=24&showchangehistorylog=1 | 17-0025769 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | FUSE | 4243 | 20170222 | 1801 | 1711260 | 1388 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 12492 | 36.9944 | -121.8462 | SCOTTDAVE21036613420822SAME | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025769 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1262556 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025710&numberofmonths=24&showchangehistorylog=1 | 17-0025710 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 7563 | 20170222 | 1543 | 1711006 | 332 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 332 | 36.9939 | -121.8962 | 1SPANLSOF7563 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025710 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1262511 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037586&numberofmonths=24&showchangehistorylog=1 | 17-0037586 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER | 11062 | 20170407 | 447 | 1749433 | 1980 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 50340 | 37.1989 | -122.1537 | STORMENT41788312780287WalkinoffHwy9bySw5999BC | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037586 | OH | Sus | 42984110 | yes | 2017 | APR | Yes | Line to Ground | 1271810 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037547&numberofmonths=24&showchangehistorylog=1 | 17-0037547 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 6087 | 20170407 | 303 | 1749043 | 711 | Distribution Circuit | Vegetation | Tree - branch fell on line | 326 | 79963 | 37.0669 | -122.0336 | ATMTR1007855481 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037547 | OH | Sus | 42984110 | yes | 2017 | APR | Yes | Multi-Fault | 1271767 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0038071&numberofmonths=24&showchangehistorylog=1 | 17-0038071 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 6161 | 20170407 | 1538 | 1751184 | 1425 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 28500 | 37.1182 | -122.0198 | 9POLESLDSIDE6161 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 17-0038071 | OH | Sus | 31316813 | yes | 2017 | APR | Yes | Line to Ground | 1272136 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0038119&numberofmonths=24&showchangehistorylog=1 | 17-0038119 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 6045 | 20170407 | 1604 | 1751262 | 1636 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 93252 | 37.097 | -121.9748 | 565TUCKERRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0038119 | OH | Sus | 42984110 | yes | 2017 | APR | Yes | Line to Line | 1272178 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037521&numberofmonths=24&showchangehistorylog=1 | 17-0037521 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2104 | 182222104 | FUSE | 2811 | 20170407 | 223 | 1747995 | 677 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 12186 | 36.5151 | -121.8129 | 1008348331ATMETER | Overcast-Fog-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037521 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1271738 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037604&numberofmonths=24&showchangehistorylog=1 | 17-0037604 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HATTON-1102 | 182291102 | FUSE | 1491 | 20170407 | 49 | 1749516 | 838 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 34358 | 36.5058 | -121.9351 | IFOMTR1008580367 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | On Ground | 17-0037604 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Line | 1271832 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037796&numberofmonths=24&showchangehistorylog=1 | 17-0037796 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2202 | 182852202 | OTHER | WIREDOWN1SSOFR813 | 20170407 | 628 | 1750338 | 546 | Distribution Circuit | Vegetation | Tree - branch fell on line | 198 | 59160 | 36.5756 | -121.9505 | 1SSOFR813 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037796 | OH | Sus | 42984159 | yes | 2017 | APR | Yes | Line to Ground | 1271968 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0056107&numberofmonths=24&showchangehistorylog=1 | 17-0056107 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | FELTON-0401 | 83140401 | OTHER | WIREDOWNLDSDFCO121 | 20170618 | 1315 | 1807762 | 685 | Distribution Circuit | Vegetation | Tree - fell into line | 1915 | 180924 | 37.0513 | -122.069 | STORMENT41788312780287CoveredBridgeRdGrahamHillRdFelton | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0056107 | OH | Sus | 0 | yes | 2017 | JUN | Yes | Open Circuit | 1285591 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0075541&numberofmonths=24&showchangehistorylog=1 | 17-0075541 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 9005 | 20170903 | 735 | 1867841 | 1091 | Distribution Circuit | Vegetation | Tree - branch fell on line | 22 | 24002 | 37.0318 | -122.1371 | 10SPANLOADSIDE9005 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0075541 | OH | Sus | 0 | yes | 2017 | SEP | Yes | Line to Line | 1299822 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0075732&numberofmonths=24&showchangehistorylog=1 | 17-0075732 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 1301 | 20170903 | 2113 | 1869254 | 1098 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 3294 | 36.9968 | -121.8858 | BOYNTON345983133166202225TROUTGULCHRD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0075732 | OH | Sus | 31348848 | yes | 2017 | SEP | Yes | Line to Line | 1300013 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0077860&numberofmonths=24&showchangehistorylog=1 | 17-0077860 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | GABILAN-1101 | 182331101 | JUMPER | WIREDOWN1SSOF25027 | 20170911 | 1751 | 1875982 | 436 | Distribution Circuit | Environmental/External | Lightning | 36 | 13596 | 36.7978 | -121.5704 | 25027 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0077860 | OH | Sus | 0 | yes | 2017 | SEP | Yes | Open Circuit | 1301626 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0077544&numberofmonths=24&showchangehistorylog=1 | 17-0077544 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | OTHER | WIREDOWNMTR100926211 | 20170911 | 626 | 1875124 | 404 | Distribution Circuit | Vegetation | Tree - branch fell on line | 69 | 19830 | 37.0676 | -122.1271 | MTR100926211 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0077544 | OH | Sus | 0 | yes | 2017 | SEP | Yes | Line to Ground | 1301416 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0085312&numberofmonths=24&showchangehistorylog=1 | 17-0085312 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | TRIP-SAVER | 6577 | 20171008 | 2151 | 1893977 | 559 | Distribution Circuit | Equipment Failure/Involved | Overhead | 48 | 26832 | 37.048 | -121.8081 | 2115EurekaCanyon | Clear-32-90 F | Insulator | Broken, wire on object | 17-0085312 | OH | Sus | 43169679 | yes | 2017 | OCT | Yes | Line to Ground | 1306761 | INS | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0085482&numberofmonths=24&showchangehistorylog=1 | 17-0085482 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 7593 | 20171009 | 131 | 1894906 | 984 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 50249 | 37.1058 | -121.9724 | 1polessmtr1010153048 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085482 | OH | Sus | 31355742 | yes | 2017 | OCT | Yes | Line to Ground | 1306943 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0089038&numberofmonths=24&showchangehistorylog=1 | 17-0089038 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | JUMPER | WIREDOWNMTR1007590728 | 20171020 | 715 | 1905815 | 433 | Distribution Circuit | Equipment Failure/Involved | Overhead | 36 | 9010 | 37.1392 | -122.1515 | WIREDOWNMTR1007590728 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0089038 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Open Circuit | 1309604 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0089318&numberofmonths=24&showchangehistorylog=1 | 17-0089318 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 8501 | 20171020 | 412 | 1906576 | 2175 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 43500 | 37.1653 | -122.201 | 15LSOF8501 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0089318 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1309798 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0088877&numberofmonths=24&showchangehistorylog=1 | 17-0088877 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | FELTON-0401 | 83140401 | JUMPER | WIREDOWN519075 | 20171020 | 313 | 1905181 | 408 | Distribution Circuit | Vegetation | Tree - fell into line | 1912 | 52596 | 37.0326 | -122.0904 | 519075 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0088877 | OH | Sus | 43198596 | yes | 2017 | OCT | Yes | Line to Ground | 1309456 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0088903&numberofmonths=24&showchangehistorylog=1 | 17-0088903 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | SAN BENITO-2104 | 182742104 | RECLOSER | 88772 | 20171020 | 440 | 1905242 | 339 | Distribution Circuit | 3rd Party | Vehicle | 135 | 37765 | 36.904 | -121.6087 | 13polesloadside2719 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 17-0088903 | OH | Sus | 31361694 | yes | 2017 | OCT | Yes | Line to Ground | 1309484 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0099694&numberofmonths=24&showchangehistorylog=1 | 17-0099694 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | RECLOSER | 5028 | 20171204 | 1352 | 1935401 | 494 | Distribution Circuit | Vegetation | Tree - fell into line | 2200 | 442980 | 37.1284 | -122.1222 | NYSTROMERIK105840879987993spansloadsideofLcos9779 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0099694 | OH | Sus | 0 | yes | 2017 | DEC | Yes | Line to Ground | 1317458 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0099716&numberofmonths=24&showchangehistorylog=1 | 17-0099716 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER | 96986 | 20171204 | 1359 | 1935552 | 1604 | Distribution Circuit | Vegetation | Tree - fell into line | 750 | 355891 | 37.1987 | -122.1536 | NYSTROMERIK1058408799879915930Hwy9 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0099716 | OH | Sus | 0 | yes | 2017 | DEC | Yes | Line to Line | 1317474 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0099755&numberofmonths=24&showchangehistorylog=1 | 17-0099755 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 2161 | 20171204 | 1444 | 1935590 | 664 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2656 | 36.9968 | -121.7383 | 4LDSIDEOF2161 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0099755 | OH | Sus | 0 | yes | 2017 | DEC | Yes | Line to Ground | 1317502 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0099837&numberofmonths=24&showchangehistorylog=1 | 17-0099837 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 5415 | 20171204 | 1927 | 1936047 | 463 | Distribution Circuit | Equipment Failure/Involved | Overhead | 61 | 28243 | 37.0632 | -122.1475 | 222ICECREAMGRADERD | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0099837 | OH | Sus | 0 | yes | 2017 | DEC | Yes | Line to Ground | 1317579 | CSO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0102088&numberofmonths=24&showchangehistorylog=1 | 17-0102088 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER | 12758 | 20171216 | 1225 | 1944818 | 1396 | Distribution Circuit | Vegetation | Tree - fell into line | 295 | 28283 | 37.1486 | -122.1748 | 3017 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0102088 | OH | Sus | 0 | yes | 2017 | DEC | Yes | Line to Line | 1319999 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0102009&numberofmonths=24&showchangehistorylog=1 | 17-0102009 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 6161 | 20171216 | 919 | 1944344 | 683 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 14343 | 37.1182 | -122.0198 | 6POLESLOADSIDE6161 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0102009 | OH | Sus | 1370082 | yes | 2017 | DEC | Yes | Line to Ground | 1319919 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0101957&numberofmonths=24&showchangehistorylog=1 | 17-0101957 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER | 12518 | 20171216 | 935 | 1944224 | 1352 | Distribution Circuit | Vegetation | Tree - fell into line | 527 | 38602 | 37.079 | -122.0037 | NYSTROMERIK10584087998799365EagleCrest | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0101957 | OH | Sus | 31370082 | yes | 2017 | DEC | Yes | Line to Ground | 1319870 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0102065&numberofmonths=24&showchangehistorylog=1 | 17-0102065 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 11737 | 20171216 | 931 | 1944249 | 570 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 6946 | 37.0698 | -122.1303 | 701SunlitLane | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0102065 | OH | Sus | 0 | yes | 2017 | DEC | Yes | Line to Ground | 1319975 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0023410&numberofmonths=24&showchangehistorylog=1 | 18-0023410 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE | 9125 | 20180316 | 1202 | 45737 | 334 | Distribution Circuit | Vegetation | Tree - branch fell on line | 42 | 8196 | 37.1005 | -122.086 | 1LOADSIDEfuse5149 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023410 | OH | Sus | 43302840 | yes | 2018 | MAR | Yes | Line to Ground | 1336273 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0023295&numberofmonths=24&showchangehistorylog=1 | 18-0023295 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 2705 | 20180316 | 629 | 45299 | 249 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 3924 | 37.0005 | -121.7405 | 2SPANSLOADSIDECO2705 | Partly Cloudy-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023295 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1336191 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0023231&numberofmonths=24&showchangehistorylog=1 | 18-0023231 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | FUSE | 7989 | 20180316 | 205 | 45189 | 678 | Distribution Circuit | Vegetation | Tree - branch fell on line | 263 | 73608 | 36.9817 | -121.8645 | 3100VALENCIARD | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023231 | OH | Sus | 43301937 | yes | 2018 | MAR | Yes | Line to Ground | 1336139 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0064531&numberofmonths=24&showchangehistorylog=1 | 18-0064531 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | LAURELES-1111 | 182371111 | FUSE | 6625 | 20180728 | 108 | 142200 | 688 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 19264 | 36.376 | -121.5912 | 1SPANLDSIDEOF6625 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0064531 | OH | Sus | 43422806 | No | 2018 | JUL | Yes | Line to Line | 1367297 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0098292&numberofmonths=24&showchangehistorylog=1 | 18-0098292 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 4355 | 20181108 | 1202 | 211662 | 470 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 10810 | 37.0602 | -122.064 | 7050MCADAMSLN | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0098292 | OH | Sus | 43534781 | yes | 2018 | NOV | Yes | Line to Ground | 1391471 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0098270&numberofmonths=24&showchangehistorylog=1 | 18-0098270 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | LAURELES-1111 | 182371111 | FUSE | 2949 | 20181108 | 1239 | 211702 | 89 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 848 | 51106 | 36.4414 | -121.6437 | 34000CARMELVALLEYRD | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 18-0098270 | OH | Sus | 0 | yes | 2018 | NOV | Yes | Line to Ground | 1391460 | CSO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0101851&numberofmonths=24&showchangehistorylog=1 | 18-0101851 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 10717 | 20181121 | 1051 | 219955 | 634 | Distribution Circuit | Vegetation | Tree - branch fell on line | 26 | 16484 | 37.0914 | -122.1045 | ATCOUTS10719 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0101851 | OH | Sus | 43584947 | yes | 2018 | NOV | Yes | Multi-Fault | 1394071 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0102192&numberofmonths=24&showchangehistorylog=1 | 18-0102192 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE | 5977 | 20181121 | 1541 | 220657 | 570 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 5700 | 37.0319 | -121.947 | 3PSOURCESIDEOFMTR1008735930 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0102192 | OH | Sus | 0 | yes | 2018 | NOV | Yes | Line to Ground | 1394329 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0101966&numberofmonths=24&showchangehistorylog=1 | 18-0101966 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | POINT MORETTI-1101 | 82931101 | RECLOSER | 5076 | 20181121 | 1505 | 220593 | 4167 | Distribution Circuit | Equipment Failure/Involved | Overhead | 123 | 216927 | 37.0321 | -122.1892 | 10SPLDSIDEOF10977brokenpoleat2polessouthof58973 | Overcast-Rain-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 18-0101966 | OH | Sus | 31416550 | yes | 2018 | NOV | Yes | Multi-Fault | 1394138 | CSO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0104854&numberofmonths=24&showchangehistorylog=1 | 18-0104854 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 9723 | 20181129 | 753 | 228017 | 2045 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 22495 | 37.152 | -122.135 | 23SPANSFROM9723 | Overcast-Rain-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 18-0104854 | OH | Sus | 0 | yes | 2018 | NOV | Yes | Line to Ground | 1396152 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0105021&numberofmonths=24&showchangehistorylog=1 | 18-0105021 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 8015 | 20181129 | 754 | 228179 | 1646 | Distribution Circuit | Vegetation | Tree - fell into line | 135 | 106771 | 37.1536 | -122.1616 | 320EVEREST | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0105021 | OH | Sus | 0 | yes | 2018 | NOV | Yes | Line to Ground | 1396269 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0105322&numberofmonths=24&showchangehistorylog=1 | 18-0105322 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 66253 | 20181129 | 959 | 228569 | 1815 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 21780 | 37.096 | -122.0136 | BARGAS149683168218307polesloadside66253 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0105322 | OH | Sus | 43586641 | yes | 2018 | NOV | Yes | Line to Ground | 1396417 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0104884&numberofmonths=24&showchangehistorylog=1 | 18-0104884 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 6053 | 20181129 | 659 | 227935 | 1626 | Distribution Circuit | Vegetation | Tree - fell into line | 66 | 85596 | 37.1033 | -121.9881 | 1SPANNOFNORTHRIDGEONGLENWOOD | Strong Winds-Heavy Rain-Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0104884 | OH | Sus | 0 | yes | 2018 | NOV | Yes | Line to Line | 1396175 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0105107&numberofmonths=24&showchangehistorylog=1 | 18-0105107 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 5587 | 20181129 | 1031 | 228670 | 429 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 3432 | 37.0672 | -122.0586 | MITCHELLDAN329ELALAMEINRDWIREDOWNPN | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0105107 | OH | Sus | 0 | yes | 2018 | NOV | Yes | Line to Ground | 1396323 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0105156&numberofmonths=24&showchangehistorylog=1 | 18-0105156 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | FELTON-0401 | 83140401 | FUSE | 5215 | 20181129 | 819 | 228367 | 1711 | Distribution Circuit | Equipment Failure/Involved | Overhead | 60 | 102660 | 37.0325 | -122.0765 | CGC315403519756 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0105156 | OH | Sus | 43586641 | yes | 2018 | NOV | Yes | Line to Ground | 1396352 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0105440&numberofmonths=24&showchangehistorylog=1 | 18-0105440 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | FELTON-0401 | 83140401 | FUSE | 7309 | 20181129 | 1512 | 229261 | 1268 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 20288 | 37.0328 | -122.0754 | 200MADRONAROAD | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0105440 | OH | Sus | 43586641 | yes | 2018 | NOV | Yes | Line to Ground | 1396474 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0104665&numberofmonths=24&showchangehistorylog=1 | 18-0104665 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1102 | 182941102 | RECLOSER | 63868 | 20181129 | 48 | 227377 | 1118 | Distribution Circuit | Vegetation | Tree - fell into line | 417 | 462449 | 36.2641 | -121.7954 | 7SPANSLSOF10441 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0104665 | OH | Sus | 31416754 | yes | 2018 | NOV | Yes | Line to Line | 1395979 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0105146&numberofmonths=24&showchangehistorylog=1 | 18-0105146 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2105 | 83252105 | FUSE | 5559 | 20181129 | 854 | 228337 | 2268 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 49896 | 37.0123 | -122.1224 | COLLINSEANrear2300smithgrade | Overcast-Heavy Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 18-0105146 | OH | Sus | 0 | yes | 2018 | NOV | Yes | Line to Line | 1396347 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0104810&numberofmonths=24&showchangehistorylog=1 | 18-0104810 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | RECLOSER | 5178 | 20181129 | 740 | 227969 | 1778 | Distribution Circuit | Vegetation | Tree - fell into line | 267 | 117726 | 37.0326 | -121.9462 | NYSTROMERIK10584087998799190PauHana | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0104810 | OH | Sus | 31416754 | yes | 2018 | NOV | Yes | Line to Line | 1396112 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0105091&numberofmonths=24&showchangehistorylog=1 | 18-0105091 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | TRIP-SAVER | 6577 | 20181129 | 1026 | 228660 | 1759 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 84432 | 37.048 | -121.8081 | NYSTROMERIK10584087998799Near5400EurekaCanyonRdDoveLane | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0105091 | OH | Sus | 0 | yes | 2018 | NOV | Yes | Line to Ground | 1396315 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0105438&numberofmonths=24&showchangehistorylog=1 | 18-0105438 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | JUMPER | FUCO27429 | 20181129 | 1213 | 228898 | 1555 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1555 | 36.9878 | -121.8391 | MTR10089746035177FREEDOMBLVD | Partly Cloudy-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0105438 | OH | Sus | 0 | yes | 2018 | NOV | Yes | Line to Ground | 1396473 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0105138&numberofmonths=24&showchangehistorylog=1 | 18-0105138 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 3459 | 20181129 | 210 | 227530 | 2695 | Distribution Circuit | Vegetation | Tree - fell into line | 64 | 63343 | 37.0246 | -121.8841 | 2647FUCO | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0105138 | OH | Sus | 31416754 | yes | 2018 | NOV | Yes | Line to Ground | 1396341 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005120&numberofmonths=24&showchangehistorylog=1 | 19-0005120 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE | 9421 | 20190106 | 1336 | 255338 | 1181 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 35430 | 37.077 | -122.0861 | 2SPANSLDSIDEOF9421 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005120 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1403592 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005074&numberofmonths=24&showchangehistorylog=1 | 19-0005074 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE | 5443 | 20190106 | 1133 | 255153 | 396 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 2772 | 37.1106 | -122.1143 | 2SPANOFWIREDOWNONLDOFFUSES5074 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005074 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1403547 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005117&numberofmonths=24&showchangehistorylog=1 | 19-0005117 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | RECLOSER | 5028 | 20190106 | 1507 | 255478 | 1258 | Distribution Circuit | Vegetation | Tree - fell into line | 638 | 46169 | 37.1284 | -122.1222 | 3SO2539 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005117 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1403589 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005408&numberofmonths=24&showchangehistorylog=1 | 19-0005408 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 3005 | 20190106 | 1806 | 257734 | 1202 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 3606 | 37.0992 | -122.1434 | CAPWELL39158312061280SANVINCENTEATEMPIREGRADE | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0005408 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1403856 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005550&numberofmonths=24&showchangehistorylog=1 | 19-0005550 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | JUMPER | WIREDOWN | 20190106 | 1839 | 258408 | 1241 | Distribution Circuit | Vegetation | Tree - fell into line | 473 | 200329 | 37.1632 | -122.1622 | BET468158021 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005550 | OH | Sus | 31420594 | yes | 2019 | JAN | Yes | Line to Ground | 1403998 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005780&numberofmonths=24&showchangehistorylog=1 | 19-0005780 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | TRANSFORMER | 315133224442 | 20190106 | 2239 | 258320 | 1077 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1077 | 37.1596 | -122.1709 | 315133224442 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005780 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1404159 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005332&numberofmonths=24&showchangehistorylog=1 | 19-0005332 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | SECTIONALIZER | 12013 | 20190106 | 1818 | 256412 | 505 | Distribution Circuit | Vegetation | Tree - fell into line | 2129 | 376381 | 37.0177 | -122.0269 | WIREDOWNATCGC315534819096ONSIMSRD | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005332 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1403785 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005092&numberofmonths=24&showchangehistorylog=1 | 19-0005092 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 8315 | 20190106 | 1418 | 255311 | 1323 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 33075 | 37.0997 | -122.118 | ALVAREZ34638315359251169SequoiaGrvBenLomond | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005092 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Multi-Fault | 1403565 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005150&numberofmonths=24&showchangehistorylog=1 | 19-0005150 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 10457 | 20190106 | 1353 | 255363 | 1262 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 20192 | 37.1087 | -122.046 | 2SPANSNORTHOF10457 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005150 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1403621 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005652&numberofmonths=24&showchangehistorylog=1 | 19-0005652 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | TRIP-SAVER | 5577 | 20190106 | 1808 | 256225 | 1181 | Distribution Circuit | Equipment Failure/Involved | Overhead | 97 | 101519 | 37.0487 | -122.0616 | 70MANINZITA3SPANSLDSIDEOF1623 | Overcast-Heavy Rain-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0005652 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1404091 | CSO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005486&numberofmonths=24&showchangehistorylog=1 | 19-0005486 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | FELTON-0401 | 83140401 | OCB | 4012 | 20190106 | 1917 | 258251 | 1003 | Distribution Circuit | Vegetation | Tree - branch fell on line | 912 | 632115 | 37.0491 | -122.0645 | BOYNTON345983133166205334HWY9 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005486 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1403935 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005554&numberofmonths=24&showchangehistorylog=1 | 19-0005554 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | HATTON-1101 | 182291101 | FUSE | 9302 | 20190106 | 2124 | 258155 | 1208 | Distribution Circuit | Vegetation | Tree - fell into line | 98 | 118384 | 36.4377 | -121.7935 | 15SPANSLOADSIDEOF9302 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005554 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1404003 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005263&numberofmonths=24&showchangehistorylog=1 | 19-0005263 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2104 | 83252104 | OTHER | WIREDOWNONMAINLINE2SPANSSSIDE857TAP | 20190106 | 1713 | 255929 | 425 | Distribution Circuit | Vegetation | Tree - fell into line | 295 | 58445 | 36.9982 | -121.9705 | 2SPANSSSOF857TAP | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005263 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1403734 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005466&numberofmonths=24&showchangehistorylog=1 | 19-0005466 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2105 | 83252105 | FUSE | 12119 | 20190106 | 1743 | 256015 | 1202 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 4808 | 37.0052 | -121.9836 | 3NO2441 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005466 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Three Phase Fault | 1403916 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005357&numberofmonths=24&showchangehistorylog=1 | 19-0005357 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 711 | 20190106 | 1735 | 255942 | 1123 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 23583 | 37.0531 | -122.1603 | BOYNTON34598313316620105COUNTRYESTATESTER | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005357 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1403808 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005378&numberofmonths=24&showchangehistorylog=1 | 19-0005378 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | RECLOSER | 39126 | 20190106 | 1906 | 256877 | 1223 | Distribution Circuit | Vegetation | Tree - branch fell on line | 136 | 143283 | 37.0778 | -122.1326 | 203SUNLITLNLIMBONLINEAT8445EMPIREGRADERDTX315240021354NG | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005378 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1403829 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005932&numberofmonths=24&showchangehistorylog=1 | 19-0005932 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 6465 | 20190106 | 1830 | 256499 | 2370 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2370 | 37.0543 | -122.1694 | 2SPANSOFWIREDOWNFROMEOLATMTR7290R8 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005932 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1404272 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005454&numberofmonths=24&showchangehistorylog=1 | 19-0005454 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | TRIP-SAVER | 6577 | 20190106 | 1736 | 255948 | 2696 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 133985 | 37.048 | -121.8081 | EUREKACANYONANDDOVELANE | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005454 | OH | Sus | 31420894 | yes | 2019 | JAN | Yes | Line to Ground | 1403906 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005797&numberofmonths=24&showchangehistorylog=1 | 19-0005797 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 1003 | 20190106 | 1726 | 255878 | 1457 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 85963 | 36.999 | -121.8643 | 2SPANSNORTHOF2321 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005797 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Multi-Fault | 1404169 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005363&numberofmonths=24&showchangehistorylog=1 | 19-0005363 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | RECLOSER | 5166 | 20190106 | 1944 | 257358 | 1633 | Distribution Circuit | Equipment Failure/Involved | Overhead | 269 | 262292 | 36.9818 | -121.901 | POLEWIREDOWN911REDWOODDR | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0005363 | OH | Sus | 31420586 | yes | 2019 | JAN | Yes | Line to Ground | 1403814 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005661&numberofmonths=24&showchangehistorylog=1 | 19-0005661 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | SAN BENITO-2104 | 182742104 | FUSE | 6523 | 20190106 | 2038 | 258732 | 1422 | Distribution Circuit | Vegetation | Tree - fell into line | 163 | 72469 | 36.8749 | -121.6417 | KELLY40178316821802601SnyderRd | Overcast-32-90 F | Conductor, Overhead | On Ground | 19-0005661 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1404100 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005268&numberofmonths=24&showchangehistorylog=1 | 19-0005268 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | SECTIONALIZER | 40017 | 20190106 | 1814 | 256397 | 1422 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 55681 | 36.5815 | -121.9256 | BET9638C399BET433657855 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005268 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Multi-Fault | 1403745 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005269&numberofmonths=24&showchangehistorylog=1 | 19-0005269 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2203 | 182852203 | JUMPER | WIREDOWNSOURCESIDEOF7625 | 20190106 | 1658 | 255732 | 1448 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1448 | 36.5723 | -121.9002 | 1SPANSOURCESIDEOF7625 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005269 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Open Circuit | 1403740 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005401&numberofmonths=24&showchangehistorylog=1 | 19-0005401 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2203 | 182852203 | FUSE | 495039 | 20190106 | 1657 | 255730 | 2988 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 42633 | 36.5692 | -121.912 | 411467646320 | Overcast-Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0005401 | OH | Sus | 31420586 | yes | 2019 | JAN | Yes | Line to Ground | 1403849 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010150&numberofmonths=24&showchangehistorylog=1 | 19-0010150 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE | 5131 | 20190116 | 1844 | 269526 | 1334 | Distribution Circuit | Equipment Failure/Involved | Overhead | 112 | 143805 | 37.0901 | -122.0899 | CGC315359321915OPENJUMPER2PNOF5131 | Overcast-Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0010150 | OH | Sus | 31422113 | yes | 2019 | JAN | Yes | Line to Ground | 1407018 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010253&numberofmonths=24&showchangehistorylog=1 | 19-0010253 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | RECLOSER | 5144 | 20190116 | 2104 | 270974 | 1195 | Distribution Circuit | Vegetation | Tree - branch fell on line | 23 | 25015 | 37.0911 | -122.0774 | 11027SSOF11027 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010253 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407118 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011197&numberofmonths=24&showchangehistorylog=1 | 19-0011197 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE | 9125 | 20190116 | 1830 | 274100 | 3274 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 65580 | 37.1005 | -122.086 | 6SPLS91252SPLSOF5149 | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011197 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407792 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010389&numberofmonths=24&showchangehistorylog=1 | 19-0010389 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE | 5443 | 20190116 | 1743 | 271848 | 1127 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 7889 | 37.1106 | -122.1143 | 2SPANSLDSIDEOF5443 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | On Ground | 19-0010389 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Multi-Fault | 1407254 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0009363&numberofmonths=24&showchangehistorylog=1 | 19-0009363 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5501 | 20190116 | 49 | 266427 | 688 | Distribution Circuit | Vegetation | Tree - fell into line | 142 | 67211 | 37.1432 | -122.1317 | 15505TWOBARRD | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009363 | OH | Sus | 31422113 | yes | 2019 | JAN | Yes | Line to Line | 1406490 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0009903&numberofmonths=24&showchangehistorylog=1 | 19-0009903 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 12383 | 20190116 | 1410 | 267804 | 4130 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 167220 | 37.165 | -122.1935 | BARGAS14968316821830bloomcreekcampground2spansloadsideoffuses8503 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009903 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1406778 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010576&numberofmonths=24&showchangehistorylog=1 | 19-0010576 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 8259 | 20190116 | 1518 | 272507 | 2684 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 48312 | 37.1593 | -122.1271 | BRANDT4179831212208817505KingsCreekRdlargeoakpinnedwiretogroundnotbroken | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010576 | OH | Sus | 43634211 | yes | 2019 | JAN | Yes | Multi-Fault | 1407439 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010606&numberofmonths=24&showchangehistorylog=1 | 19-0010606 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 5511 | 20190116 | 1822 | 272725 | 3034 | Distribution Circuit | Vegetation | Tree - branch fell on line | 42 | 127428 | 37.1499 | -122.1363 | MTR1009004306 | Overcast-Heavy Rain-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0010606 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407466 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010978&numberofmonths=24&showchangehistorylog=1 | 19-0010978 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 7949 | 20190116 | 1609 | 267716 | 2762 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 49716 | 37.1889 | -122.1432 | 5SPANLDOF7949 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010978 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Force Out | 1407642 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011376&numberofmonths=24&showchangehistorylog=1 | 19-0011376 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 7289 | 20190116 | 1809 | 267626 | 3989 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 26518 | 37.1709 | -122.1805 | 1SPLSCGC315097825059 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011376 | OH | Sus | 43634211 | yes | 2019 | JAN | Yes | Line to Ground | 1407921 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010673&numberofmonths=24&showchangehistorylog=1 | 19-0010673 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 6087 | 20190116 | 1925 | 272969 | 1414 | Distribution Circuit | Vegetation | Tree - branch fell on line | 184 | 260176 | 37.0669 | -122.0336 | KELLEYRANDALLss60871210LockhartGulch | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010673 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407489 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0012097&numberofmonths=24&showchangehistorylog=1 | 19-0012097 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2104 | 83622104 | RECLOSER | 5020 | 20190116 | 2025 | 276631 | 4153 | Distribution Circuit | Vegetation | Tree - fell into line | 219 | 909507 | 37.1024 | -121.9848 | 10SPANSSOUTHOFFUSE18441ONMAINLINE | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0012097 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1408447 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010224&numberofmonths=24&showchangehistorylog=1 | 19-0010224 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | CAMP EVERS-2106 | 83622106 | RECLOSER | 5302 | 20190116 | 2302 | 271783 | 1047 | Distribution Circuit | Vegetation | Tree - fell into line | 517 | 294924 | 37.0438 | -122.0755 | FELTONQUARRYRDATEMPIREGRADE | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0010224 | OH | Sus | 31422113 | yes | 2019 | JAN | Yes | Line to Ground | 1407240 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010731&numberofmonths=24&showchangehistorylog=1 | 19-0010731 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 2487 | 20190116 | 2301 | 273141 | 1215 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 21870 | 37.0456 | -122.1099 | 1SPANLDSIDEOF2487 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010731 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407512 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011129&numberofmonths=24&showchangehistorylog=1 | 19-0011129 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE | 8553 | 20190116 | 2142 | 274260 | 2732 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 19124 | 36.5682 | -121.8959 | 2SPLS8553 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011129 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407748 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011468&numberofmonths=24&showchangehistorylog=1 | 19-0011468 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE | 6753 | 20190116 | 2142 | 275017 | 2725 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 84475 | 36.5659 | -121.8877 | CGC411514446174 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011468 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1408008 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011728&numberofmonths=24&showchangehistorylog=1 | 19-0011728 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE | 8557 | 20190116 | 2142 | 275690 | 3843 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 23058 | 36.5665 | -121.8861 | 4SPANSLSOF8557 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011728 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1408179 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011094&numberofmonths=24&showchangehistorylog=1 | 19-0011094 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2104 | 182222104 | FUSE | 9509 | 20190116 | 2300 | 271781 | 1301 | Distribution Circuit | Vegetation | Tree - fell into line | 132 | 171732 | 36.5248 | -121.8104 | 10SPANSLSOF9509 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011094 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407719 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010481&numberofmonths=24&showchangehistorylog=1 | 19-0010481 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | FELTON-0401 | 83140401 | OCB | 4012 | 20190116 | 2308 | 271960 | 2049 | Distribution Circuit | Vegetation | Tree - fell into line | 912 | 639550 | 37.0491 | -122.0645 | ROGERSJAMES5592404392ATCOPOLE12887NEAR140HWY9FELTON | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010481 | OH | Sus | 31422113 | yes | 2019 | JAN | Yes | Line to Ground | 1407345 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0009860&numberofmonths=24&showchangehistorylog=1 | 19-0009860 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HATTON-1101 | 182291101 | OCB | 11012 | 20190116 | 1608 | 267368 | 1702 | Distribution Circuit | Vegetation | Tree - fell into line | 2026 | 1063227 | 36.5569 | -121.8976 | DANIELIDICKRIOVISTARD2SPANSNO37088HARDTAPTWDMTR1008446066 | Overcast-Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0009860 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Multi-Fault | 1406741 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0009950&numberofmonths=24&showchangehistorylog=1 | 19-0009950 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1101 | 182941101 | FUSE | 2181 | 20190116 | 1553 | 267639 | 1703 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 133721 | 36.4893 | -121.9363 | 5SPSSOF7035 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009950 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1406820 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010513&numberofmonths=24&showchangehistorylog=1 | 19-0010513 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | OTTER-1101 | 182941101 | OTHER | WIREDOWN1SPANSOURCESIDE40283 | 20190116 | 2147 | 271259 | 2308 | Distribution Circuit | Equipment Failure/Involved | Overhead | 442 | 215330 | 36.4045 | -121.909 | 1SPANSOURCESIDEOVERHILLFROM40283 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010513 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407376 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010102&numberofmonths=24&showchangehistorylog=1 | 19-0010102 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1102 | 182941102 | RECLOSER | 2002 | 20190116 | 1922 | 269755 | 2778 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 256680 | 36.2249 | -121.7589 | 3SPLS6947 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010102 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1406970 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0009718&numberofmonths=24&showchangehistorylog=1 | 19-0009718 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | RECLOSER | 39126 | 20190116 | 1408 | 267109 | 1452 | Distribution Circuit | Vegetation | Tree - branch fell on line | 136 | 28333 | 37.0778 | -122.1326 | ALVAREZ346383153592518540EmpireGradeSantaCruz | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009718 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1406648 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0009760&numberofmonths=24&showchangehistorylog=1 | 19-0009760 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 4355 | 20190116 | 1313 | 266969 | 1283 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 29509 | 37.0602 | -122.064 | BARGAS14968316821830endofHihnrd3spansloadsideof4355 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009760 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1406667 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010133&numberofmonths=24&showchangehistorylog=1 | 19-0010133 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | RECLOSER | 11010 | 20190116 | 1945 | 270127 | 1231 | Distribution Circuit | Vegetation | Tree - fell into line | 123 | 42967 | 37.1053 | -122.0518 | 3SPLS110969 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010133 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407001 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010922&numberofmonths=24&showchangehistorylog=1 | 19-0010922 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 7799 | 20190116 | 1817 | 273676 | 2738 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 167018 | 37.0909 | -122.1397 | 124VICK160VICK405VICK444VICK445VICK | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010922 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Multi-Fault | 1407609 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011118&numberofmonths=24&showchangehistorylog=1 | 19-0011118 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 11929 | 20190116 | 1949 | 274220 | 2966 | Distribution Circuit | Vegetation | Tree - fell into line | 96 | 118074 | 37.0999 | -122.0343 | JUDDJEFF4spansLSoffuses7201 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011118 | OH | Sus | 43634211 | yes | 2019 | JAN | Yes | Line to Line | 1407737 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011144&numberofmonths=24&showchangehistorylog=1 | 19-0011144 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 10433 | 20190116 | 1918 | 269709 | 2478 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 11190 | 37.1051 | -122.047 | LSMTR1006214878 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011144 | OH | Sus | 43634211 | yes | 2019 | JAN | Yes | Line to Line | 1407757 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011278&numberofmonths=24&showchangehistorylog=1 | 19-0011278 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 9251 | 20190116 | 2119 | 271061 | 2783 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 19481 | 37.0934 | -122.0428 | MTR1007589794 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011278 | OH | Sus | 31422113 | yes | 2019 | JAN | Yes | Line to Ground | 1407846 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0009896&numberofmonths=24&showchangehistorylog=1 | 19-0009896 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | RECLOSER | 2064 | 20190116 | 1616 | 267767 | 1243 | Distribution Circuit | Equipment Failure/Involved | Overhead | 600 | 198534 | 36.5823 | -121.9204 | FUCO956007ONMAINLINE | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009896 | OH | Sus | 43634200 | yes | 2019 | JAN | Yes | Line to Ground | 1406771 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010516&numberofmonths=24&showchangehistorylog=1 | 19-0010516 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 6973 | 20190116 | 2036 | 270730 | 984 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 35424 | 36.5817 | -121.9216 | 3SPANSLDSIDEOFFUCO6973 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010516 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407379 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0009754&numberofmonths=24&showchangehistorylog=1 | 19-0009754 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2202 | 182852202 | RECLOSER | 9488 | 20190116 | 1439 | 267213 | 1794 | Distribution Circuit | Vegetation | Tree - fell into line | 380 | 79995 | 36.5902 | -121.9442 | FORESTLAKEANDHAWKINS | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 19-0009754 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1406663 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010136&numberofmonths=24&showchangehistorylog=1 | 19-0010136 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2202 | 182852202 | RECLOSER | 9104 | 20190116 | 1947 | 270139 | 1468 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1193 | 406884 | 36.5869 | -121.9142 | SW2319 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010136 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407003 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011063&numberofmonths=24&showchangehistorylog=1 | 19-0011063 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2202 | 182852202 | FUSE | 55781 | 20190116 | 1907 | 269626 | 2702 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 62354 | 36.6018 | -121.9374 | 4SPANSLSOF55781LINEBUCKPOLE | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011063 | OH | Sus | 31422108 | yes | 2019 | JAN | Yes | Line to Ground | 1407698 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010273&numberofmonths=24&showchangehistorylog=1 | 19-0010273 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2203 | 182852203 | OCB | 22032 | 20190116 | 2123 | 270492 | 2667 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5206 | 4928972 | 36.5786 | -121.9085 | BROKENCROSSARMSANDWIREDOWN6SPANSLDSIDELR93964WIREDOWNSOURCESIDE6181TWDJUNIPEROAVE | Overcast-Rain-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0010273 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Multi-Fault | 1407138 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011489&numberofmonths=24&showchangehistorylog=1 | 19-0011489 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2203 | 182852203 | FUSE | 1489 | 20190116 | 1559 | 275086 | 4111 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 45221 | 36.5665 | -121.9355 | 4SPANSLOADSIDEOF1489ATLINEANDBUCK | Overcast-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0011489 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1408031 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011497&numberofmonths=24&showchangehistorylog=1 | 19-0011497 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2203 | 182852203 | FUSE | 10421 | 20190116 | 2123 | 275097 | 2666 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 39990 | 36.5659 | -121.9347 | WILLIAMSBRYAN10ALPriNmidspanOQTNOTEODTSHOWSFAULTLOCATIONOF1SPANNOF766491WHICHISSOURCESIDEOF10421 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011497 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Open Circuit | 1408039 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011333&numberofmonths=24&showchangehistorylog=1 | 19-0011333 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE | 1653 | 20190117 | 1520 | 274412 | 1244 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 14928 | 37.1577 | -122.1392 | 5SPANSLSOF1653 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011333 | OH | Sus | 43634211 | yes | 2019 | JAN | Yes | Line to Ground | 1407884 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011417&numberofmonths=24&showchangehistorylog=1 | 19-0011417 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE | 2887 | 20190117 | 1520 | 274413 | 1367 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2734 | 37.139 | -122.0949 | 3SPANSLS2887 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011417 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407957 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010638&numberofmonths=24&showchangehistorylog=1 | 19-0010638 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | JUMPER | OJCGC315145724442 | 20190117 | 557 | 272838 | 2207 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 17656 | 37.1592 | -122.167 | CGC315145724442 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010638 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Force Out | 1407475 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011078&numberofmonths=24&showchangehistorylog=1 | 19-0011078 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 9779 | 20190117 | 634 | 274135 | 2101 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 12606 | 37.1545 | -122.0827 | 530WHALEBONEGULCH | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011078 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407706 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010628&numberofmonths=24&showchangehistorylog=1 | 19-0010628 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | RECLOSER | 12990 | 20190117 | 723 | 272664 | 2214 | Distribution Circuit | Vegetation | Tree - fell into line | 277 | 268878 | 37.039 | -122.0215 | SOF47234SPANS | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 19-0010628 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Force Out | 1407472 | PW | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011375&numberofmonths=24&showchangehistorylog=1 | 19-0011375 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 177 | 20190117 | 1139 | 274879 | 3071 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 6142 | 37.0618 | -122.0348 | 2SPANSLDSIDE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011375 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407920 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011432&numberofmonths=24&showchangehistorylog=1 | 19-0011432 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 2161 | 20190117 | 1500 | 275004 | 1282 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1282 | 36.9968 | -121.7383 | 4POLESLDSIDE | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011432 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407972 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011498&numberofmonths=24&showchangehistorylog=1 | 19-0011498 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HATTON-1101 | 182291101 | JUMPER | OJATHARD6POLESTOEOLTWDNE | 20190117 | 2112 | 275005 | 2237 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 6711 | 36.5503 | -121.8986 | 6POLELDSIDEOF627 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011498 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Open Circuit | 1408040 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011238&numberofmonths=24&showchangehistorylog=1 | 19-0011238 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HATTON-1102 | 182291102 | FUSE | 8937 | 20190117 | 712 | 272776 | 677 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 32496 | 36.5029 | -121.9342 | 3SPLS8937 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011238 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1407816 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011306&numberofmonths=24&showchangehistorylog=1 | 19-0011306 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | POINT MORETTI-1101 | 82931101 | OTHER | WIREDOWN | 20190117 | 1513 | 274401 | 659 | Distribution Circuit | Vegetation | Tree - branch fell on line | 116 | 8044 | 37.063 | -122.2266 | 297SWANTONRDDAVINPORT | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011306 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407867 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010915&numberofmonths=24&showchangehistorylog=1 | 19-0010915 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | SWITCH | 794081 | 20190117 | 829 | 273472 | 541 | Distribution Circuit | Vegetation | Tree - fell into line | 97 | 52477 | 37.0345 | -121.8203 | KELLY401783168218021245EurekaCauyonRdWat | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010915 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Force Out | 1407605 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010474&numberofmonths=24&showchangehistorylog=1 | 19-0010474 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | OCB | 22012 | 20190117 | 59 | 272227 | 463 | Distribution Circuit | Vegetation | Tree - fell into line | 209 | 86031 | 36.5786 | -121.9085 | LDSIDEOF9893 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010474 | OH | Sus | 43634200 | yes | 2019 | JAN | Yes | Line to Ground | 1407339 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0017058&numberofmonths=24&showchangehistorylog=1 | 19-0017058 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE | 5151 | 20190202 | 748 | 286838 | 517 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 3102 | 37.1109 | -122.0898 | CAPWELL391583120612807SPANSLOADSIDEOFCO5151ONLOVECREEKRD | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017058 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1411507 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0017082&numberofmonths=24&showchangehistorylog=1 | 19-0017082 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 12383 | 20190202 | 543 | 286625 | 332 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 15017 | 37.165 | -122.1935 | LOADSIDEOFSB77767 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017082 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1411531 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0017233&numberofmonths=24&showchangehistorylog=1 | 19-0017233 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 6355 | 20190202 | 1434 | 287731 | 1176 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 50568 | 37.0506 | -122.0594 | 2SPANSLSOF6355 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017233 | OH | Sus | 43665416 | yes | 2019 | FEB | Yes | Line to Ground | 1411660 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0017469&numberofmonths=24&showchangehistorylog=1 | 19-0017469 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 8239 | 20190202 | 2327 | 288286 | 1123 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 14599 | 37.1187 | -121.9639 | MTR5000136784NEXTTOLASTSPANOFWIREDOWN | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | On Ground | 19-0017469 | OH | Sus | 31424211 | yes | 2019 | FEB | Yes | Line to Ground | 1411884 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0016957&numberofmonths=24&showchangehistorylog=1 | 19-0016957 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE | 6743 | 20190202 | 242 | 286104 | 844 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 29540 | 36.5712 | -121.8899 | 1NOFFAIRFIELD | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0016957 | OH | Sus | 31424211 | yes | 2019 | FEB | Yes | Line to Ground | 1411415 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0017100&numberofmonths=24&showchangehistorylog=1 | 19-0017100 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2104 | 182222104 | FUSE | 2811 | 20190202 | 55 | 286920 | 3747 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 71193 | 36.5151 | -121.8129 | 2SPANSLOADSIDE2811 | Overcast-Heavy Rain-Strong Winds-32-90 F | Insulator | Broken, wire on ground | 19-0017100 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1411547 | INS | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0017264&numberofmonths=24&showchangehistorylog=1 | 19-0017264 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2105 | 182222105 | FUSE | 6029 | 20190202 | 437 | 286379 | 3581 | Distribution Circuit | Vegetation | Tree - fell into line | 111 | 89931 | 36.6088 | -121.9304 | RENVILLEGREGORY5598405341SPANLDSIDEOF6029TWD8193 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017264 | OH | Sus | 31424211 | yes | 2019 | FEB | Yes | Line to Ground | 1411684 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0016919&numberofmonths=24&showchangehistorylog=1 | 19-0016919 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HATTON-1101 | 182291101 | FUSE | 2283 | 20190202 | 338 | 286281 | 1847 | Distribution Circuit | Vegetation | Tree - fell into line | 383 | 707401 | 36.5564 | -121.9088 | 2SPANSLSOF1463WIREDOWN5SPANSLSOF1463 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0016919 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1411383 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0017244&numberofmonths=24&showchangehistorylog=1 | 19-0017244 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | HATTON-1101 | 182291101 | FUSE | 9302 | 20190202 | 1306 | 287423 | 2931 | Distribution Circuit | Vegetation | Tree - fell into line | 98 | 287238 | 36.4377 | -121.7935 | 8SPANSLOADSIDEOFSBCO117919 | Heavy Rain-Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017244 | OH | Sus | 43665416 | yes | 2019 | FEB | Yes | Line to Ground | 1411667 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0017292&numberofmonths=24&showchangehistorylog=1 | 19-0017292 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HATTON-1101 | 182291101 | RECLOSER | 2654 | 20190202 | 1702 | 287895 | 1602 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 26675 | 36.5571 | -121.9039 | 2SPANSEOF92259 | Partly Cloudy-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017292 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1411704 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0017178&numberofmonths=24&showchangehistorylog=1 | 19-0017178 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HATTON-1102 | 182291102 | TRANSFORMER | 411370744360 | 20190202 | 1315 | 287507 | 1900 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 9525 | 36.5154 | -121.9369 | TREVINOVINCENT5593562801POINTLOBOSSTATERESERVEHWY1CARMELHIGHLANDS | Overcast-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0017178 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1411608 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0017217&numberofmonths=24&showchangehistorylog=1 | 19-0017217 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HATTON-1102 | 182291102 | RECLOSER | 2010 | 20190202 | 357 | 287686 | 2807 | Distribution Circuit | Vegetation | Tree - fell into line | 104 | 160135 | 36.506 | -121.936 | ATTAP1491SOURCESIDE | Partly Cloudy-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017217 | OH | Sus | 31424211 | yes | 2019 | FEB | Yes | Line to Ground | 1411644 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0017224&numberofmonths=24&showchangehistorylog=1 | 19-0017224 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HATTON-1102 | 182291102 | FUSE | 8937 | 20190202 | 258 | 286135 | 2199 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 52824 | 36.5029 | -121.9342 | 2SPANSNOF8943 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017224 | OH | Sus | 43665408 | yes | 2019 | FEB | Yes | Line to Line | 1411650 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0016851&numberofmonths=24&showchangehistorylog=1 | 19-0016851 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | OTTER-1101 | 182941101 | FUSE | 637 | 20190202 | 2 | 285892 | 1050 | Distribution Circuit | Vegetation | Tree - fell into line | 72 | 75600 | 36.3945 | -121.8788 | 3SPANSLSOF637 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0016851 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1411311 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0016970&numberofmonths=24&showchangehistorylog=1 | 19-0016970 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1101 | 182941101 | FUSE | 2181 | 20190202 | 103 | 285962 | 2331 | Distribution Circuit | Vegetation | Tree - fell into line | 82 | 77094 | 36.4893 | -121.9363 | 18MENTONEST | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0016970 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1411429 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0016999&numberofmonths=24&showchangehistorylog=1 | 19-0016999 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1101 | 182941101 | FUSE | 40411 | 20190202 | 243 | 286316 | 1149 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 70861 | 36.4918 | -121.938 | SANREMORD | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0016999 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1411454 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0017171&numberofmonths=24&showchangehistorylog=1 | 19-0017171 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | OTTER-1101 | 182941101 | FUSE | 1279 | 20190202 | 834 | 286973 | 3086 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 15430 | 36.3999 | -121.8709 | 2SPANSLDOFFUSES1279 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017171 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1411600 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0016877&numberofmonths=24&showchangehistorylog=1 | 19-0016877 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1102 | 182941102 | RECLOSER | 2012 | 20190202 | 322 | 286174 | 4108 | Distribution Circuit | Equipment Failure/Involved | Overhead | 441 | 1790658 | 36.3314 | -121.8829 | ATMTR1009655779ANDLOADSIDEOFFUSE9015 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0016877 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1411337 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0016908&numberofmonths=24&showchangehistorylog=1 | 19-0016908 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | RECLOSER | 5178 | 20190202 | 425 | 286360 | 415 | Distribution Circuit | Vegetation | Tree - branch fell on line | 267 | 110805 | 37.0326 | -121.9462 | WELSHMARK3800OLDSANJOSERD | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0016908 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1411370 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0017371&numberofmonths=24&showchangehistorylog=1 | 19-0017371 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE | 8351 | 20190202 | 1804 | 288221 | 1189 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 10701 | 37.0539 | -121.9394 | LOADSIDEMTR50000038043 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017371 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1411783 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0017259&numberofmonths=24&showchangehistorylog=1 | 19-0017259 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | TRIP-SAVER | 5401 | 20190202 | 1411 | 287808 | 1207 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 13657 | 37.0648 | -122.1233 | CAPWELL391583120612803SPANSLOADSIDEOFCO11739 | Partly Cloudy-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017259 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1411680 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0017333&numberofmonths=24&showchangehistorylog=1 | 19-0017333 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | SEACLIFF-0401 | 83500401 | JUMPER | WIREDOWN997MESAGRANDECT | 20190202 | 1714 | 287911 | 1103 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 7721 | 37.0027 | -121.9072 | 997MESAGRANDECT | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017333 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1411747 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0016884&numberofmonths=24&showchangehistorylog=1 | 19-0016884 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | OCB | 22012 | 20190202 | 330 | 286230 | 3602 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5926 | 1943971 | 36.5786 | -121.9085 | ANDERSONJARED8316821761BHND4134ELBOSQUESLOATANDBIRDROCK | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0016884 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1411345 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0017265&numberofmonths=24&showchangehistorylog=1 | 19-0017265 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 7257 | 20190202 | 724 | 287587 | 2126 | Distribution Circuit | Vegetation | Tree - fell into line | 82 | 174332 | 36.5767 | -121.9393 | 9SPANLDSIDEOFFUSES3930RHONDADR | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017265 | OH | Sus | 43665408 | yes | 2019 | FEB | Yes | Line to Line | 1411685 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0017327&numberofmonths=24&showchangehistorylog=1 | 19-0017327 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 9655 | 20190202 | 1416 | 287589 | 1794 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 20673 | 36.5665 | -121.9305 | 1SPANLDOF9657 | Partly Cloudy-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017327 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1411741 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0017123&numberofmonths=24&showchangehistorylog=1 | 19-0017123 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2204 | 182852204 | FUSE | 6409 | 20190202 | 354 | 286363 | 2295 | Distribution Circuit | Vegetation | Tree - fell into line | 108 | 139500 | 36.59 | -121.9114 | 10VIALADERA | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017123 | OH | Sus | 31424211 | yes | 2019 | FEB | Yes | Line to Line | 1411562 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0017748&numberofmonths=24&showchangehistorylog=1 | 19-0017748 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 11929 | 20190204 | 601 | 289532 | 637 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1274 | 37.0999 | -122.0343 | 10SPANSLDSIDE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017748 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1412144 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018007&numberofmonths=24&showchangehistorylog=1 | 19-0018007 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 1655 | 20190204 | 1100 | 290040 | 1668 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 16680 | 37.1027 | -122.0483 | 2SPANSLDOFFUSES1655 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0018007 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1412292 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018112&numberofmonths=24&showchangehistorylog=1 | 19-0018112 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 5873 | 20190204 | 1208 | 290216 | 1416 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2832 | 37.0873 | -121.8616 | 25MILESLDSIDEOF5873 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0018112 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1412355 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0017871&numberofmonths=24&showchangehistorylog=1 | 19-0017871 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | TRIP-SAVER | 5401 | 20190204 | 730 | 289633 | 471 | Distribution Circuit | Vegetation | Tree - branch fell on line | 69 | 32499 | 37.0648 | -122.1233 | 5SPANSLDSIDEOF5401 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017871 | OH | Sus | 31424216 | yes | 2019 | FEB | Yes | Line to Ground | 1412213 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0017769&numberofmonths=24&showchangehistorylog=1 | 19-0017769 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 1003 | 20190204 | 636 | 289615 | 324 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 19116 | 36.999 | -121.8643 | 2321 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017769 | OH | Sus | 31424216 | yes | 2019 | FEB | Yes | Line to Ground | 1412157 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018645&numberofmonths=24&showchangehistorylog=1 | 19-0018645 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 6209 | 20190205 | 1258 | 292704 | 497 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1491 | 37.1791 | -122.1392 | 1SPLDSIDE6209 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0018645 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1412734 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020495&numberofmonths=24&showchangehistorylog=1 | 19-0020495 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | RECLOSER | 65444 | 20190209 | 2250 | 297547 | 980 | Distribution Circuit | Vegetation | Tree - fell into line | 985 | 191758 | 37.1278 | -122.1229 | 15SPLDSIDEOF9735 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020495 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1414169 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020625&numberofmonths=24&showchangehistorylog=1 | 19-0020625 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE | 12377 | 20190210 | 642 | 298482 | 951 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 22824 | 37.1052 | -122.1064 | NYSTROMERIK10584087998799242WesternAve | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0020625 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1414316 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020758&numberofmonths=24&showchangehistorylog=1 | 19-0020758 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | SEACLIFF-0401 | 83500401 | FUSE | 6005 | 20190210 | 1343 | 298992 | 484 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 9196 | 36.9959 | -121.9233 | 4SPLS6005 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020758 | OH | Sus | 43676142 | yes | 2019 | FEB | Yes | Line to Ground | 1414460 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022562&numberofmonths=24&showchangehistorylog=1 | 19-0022562 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | OTHER | WIREDOWNMTR1009698877 | 20190213 | 1713 | 305362 | 1743 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 50714 | 37.1136 | -122.0886 | 12SPLDSIDEOF5151 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022562 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1415799 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022695&numberofmonths=24&showchangehistorylog=1 | 19-0022695 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 12383 | 20190213 | 2122 | 305747 | 4208 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 260896 | 37.165 | -122.1935 | 5565 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022695 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1415929 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023339&numberofmonths=24&showchangehistorylog=1 | 19-0023339 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 12125 | 20190213 | 2359 | 309562 | 3912 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 11736 | 37.2249 | -122.1471 | 2SPANSLSOF12125 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023339 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416508 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023837&numberofmonths=24&showchangehistorylog=1 | 19-0023837 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 7773 | 20190213 | 2359 | 311485 | 4193 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 142562 | 37.1882 | -122.1579 | 104MonteVista60KvEndOfOwlRidgeRd | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023837 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416978 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023839&numberofmonths=24&showchangehistorylog=1 | 19-0023839 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | TRIP-SAVER | 6219 | 20190213 | 2359 | 311487 | 3990 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 87780 | 37.184 | -122.1409 | 789QUIGGWAYBOLDERCREEK | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023839 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416979 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023843&numberofmonths=24&showchangehistorylog=1 | 19-0023843 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 1607 | 20190213 | 2359 | 311495 | 4134 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 53742 | 37.193 | -122.1558 | MTR1008865842 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023843 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416983 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023855&numberofmonths=24&showchangehistorylog=1 | 19-0023855 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER | 5066 | 20190213 | 2359 | 311558 | 4051 | Distribution Circuit | Environmental/External | Flood/Erosion | 44 | 178244 | 37.1707 | -122.1655 | 19100BIGBASINWYBOULDERCREEK | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0023855 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1416991 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022520&numberofmonths=24&showchangehistorylog=1 | 19-0022520 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 12055 | 20190213 | 1544 | 305134 | 276 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 1380 | 37.0945 | -122.0048 | 4SPLDSIDEOF12055 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022520 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1415759 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023266&numberofmonths=24&showchangehistorylog=1 | 19-0023266 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE | 8405 | 20190213 | 1308 | 304574 | 3103 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 118965 | 36.5791 | -121.8688 | PAVANAPHILdeerflatrdandJacksrd | Partly Cloudy-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023266 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416456 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023378&numberofmonths=24&showchangehistorylog=1 | 19-0023378 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE | 2233 | 20190213 | 1918 | 305568 | 2918 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 32098 | 36.5726 | -121.8828 | LOADSIDEOF2233 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023378 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416533 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024243&numberofmonths=24&showchangehistorylog=1 | 19-0024243 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2103 | 182222103 | JUMPER | OJSSSOFCGC411493846296 | 20190213 | 1926 | 312811 | 2995 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 8175 | 36.5697 | -121.8999 | 502AGUAJITORDMONTEREY | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024243 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1417323 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023655&numberofmonths=24&showchangehistorylog=1 | 19-0023655 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2104 | 182222104 | FUSE | 2845 | 20190213 | 1327 | 304621 | 2899 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 201986 | 36.5398 | -121.8653 | 6470BROOKDALEDR | Partly Cloudy-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023655 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Three Phase Fault | 1416806 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022134&numberofmonths=24&showchangehistorylog=1 | 19-0022134 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HATTON-1101 | 182291101 | OCB | 11012 | 20190213 | 1052 | 303879 | 2058 | Distribution Circuit | Vegetation | Tree - fell into line | 1959 | 957728 | 36.5569 | -121.8976 | VALLEJOCRAIG831682182625470CanadaRd | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022134 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Multi-Fault | 1415496 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022432&numberofmonths=24&showchangehistorylog=1 | 19-0022432 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HATTON-1101 | 182291101 | FUSE | 723499 | 20190213 | 1058 | 305177 | 2051 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 28714 | 36.5463 | -121.8987 | 12SPANLDSIDEOF723499 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022432 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1415691 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023140&numberofmonths=24&showchangehistorylog=1 | 19-0023140 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HATTON-1102 | 182291102 | FUSE | 10187 | 20190213 | 734 | 308658 | 6298 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 37788 | 36.514 | -121.9376 | SSOF10187 | Overcast-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0023140 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416331 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023961&numberofmonths=24&showchangehistorylog=1 | 19-0023961 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HATTON-1102 | 182291102 | FUSE | 1491 | 20190213 | 734 | 311893 | 3494 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 139760 | 36.5057 | -121.9351 | 8SPANSLSOF1491 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023961 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1417080 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024150&numberofmonths=24&showchangehistorylog=1 | 19-0024150 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HATTON-1102 | 182291102 | FUSE | 8045 | 20190213 | 734 | 312465 | 6099 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 6099 | 36.5039 | -121.9352 | LOADSIDE8045 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024150 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1417240 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022470&numberofmonths=24&showchangehistorylog=1 | 19-0022470 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | LAURELES-1111 | 182371111 | OTHER | WIREDOWN1LDSIDEOFMTR1008500619 | 20190213 | 1427 | 305024 | 4666 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 37826 | 36.4694 | -121.7336 | 1LDSIDEOFMTR1008500619 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0022470 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1415723 | CSO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022271&numberofmonths=24&showchangehistorylog=1 | 19-0022271 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | LAURELES-1112 | 182371112 | FUSE | 407 | 20190213 | 838 | 304618 | 2003 | Distribution Circuit | Vegetation | Tree - fell into line | 170 | 324263 | 36.4868 | -121.7394 | 11SPANSLOADSIDEOF407 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022271 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1415584 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022988&numberofmonths=24&showchangehistorylog=1 | 19-0022988 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1101 | 182941101 | FUSE | 40419 | 20190213 | 532 | 307974 | 4890 | Distribution Circuit | Vegetation | Tree - branch fell on line | 37 | 180930 | 36.4907 | -121.9357 | LOADSIDE40419 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022988 | OH | Sus | 0 | yes | 2019 | FEB | Yes | None | 1416211 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023478&numberofmonths=24&showchangehistorylog=1 | 19-0023478 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1101 | 182941101 | FUSE | 40411 | 20190213 | 532 | 310107 | 3680 | Distribution Circuit | Vegetation | Tree - fell into line | 96 | 353280 | 36.4918 | -121.938 | GALLEGOSHENRY8316821747SanRemoRdCOs2181 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023478 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1416627 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023971&numberofmonths=24&showchangehistorylog=1 | 19-0023971 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1101 | 182941101 | FUSE | 457 | 20190213 | 532 | 311922 | 5076 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 96444 | 36.4927 | -121.9334 | 1SPANSOUTHOF7841 | Overcast-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0023971 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Multi-Fault | 1417089 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021958&numberofmonths=24&showchangehistorylog=1 | 19-0021958 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 8513 | 20190213 | 649 | 302920 | 752 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 12032 | 37.055 | -122.1531 | CGC315187120610 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0021958 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1415378 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021965&numberofmonths=24&showchangehistorylog=1 | 19-0021965 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 7369 | 20190213 | 848 | 303431 | 1922 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 21322 | 37.0505 | -122.1532 | 1SO1009769660 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0021965 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1415385 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022151&numberofmonths=24&showchangehistorylog=1 | 19-0022151 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 5409 | 20190213 | 650 | 302922 | 670 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 3445 | 37.0658 | -122.1519 | TREEFELLONLINEMTR1008918882 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022151 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1415507 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022690&numberofmonths=24&showchangehistorylog=1 | 19-0022690 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | POINT MORETTI-1101 | 82931101 | RECLOSER | 12122 | 20190213 | 2248 | 305833 | 5541 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 437093 | 37.0664 | -122.2286 | 1POLELDSIDEWIREDOWNONTHEMAINLINE | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022690 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1415924 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021880&numberofmonths=24&showchangehistorylog=1 | 19-0021880 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | OCB | 22012 | 20190213 | 817 | 303177 | 4793 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 221714 | 36.5786 | -121.9085 | ADORNIJUSTIN8312358361mulitiplespansco42365 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021880 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1415325 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022583&numberofmonths=24&showchangehistorylog=1 | 19-0022583 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 8917 | 20190213 | 729 | 305708 | 3582 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 75222 | 36.5771 | -121.9275 | 1SPEAST1SPWESTOF8917 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022583 | OH | Sus | 0 | yes | 2019 | FEB | Yes | None | 1415816 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022677&numberofmonths=24&showchangehistorylog=1 | 19-0022677 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 7259 | 20190213 | 729 | 305820 | 4969 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 109318 | 36.5752 | -121.9365 | 5SPANSLSOF7259 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022677 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1415910 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023191&numberofmonths=24&showchangehistorylog=1 | 19-0023191 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 2453 | 20190213 | 729 | 308941 | 4969 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 64597 | 36.5723 | -121.9397 | LOADSIDE2453 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023191 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1416380 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023248&numberofmonths=24&showchangehistorylog=1 | 19-0023248 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 766491 | 20190213 | 739 | 309175 | 5058 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 60696 | 36.5664 | -121.9354 | MULTIPLELOCATIONS | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023248 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1416439 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024691&numberofmonths=24&showchangehistorylog=1 | 19-0024691 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 2451 | 20190213 | 729 | 314849 | 6124 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 42868 | 36.5723 | -121.9406 | 2SPANSLSOF2451 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024691 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1417766 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024692&numberofmonths=24&showchangehistorylog=1 | 19-0024692 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 7873 | 20190213 | 739 | 314852 | 6184 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 179336 | 36.5772 | -121.9452 | 4SPANSLSOF7873 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024692 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1417767 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021875&numberofmonths=24&showchangehistorylog=1 | 19-0021875 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2202 | 182852202 | RECLOSER | 2606 | 20190213 | 807 | 303128 | 7714 | Distribution Circuit | Vegetation | Tree - fell into line | 327 | 1074917 | 36.5767 | -121.9507 | GALLEGOSHENRY83168217473273OnduladoRd | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021875 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1415319 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023117&numberofmonths=24&showchangehistorylog=1 | 19-0023117 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2202 | 182852202 | FUSE | 8167 | 20190213 | 1731 | 308454 | 5450 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 87200 | 36.58 | -121.9517 | WIREDOWNAT8167 | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023117 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Three Phase Fault | 1416310 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023555&numberofmonths=24&showchangehistorylog=1 | 19-0023555 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2202 | 182852202 | FUSE | 45255 | 20190213 | 511 | 310350 | 4940 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 192660 | 36.5864 | -121.9148 | CGC411442446816 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023555 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1416700 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023595&numberofmonths=24&showchangehistorylog=1 | 19-0023595 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2202 | 182852202 | FUSE | 1421 | 20190213 | 710 | 310527 | 4978 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 104538 | 36.5742 | -121.9483 | 7SPANSLSOF1421 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023595 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416743 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023894&numberofmonths=24&showchangehistorylog=1 | 19-0023894 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2202 | 182852202 | TRIP-SAVER | 9089 | 20190213 | 828 | 303242 | 3206 | Distribution Circuit | Vegetation | Tree - fell into line | 102 | 327012 | 36.6057 | -121.9381 | 1070MISSIONRD2908SLOATRD3071ELTORORD3115MIDDLERANCHRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023894 | OH | Sus | 43677321 | yes | 2019 | FEB | Yes | Line to Ground | 1417026 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024100&numberofmonths=24&showchangehistorylog=1 | 19-0024100 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2202 | 182852202 | FUSE | 8187 | 20190213 | 828 | 312287 | 6415 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 301505 | 36.6035 | -121.9435 | 8SPANSLSOF8187 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024100 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1417190 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023084&numberofmonths=24&showchangehistorylog=1 | 19-0023084 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2203 | 182852203 | FUSE | 1445 | 20190213 | 1816 | 305595 | 2790 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 21423 | 36.5735 | -121.9107 | 2SPANSLDSIDEOF1445 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023084 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416283 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022936&numberofmonths=24&showchangehistorylog=1 | 19-0022936 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2204 | 182852204 | FUSE | 83339 | 20190213 | 1009 | 303622 | 6204 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 55836 | 36.6033 | -121.9354 | LOADSIDE83339 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022936 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416166 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023065&numberofmonths=24&showchangehistorylog=1 | 19-0023065 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2204 | 182852204 | FUSE | 6931 | 20190213 | 1131 | 304147 | 2073 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 43896 | 36.581 | -121.9046 | 2VIACASTANADA | Overcast-Drizzle-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0023065 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416269 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023219&numberofmonths=24&showchangehistorylog=1 | 19-0023219 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | RECLOSER | 5144 | 20190214 | 1229 | 308769 | 1857 | Distribution Circuit | Vegetation | Tree - fell into line | 146 | 234460 | 37.0911 | -122.0774 | 2SPANSSOURCESIDE11027NORTH | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023219 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1416407 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023290&numberofmonths=24&showchangehistorylog=1 | 19-0023290 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE | 5131 | 20190214 | 337 | 306960 | 1941 | Distribution Circuit | Vegetation | Tree - fell into line | 112 | 83440 | 37.0901 | -122.0899 | 2SPANSNORTHOFMETER1007589126 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023290 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1416477 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024032&numberofmonths=24&showchangehistorylog=1 | 19-0024032 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE | 5141 | 20190214 | 419 | 306746 | 2028 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 24336 | 37.0946 | -122.0864 | 2SPANSLDSIDEOF5141 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024032 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1417138 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023421&numberofmonths=24&showchangehistorylog=1 | 19-0023421 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE | 3603 | 20190214 | 558 | 308250 | 3342 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 30078 | 37.1149 | -122.1138 | TINKERSTRAILS2SPANSLDOF3603 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023421 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416575 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024523&numberofmonths=24&showchangehistorylog=1 | 19-0024523 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 9779 | 20190214 | 508 | 306959 | 3502 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 21012 | 37.1545 | -122.0827 | 135WHALEBONEGULCH | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024523 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1417605 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022890&numberofmonths=24&showchangehistorylog=1 | 19-0022890 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 5465 | 20190214 | 629 | 307462 | 467 | Distribution Circuit | Vegetation | Tree - branch fell on line | 55 | 25685 | 37.1392 | -122.1485 | 1SPANLOADSIDE5465 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022890 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416128 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023017&numberofmonths=24&showchangehistorylog=1 | 19-0023017 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2104 | 83622104 | JUMPER | WIREDOWN2SPANSPASTMT1007328258 | 20190214 | 606 | 308087 | 1808 | Distribution Circuit | Vegetation | Tree - branch fell on line | 27 | 23868 | 37.1523 | -122.1386 | 2SPANSPASTMTR1007328258 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023017 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1416237 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023038&numberofmonths=24&showchangehistorylog=1 | 19-0023038 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 6087 | 20190214 | 414 | 306780 | 2092 | Distribution Circuit | Vegetation | Tree - fell into line | 666 | 531645 | 37.0669 | -122.0336 | WOLVERINEANDWESTONRD2SPANLDSIDEOF608510010MARINERARD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023038 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1416255 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023166&numberofmonths=24&showchangehistorylog=1 | 19-0023166 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 9733 | 20190214 | 739 | 307463 | 884 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 36244 | 37.158 | -122.1357 | MTR1009946190 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023166 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1416359 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023587&numberofmonths=24&showchangehistorylog=1 | 19-0023587 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 11645 | 20190214 | 213 | 306350 | 3865 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 12540 | 37.0695 | -122.0913 | 3SPANSLSOF11645 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023587 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416735 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023672&numberofmonths=24&showchangehistorylog=1 | 19-0023672 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 7799 | 20190214 | 1419 | 310290 | 2096 | Distribution Circuit | Vegetation | Tree - branch fell on line | 61 | 32428 | 37.0909 | -122.1397 | 101VERDEDRTRANSFORMERMTR1008444897 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023672 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416823 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024449&numberofmonths=24&showchangehistorylog=1 | 19-0024449 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 5225 | 20190214 | 216 | 306571 | 3514 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 35140 | 37.0498 | -122.0856 | loadside5225 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024449 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1417535 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022802&numberofmonths=24&showchangehistorylog=1 | 19-0022802 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER | 10294 | 20190214 | 415 | 306745 | 2392 | Distribution Circuit | Vegetation | Tree - fell into line | 430 | 670999 | 37.0992 | -122.0531 | CAPWELL3915831206128010775LOMPICORD | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0022802 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416046 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023080&numberofmonths=24&showchangehistorylog=1 | 19-0023080 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 3753 | 20190214 | 227 | 306382 | 2088 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 7464 | 37.0539 | -121.9528 | BRANDT41798312122088lastspanat790TwinLanessmallredwoodfellintolines | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023080 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416279 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023240&numberofmonths=24&showchangehistorylog=1 | 19-0023240 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | FELTON-0401 | 83140401 | FUSE | 5217 | 20190214 | 1243 | 309139 | 1547 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 23205 | 37.0374 | -122.0662 | DARBYSHIRE41778312122089ONANDREALANE4POLESLOADSIDEOFSSD5217 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023240 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416432 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024114&numberofmonths=24&showchangehistorylog=1 | 19-0024114 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | FELTON-0401 | 83140401 | TRANSFORMER | 315427019690 | 20190214 | 1635 | 310209 | 4229 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 4229 | 37.0302 | -122.0674 | BOYNTON34598313316620410GLENGARRYRD | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024114 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1417202 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024520&numberofmonths=24&showchangehistorylog=1 | 19-0024520 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2102 | 83252102 | FUSE | 11829 | 20190214 | 1803 | 310520 | 2587 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 12935 | 37.009 | -122.0756 | LOADSIDE11829 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024520 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1417603 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023331&numberofmonths=24&showchangehistorylog=1 | 19-0023331 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | FUSE | 1033 | 20190214 | 950 | 308325 | 1900 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 11400 | 36.9853 | -121.8621 | TRANSF316022018005 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0023331 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416504 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023424&numberofmonths=24&showchangehistorylog=1 | 19-0023424 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 4431 | 20190214 | 1235 | 309634 | 2300 | Distribution Circuit | Vegetation | Tree - fell into line | 108 | 248400 | 37.0195 | -121.8182 | 1SPANLSOF4431 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023424 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416577 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023087&numberofmonths=24&showchangehistorylog=1 | 19-0023087 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | JUMPER | WIREDOWNSSOF6445 | 20190214 | 658 | 307269 | 3482 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 24374 | 36.5808 | -121.9189 | WIREDOWNTOEOL | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023087 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416286 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022824&numberofmonths=24&showchangehistorylog=1 | 19-0022824 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2202 | 182852202 | OCB | 22022 | 20190214 | 507 | 306671 | 4892 | Distribution Circuit | Vegetation | Tree - fell into line | 4847 | 1473842 | 36.5786 | -121.9085 | VALLEJOCRAIG831682182658LindaVista | Partly Cloudy-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022824 | OH | Sus | 31425388 | yes | 2019 | FEB | Yes | Line to Ground | 1416070 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023034&numberofmonths=24&showchangehistorylog=1 | 19-0023034 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2204 | 182852204 | FUSE | 6117 | 20190214 | 601 | 307620 | 2069 | Distribution Circuit | Equipment Failure/Involved | Overhead | 156 | 271244 | 36.5927 | -121.9073 | SOURCESIDEOF6779 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023034 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416253 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024014&numberofmonths=24&showchangehistorylog=1 | 19-0024014 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2204 | 182852204 | FUSE | 8895 | 20190214 | 552 | s1417125 | 1900 | Distribution Circuit | Vegetation | Tree - fell into line | 105 | 199500 | 36.5891 | -121.9104 | 2SPANSSOF8135 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024014 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1417125 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024654&numberofmonths=24&showchangehistorylog=1 | 19-0024654 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 5331 | 20190215 | 1359 | 312294 | 1681 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 33620 | 37.0245 | -121.9879 | 2SPANSSOUTHOFFUES5331 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024654 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1417725 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023950&numberofmonths=24&showchangehistorylog=1 | 19-0023950 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 9237 | 20190215 | 1032 | 311864 | 356 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1068 | 37.0789 | -122.0518 | ZAYANTERDZAYANTESCHOOLRDLOMPICO | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 19-0023950 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1417070 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024123&numberofmonths=24&showchangehistorylog=1 | 19-0024123 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | LAURELES-1111 | 182371111 | FUSE | 7601 | 20190215 | 913 | 311642 | 1927 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3854 | 36.4483 | -121.6838 | 6SPANSLSOF7601 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024123 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1417211 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024197&numberofmonths=24&showchangehistorylog=1 | 19-0024197 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE | 8353 | 20190215 | 1650 | 312641 | 1208 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 9664 | 37.0582 | -121.9417 | 6SPANNOF5991 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024197 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1417278 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024269&numberofmonths=24&showchangehistorylog=1 | 19-0024269 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | OTHER | WIREDOWNCGC315933018430 | 20190215 | 1737 | 312721 | 1408 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 11881 | 36.9972 | -121.8948 | CGC315933018430 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024269 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1417347 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024742&numberofmonths=24&showchangehistorylog=1 | 19-0024742 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 1655 | 20190216 | 1721 | 314835 | 1226 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 12260 | 37.1027 | -122.0483 | 2SPANSLOADSIDE2655 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024742 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1417815 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024443&numberofmonths=24&showchangehistorylog=1 | 19-0024443 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE | 2233 | 20190216 | 556 | 313437 | 238 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 2142 | 36.5726 | -121.8828 | VALLEJOCRAIG8316821826571AquajitoRd | Partly Cloudy-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024443 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1417528 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025152&numberofmonths=24&showchangehistorylog=1 | 19-0025152 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 8503 | 20190217 | 1302 | 315896 | 215 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 430 | 37.1711 | -122.2183 | 2SPNSLDSIDEOF77767 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025152 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1418231 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025123&numberofmonths=24&showchangehistorylog=1 | 19-0025123 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | LAURELES-1111 | 182371111 | FUSE | 2949 | 20190217 | 620 | 315261 | 820 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 50840 | 36.445 | -121.6735 | LOADSIDE2949 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025123 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1418203 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028597&numberofmonths=24&showchangehistorylog=1 | 19-0028597 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE | 3603 | 20190226 | 2132 | 325323 | 946 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 8514 | 37.1149 | -122.1138 | 825TINKERSTRAIL | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028597 | OH | Sus | 43685094 | yes | 2019 | FEB | Yes | Line to Ground | 1420503 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0029083&numberofmonths=24&showchangehistorylog=1 | 19-0029083 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5515 | 20190227 | 1332 | 327115 | 1321 | Distribution Circuit | Vegetation | Tree - fell into line | 91 | 48747 | 37.1524 | -122.1342 | 1SPSS2SPLS8257 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0029083 | OH | Sus | 43687242 | yes | 2019 | FEB | Yes | Line to Ground | 1420863 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028703&numberofmonths=24&showchangehistorylog=1 | 19-0028703 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | TRIP-SAVER | 8403 | 20190227 | 221 | 326153 | 631 | Distribution Circuit | Vegetation | Tree - fell into line | 141 | 20772 | 37.1548 | -122.1333 | 12SPANSLOADSIDE9133 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028703 | OH | Sus | 43685094 | yes | 2019 | FEB | Yes | Multi-Fault | 1420614 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028797&numberofmonths=24&showchangehistorylog=1 | 19-0028797 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | POINT MORETTI-1101 | 82931101 | FUSE | 5995 | 20190227 | 518 | 326347 | 2097 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 5079 | 37.078 | -122.244 | MTR10702J | Overcast-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0028797 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1420685 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028656&numberofmonths=24&showchangehistorylog=1 | 19-0028656 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | OCB | 22012 | 20190227 | 43 | 325967 | 455 | Distribution Circuit | Vegetation | Tree - fell into line | 849 | 165487 | 36.5786 | -121.9085 | 3SPANNORTHOF40333 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028656 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1420562 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0064604&numberofmonths=24&showchangehistorylog=1 | 19-0064604 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2107 | 83252107 | OTHER | WIREDOWN | 20190608 | 1043 | 401447 | 29267 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 65606 | 37.0055 | -122.1157 | 1015SMITHGRADE | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0064604 | OH | Sus | 0 | yes | 2019 | JUN | Yes | Line to Ground | 1446821 | PW | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0065104&numberofmonths=24&showchangehistorylog=1 | 19-0065104 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2104 | 182222104 | FUSE | 23665 | 20190610 | 436 | 403105 | 708 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 8889 | 36.5367 | -121.7377 | ADORNIJUSTIN8312358361copole3207 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0065104 | OH | Sus | 0 | yes | 2019 | JUN | Yes | Line to Ground | 1447415 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0088407&numberofmonths=24&showchangehistorylog=1 | 19-0088407 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE | 5985 | 20190815 | 1444 | 513553 | 72 | Distribution Circuit | Equipment Failure/Involved | Overhead | 88 | 6336 | 37.045 | -121.9384 | 854OLIVESPRINGRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0088407 | OH | Sus | 0 | yes | 2019 | AUG | Yes | Force Out | 1463357 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0118288&numberofmonths=24&showchangehistorylog=1 | 19-0118288 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 7969 | 20191026 | 2042 | 692818 | 4436 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 8872 | 37.0686 | -122.0158 | LDSIDEOF7969 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0118288 | OH | Sus | 0 | yes | 2019 | OCT | Yes | Line to Ground | 1487290 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0010232&numberofmonths=24&showchangehistorylog=1 | 20-0010232 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BURNS-2101 | 183582101 | JUMPER | OJ2SSSOF90CARTER | 20200116 | 904 | 763185 | 658 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1316 | 37.054 | -122.1588 | 90CARTER | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0010232 | OH | Sus | 44157208 | yes | 2020 | JAN | Yes | Line to Ground | 1506962 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0010080&numberofmonths=24&showchangehistorylog=1 | 20-0010080 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE | 2233 | 20200116 | 1436 | 763116 | 139 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 1529 | 36.5726 | -121.8828 | 5SNEOF2233 | Overcast-Rain-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 20-0010080 | OH | Sus | 0 | yes | 2020 | JAN | Yes | Open Circuit | 1506910 | CSO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0009638&numberofmonths=24&showchangehistorylog=1 | 20-0009638 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | POINT MORETTI-1101 | 82931101 | RECLOSER | 5078 | 20200116 | 906 | 762422 | 494 | Distribution Circuit | Vegetation | Tree - branch fell on line | 800 | 171201 | 37.0315 | -122.1867 | 8759 | Partly Cloudy-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0009638 | OH | Sus | 44157208 | yes | 2020 | JAN | Yes | Line to Ground | 1506749 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0009991&numberofmonths=24&showchangehistorylog=1 | 20-0009991 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 5411 | 20200116 | 906 | 763040 | 549 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 9333 | 37.0549 | -122.1609 | 150THAYERROAD | Partly Cloudy-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0009991 | OH | Sus | 31486501 | yes | 2020 | JAN | Yes | Line to Line | 1506879 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0019015&numberofmonths=24&showchangehistorylog=1 | 20-0019015 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 6911 | 20200209 | 816 | 781532 | 335 | Distribution Circuit | Vegetation | Tree - branch fell on line | 94 | 31490 | 37.0172 | -121.7218 | 10SPLDSIDEOF6911 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0019015 | OH | Sus | 0 | yes | 2020 | FEB | Yes | Line to Line | 1513028 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0032166&numberofmonths=24&showchangehistorylog=1 | 20-0032166 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 12455 | 20200315 | 100 | 851642 | 512 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 5760 | 37.0966 | -121.9931 | 2SOURCESIDEOF4607EASTSIDE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0032166 | OH | Sus | 31495831 | yes | 2020 | MAR | Yes | Line to Ground | 1521499 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0032258&numberofmonths=24&showchangehistorylog=1 | 20-0032258 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | OCB | 22012 | 20200315 | 934 | 852139 | 86 | Distribution Circuit | Vegetation | Tree - fell into line | 82 | 5732 | 36.5786 | -121.9085 | 1SPANNOF9893 | Overcast-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on ground | 20-0032258 | OH | Sus | 0 | yes | 2020 | MAR | Yes | Multi-Fault | 1521592 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0032480&numberofmonths=24&showchangehistorylog=1 | 20-0032480 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 6087 | 20200316 | 7 | 853030 | 182 | Distribution Circuit | Vegetation | Tree - bark fell into line | 181 | 32942 | 37.0669 | -122.0336 | JUSTLDSIDEOF2969 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0032480 | OH | Sus | 0 | yes | 2020 | MAR | Yes | Line to Line | 1521812 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0032481&numberofmonths=24&showchangehistorylog=1 | 20-0032481 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 2969 | 20200316 | 7 | 853308 | 698 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 2094 | 37.0674 | -122.0334 | JUSTLDSIDEOF2969 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0032481 | OH | Sus | 0 | yes | 2020 | MAR | Yes | Line to Line | 1521813 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0085566&numberofmonths=24&showchangehistorylog=1 | 20-0085566 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5477 | 20200816 | 2103 | 1014188 | 1305 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 67744 | 37.1291 | -122.1142 | LDSIDEOF5477 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0085566 | OH | Sus | 0 | yes | 2020 | AUG | Yes | Force Out | 1555963 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0085007&numberofmonths=24&showchangehistorylog=1 | 20-0085007 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 6161 | 20200816 | 252 | 1012937 | 898 | Distribution Circuit | Equipment Failure/Involved | Overhead | 23 | 20654 | 37.1182 | -122.0198 | LDSIDEOF6161 | Partly Cloudy-32-90 F | Crossarm, Wood | Broken, wire on ground | 20-0085007 | OH | Sus | 0 | yes | 2020 | AUG | Yes | Line to Ground | 1555454 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0084687&numberofmonths=24&showchangehistorylog=1 | 20-0084687 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | CAMP EVERS-2106 | 83622106 | RECLOSER | 12760 | 20200816 | 434 | 1010524 | 749 | Distribution Circuit | Equipment Failure/Involved | Overhead | 397 | 68445 | 37.0676 | -121.9966 | 1SOF2535 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0084687 | OH | Sus | 0 | yes | 2020 | AUG | Yes | Line to Line | 1555156 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0084706&numberofmonths=24&showchangehistorylog=1 | 20-0084706 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 8137 | 20200816 | 252 | 1010502 | 1000 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 14000 | 37.0581 | -121.9803 | CLARKROBERT510JarvisRd | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0084706 | OH | Sus | 0 | yes | 2020 | AUG | Yes | Line to Ground | 1555177 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0084775&numberofmonths=24&showchangehistorylog=1 | 20-0084775 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 1159 | 20200816 | 241 | 1011479 | 1260 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 42840 | 37.0409 | -122.0795 | 2PNORTHOF1159 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0084775 | OH | Sus | 0 | yes | 2020 | AUG | Yes | Line to Ground | 1555246 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0084611&numberofmonths=24&showchangehistorylog=1 | 20-0084611 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 6121 | 20200816 | 239 | 1011539 | 1015 | Distribution Circuit | Vegetation | Tree - fell into line | 108 | 109620 | 36.9836 | -121.8848 | VEDERNACK8312330543110RossRd | Partly Cloudy-32-90 F | Crossarm, Wood | Broken, wire on ground | 20-0084611 | OH | Sus | 0 | yes | 2020 | AUG | Yes | Line to Ground | 1555259 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0085160&numberofmonths=24&showchangehistorylog=1 | 20-0085160 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 3459 | 20200816 | 1146 | 1013115 | 364 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 33545 | 37.0246 | -121.8841 | 13NOF12673 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0085160 | OH | Sus | 0 | yes | 2020 | AUG | Yes | Line to Ground | 1555589 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0085524&numberofmonths=24&showchangehistorylog=1 | 20-0085524 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 6087 | 20200817 | 322 | 1014489 | 1061 | Distribution Circuit | Vegetation | Tree - fell into line | 181 | 141530 | 37.0667 | -122.0336 | 9SPANSNOF6087 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0085524 | OH | Sus | 0 | yes | 2020 | AUG | Yes | Line to Ground | 1555927 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0094801&numberofmonths=24&showchangehistorylog=1 | 20-0094801 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | RIO DEL MAR-0401 | 83260401 | FUSE | 7075 | 20200908 | 653 | 1060599 | 783 | Distribution Circuit | Vegetation | Tree - fell into line | 244 | 54525 | 36.9717 | -121.9021 | CGC315900517394 | Clear-32-90 F | Transformer (OH) | Broken, wire on ground | 20-0094801 | OH | Sus | 0 | yes | 2020 | SEP | Yes | Line to Ground | 1562186 | TXO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0009704&numberofmonths=24&showchangehistorylog=1 | 21-0009704 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 7593 | 20210118 | 1001 | 1212381 | 532 | Distribution Circuit | Vegetation | Tree - branch fell on line | 85 | 37226 | 37.1057 | -121.9724 | 17240LAURELRD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0009704 | OH | Sus | 44628039 | No | 2021 | JAN | Yes | Open Circuit | 1593701 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0010780&numberofmonths=24&showchangehistorylog=1 | 21-0010780 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 764889 | 20210119 | 512 | 1214819 | 815 | Distribution Circuit | Equipment Failure/Involved | Overhead | 344 | 169471 | 37.0019 | -122.0376 | 149STALBANST | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 21-0010780 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Line | 1594649 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0011105&numberofmonths=24&showchangehistorylog=1 | 21-0011105 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 3279 | 20210119 | 1025 | 1217223 | 499 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 10479 | 37.0434 | -121.9977 | 7SPANSLOADSIDEOF3279 | Strong Winds-Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0011105 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1594871 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0012724&numberofmonths=24&showchangehistorylog=1 | 21-0012724 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 3537 | 20210119 | 17 | 1221136 | 5263 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 105260 | 37.0747 | -121.9603 | CGC315755021200 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0012724 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1595774 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0010509&numberofmonths=24&showchangehistorylog=1 | 21-0010509 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1102 | 182941102 | FUSE | 7793 | 20210119 | 853 | 1215368 | 282 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 1692 | 36.2639 | -121.8002 | LASTSPANOF7793 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0010509 | OH | Sus | 0 | No | 2021 | JAN | Yes | Force Out | 1594456 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0013207&numberofmonths=24&showchangehistorylog=1 | 21-0013207 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | JUMPER | FUSE11739 | 20210119 | 41 | 1221607 | 6799 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 61191 | 37.0654 | -122.1256 | THORNEALLANIFO500WILDIRISLNTREEFELL | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0013207 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1596188 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0014252&numberofmonths=24&showchangehistorylog=1 | 21-0014252 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 8259 | 20210125 | 2240 | 1225431 | 835 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 12482 | 37.1594 | -122.1269 | CGC315277025320 | Clear-32-90F | Crossarm, Wood | Broken, wire on ground | 21-0014252 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1597048 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0013669&numberofmonths=24&showchangehistorylog=1 | 21-0013669 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER | 11384 | 20210125 | 759 | 1223696 | 343 | Distribution Circuit | Vegetation | Tree - fell into line | 2398 | 306988 | 37.0534 | -122.0437 | ATCGC315462020347 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0013669 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Line | 1596629 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0013541&numberofmonths=24&showchangehistorylog=1 | 21-0013541 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | POINT MORETTI-1101 | 82931101 | RECLOSER | 35874 | 20210125 | 7 | 1222992 | 703 | Distribution Circuit | Vegetation | Tree - branch fell on line | 558 | 164396 | 37.0312 | -122.1882 | VEDERNACK83123305434600BonnyDoonRdSSOF5078 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0013541 | OH | Sus | 44633345 | No | 2021 | JAN | Yes | Line to Line | 1596529 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0016196&numberofmonths=24&showchangehistorylog=1 | 21-0016196 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE | 12377 | 20210127 | 1027 | 1234876 | 388 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 3262 | 37.1052 | -122.1064 | CGC315311622349 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0016196 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Line | 1598651 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0016912&numberofmonths=24&showchangehistorylog=1 | 21-0016912 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | RECLOSER | 5028 | 20210127 | 2049 | 1237733 | 89 | Distribution Circuit | Vegetation | Tree - fell into line | 584 | 51976 | 37.1284 | -122.1222 | 650MANZANITAAVE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0016912 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1599219 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0015778&numberofmonths=24&showchangehistorylog=1 | 21-0015778 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 5339 | 20210127 | 245 | 1232391 | 637 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 8281 | 37.0502 | -121.981 | 2SPANSSOURCESIDEOFCGC315665120487 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0015778 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1598321 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0015501&numberofmonths=24&showchangehistorylog=1 | 21-0015501 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2103 | 182222103 | RECLOSER | 2000 | 20210127 | 128 | 1231910 | 844 | Distribution Circuit | Vegetation | Tree - fell into line | 217 | 183148 | 36.5852 | -121.8743 | VALENZUELAJAIME8316821682528LOMAALTAMONTEREYCA | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0015501 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1598041 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0015454&numberofmonths=24&showchangehistorylog=1 | 21-0015454 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HATTON-1101 | 182291101 | SWITCH | 8687 | 20210127 | 112 | 1233712 | 1106 | Distribution Circuit | Vegetation | Tree - fell into line | 90 | 99540 | 36.5559 | -121.898 | SISSOM580883120626171spansouth627onmainline | Clear-32-90F | Crossarm, Wood | Broken, wire on ground | 21-0015454 | OH | Sus | 0 | No | 2021 | JAN | Yes | Force Out | 1598320 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0017127&numberofmonths=24&showchangehistorylog=1 | 21-0017127 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE | 7349 | 20210127 | 2356 | 1238548 | 676 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2704 | 37.0565 | -121.942 | 5601OLDSANJOSERD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0017127 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1599440 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0015710&numberofmonths=24&showchangehistorylog=1 | 21-0015710 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 5411 | 20210127 | 46 | 1231559 | 703 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 11951 | 37.0548 | -122.161 | 3PWOF5411 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0015710 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Line | 1598259 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0016234&numberofmonths=24&showchangehistorylog=1 | 21-0016234 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 8097 | 20210127 | 614 | 1233126 | 698 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 11866 | 37.0785 | -122.139 | BARGAS149683168218306spansLScouts8097 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 21-0016234 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Line | 1598683 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0016057&numberofmonths=24&showchangehistorylog=1 | 21-0016057 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 11333 | 20210127 | 121 | 1234911 | 909 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 4545 | 37.0122 | -121.8885 | CGC315937618970 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0016057 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1598537 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0016100&numberofmonths=24&showchangehistorylog=1 | 21-0016100 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 8643 | 20210127 | 126 | 1231867 | 567 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 22680 | 37.01 | -121.8859 | CLARKROBERTUpDrivewayfor814WestwoodDrive | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0016100 | OH | Sus | 0 | No | 2021 | JAN | Yes |  | 1598570 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0017284&numberofmonths=24&showchangehistorylog=1 | 21-0017284 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 8313 | 20210128 | 631 | 1238626 | 516 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 8772 | 37.099 | -122.12 | 3PSOF8313 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0017284 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1599535 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0099476&numberofmonths=24&showchangehistorylog=1 | 21-0099476 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER | 95050 | 20210804 | 755 | 1433409 | 610 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1970 | 512625 | 37.0888 | -122.0877 | WIREDOWNLDSIDE4743BRANCHATHWY9ANDALBATREE1LDSIDE7279 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0099476 | OH | Sus | 44932682 | No | 2021 | AUG | Yes | Line to Ground | 1654432 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0128730&numberofmonths=24&showchangehistorylog=1 | 21-0128730 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER | 243760 | 20211011 | 1034 | 1492771 | 391 | Distribution Circuit | Vegetation | Tree - fell into line | 1682 | 559642 | 37.1386 | -122.1775 | 3SPANSLOADSIDEOF9353ONTHEMAINLINETWD3017HWY236FALLENLEAFSAP103994918 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 21-0128730 | OH | Sus | 31554589 | No | 2021 | OCT | Yes | Line to Line | 1672829 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0136028&numberofmonths=24&showchangehistorylog=1 | 21-0136028 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE | 5143 | 20211024 | 932 | 1509231 | 238 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 6426 | 37.0994 | -122.0868 | 2SPLDSIDEOF5143 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0136028 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Ground | 1677497 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0135836&numberofmonths=24&showchangehistorylog=1 | 21-0135836 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE | 5743 | 20211024 | 744 | 1508408 | 508 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2540 | 37.1049 | -122.116 | 2SPANSLDSIDE5743 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0135836 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Line | 1677313 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0136517&numberofmonths=24&showchangehistorylog=1 | 21-0136517 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | OTHER | WIREDOWN6868SANLARENZOWY | 20211024 | 1459 | 1514519 | 209 | Distribution Circuit | Vegetation | Tree - branch fell on line | 23 | 3647 | 37.0592 | -122.0769 | 6869SANLARENZOWY | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0136517 | OH | Sus | 0 | No | 2021 | OCT | Yes | Open Circuit | 1677995 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0136413&numberofmonths=24&showchangehistorylog=1 | 21-0136413 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | OTHER | WIREDOWN5SPLDSDOF7565 | 20211024 | 1323 | 1513778 | 348 | Distribution Circuit | Vegetation | Tree - fell into line | 271 | 39604 | 37.005 | -121.9014 | 5SPLDSDOF7565 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0136413 | OH | Sus | 0 | No | 2021 | OCT | Yes | Open Circuit | 1677894 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0135694&numberofmonths=24&showchangehistorylog=1 | 21-0135694 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | OCB | 22012 | 20211024 | 723 | 1508276 | 493 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1798 | 90303 | 36.5786 | -121.9085 | 4SPANSNWOF912709LOPEZRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0135694 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Ground | 1677169 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0137039&numberofmonths=24&showchangehistorylog=1 | 21-0137039 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | OTTER-1102 | 182941102 | OTHER | WIREDOWNEOF6939 | 20211025 | 521 | 1516997 | 682 | Distribution Circuit | Vegetation | Tree - fell into line | 73 | 47368 | 36.3916 | -121.8754 | 37715PALOCOLORADO | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0137039 | OH | Sus | 0 | No | 2021 | OCT | Yes | Open Circuit | 1678493 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0156934&numberofmonths=24&showchangehistorylog=1 | 21-0156934 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | OTHER | WIREDOWN391980 | 20211213 | 37 | 1565601 | 980 | Distribution Circuit | Vegetation | Tree - fell into line | 175 | 118292 | 37.1468 | -122.0881 | 16201BEARCREEKRDLR3919802SPANSLSOF2829 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0156934 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1693825 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0157313&numberofmonths=24&showchangehistorylog=1 | 21-0157313 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 2923 | 20211213 | 705 | 1565815 | 625 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 30625 | 37.1737 | -122.1456 | 4SPANSLDSIDE2923 | Clear-32-90F | Conductor, Overhead | Broken, wire on object | 21-0157313 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1694225 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0156952&numberofmonths=24&showchangehistorylog=1 | 21-0156952 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 6087 | 20211213 | 426 | 1565708 | 406 | Distribution Circuit | Vegetation | Tree - branch fell on line | 186 | 75516 | 37.0665 | -122.0336 | ATCGC315535421319 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0156952 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1693849 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0156949&numberofmonths=24&showchangehistorylog=1 | 21-0156949 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 9463 | 20211213 | 559 | 1565765 | 278 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 16680 | 37.0697 | -122.0714 | 7860HIHNRD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0156949 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Line | 1693846 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0160562&numberofmonths=24&showchangehistorylog=1 | 21-0160562 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | RECLOSER | 16010 | 20211225 | 1124 | 1581319 | 304 | Distribution Circuit | Vegetation | Tree - branch fell on line | 140 | 24056 | 37.0886 | -122.0874 | IFO215RiversideAve37087918122085812 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0160562 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Line | 1698034 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0161049&numberofmonths=24&showchangehistorylog=1 | 21-0161049 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 5225 | 20211227 | 142 | 1583811 | 944 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 7235 | 37.0496 | -122.0856 | 2SPANLDSIDEOF969667 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0161049 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1698603 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0161023&numberofmonths=24&showchangehistorylog=1 | 21-0161023 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | TRIP-SAVER | 6601 | 20211227 | 420 | 1584296 | 455 | Distribution Circuit | Vegetation | Tree - branch fell on line | 35 | 15925 | 36.9942 | -121.7176 | 1SOURCESIDEOFCGC316458517967 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0161023 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1698570 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0106392&numberofmonths=24&showchangehistorylog=1 | 22-0106392 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | LAURELES-1111 | 182371111 | RECLOSER | 2020 | 20220906 | 1033 | 1801698 | 293 | Distribution Circuit | Vegetation | Tree - fell into line | 849 | 87909 | 36.4632 | -121.7119 | NOFCGC41235003953021760CACHAGUARD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0106392 | OH | Sus | 31615345 | No | 2022 | SEP | Yes | Line to Ground | 1766180 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0107132&numberofmonths=24&showchangehistorylog=1 | 22-0107132 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER | 12758 | 20220907 | 547 | 1803969 | 161 | Distribution Circuit | Vegetation | Tree - fell into line | 279 | 44919 | 37.1486 | -122.1745 | 4SPANSNOFLR12758JAMISONCREEK3POLESNOFSBS327 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0107132 | OH | Sus | 0 | No | 2022 | SEP | Yes | Line to Line | 1766626 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0138371&numberofmonths=24&showchangehistorylog=1 | 22-0138371 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5435 | 20221210 | 1044 | 1881626 | 375 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 2625 | 37.1175 | -122.1214 | 1SPANLDSIDEOF5435 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0138371 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1789199 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0138456&numberofmonths=24&showchangehistorylog=1 | 22-0138456 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 9769 | 20221210 | 1158 | 1881941 | 322 | Distribution Circuit | Vegetation | Tree - branch fell on line | 33 | 10626 | 37.1293 | -122.1204 | 390HUCKLEBERRYLANEORCGC315265423405 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0138456 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1789282 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0138154&numberofmonths=24&showchangehistorylog=1 | 22-0138154 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER | 5066 | 20221210 | 849 | 1880962 | 628 | Distribution Circuit | Vegetation | Tree - branch fell on line | 33 | 20724 | 37.1706 | -122.1655 | 19145BigBasinWay | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0138154 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1788988 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0138442&numberofmonths=24&showchangehistorylog=1 | 22-0138442 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 2923 | 20221210 | 953 | 1881335 | 537 | Distribution Circuit | Vegetation | Tree - branch fell on line | 45 | 24165 | 37.1737 | -122.1456 | 2SPANSLDSIDEOF2923 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0138442 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Line | 1789269 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0138126&numberofmonths=24&showchangehistorylog=1 | 22-0138126 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BURNS-2101 | 183582101 | FUSE | 1995 | 20221210 | 700 | 1880720 | 400 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 800 | 37.0556 | -122.1209 | 2SPANSLDSIDEOF1995 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0138126 | OH | Sus | 0 | No | 2022 | DEC | Yes | Force Out | 1788957 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0138226&numberofmonths=24&showchangehistorylog=1 | 22-0138226 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | OTHER | WIREDOWN1SPANLDSIDEOFCFC315508318685 | 20221210 | 844 | 1880911 | 145 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 1595 | 37.0026 | -122.0384 | 1SPANLDSIDEOFCGC315508318685 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0138226 | OH | Sus | 0 | No | 2022 | DEC | Yes | Open Circuit | 1789063 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0138235&numberofmonths=24&showchangehistorylog=1 | 22-0138235 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | JUMPER | OJ1SPANLDSIDEOFCGCG315455021192 | 20221210 | 824 | 1881394 | 688 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 3440 | 37.0716 | -122.0588 | 1SPANLDSIDEOFCGC315455021192 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0138235 | OH | Sus | 0 | No | 2022 | DEC | Yes | None | 1789072 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0138296&numberofmonths=24&showchangehistorylog=1 | 22-0138296 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1101 | 182941101 | FUSE | 1491 | 20221210 | 922 | 1881113 | 585 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 23400 | 36.5057 | -121.9352 | 1SPANLDSIDEOFCGC411391344074SAPID110390850 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 22-0138296 | OH | Sus | 0 | No | 2022 | DEC | Yes | Three Phase Fault | 1789129 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0142448&numberofmonths=24&showchangehistorylog=1 | 22-0142448 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE | 5955 | 20221231 | 12 | 1902898 | 933 | Distribution Circuit | Vegetation | Tree - fell into line | 167 | 155811 | 37.0022 | -121.942 | 7757 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0142448 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1794246 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0142481&numberofmonths=24&showchangehistorylog=1 | 22-0142481 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | POINT MORETTI-1101 | 82931101 | OTHER | 12122 | 20221231 | 450 | 1902999 | 622 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 39186 | 37.0666 | -122.2288 | 4SPANSSOF252963 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0142481 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1794279 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0142489&numberofmonths=24&showchangehistorylog=1 | 22-0142489 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | RECLOSER | 796388 | 20221231 | 529 | 1903038 | 539 | Distribution Circuit | Vegetation | Tree - fell into line | 269 | 118531 | 36.9818 | -121.901 | 895REDWOODDR | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0142489 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1794287 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0142449&numberofmonths=24&showchangehistorylog=1 | 22-0142449 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2203 | 182852203 | OCB | 22032 | 20221231 | 309 | 1902974 | 849 | Distribution Circuit | Vegetation | Tree - fell into line | 4856 | 1942256 | 36.5786 | -121.9085 | BET173393AND528872NDTORRESFUCO8247 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0142449 | OH | Sus | 0 | No | 2022 | DEC | Yes | Three Phase Fault | 1794247 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0007591&numberofmonths=24&showchangehistorylog=1 | 23-0007591 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 5219 | 20230105 | 1435 | 1922791 | 327 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 6213 | 37.0371 | -122.066 | 1SPLDSIDEOFCGC315438920007 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0007591 | OH | Sus | 0 | No | 2023 | JAN | Yes | Force Out | 1797801 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0007028&numberofmonths=24&showchangehistorylog=1 | 23-0007028 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2204 | 182852204 | FUSE | 6409 | 20230105 | 230 | 1920381 | 1032 | Distribution Circuit | Vegetation | Tree - fell into line | 108 | 111456 | 36.59 | -121.9115 | JUSTEASTOFCGC411446547163 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0007028 | OH | Sus | 0 | No | 2023 | JAN | Yes | Three Phase Fault | 1797329 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0008847&numberofmonths=24&showchangehistorylog=1 | 23-0008847 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 9769 | 20230107 | 1249 | 1926605 | 282 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 9306 | 37.1293 | -122.1204 | NEOF9769 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0008847 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1798705 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0006449&numberofmonths=24&showchangehistorylog=1 | 23-0006449 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1102 | 182941102 | RECLOSER | 2002 | 20230107 | 901 | 1926203 | 29 | Distribution Circuit | Vegetation | Tree - branch fell on line | 30 | 870 | 36.2248 | -121.7587 | 4SPANSLDSIDE1375 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 23-0006449 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1798580 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0010216&numberofmonths=24&showchangehistorylog=1 | 23-0010216 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 1143 | 20230108 | 129 | 1931781 | 998 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 13972 | 37.0043 | -122.0202 | 1PLDSIDEOF1143 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0010216 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Line | 1800067 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0010256&numberofmonths=24&showchangehistorylog=1 | 23-0010256 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE | 7681 | 20230108 | 1355 | 1933716 | 276 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 2760 | 36.5832 | -121.865 | 7681SSTWD1SPANLDSIDE | Clear-32-90 F | Conductor, Overhead | On Ground | 23-0010256 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1800105 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0010081&numberofmonths=24&showchangehistorylog=1 | 23-0010081 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2104 | 182222104 | FUSE | 2811 | 20230108 | 948 | 1932990 | 160 | Distribution Circuit | Vegetation | Tree - branch fell on line | 20 | 3200 | 36.5143 | -121.8127 | 1SPANLDSIDEOF411738444188 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0010081 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1799927 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0009843&numberofmonths=24&showchangehistorylog=1 | 23-0009843 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2202 | 182852202 | FUSE | 8895 | 20230108 | 106 | 1931497 | 816 | Distribution Circuit | Vegetation | Tree - branch fell on line | 144 | 99272 | 36.5891 | -121.9104 | 2SPANSSSO8135 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0009843 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Line | 1799693 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0009789&numberofmonths=24&showchangehistorylog=1 | 23-0009789 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2203 | 182852203 | FUSE | 1445 | 20230108 | 7 | 1930410 | 1109 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 13308 | 36.5735 | -121.9108 | 7347 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0009789 | OH | Sus | 0 | No | 2023 | JAN | Yes | Three Phase Fault | 1799628 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0010784&numberofmonths=24&showchangehistorylog=1 | 23-0010784 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | RECLOSER | 5400 | 20230109 | 518 | 1935806 | 570 | Distribution Circuit | Environmental/External | Flood/Erosion | 9 | 5130 | 37.0801 | -122.0838 | 7231 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0010784 | OH | Sus | 0 | No | 2023 | JAN | Yes | Multi-Fault | 1800648 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0010782&numberofmonths=24&showchangehistorylog=1 | 23-0010782 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | JUMPER | OPENCREATEFORLR698634 | 20230109 | 519 | 1938059 | 543 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 43440 | 37.0955 | -122.0856 | 1TXNOF9125 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0010782 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1800966 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0010784&numberofmonths=24&showchangehistorylog=1 | 23-0010784 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER | 10996 | 20230109 | 518 | 1935780 | 435 | Distribution Circuit | Environmental/External | Flood/Erosion | 257 | 111795 | 37.0748 | -122.0845 | JUSTSOF7231 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 23-0010784 | OH | Sus | 0 | No | 2023 | JAN | Yes | Multi-Fault | 1800645 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0011010&numberofmonths=24&showchangehistorylog=1 | 23-0011010 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HATTON-1101 | 182291101 | FUSE | 627 | 20230109 | 337 | 1935465 | 1060 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 23320 | 36.5489 | -121.8966 | 4320TOLANDOTRL | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0011010 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Line | 1800841 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0010788&numberofmonths=24&showchangehistorylog=1 | 23-0010788 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | PANOCHE-1103 | 253671103 | RECLOSER | 4008 | 20230109 | 531 | 1935817 | 558 | Distribution Circuit | Vegetation | Tree - branch fell on line | 118 | 42833 | 36.6116 | -120.9293 | 1POLELOADSIDEOFCGC413946048765 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0010788 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1800649 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0010785&numberofmonths=24&showchangehistorylog=1 | 23-0010785 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | RECLOSER | 5178 | 20230109 | 524 | 1935790 | 480 | Distribution Circuit | Vegetation | Tree - fell into line | 267 | 99296 | 37.0324 | -121.9467 | MULTLOCATIONS | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0010785 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1800646 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0011143&numberofmonths=24&showchangehistorylog=1 | 23-0011143 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 68191 | 20230109 | 1156 | 1937988 | 205 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 3895 | 36.9816 | -121.9026 | LDSIDEOF68191 | Clear-32-90 F | Conductor, Overhead | On Ground | 23-0011143 | OH | Sus | 0 | No | 2023 | JAN | Yes | Force Out | 1800949 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0010786&numberofmonths=24&showchangehistorylog=1 | 23-0010786 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | OCB | 22012 | 20230109 | 216 | 1935800 | 1244 | Distribution Circuit | Vegetation | Tree - fell into line | 1289 | 1601657 | 36.5786 | -121.9085 | 2SPANWOF85171SPANSSOF40647 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0010786 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Line | 1800647 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0011726&numberofmonths=24&showchangehistorylog=1 | 23-0011726 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | SWITCH | 80069 | 20230110 | 202 | 1942969 | 767 | Distribution Circuit | Vegetation | Tree - branch fell on line | 423 | 129242 | 37.0455 | -122.0556 | THORNEALLAN2823ATSSD145NGXARMWIREDOWN | Overcast-Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 23-0011726 | OH | Sus | 0 | No | 2023 | JAN | Yes | None | 1801715 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0011726&numberofmonths=24&showchangehistorylog=1 | 23-0011726 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | SWITCH | 11025 | 20230110 | 202 | 1943868 | 531 | Distribution Circuit | Company Initiated | Return Circuit Normal | 172 | 91332 | 37.0508 | -122.0677 |  | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0011726 | OH | Sus | 0 | No | 2023 | JAN | Yes | None | 1801839 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0012684&numberofmonths=24&showchangehistorylog=1 | 23-0012684 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HATTON-1102 | 182291102 | FUSE | 10189 | 20230110 | 1528 | 1945741 | 129 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 516 | 36.5056 | -121.9365 | 1SPLDSIDEOF10189 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0012684 | OH | Sus | 0 | No | 2023 | JAN | Yes | Force Out | 1802327 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0015922&numberofmonths=24&showchangehistorylog=1 | 23-0015922 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HATTON SUB | 18229 | OCB | 11012 | 20230114 | 836 | 1953363 | 930 | Distribution Circuit | Vegetation | Tree - fell into line | 505 | 136405 | 36.5569 | -121.8976 | JUSTSOURCESIDEOF62725687CANADADR | Clear-32-90F | Crossarm, Wood | Broken, wire on ground | 23-0015922 | OH | Sus | 0 | No | 2023 | JAN | Yes | Three Phase Fault | 1804756 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0016178&numberofmonths=24&showchangehistorylog=1 | 23-0016178 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HATTON-1102 | 182291102 | FUSE | 1491 | 20230114 | 1015 | 1953903 | 715 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 15088 | 36.5057 | -121.9352 | CGC411390644052 | Clear-32-90 F | Conductor, Overhead | On Ground | 23-0016178 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Line | 1804955 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0016929&numberofmonths=24&showchangehistorylog=1 | 23-0016929 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER | 11384 | 20230116 | 518 | 1956858 | 769 | Distribution Circuit | Vegetation | Tree - fell into line | 416 | 88568 | 37.0534 | -122.0437 | FUCO1535CONFERENCDRCO153 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0016929 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1805636 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0017049&numberofmonths=24&showchangehistorylog=1 | 23-0017049 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 7593 | 20230116 | 250 | 1956601 | 655 | Distribution Circuit | Vegetation | Tree - fell into line | 68 | 44540 | 37.1057 | -121.9724 | 2SPANSLDSIDEOFCGC315708022457 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0017049 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1805748 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0017031&numberofmonths=24&showchangehistorylog=1 | 23-0017031 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2105 | 83692105 | JUMPER | WIREDOWN | 20230116 | 211 | 1956542 | 450 | Distribution Circuit | Vegetation | Tree - fell into line | 83 | 27288 | 36.9696 | -121.876 | 4SPANSLOADSIDEOF4399 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0017031 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1805735 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0017064&numberofmonths=24&showchangehistorylog=1 | 23-0017064 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 11327 | 20230116 | 538 | 1956873 | 682 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 682 | 36.9868 | -121.8846 | 1540TROUTGULCHRDAPTOS | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0017064 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1805762 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0016880&numberofmonths=24&showchangehistorylog=1 | 23-0016880 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | SEACLIFF-0401 | 83500401 | RECLOSER | 929132 | 20230116 | 240 | 1956588 | 837 | Distribution Circuit | Vegetation | Tree - fell into line | 127 | 106299 | 36.9919 | -121.927 | 1LDSIDEOFCGC315839418455 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0016880 | OH | Sus | 0 | No | 2023 | JAN | Yes | Three Phase Fault | 1805581 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0016893&numberofmonths=24&showchangehistorylog=1 | 23-0016893 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | SEACLIFF-0401 | 83500401 | RECLOSER | 12946 | 20230116 | 324 | 1956683 | 662 | Distribution Circuit | Vegetation | Tree - fell into line | 213 | 136302 | 36.9875 | -121.9186 | 1PLDSIDEOF7533VIENNADRNOFMESADR | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0016893 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Line | 1805594 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0016911&numberofmonths=24&showchangehistorylog=1 | 23-0016911 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 8917 | 20230116 | 342 | 1956737 | 551 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 11571 | 36.5771 | -121.9274 | 2POLESLDSIDEOF8917 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 23-0016911 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1805618 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0031165&numberofmonths=24&showchangehistorylog=1 | 23-0031165 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | RECLOSER | 5090 | 20230221 | 1407 | 1991279 | 38 | Distribution Circuit | Equipment Failure/Involved | Overhead | 325 | 12350 | 36.9804 | -121.892 | CGC315963317887 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0031165 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Ground | 1814859 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0031165&numberofmonths=24&showchangehistorylog=1 | 23-0031165 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 6121 | 20230221 | 1407 | 1991849 | 559 | Distribution Circuit | Equipment Failure/Involved | Overhead | 109 | 60931 | 36.9835 | -121.8848 | CGC315963317887 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0031165 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Ground | 1814938 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0033657&numberofmonths=24&showchangehistorylog=1 | 23-0033657 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BURNS-2101 | 183582101 | OCB | 21012 | 20230224 | 500 | 2002630 | 959 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1264 | 1179857 | 37.0953 | -122.1437 | 6LDSIDEOF983849 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0033657 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Ground | 1816695 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0036162&numberofmonths=24&showchangehistorylog=1 | 23-0036162 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BURNS SUB | 18358 | SWITCH | BURNS | 20230228 | 1205 | 2015200 | 87 | Distribution Circuit | Vegetation | Tree - fell into line | 2568 | 223416 | 37.0953 | -122.1438 | MONTEVISTABURNS60KVLINESAFETYCLEARANCETWR009074 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0036162 | OH | Sus | 0 | No | 2023 | FEB | Yes | Force Out | 1819747 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0036162&numberofmonths=24&showchangehistorylog=1 | 23-0036162 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | POINT MORETTI SUB | 8293 | SWITCH | POINTMORETTI | 20230228 | 1206 | 2015195 | 86 | Distribution Circuit | Vegetation | Tree - fell into line | 636 | 54696 | 37.0313 | -122.1875 | MONTEVISTABURNS60KVLINESAFETYCLEARANCETWR009074 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0036162 | OH | Sus | 0 | No | 2023 | FEB | Yes | Force Out | 1819749 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0044704&numberofmonths=24&showchangehistorylog=1 | 23-0044704 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 9005 | 20230314 | 912 | 2035418 | 522 | Distribution Circuit | Vegetation | Tree - branch fell on line | 22 | 11484 | 37.0318 | -122.1369 | CGC315228520045 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0044704 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Line | 1824849 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0044931&numberofmonths=24&showchangehistorylog=1 | 23-0044931 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 8097 | 20230314 | 1022 | 2035864 | 368 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 6256 | 37.0785 | -122.139 | CGC315222721433 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0044931 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1825021 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0045877&numberofmonths=24&showchangehistorylog=1 | 23-0045877 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | FUSE | 737 | 20230314 | 1821 | 2044095 | 202 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 11568 | 37.0046 | -121.8551 | 2429 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0045877 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1825801 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0045535&numberofmonths=24&showchangehistorylog=1 | 23-0045535 | CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | RECLOSER | 5090 | 20230314 | 1613 | 2042186 | 255 | Distribution Circuit | Vegetation | Tree - fell into line | 428 | 109140 | 36.9804 | -121.892 | 705SKYWARDDR | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0045535 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1825497 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0049798&numberofmonths=24&showchangehistorylog=1 | 23-0049798 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE | 6753 | 20230321 | 1426 | 2056682 | 419 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 15922 | 36.5659 | -121.8876 | SSOF6635ONTAPLINEFROM6753 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0049798 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1828504 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0049710&numberofmonths=24&showchangehistorylog=1 | 23-0049710 | CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HATTON-1101 | 182291101 | FUSE | 627 | 20230321 | 1255 | 2054707 | 401 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 8822 | 36.5489 | -121.8966 | 2LDSIDEOF627 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0049710 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Line | 1828432 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0022721&numberofmonths=24&showchangehistorylog=1 | 13-0022721 | DE ANZA | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | OTHER |  | 20130408 | 1421 | 770356 | 596 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 596 | 37.1447 | -121.9859 | 22235SUMMITRD | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 13-0022721 | OH | Sus | 0 | yes | 2013 | APR | Yes | Line to Ground | 99291926 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0022728&numberofmonths=24&showchangehistorylog=1 | 13-0022728 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | SWITCH | SB15 | 20130408 | 1555 | 770621 | 167 | Distribution Circuit | Equipment Failure/Involved | Other | 170 | 28390 | 37.1931 | -122.0196 | 3SPEOR119 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 13-0022728 | OH | Sus | 0 | yes | 2013 | APR | Yes | None | 99291922 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0073571&numberofmonths=24&showchangehistorylog=1 | 14-0073571 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | SWITCH | SB15 | 20141203 | 1707 | 1123765 | 1242 | Distribution Circuit | Vegetation | Tree - fell into line | 167 | 51262 | 37.1931 | -122.0196 | AGBALOGVINCEsame | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073571 | OH | Sus | 0 | yes | 2014 | DEC | Yes | None | 99196567 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0073128&numberofmonths=24&showchangehistorylog=1 | 14-0073128 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | RECLOSER | 60114 | 20141203 | 245 | 1121657 | 1157 | Distribution Circuit | Vegetation | Tree - fell into line | 291 | 274737 | 37.1191 | -121.9205 | 92101ONMAINLINE | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073128 | OH | Sus | 42284329 | yes | 2014 | DEC | Yes | Line to Ground | 99196307 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0073146&numberofmonths=24&showchangehistorylog=1 | 14-0073146 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 17431 | 20141203 | 344 | 1121676 | 766 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 24512 | 37.1103 | -121.951 | 16304REDWOODLODGERD | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073146 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99197001 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0073409&numberofmonths=24&showchangehistorylog=1 | 14-0073409 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 6947 | 20141203 | 1225 | 1123091 | 1055 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 9245 | 37.1172 | -121.9243 | 33257 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073409 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99196577 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0073519&numberofmonths=24&showchangehistorylog=1 | 14-0073519 | DE ANZA | FIELD OPS SOUTH | Tier 2 | SARATOGA-1106 | 83371106 | OTHER |  | 20141203 | 1528 | 1123621 | 1153 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1153 | 37.2408 | -122.0046 | AUSTINWAYSARALG | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073519 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99196572 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0073545&numberofmonths=24&showchangehistorylog=1 | 14-0073545 | DE ANZA | FIELD OPS SOUTH | Tier 2 | SARATOGA-1106 | 83371106 | FUSE | 5089 | 20141203 | 1129 | 1122897 | 1068 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 54353 | 37.2339 | -121.9978 | 18650WHITHEYRD | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073545 | OH | Sus | 3118510 | yes | 2014 | DEC | Yes | Three Phase Fault | 99196721 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075200&numberofmonths=24&showchangehistorylog=1 | 14-0075200 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | OTHER | 60124 | 20141211 | 859 | 1131925 | 596 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1574 | 548748 | 37.1732 | -121.9929 | G1IPJRHtreedownaccrossroadandwiresinsupportoftman | Strong winds-32 - 90 F | Other | Broken, wire on ground | 14-0075200 | OH | Sus | 42293239 | yes | 2014 | DEC | Yes |  | 99195066 | NON | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075306&numberofmonths=24&showchangehistorylog=1 | 14-0075306 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 9125 | 20141211 | 927 | 1132231 | 812 | Distribution Circuit | Equipment Failure/Involved | Other | 476 | 105949 | 37.1653 | -122.0175 | LGHBEARCREEKRDWOSUMMITRD | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075306 | OH | Sus | 42293239 | yes | 2014 | DEC | Yes | Line to Line | 99194361 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075384&numberofmonths=24&showchangehistorylog=1 | 14-0075384 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 7651 | 20141211 | 1122 | 1133222 | 618 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 4326 | 37.1945 | -122.0226 | 1SPANLOADSIDEOF7651 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075384 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194911 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075669&numberofmonths=24&showchangehistorylog=1 | 14-0075669 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | OTHER |  | 20141211 | 1427 | 1134340 | 678 | Distribution Circuit | Vegetation | Tree - fell into line | 86 | 20400 | 37.0989 | -121.9475 | LOADSIDEOF2911 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075669 | OH | Sus | 31120396 | yes | 2014 | DEC | Yes | Line to Ground | 99194703 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075428&numberofmonths=24&showchangehistorylog=1 | 14-0075428 | DE ANZA | FIELD OPS SOUTH | Tier 3 | SARATOGA-1107 | 83371107 | FUSE | 5203 | 20141211 | 852 | 1133449 | 899 | Distribution Circuit | Equipment Failure/Involved | Other | 99 | 35300 | 37.2351 | -122.0625 | 10SPANSWO5203 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075428 | OH | Sus | 42293239 | yes | 2014 | DEC | Yes | Line to Ground | 99194880 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075630&numberofmonths=24&showchangehistorylog=1 | 14-0075630 | DE ANZA | FIELD OPS SOUTH | Tier 3 | SARATOGA-1107 | 83371107 | FUSE | 15767 | 20141211 | 1536 | 1134656 | 69 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 621 | 37.2363 | -122.066 | ENDOFLINEWIREDOWNFEEDSIDLETRANSF | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075630 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Three Phase Fault | 99194734 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075295&numberofmonths=24&showchangehistorylog=1 | 14-0075295 | DE ANZA | FIELD OPS SOUTH | Tier 3 | STELLING-1110 | 83481110 | RECLOSER | 60094 | 20141211 | 917 | 1131873 | 853 | Distribution Circuit | Vegetation | Tree - fell into line | 270 | 47238 | 37.2571 | -122.1203 | STEVENSROBERT2polessok164 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075295 | OH | Sus | 31120421 | yes | 2014 | DEC | Yes |  | 99194986 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079406&numberofmonths=24&showchangehistorylog=1 | 14-0079406 | DE ANZA | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 5617 | 20141230 | 1605 | 1153765 | 1695 | Distribution Circuit | Equipment Failure/Involved | Other | 12 | 20340 | 37.1592 | -122.0189 | WILDERFIELDRD | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079406 | OH | Sus | 42304600 | yes | 2014 | DEC | Yes | Line to Line | 99190144 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079551&numberofmonths=24&showchangehistorylog=1 | 14-0079551 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | SWITCH | SA07 | 20141230 | 2034 | 1155873 | 2945 | Distribution Circuit | Vegetation | Tree - fell into line | 491 | 291402 | 37.1537 | -121.982 | BETFLYINGBELLSSO29129MTR100633641017035MELODY | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079551 | OH | Sus | 31124019 | yes | 2014 | DEC | Yes | Line to Ground | 99189717 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079668&numberofmonths=24&showchangehistorylog=1 | 14-0079668 | DE ANZA | FIELD OPS SOUTH | Tier 2 | SARATOGA-1107 | 83371107 | FUSE | 15771 | 20141230 | 2000 | 1156062 | 1808 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 33308 | 37.2482 | -122.0708 | 24500BIGBASINRDMTR1006719078 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079668 | OH | Sus | 31124019 | yes | 2014 | DEC | Yes | Line to Ground | 99189552 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079733&numberofmonths=24&showchangehistorylog=1 | 14-0079733 | DE ANZA | FIELD OPS SOUTH | Tier 3 | STELLING-1110 | 83481110 | FUSE | 8051 | 20141230 | 1940 | 1155271 | 1605 | Distribution Circuit | Vegetation | Tree - branch fell on line | 25 | 40125 | 37.2539 | -122.1236 | 12334FIRSTFORDRD | Strong winds-32 - 90 F | Conductor, Underground | Broken, wire on ground | 14-0079733 | OH | Sus | 42304601 | yes | 2014 | DEC | Yes | Line to Ground | 99189982 | CU | UG | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010831&numberofmonths=24&showchangehistorylog=1 | 15-0010831 | DE ANZA | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 18597 | 20150206 | 2056 | 1178468 | 1324 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 9584 | 37.1458 | -121.9835 | 315681923886 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010831 | OH | Sus | 42328658 | yes | 2015 | FEB | Yes | Line to Ground | 99184532 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010837&numberofmonths=24&showchangehistorylog=1 | 15-0010837 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | RECLOSER | 60092 | 20150206 | 2113 | 1178840 | 3338 | Distribution Circuit | Equipment Failure/Involved | Other | 204 | 52093 | 37.1817 | -121.9846 | 315679525167 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010837 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183397 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010384&numberofmonths=24&showchangehistorylog=1 | 15-0010384 | DE ANZA | FIELD OPS SOUTH | Tier 2 | SARATOGA-1107 | 83371107 | FUSE | 3721 | 20150206 | 1535 | 1176037 | 520 | Distribution Circuit | Equipment Failure/Involved | Other | 5 | 2600 | 37.25 | -122.032 | 315546527622 | Clear-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 15-0010384 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99185002 | CSO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010269&numberofmonths=24&showchangehistorylog=1 | 15-0010269 | DE ANZA | FIELD OPS SOUTH | Tier 2 | STELLING-1110 | 83481110 | FUSE | 1251 | 20150206 | 1408 | 1175762 | 122 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 652 | 37.2947 | -122.0821 | 315401429289 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010269 | OH | Sus | 31132912 | yes | 2015 | FEB | Yes | Line to Ground | 99183955 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011415&numberofmonths=24&showchangehistorylog=1 | 15-0011415 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 31331 | 20150207 | 2130 | 1181937 | 2086 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 16688 | 37.1606 | -121.9681 | 315724824382 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011415 | OH | Sus | 31132912 | yes | 2015 | FEB | Yes | Line to Line | 99183355 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010269&numberofmonths=24&showchangehistorylog=1 | 15-0010269 | DE ANZA | FIELD OPS SOUTH | Tier 2 | SARATOGA-1105 | 83371105 | SWITCH |  | 20150207 | 331 | 1179973 | 30 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 0 | 37.2789 | -122.0711 | 34MILELDSIDE1251 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010269 | OH | Sus | 31132912 | yes | 2015 | FEB | Yes |  | 99184696 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011044&numberofmonths=24&showchangehistorylog=1 | 15-0011044 | DE ANZA | FIELD OPS SOUTH | Tier 3 | SARATOGA-1107 | 83371107 | FUSE | 15769 | 20150207 | 634 | 1180520 | 1236 | Distribution Circuit | Vegetation | Tree - fell into line | 496 | 47618 | 37.2474 | -122.068 | 315438727544 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011044 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99184437 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011611&numberofmonths=24&showchangehistorylog=1 | 15-0011611 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 4417 | 20150208 | 1419 | 1182959 | 2351 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 6851 | 37.1978 | -122.0275 | 315552725781 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011611 | OH | Sus | 31132912 | yes | 2015 | FEB | Yes | Line to Line | 99182839 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011548&numberofmonths=24&showchangehistorylog=1 | 15-0011548 | DE ANZA | FIELD OPS SOUTH | Tier 2 | SARATOGA-1107 | 83371107 | FUSE | 15771 | 20150208 | 1219 | 1182674 | 963 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 18784 | 37.2482 | -122.0708 | 315426727623 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011548 | OH | Sus | 31132916 | yes | 2015 | FEB | Yes | Line to Ground | 99183732 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0084768&numberofmonths=24&showchangehistorylog=1 | 15-0084768 | DE ANZA | FIELD OPS SOUTH | Tier 3 | SARATOGA-1107 | 83371107 | OTHER | WIREDOWN5PLOADSIDE23069 | 20151213 | 1023 | 1361691 | 911 | Distribution Circuit | Vegetation | Tree - fell into line | 500 | 125830 | 37.2515 | -122.0662 | CONGRESSSPRINGSRDWOPIERCERD | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084768 | OH | Sus | 42588469 | yes | 2015 | DEC | Yes | Force Out | 1174436 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0013277&numberofmonths=24&showchangehistorylog=1 | 16-0013277 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 4451 | 20160217 | 1612 | 1405976 | 633 | Distribution Circuit | Vegetation | Tree - fell into line | 337 | 135477 | 37.1392 | -121.9747 | 23075OLDSANTACRUZHWY | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013277 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Line to Line | 1186364 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0013459&numberofmonths=24&showchangehistorylog=1 | 16-0013459 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 8349 | 20160217 | 2137 | 1407390 | 1838 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1838 | 37.1681 | -121.9802 | ALMABRIDGERDEASTOFLCO8349 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013459 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Line to Ground | 1186542 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0013647&numberofmonths=24&showchangehistorylog=1 | 16-0013647 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | OTHER | WIREDOWNONESPANNORTHOFMETER5000058672 | 20160217 | 2129 | 1407539 | 1006 | Distribution Circuit | Vegetation | Tree - branch fell on line | 129 | 111744 | 37.1008 | -121.9494 | HAUGENKIRK2SpansnorthofOHTXCCG315761822158 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013647 | OH | Sus | 42632627 | yes | 2016 | FEB | Yes | Open Circuit | 1186722 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0013316&numberofmonths=24&showchangehistorylog=1 | 16-0013316 | DE ANZA | FIELD OPS SOUTH | Tier 2 | SARATOGA-1104 | 83371104 | FUSE | 3571 | 20160217 | 1552 | 1405667 | 652 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 4564 | 37.2416 | -121.9919 | WESTOFCOUT3571 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013316 | OH | Sus | 42632627 | yes | 2016 | FEB | Yes | Line to Ground | 1186400 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0013596&numberofmonths=24&showchangehistorylog=1 | 16-0013596 | DE ANZA | FIELD OPS SOUTH | Tier 3 | SARATOGA-1107 | 83371107 | FUSE | 29951 | 20160217 | 1909 | 1406369 | 1157 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2314 | 37.2413 | -122.0413 | WILDCATRIDGERDPVTOFFQUICKERTRD | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | On Ground | 16-0013596 | OH | Sus | 42632627 | yes | 2016 | FEB | Yes | None | 1186676 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017487&numberofmonths=24&showchangehistorylog=1 | 16-0017487 | DE ANZA | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER | 60124 | 20160305 | 1347 | 1416718 | 1151 | Distribution Circuit | Vegetation | Tree - fell into line | 789 | 117853 | 37.1462 | -121.9823 | SummitRdandMtCharlieRdLoadSOMtr1007449626 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 16-0017487 | OH | Sus | 31222889 | yes | 2016 | MAR | Yes | Line to Ground | 1189367 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017809&numberofmonths=24&showchangehistorylog=1 | 16-0017809 | DE ANZA | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER | 60124 | 20160305 | 1727 | 1419060 | 1390 | Distribution Circuit | Equipment Failure/Involved | Overhead | 716 | 339716 | 37.1462 | -121.9823 | MADRONE2PNOFSW32915 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017809 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1189662 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017451&numberofmonths=24&showchangehistorylog=1 | 16-0017451 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER | 60116 | 20160305 | 1124 | 1416563 | 656 | Distribution Circuit | Vegetation | Tree - fell into line | 612 | 34496 | 37.1734 | -121.9929 | WSOFCOUTS965 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017451 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Multi-Fault | 1189334 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017573&numberofmonths=24&showchangehistorylog=1 | 16-0017573 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER | LB44 | 20160305 | 1624 | 1417274 | 2291 | Distribution Circuit | Vegetation | Tree - fell into line | 328 | 185751 | 37.1938 | -121.9959 | 18650BLACKRD3POLESLDSIDEOF21295 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017573 | OH | Sus | 31222889 | yes | 2016 | MAR | Yes | Line to Ground | 1189429 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017815&numberofmonths=24&showchangehistorylog=1 | 16-0017815 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 1429 | 20160305 | 1810 | 1418995 | 759 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 5184 | 37.1474 | -121.9749 | BILBREY52317957mtcharlie | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017815 | OH | Sus | 42646371 | yes | 2016 | MAR | Yes | Line to Ground | 1189668 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017840&numberofmonths=24&showchangehistorylog=1 | 16-0017840 | DE ANZA | FIELD OPS SOUTH | Tier 2 | STELLING-1110 | 83481110 | FUSE | 9265 | 20160305 | 1839 | 1418253 | 1211 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 70238 | 37.2937 | -122.102 | MTR235R13 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017840 | OH | Sus | 42646371 | yes | 2016 | MAR | Yes | Line to Ground | 1189694 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0018071&numberofmonths=24&showchangehistorylog=1 | 16-0018071 | DE ANZA | FIELD OPS SOUTH | Tier 3 | STELLING-1110 | 83481110 | JUMPER | 1SPANOFWIREDOWN7653TWD4985 | 20160305 | 2229 | 1420792 | 2916 | Distribution Circuit | Equipment Failure/Involved | Overhead | 171 | 227228 | 37.1991 | -122.0307 | FUCO7653JUMPER20202BLACKRDXARMMTR1007574757 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018071 | OH | Sus | 42646371 | yes | 2016 | MAR | Yes | Line to Ground | 1189944 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0003164&numberofmonths=24&showchangehistorylog=1 | 17-0003164 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 9125 | 20170103 | 1547 | 1615982 | 660 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 26457 | 37.1654 | -122.0173 | NSBEARCREEK1400WOSKYLINE20741 | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003164 | OH | Sus | 42909755 | yes | 2017 | JAN | Yes | Line to Ground | 1243332 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0002877&numberofmonths=24&showchangehistorylog=1 | 17-0002877 | DE ANZA | FIELD OPS SOUTH | Tier 3 | SARATOGA-1107 | 83371107 | FUSE | 7163 | 20170103 | 40 | 1615236 | 787 | Distribution Circuit | Vegetation | Tree - fell into line | 100 | 30724 | 37.2275 | -122.0525 | HAUGENKIRKatcopole5387 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0002877 | OH | Sus | 31292530 | yes | 2017 | JAN | Yes | Line to Ground | 1243197 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0003333&numberofmonths=24&showchangehistorylog=1 | 17-0003333 | DE ANZA | FIELD OPS SOUTH | Tier 3 | SARATOGA-1107 | 83371107 | JUMPER | WIREDOWN1SPANSSDOF11239 | 20170103 | 2130 | 1616948 | 1280 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 1280 | 37.2508 | -122.0942 | LAFON508endofbookercreekrd1spansourcesideof1123912kvdown | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003333 | OH | Sus | 42909755 | yes | 2017 | JAN | Yes | Line to Ground | 1243506 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005385&numberofmonths=24&showchangehistorylog=1 | 17-0005385 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 4451 | 20170108 | 1318 | 1627251 | 1197 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 34713 | 37.1365 | -121.9683 | WIREDOWNEO31297 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005385 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1245170 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005604&numberofmonths=24&showchangehistorylog=1 | 17-0005604 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | RECLOSER | 60092 | 20170108 | 1842 | 1627933 | 1149 | Distribution Circuit | Vegetation | Tree - fell into line | 843 | 919162 | 37.1825 | -121.985 | AGBALOGVINCEsame | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005604 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245382 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005263&numberofmonths=24&showchangehistorylog=1 | 17-0005263 | DE ANZA | FIELD OPS SOUTH | Tier 3 | SARATOGA-1107 | 83371107 | OTHER | WIREDOWN2PWO23069 | 20170108 | 1018 | 1624830 | 1922 | Distribution Circuit | Vegetation | Tree - fell into line | 494 | 174739 | 37.251 | -122.0649 | 2PWO23069NO29993 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005263 | OH | Sus | 31294278 | yes | 2017 | JAN | Yes | Force Out | 1245053 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0004885&numberofmonths=24&showchangehistorylog=1 | 17-0004885 | DE ANZA | FIELD OPS SOUTH | Tier 2 | STELLING-1110 | 83481110 | OTHER | WIREDOWN1PSO33481 | 20170108 | 42 | 1622449 | 643 | Distribution Circuit | Vegetation | Tree - branch fell on line | 63 | 6018 | 37.2849 | -122.078 | 1PSO33481 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004885 | OH | Sus | 42913015 | yes | 2017 | JAN | Yes | Line to Ground | 1244684 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006375&numberofmonths=24&showchangehistorylog=1 | 17-0006375 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 4533 | 20170109 | 1529 | 1631634 | 4281 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 10369 | 37.1748 | -122.0608 | 8SNO4533 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006375 | OH | Sus | 31294361 | yes | 2017 | JAN | Yes | Line to Ground | 1246081 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006326&numberofmonths=24&showchangehistorylog=1 | 17-0006326 | DE ANZA | FIELD OPS SOUTH | Tier 2 | SARATOGA-1107 | 83371107 | FUSE | 11753 | 20170109 | 2002 | 1632193 | 4058 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 36522 | 37.2586 | -122.0952 | HAUGENKIRK1SPANLOADSIDEOFCOS31619 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006326 | OH | Sus | 31294278 | yes | 2017 | JAN | Yes | Line to Line | 1246029 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006519&numberofmonths=24&showchangehistorylog=1 | 17-0006519 | DE ANZA | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | JUMPER | TAPS26199PIERCERDLG | 20170110 | 1028 | 1632615 | 2661 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 7626 | 37.1261 | -121.9922 | 1PSOF26199PIERCERDLG | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0006519 | OH | Sus | 31294361 | yes | 2017 | JAN | Yes | Line to Ground | 1246178 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006382&numberofmonths=24&showchangehistorylog=1 | 17-0006382 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 12741 | 20170110 | 27 | 1632419 | 852 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 8470 | 37.1509 | -121.9736 | NGUYENIFO22152OldSantaCruzHwy | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006382 | OH | Sus | 31294278 | yes | 2017 | JAN | Yes | Line to Ground | 1246090 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007001&numberofmonths=24&showchangehistorylog=1 | 17-0007001 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | SWITCH | SA07 | 20170110 | 1954 | 1636576 | 4017 | Distribution Circuit | Vegetation | Tree - fell into line | 469 | 208453 | 37.1538 | -121.9821 | HAUGENKIRK8POLESLOADSIDEOFSA07 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007001 | OH | Sus | 31294278 | yes | 2017 | JAN | Yes | Line to Ground | 1246583 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007211&numberofmonths=24&showchangehistorylog=1 | 17-0007211 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 4415 | 20170110 | 2046 | 1637006 | 4293 | Distribution Circuit | Environmental/External | Flood/Erosion | 104 | 446472 | 37.1936 | -121.9983 | lLSOF4415 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007211 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246790 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006576&numberofmonths=24&showchangehistorylog=1 | 17-0006576 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 949 | 20170110 | 1040 | 1632952 | 412 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1236 | 37.1641 | -121.9761 | AGBALOGVINCEsame | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006576 | OH | Sus | 42913015 | yes | 2017 | JAN | Yes | Line to Ground | 1246227 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006882&numberofmonths=24&showchangehistorylog=1 | 17-0006882 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 21117 | 20170110 | 1328 | 1633397 | 3142 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 95536 | 37.1086 | -121.8338 | WIREDOWN3PEO30643 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006882 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246460 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006848&numberofmonths=24&showchangehistorylog=1 | 17-0006848 | DE ANZA | FIELD OPS SOUTH | Tier 2 | SARATOGA-1106 | 83371106 | FUSE | 5089 | 20170110 | 1545 | 1634134 | 1509 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 60903 | 37.2339 | -121.9979 | 18800FARVUEMONTESERENO | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006848 | OH | Sus | 31294278 | yes | 2017 | JAN | Yes | Three Phase Fault | 1246429 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006782&numberofmonths=24&showchangehistorylog=1 | 17-0006782 | DE ANZA | FIELD OPS SOUTH | Tier 3 | SARATOGA-1107 | 83371107 | FUSE | 15769 | 20170110 | 1448 | 1634151 | 1717 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 25755 | 37.2474 | -122.068 | SANBORNRD3SPANSSOCONGRESSSPRINGS | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006782 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246374 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007514&numberofmonths=24&showchangehistorylog=1 | 17-0007514 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | JUMPER | WIREDOWN2897 | 20170111 | 856 | 1639138 | 3289 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 16445 | 37.1219 | -121.9261 | 2897 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007514 | OH | Sus | 31294278 | yes | 2017 | JAN | Yes | Force Out | 1247059 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007560&numberofmonths=24&showchangehistorylog=1 | 17-0007560 | DE ANZA | FIELD OPS SOUTH | Tier 2 | SARATOGA-1106 | 83371106 | FUSE | 7419 | 20170111 | 913 | 1639242 | 1664 | Distribution Circuit | Vegetation | Tree - fell into line | 89 | 99102 | 37.2351 | -121.9911 | GARCIA16177RIDGECRESTAVE | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007560 | OH | Sus | 42913015 | yes | 2017 | JAN | Yes | Line to Ground | 1247090 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011564&numberofmonths=24&showchangehistorylog=1 | 17-0011564 | DE ANZA | FIELD OPS SOUTH | Tier 3 | STELLING-1110 | 83481110 | FUSE | 4417 | 20170120 | 1210 | 1654124 | 3401 | Distribution Circuit | Environmental/External | Flood/Erosion | 31 | 25753 | 37.1978 | -122.0278 | STEVENSROBERT3polesloadsidelc04417 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011564 | OH | Sus | 31297028 | yes | 2017 | JAN | Yes | Line to Ground | 1250427 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013294&numberofmonths=24&showchangehistorylog=1 | 17-0013294 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 17345 | 20170122 | 1127 | 1660580 | 3234 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 19404 | 37.1728 | -122.0698 | LDSIDEOF17345 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013294 | OH | Sus | 31297030 | yes | 2017 | JAN | Yes | Line to Ground | 1252106 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013552&numberofmonths=24&showchangehistorylog=1 | 17-0013552 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 21295 | 20170122 | 2317 | 1662576 | 890 | Distribution Circuit | Environmental/External | Flood/Erosion | 20 | 17800 | 37.1983 | -122.0115 | HAUGENKIRK2ndand3rdspanLOADSIDEofCos21295 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013552 | OH | Sus | 42928670 | yes | 2017 | JAN | Yes | Line to Ground | 1252370 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012915&numberofmonths=24&showchangehistorylog=1 | 17-0012915 | DE ANZA | FIELD OPS SOUTH | Tier 2 | SARATOGA-1107 | 83371107 | FUSE | 11753 | 20170122 | 716 | 1659461 | 2384 | Distribution Circuit | Environmental/External | Flood/Erosion | 9 | 21456 | 37.2586 | -122.0952 | ZANDATEBOBBY10PolesLoadsideof11753 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012915 | OH | Sus | 31297028 | yes | 2017 | JAN | Yes | Line to Ground | 1251735 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013603&numberofmonths=24&showchangehistorylog=1 | 17-0013603 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 4469 | 20170123 | 408 | 1662752 | 937 | Distribution Circuit | Vegetation | Tree - branch fell on line | 71 | 61407 | 37.1056 | -121.9326 | Knapp3823BTWN29772979 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013603 | OH | Sus | 31297030 | yes | 2017 | JAN | Yes | Line to Ground | 1252425 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018174&numberofmonths=24&showchangehistorylog=1 | 17-0018174 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER | LA64 | 20170207 | 629 | 1678191 | 1906 | Distribution Circuit | Vegetation | Tree - fell into line | 338 | 175889 | 37.1373 | -121.9674 | STEVENSROBERT78SPANSSWLCO31297 | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018174 | OH | Sus | 31304239 | yes | 2017 | FEB | Yes | Line to Line | 1256037 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018321&numberofmonths=24&showchangehistorylog=1 | 17-0018321 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER | LB48 | 20170207 | 833 | 1679023 | 178 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 16554 | 37.19 | -121.9942 | STEVENSROBERT3POLESSOLCO953 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0018321 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Multi-Fault | 1256157 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018469&numberofmonths=24&showchangehistorylog=1 | 17-0018469 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | TRIP-SAVER | 12041 | 20170207 | 848 | 1679132 | 381 | Distribution Circuit | Vegetation | Tree - fell into line | 78 | 29718 | 37.0983 | -121.9473 | 25510SOQUELSANJOSERDLOSGATOS | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018469 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1256279 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018532&numberofmonths=24&showchangehistorylog=1 | 17-0018532 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 12371 | 20170207 | 639 | 1680008 | 2298 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 11490 | 37.0904 | -121.9203 | HAWKCRESTRDWOLONGRIDGERD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018532 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1256326 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018656&numberofmonths=24&showchangehistorylog=1 | 17-0018656 | DE ANZA | FIELD OPS SOUTH | Tier 2 | SARATOGA-1105 | 83371105 | SWITCH | SC01 | 20170207 | 1512 | 1680535 | 2008 | Distribution Circuit | Vegetation | Tree - branch fell on line | 310 | 35608 | 37.2674 | -122.0498 | PIERCERD2PSOPIKERD | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018656 | OH | Sus | 31304239 | yes | 2017 | FEB | Yes | Force Out | 1256425 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018379&numberofmonths=24&showchangehistorylog=1 | 17-0018379 | DE ANZA | FIELD OPS SOUTH | Tier 2 | STELLING-1110 | 83481110 | TRIP-SAVER | 9265 | 20170207 | 512 | 1678870 | 1929 | Distribution Circuit | Equipment Failure/Involved | Overhead | 461 | 309020 | 37.2937 | -122.102 | MONTEBELLORD1PWOF18993 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018379 | OH | Sus | 42939926 | yes | 2017 | FEB | Yes | Line to Line | 1256210 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0019734&numberofmonths=24&showchangehistorylog=1 | 17-0019734 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | OTHER | WIREDOWN23400OLDSANTACRUZHWY | 20170209 | 1918 | 1684101 | 1853 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 17557 | 37.1391 | -121.9823 | 23400OLDSANTACRUZHWY | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019734 | OH | Sus | 31304342 | yes | 2017 | FEB | Yes | Line to Ground | 1257205 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0022859&numberofmonths=24&showchangehistorylog=1 | 17-0022859 | DE ANZA | FIELD OPS SOUTH | Tier 3 | SARATOGA-1107 | 83371107 | FUSE | 5387 | 20170217 | 923 | 1695077 | 2239 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 17912 | 37.2294 | -122.0545 | NGUYEN16400SanbornRd | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022859 | OH | Sus | 31306421 | yes | 2017 | FEB | Yes | Line to Ground | 1259875 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023041&numberofmonths=24&showchangehistorylog=1 | 17-0023041 | DE ANZA | FIELD OPS SOUTH | Tier 2 | SARATOGA-1107 | 83371107 | FUSE | 30547 | 20170217 | 1540 | 1693227 | 1771 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 8855 | 37.2501 | -122.0321 | BETWEEN372130547 | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023041 | OH | Sus | 31306421 | yes | 2017 | FEB | Yes | Line to Line | 1260052 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023867&numberofmonths=24&showchangehistorylog=1 | 17-0023867 | DE ANZA | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER | 60124 | 20170220 | 1503 | 1703629 | 5850 | Distribution Circuit | Vegetation | Tree - fell into line | 718 | 3670876 | 37.1462 | -121.9823 | STEVENSROBERT22529SUMMITRDAPPROX1MIEOHWY17 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023867 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1260852 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025621&numberofmonths=24&showchangehistorylog=1 | 17-0025621 | DE ANZA | FIELD OPS SOUTH | Tier 2 | HICKS-1116 | 83431116 | OTHER | WIREDOWN1SPSSOF18667 | 20170220 | 1706 | 1704476 | 4028 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 108756 | 37.236 | -121.9402 | FUCO18667 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025621 | OH | Sus | 42950074 | yes | 2017 | FEB | Yes | None | 1262452 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025632&numberofmonths=24&showchangehistorylog=1 | 17-0025632 | DE ANZA | FIELD OPS SOUTH | Tier 2 | LOS GATOS-1101 | 82021101 | FUSE | 1425 | 20170220 | 1642 | 1705251 | 2916 | Distribution Circuit | Environmental/External | Flood/Erosion | 84 | 244944 | 37.2246 | -121.9591 | LGCORNEROFSKENNEDYANDKENNEDYROAD | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025632 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1262457 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023898&numberofmonths=24&showchangehistorylog=1 | 17-0023898 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER | LA64 | 20170220 | 1550 | 1703743 | 7049 | Distribution Circuit | Vegetation | Tree - fell into line | 338 | 1772057 | 37.1373 | -121.9674 | 16440SODASPRINGSROAD | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023898 | OH | Sus | 31306421 | yes | 2017 | FEB | Yes | Line to Ground | 1260874 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023899&numberofmonths=24&showchangehistorylog=1 | 17-0023899 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER | LA46 | 20170220 | 1552 | 1703842 | 1649 | Distribution Circuit | Vegetation | Tree - fell into line | 135 | 222615 | 37.1615 | -121.9817 | 20936NEZPERCETRLLOSGATOS | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023899 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1260875 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023924&numberofmonths=24&showchangehistorylog=1 | 17-0023924 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | SWITCH | SA07 | 20170220 | 1620 | 1704048 | 4331 | Distribution Circuit | Vegetation | Tree - fell into line | 160 | 694083 | 37.1538 | -121.9821 | 17140MELODYLANE | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023924 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Multi-Fault | 1260898 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023990&numberofmonths=24&showchangehistorylog=1 | 17-0023990 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER | LB44 | 20170220 | 1748 | 1704704 | 7629 | Distribution Circuit | Equipment Failure/Involved | Overhead | 508 | 2696073 | 37.1938 | -121.9959 | STEVENSROBERT20070gistrdWOF4417 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023990 | OH | Sus | 31306421 | yes | 2017 | FEB | Yes | Line to Line | 1260960 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024200&numberofmonths=24&showchangehistorylog=1 | 17-0024200 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER | 60116 | 20170220 | 2111 | 1704263 | 3968 | Distribution Circuit | Vegetation | Tree - fell into line | 309 | 1136634 | 37.1734 | -121.9929 | OWENJACOB20780BrushRd | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024200 | OH | Sus | 31306421 | yes | 2017 | FEB | Yes | Line to Ground | 1261165 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024916&numberofmonths=24&showchangehistorylog=1 | 17-0024916 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | SWITCH | SB19 | 20170220 | 1859 | 1705660 | 5715 | Distribution Circuit | Environmental/External | Flood/Erosion | 9 | 51435 | 37.1751 | -122.0105 | EVERYWHERE | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024916 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1261890 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024730&numberofmonths=24&showchangehistorylog=1 | 17-0024730 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 2909 | 20170220 | 1634 | 1704184 | 1676 | Distribution Circuit | Vegetation | Tree - fell into line | 207 | 346932 | 37.1116 | -121.9459 | 24500MILLERHILLRD | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024730 | OH | Sus | 31306426 | yes | 2017 | FEB | Yes | Line to Ground | 1261698 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024806&numberofmonths=24&showchangehistorylog=1 | 17-0024806 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 19887 | 20170220 | 1737 | 1704989 | 4245 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 12735 | 37.1006 | -121.9322 | AGBALOGVINCEsame | Overcast-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0024806 | OH | Sus | 31306426 | yes | 2017 | FEB | Yes | Line to Ground | 1261775 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025464&numberofmonths=24&showchangehistorylog=1 | 17-0025464 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 2915 | 20170220 | 1619 | 1704013 | 3142 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 78385 | 37.1096 | -121.9379 | 11697 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025464 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1262365 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025761&numberofmonths=24&showchangehistorylog=1 | 17-0025761 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 21117 | 20170220 | 1707 | 1704480 | 4216 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 139104 | 37.1086 | -121.8338 | 30000LOMACHIQUITARD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025761 | OH | Sus | 31306421 | yes | 2017 | FEB | Yes | Line to Line | 1262548 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024892&numberofmonths=24&showchangehistorylog=1 | 17-0024892 | DE ANZA | FIELD OPS SOUTH | Tier 2 | SARATOGA-1107 | 83371107 | FUSE | 15771 | 20170220 | 1747 | 1705726 | 5799 | Distribution Circuit | Environmental/External | Flood/Erosion | 35 | 124357 | 37.2482 | -122.0708 | LDSIDEOF15771IFO23600CONGRESSSPRINGSRD | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024892 | OH | Sus | 31306421 | yes | 2017 | FEB | Yes | Line to Line | 1261866 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0026749&numberofmonths=24&showchangehistorylog=1 | 17-0026749 | DE ANZA | FIELD OPS SOUTH | Tier 3 | STELLING-1110 | 83481110 | FUSE | 22639 | 20170220 | 1543 | 1704777 | 9909 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 56984 | 37.1957 | -122.0542 | EO22639TWDEOL | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0026749 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1263442 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025874&numberofmonths=24&showchangehistorylog=1 | 17-0025874 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | JUMPER | OJS | 20170222 | 640 | 1711513 | 992 | Distribution Circuit | Environmental/External | Flood/Erosion | 8 | 7936 | 37.1723 | -121.9937 | PASTOPENJUMPERSHEBARDWAYONIRONSPRINGSRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025874 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Three Phase Fault | 1262671 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025855&numberofmonths=24&showchangehistorylog=1 | 17-0025855 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 17431 | 20170222 | 1652 | 1711126 | 308 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 9856 | 37.1102 | -121.9509 | WOFADDRESS16035 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025855 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1262650 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0038433&numberofmonths=24&showchangehistorylog=1 | 17-0038433 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 12371 | 20170406 | 2018 | 1751187 | 4365 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 21825 | 37.0904 | -121.9203 | GUPHILLOPPOSITE13834LONGRIDGERD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0038433 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1272488 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0077619&numberofmonths=24&showchangehistorylog=1 | 17-0077619 | DE ANZA | FIELD OPS SOUTH | Tier 2 | SARATOGA-1103 | 83371103 | JUMPER | CUTINCLERAR | 20170911 | 327 | 1874784 | 713 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 7184 | 37.2651 | -122.0444 | NORTHOF4021 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0077619 | OH | Sus | 0 | yes | 2017 | SEP | Yes | Line to Ground | 1301479 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0077592&numberofmonths=24&showchangehistorylog=1 | 17-0077592 | DE ANZA | FIELD OPS SOUTH | Tier 2 | SARATOGA-1107 | 83371107 | FUSE | 22529 | 20170911 | 314 | 1875033 | 805 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 15295 | 37.2399 | -122.0211 | PeachHillRDGlenUnaDr | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0077592 | OH | Sus | 0 | yes | 2017 | SEP | Yes | Line to Ground | 1301468 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0085291&numberofmonths=24&showchangehistorylog=1 | 17-0085291 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 9125 | 20171008 | 2221 | 1894126 | 928 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 24464 | 37.1654 | -122.0173 | BEARCREEKRDSUMMIT | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085291 | OH | Sus | 31355577 | yes | 2017 | OCT | Yes | Line to Ground | 1306738 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0099810&numberofmonths=24&showchangehistorylog=1 | 17-0099810 | DE ANZA | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 17499 | 20171204 | 1826 | 1935939 | 753 | Distribution Circuit | Vegetation | Tree - branch fell on line | 36 | 27108 | 37.1519 | -121.9976 | ZandateLouie1058790MARTYRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0099810 | OH | Sus | 43227153 | yes | 2017 | DEC | Yes | Line to Ground | 1317552 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0099811&numberofmonths=24&showchangehistorylog=1 | 17-0099811 | DE ANZA | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER | 60120 | 20171204 | 2006 | 1936048 | 2249 | Distribution Circuit | Vegetation | Tree - fell into line | 685 | 35805 | 37.1305 | -121.9785 | RISERSWITCH10963 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0099811 | OH | Sus | 0 | yes | 2017 | DEC | Yes | Line to Ground | 1317554 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0099865&numberofmonths=24&showchangehistorylog=1 | 17-0099865 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 4417 | 20171204 | 2152 | 1936115 | 1058 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 17876 | 37.1979 | -122.0277 | ZandateLouie105820624BLACKRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0099865 | OH | Sus | 31368279 | yes | 2017 | DEC | Yes | Line to Line | 1317602 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0101950&numberofmonths=24&showchangehistorylog=1 | 17-0101950 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER | 60116 | 20171216 | 924 | 1944237 | 3342 | Distribution Circuit | Vegetation | Tree - fell into line | 2232 | 3670529 | 37.1734 | -121.9929 | NORTHOF20890COMANCHE | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0101950 | OH | Sus | 31370183 | yes | 2017 | DEC | Yes | Multi-Fault | 1319862 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0101910&numberofmonths=24&showchangehistorylog=1 | 17-0101910 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | RECLOSER | 60118 | 20171216 | 646 | 1944042 | 3186 | Distribution Circuit | Vegetation | Tree - fell into line | 908 | 1847418 | 37.1246 | -121.9354 | 24550MILLERHILLRDWO19731 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0101910 | OH | Sus | 31370181 | yes | 2017 | DEC | Yes | Line to Line | 1319810 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0064573&numberofmonths=24&showchangehistorylog=1 | 18-0064573 | DE ANZA | FIELD OPS SOUTH | Tier 3 | SARATOGA-1107 | 83371107 | OTHER | WIREDOWN1POLESOF13831 | 20180728 | 838 | 142285 | 394 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 2321 | 37.2381 | -122.0693 | 1POLESOF13831 | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 18-0064573 | OH | Sus | 43422814 | No | 2018 | JUL | Yes | Line to Ground | 1367375 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0098245&numberofmonths=24&showchangehistorylog=1 | 18-0098245 | DE ANZA | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 21063 | 20181108 | 931 | 211438 | 902 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 8118 | 37.156 | -121.9878 | LDSIDE21063 | Strong Winds-Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0098245 | OH | Sus | 0 | yes | 2018 | NOV | Yes | Force Out | 1391447 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0104832&numberofmonths=24&showchangehistorylog=1 | 18-0104832 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER | LB48 | 20181129 | 822 | 228166 | 509 | Distribution Circuit | Vegetation | Tree - branch fell on line | 143 | 53737 | 37.19 | -121.9942 | BEARCREEKROADHWY178POLESNO31571 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0104832 | OH | Sus | 31416747 | yes | 2018 | NOV | Yes | Line to Ground | 1396134 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0105018&numberofmonths=24&showchangehistorylog=1 | 18-0105018 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | JUMPER | WIREDOWN | 20181129 | 818 | 228121 | 1752 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1752 | 37.1758 | -122.0271 | 20233SKYLINEBLVD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0105018 | OH | Sus | 31416745 | yes | 2018 | NOV | Yes | Line to Ground | 1396267 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0104981&numberofmonths=24&showchangehistorylog=1 | 18-0104981 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 4461 | 20181129 | 837 | 228279 | 562 | Distribution Circuit | Vegetation | Tree - branch fell on line | 38 | 21356 | 37.1079 | -121.9469 | BET446117431 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0104981 | OH | Sus | 43586552 | yes | 2018 | NOV | Yes | Line to Ground | 1396244 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005194&numberofmonths=24&showchangehistorylog=1 | 19-0005194 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 31297 | 20190106 | 1632 | 255654 | 382 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 6494 | 37.1392 | -121.9747 | STEVENSROBERT23175OLDSANTACRUZHWY | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005194 | OH | Sus | 31420581 | yes | 2019 | JAN | Yes | Line to Ground | 1403665 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005341&numberofmonths=24&showchangehistorylog=1 | 19-0005341 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | OTHER | WIREDOWNCOUT4421TWDWEST | 20190106 | 1748 | 256034 | 426 | Distribution Circuit | Equipment Failure/Involved | Overhead | 172 | 40440 | 37.1901 | -122.0311 | COUT4421TOWEST | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005341 | OH | Sus | 43625028 | yes | 2019 | JAN | Yes | Line to Ground | 1403794 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005414&numberofmonths=24&showchangehistorylog=1 | 19-0005414 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 11401 | 20190106 | 1815 | 256332 | 2071 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 84994 | 37.1132 | -121.8383 | LOMACHIQUITARD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005414 | OH | Sus | 31420535 | yes | 2019 | JAN | Yes | Line to Line | 1403865 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005084&numberofmonths=24&showchangehistorylog=1 | 19-0005084 | DE ANZA | FIELD OPS SOUTH | Tier 3 | SARATOGA-1107 | 83371107 | FUSE | 15777 | 20190106 | 1111 | 255170 | 1893 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 11358 | 37.2542 | -122.0893 | 2WO15777 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005084 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1403556 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010191&numberofmonths=24&showchangehistorylog=1 | 19-0010191 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER | LB48 | 20190116 | 2022 | 270595 | 5229 | Distribution Circuit | Vegetation | Tree - fell into line | 122 | 392405 | 37.19 | -121.9942 | 953and19320HIDDENSPRINGS | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010191 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407058 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010569&numberofmonths=24&showchangehistorylog=1 | 19-0010569 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 4451 | 20190116 | 1950 | 271687 | 1522 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 44138 | 37.1365 | -121.9683 | LG23020OLDSANTACRUZHWYLOSGATOS | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010569 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407432 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010970&numberofmonths=24&showchangehistorylog=1 | 19-0010970 | DE ANZA | FIELD OPS SOUTH | Tier 2 | LOS GATOS-1106 | 82021106 | FUSE | 1573 | 20190116 | 1954 | 270207 | 4091 | Distribution Circuit | Vegetation | Tree - branch fell on line | 41 | 46585 | 37.1981 | -121.9928 | STEVENSROBERTSAPPOLEID100552641 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010970 | OH | Sus | 43634152 | yes | 2019 | JAN | Yes | Line to Ground | 1407636 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011363&numberofmonths=24&showchangehistorylog=1 | 19-0011363 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 17121 | 20190116 | 2045 | 274832 | 3055 | Distribution Circuit | Equipment Failure/Involved | Overhead | 37 | 113035 | 37.1634 | -122.0139 | 4670OUTERZAYANTE | Overcast-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0011363 | OH | Sus | 31422106 | yes | 2019 | JAN | Yes | Line to Ground | 1407909 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0009835&numberofmonths=24&showchangehistorylog=1 | 19-0009835 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | RECLOSER | LA60 | 20190116 | 1548 | 267619 | 2838 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 263305 | 37.1839 | -121.9823 | SODASPRINGS | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009835 | OH | Sus | 43634152 | yes | 2019 | JAN | Yes | Line to Line | 1406722 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010265&numberofmonths=24&showchangehistorylog=1 | 19-0010265 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | TRIP-SAVER | 2917 | 20190116 | 2100 | 275113 | 2476 | Distribution Circuit | Vegetation | Tree - fell into line | 117 | 224036 | 37.1092 | -121.9355 | 15335STETSONRD | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010265 | OH | Sus | 43634154 | yes | 2019 | JAN | Yes | Line to Ground | 1408050 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0009938&numberofmonths=24&showchangehistorylog=1 | 19-0009938 | DE ANZA | FIELD OPS SOUTH | Tier 2 | SARATOGA-1107 | 83371107 | RECLOSER | 167792 | 20190116 | 1705 | 268225 | 2921 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 93472 | 37.2482 | -122.0709 | FROM15775TWD157777 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009938 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1406809 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010340&numberofmonths=24&showchangehistorylog=1 | 19-0010340 | DE ANZA | FIELD OPS SOUTH | Tier 3 | SARATOGA-1107 | 83371107 | FUSE | 15769 | 20190116 | 2010 | 270659 | 1369 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 127275 | 37.2474 | -122.068 | 13SPLOADSIDEOF15769 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010340 | OH | Sus | 31422104 | yes | 2019 | JAN | Yes | Force Out | 1407205 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010840&numberofmonths=24&showchangehistorylog=1 | 19-0010840 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 7651 | 20190117 | 614 | 273173 | 850 | Distribution Circuit | Vegetation | Tree - fell into line | 135 | 36238 | 37.1945 | -122.0226 | BLACKRD5PLSNWOTHOMPSONROAD | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on object | 19-0010840 | OH | Sus | 43634152 | yes | 2019 | JAN | Yes | Open Circuit | 1407561 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021961&numberofmonths=24&showchangehistorylog=1 | 19-0021961 | DE ANZA | FIELD OPS SOUTH | Tier 2 | SARATOGA-1107 | 83371107 | FUSE | 6757 | 20190213 | 802 | 303116 | 358 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 14678 | 37.2498 | -122.0197 | IFO15195PARLDR | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021961 | OH | Sus | 31425395 | yes | 2019 | FEB | Yes | Open Circuit | 1415382 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023198&numberofmonths=24&showchangehistorylog=1 | 19-0023198 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 4421 | 20190214 | 605 | 307160 | 1345 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 69940 | 37.1899 | -122.031 | 19715SKYLINEBLVD | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023198 | OH | Sus | 43677333 | yes | 2019 | FEB | Yes | Line to Ground | 1416386 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022717&numberofmonths=24&showchangehistorylog=1 | 19-0022717 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | RECLOSER | 60092 | 20190214 | 6 | 306012 | 2619 | Distribution Circuit | Vegetation | Tree - fell into line | 186 | 50318 | 37.1825 | -121.985 | NOR1245SPANSOFWIREDOWNDUETOBROKENPOLEALSO9533TREEONROADBLOCKINGACCESS | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0022717 | OH | Sus | 31425395 | yes | 2019 | FEB | Yes | Line to Ground | 1415951 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022748&numberofmonths=24&showchangehistorylog=1 | 19-0022748 | DE ANZA | FIELD OPS SOUTH | Tier 2 | SARATOGA-1107 | 83371107 | RECLOSER | 167792 | 20190214 | 143 | 306368 | 2432 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 77824 | 37.2482 | -122.0709 | WHITEERICSW685 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022748 | OH | Sus | 31425395 | yes | 2019 | FEB | Yes | Line to Ground | 1415988 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028735&numberofmonths=24&showchangehistorylog=1 | 19-0028735 | DE ANZA | FIELD OPS SOUTH | Tier 3 | SARATOGA-1107 | 83371107 | FUSE | 15777 | 20190227 | 541 | 326371 | 664 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 3984 | 37.2542 | -122.0893 | 5SPANSSOUTHOF15777 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028735 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1420646 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0064523&numberofmonths=24&showchangehistorylog=1 | 19-0064523 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 4421 | 20190608 | 519 | 401182 | 941 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 21392 | 37.1899 | -122.031 | CO20157THOMPSONRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0064523 | OH | Sus | 43832032 | yes | 2019 | JUN | Yes | Line to Ground | 1446715 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0114891&numberofmonths=24&showchangehistorylog=1 | 19-0114891 | DE ANZA | FIELD OPS SOUTH | Tier 2 | STELLING-1110 | 83481110 | JUMPER | OJS | 20191023 | 130 | 677261 | 879 | Distribution Circuit | 3rd Party | Vehicle | 1 | 879 | 37.261 | -122.1316 | 12900SKYLINEBLVDLOSGATOS | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0114891 | OH | Sus | 0 | yes | 2019 | OCT | Yes | Line to Ground | 1481958 | PW | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0118769&numberofmonths=24&showchangehistorylog=1 | 19-0118769 | DE ANZA | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | OTHER | 8051 | 20191029 | 1945 | 694583 | 349 | Distribution Circuit | Vegetation | Tree - branch fell on line | 25 | 8725 | 37.2533 | -122.1237 | 3EASTOF8051 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0118769 | OH | Sus | 44082355 | yes | 2019 | OCT | Yes | Line to Ground | 1487837 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0010328&numberofmonths=24&showchangehistorylog=1 | 20-0010328 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 1579 | 20200116 | 934 | 763363 | 1811 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1811 | 37.0754 | -121.9395 | 7107SOQUELSANJOSERD | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0010328 | OH | Sus | 31486644 | yes | 2020 | JAN | Yes | Line to Ground | 1507045 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0084746&numberofmonths=24&showchangehistorylog=1 | 20-0084746 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 4435 | 20200816 | 254 | 1011258 | 1101 | Distribution Circuit | Environmental/External | Lightning | 34 | 37434 | 37.1664 | -121.9895 | 20730BRUSHRDLOSGATOS | Lightning-Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0084746 | OH | Sus | 0 | yes | 2020 | AUG | Yes | Line to Ground | 1555219 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0009632&numberofmonths=24&showchangehistorylog=1 | 21-0009632 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER | LA64 | 20210118 | 950 | 1212195 | 493 | Distribution Circuit | Vegetation | Tree - branch fell on line | 337 | 30511 | 37.1372 | -121.9674 | SOFUCO3461FOUND1SPANWIREDOWNFROM1STPOTSOUTHOFMAINLINETOEOL | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0009632 | OH | Sus | 31528401 | No | 2021 | JAN | Yes | Line to Ground | 1593656 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0013574&numberofmonths=24&showchangehistorylog=1 | 21-0013574 | DE ANZA | FIELD OPS SOUTH | Tier 2 | SARATOGA-1107 | 83371107 | OTHER | 15775 | 20210125 | 115 | 1223103 | 609 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 12931 | 37.2489 | -122.0793 | 1NWOF15775 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0013574 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1596560 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0015496&numberofmonths=24&showchangehistorylog=1 | 21-0015496 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | RECLOSER | 60114 | 20210127 | 132 | 1231923 | 2381 | Distribution Circuit | Equipment Failure/Involved | Overhead | 248 | 176225 | 37.119 | -121.9205 | nofk003 | Strong Winds-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0015496 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1598036 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0135727&numberofmonths=24&showchangehistorylog=1 | 21-0135727 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 6947 | 20211024 | 558 | 1508380 | 527 | Distribution Circuit | Vegetation | Tree - branch fell on line | 20 | 10540 | 37.1169 | -121.924 | 24519HIGHLANDWAYLOSGATOS | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0135727 | OH | Sus | 45018624 | No | 2021 | OCT | Yes | Line to Ground | 1677202 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0135958&numberofmonths=24&showchangehistorylog=1 | 21-0135958 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | OTHER | WIREDOWN195MILLERCUTOFFRD | 20211024 | 1028 | 1510046 | 554 | Distribution Circuit | Vegetation | Tree - fell into line | 292 | 23572 | 37.1152 | -121.9335 | 24125MILLERCUTOFFROAD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0135958 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Ground | 1677427 | PW | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0137836&numberofmonths=24&showchangehistorylog=1 | 21-0137836 | DE ANZA | FIELD OPS SOUTH | Tier 2 | STELLING-1110 | 83481110 | OTHER | WIREDOWN17294STEVENSCANYONRD | 20211024 | 2201 | 1520704 | 2701 | Distribution Circuit | Vegetation | Tree - branch fell on line | 10 | 26742 | 37.2797 | -122.1167 | ZANDATEBOBBY40847002971729417952and15853StevensCanyonRd | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0137836 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Ground | 1679125 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0138270&numberofmonths=24&showchangehistorylog=1 | 21-0138270 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 10003 | 20211025 | 2208 | 1520448 | 1232 | Distribution Circuit | Equipment Failure/Involved | Overhead | 23 | 28336 | 37.1039 | -121.95 | EOCGC315769322384 | Clear-Strong Winds-Rain-Combination-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0138270 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Ground | 1679353 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0138134&numberofmonths=24&showchangehistorylog=1 | 22-0138134 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER | 60116 | 20221210 | 821 | 1880745 | 613 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1136 | 161962 | 37.1735 | -121.9928 | ZANDATEBOBBY408470029718216ZellaCt | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0138134 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1788969 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0016872&numberofmonths=24&showchangehistorylog=1 | 23-0016872 | DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER | LA64 | 20230116 | 229 | 1956566 | 976 | Distribution Circuit | Vegetation | Tree - fell into line | 338 | 76656 | 37.1372 | -121.9674 | BRITTONWILLY2097680165MultiplelocationsonSchultiesRd | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0016872 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1805572 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0017111&numberofmonths=24&showchangehistorylog=1 | 23-0017111 | DE ANZA | FIELD OPS SOUTH | Tier 3 | SARATOGA-1105 | 83371105 | FUSE | 15767 | 20230116 | 639 | 1957030 | 641 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 1986 | 37.2364 | -122.0662 | CGC315425327299 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0017111 | OH | Sus | 0 | No | 2023 | JAN | Yes | Three Phase Fault | 1805803 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0017028&numberofmonths=24&showchangehistorylog=1 | 23-0017028 | DE ANZA | FIELD OPS SOUTH | Tier 2 | STELLING-1110 | 83481110 | FUSE | 18351 | 20230116 | 250 | 1957333 | 800 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 3200 | 37.2808 | -122.1182 | BETWEENCGC315310028930315291428814 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0017028 | OH | Sus | 0 | No | 2023 | JAN | Yes | Force Out | 1805732 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0031709&numberofmonths=24&showchangehistorylog=1 | 23-0031709 | DE ANZA | FIELD OPS SOUTH | Tier 3 | SARATOGA-1107 | 83371107 | FUSE | 7163 | 20230221 | 1457 | 1992038 | 653 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 52240 | 37.2274 | -122.0525 | ANDRADESHAWN530941566915824 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0031709 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Ground | 1815316 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075193&numberofmonths=24&showchangehistorylog=1 | 14-0075193 | DIABLO | FIELD OPS CENTRAL | Tier 2 | MORAGA-1104 | 13801104 | OTHER |  | 20141211 | 724 | 1131079 | 184 | Distribution Circuit | Equipment Failure/Involved | Other | 50 | 9200 | 37.8689 | -122.1501 | 315240250259 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on object | 14-0075193 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99195069 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075788&numberofmonths=24&showchangehistorylog=1 | 14-0075788 | DIABLO | FIELD OPS CENTRAL | Tier 2 | ROSSMOOR-1101 | 14161101 | FUSE | 2649 | 20141211 | 1729 | 1135141 | 1308 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 3924 | 37.9012 | -122.1118 | 315350951441 | Heavy rain-32 - 90 F | Conductor, Overhead | On Ground | 14-0075788 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194276 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076234&numberofmonths=24&showchangehistorylog=1 | 14-0076234 | DIABLO | FIELD OPS CENTRAL | Tier 3 | TASSAJARA-2112 | 14662112 | RECLOSER | 6392 | 20141211 | 638 | 1133429 | 2136 | Distribution Circuit | Equipment Failure/Involved | Other | 32 | 55978 | 37.8435 | -121.9461 | 315899950393 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076234 | OH | Sus | 0 | yes | 2014 | DEC | Yes |  | 99194074 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017600&numberofmonths=24&showchangehistorylog=1 | 16-0017600 | DIABLO | FIELD OPS CENTRAL | Tier 3 | MORAGA-1101 | 13801101 | FUSE | 7123 | 20160305 | 1631 | 1417302 | 653 | Distribution Circuit | Vegetation | Tree - fell into line | 78 | 43206 | 37.8513 | -122.1631 | 1WofFUCO15483 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017600 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1189455 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0018145&numberofmonths=24&showchangehistorylog=1 | 16-0018145 | DIABLO | FIELD OPS CENTRAL | Tier 3 | MORAGA-1101 | 13801101 | JUMPER | WIREDOWN236ELTOYONAL | 20160305 | 1931 | 1418518 | 745 | Distribution Circuit | Vegetation | Tree - fell into line | 220 | 144349 | 37.8832 | -122.2052 | 236ELTOYONAL | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018145 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190016 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017569&numberofmonths=24&showchangehistorylog=1 | 16-0017569 | DIABLO | FIELD OPS CENTRAL | Tier 2 | MORAGA-1104 | 13801104 | TRANSFORMER | 315232749960 | 20160305 | 1435 | 1416785 | 476 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1428 | 37.8605 | -122.1525 | OCHOAALFONSORO3SUNSETTER | Overcast-Drizzle-32-90 F | Transformer | Broken, wire on ground | 16-0017569 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1189426 | TX | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0018036&numberofmonths=24&showchangehistorylog=1 | 16-0018036 | DIABLO | FIELD OPS CENTRAL | Tier 2 | SOBRANTE-1102 | 14671102 | FUSE | 20534 | 20160305 | 2059 | 1419310 | 442 | Distribution Circuit | Vegetation | Tree - branch fell on line | 77 | 34034 | 37.8953 | -122.1519 | 4PWOF20534 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018036 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1189907 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0003314&numberofmonths=24&showchangehistorylog=1 | 17-0003314 | DIABLO | FIELD OPS CENTRAL | Tier 2 | ROSSMOOR-1101 | 14161101 | SECTIONALIZER | L551S | 20170103 | 2149 | 1617025 | 549 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1079 | 68015 | 37.9086 | -122.1019 | 1POLEWOF95523GOYAKANDSPRINGHILL | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003314 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1243493 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005186&numberofmonths=24&showchangehistorylog=1 | 17-0005186 | DIABLO | FIELD OPS CENTRAL | Tier 3 | CLAYTON-2212 | 12022212 | FUSE | 12151 | 20170108 | 649 | 1625435 | 674 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 10110 | 37.8629 | -121.8538 | 30EASTOF12151 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005186 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1244979 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005237&numberofmonths=24&showchangehistorylog=1 | 17-0005237 | DIABLO | FIELD OPS CENTRAL | Tier 2 | MORAGA-1104 | 13801104 | OCB | 11042 | 20170108 | 1145 | 1625793 | 908 | Distribution Circuit | Vegetation | Tree - fell into line | 1708 | 706554 | 37.8486 | -122.1619 | PerryRichardhallrdanddonald | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0005237 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245026 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005423&numberofmonths=24&showchangehistorylog=1 | 17-0005423 | DIABLO | FIELD OPS CENTRAL | Tier 3 | MORAGA-1105 | 13801105 | FUSE | 7194 | 20170108 | 654 | 1622872 | 1809 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 4905 | 37.8363 | -122.1733 | 3SPANSLDSIDEOFFUCO7194 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005423 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1245206 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0008230&numberofmonths=24&showchangehistorylog=1 | 17-0008230 | DIABLO | FIELD OPS CENTRAL | Tier 3 | CLAYTON-2212 | 12022212 | FUSE | 12151 | 20170110 | 1831 | 1639207 | 1835 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 27525 | 37.8629 | -121.8538 | 7007MorganTerritory | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0008230 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247673 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006571&numberofmonths=24&showchangehistorylog=1 | 17-0006571 | DIABLO | FIELD OPS CENTRAL | Tier 2 | LAS AROMAS-0401 | 13600401 | RECLOSER | 3342 | 20170110 | 1215 | 1633185 | 866 | Distribution Circuit | Vegetation | Tree - fell into line | 174 | 61530 | 37.8986 | -122.1769 | 247LaEspiral | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006571 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Three Phase Fault | 1246221 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013028&numberofmonths=24&showchangehistorylog=1 | 17-0013028 | DIABLO | FIELD OPS CENTRAL | Tier 2 | ALHAMBRA-1105 | 14101105 | FUSE | 1708 | 20170122 | 1037 | 1659787 | 550 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 3275 | 37.9593 | -122.1384 | PINETREEBRIONES | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0013028 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Force Out | 1251849 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018033&numberofmonths=24&showchangehistorylog=1 | 17-0018033 | DIABLO | FIELD OPS CENTRAL | Tier 2 | SOBRANTE-1102 | 14671102 | FUSE | 20534 | 20170207 | 111 | 1677318 | 427 | Distribution Circuit | Vegetation | Tree - fell into line | 76 | 32452 | 37.8953 | -122.1519 | 4016LOSARABISLAFAYETTE | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018033 | OH | Sus | 31304292 | yes | 2017 | FEB | Yes | Line to Ground | 1255884 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018811&numberofmonths=24&showchangehistorylog=1 | 17-0018811 | DIABLO | FIELD OPS CENTRAL | Tier 2 | TASSAJARA-2112 | 14662112 | RECLOSER | D514R | 20170207 | 2250 | 1681188 | 1273 | Distribution Circuit | Vegetation | Tree - fell into line | 1257 | 133984 | 37.8226 | -121.9235 | PEREZGABRIEL9252508184DIABLORDDANVILLE | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018811 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Multi-Fault | 1256556 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037948&numberofmonths=24&showchangehistorylog=1 | 17-0037948 | DIABLO | FIELD OPS CENTRAL | Tier 2 | CLAYTON-2212 | 12022212 | FUSE | 14795 | 20170406 | 2043 | 1747043 | 2780 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 11120 | 37.9224 | -121.905 | 2SPNOF14795 | Overcast-Rain-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0037948 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1272054 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0089040&numberofmonths=24&showchangehistorylog=1 | 17-0089040 | DIABLO | FIELD OPS CENTRAL | Tier 2 | TASSAJARA-2109 | 14662109 | OTHER | WIREDOWNIRO5433OLDSCHOOLRD | 20171020 | 801 | 1905576 | 597 | Distribution Circuit | Equipment Failure/Involved | Overhead | 46 | 23826 | 37.8029 | -121.8536 | IRO5433OLDSCHOOLRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0089040 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1309605 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011114&numberofmonths=24&showchangehistorylog=1 | 19-0011114 | DIABLO | FIELD OPS CENTRAL | Tier 2 | CLAYTON-2212 | 12022212 | FUSE | 15535 | 20190117 | 240 | 274210 | 1190 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 10970 | 37.9695 | -121.9228 | 2640HESS | Partly Cloudy-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011114 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407734 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023752&numberofmonths=24&showchangehistorylog=1 | 19-0023752 | DIABLO | FIELD OPS CENTRAL | Tier 2 | ORINDA-0401 | 12350401 | OTHER | WIREDOWNCORNEROFLACINTILLAANDDIASDOR | 20190214 | 2212 | 311050 | 240 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 5406 | 37.9013 | -122.1888 | CORNEROFLACINTILLAANDDIASDORADOS | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on object | 19-0023752 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416903 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023808&numberofmonths=24&showchangehistorylog=1 | 19-0023808 | DIABLO | FIELD OPS CENTRAL | Tier 2 | ROSSMOOR-1101 | 14161101 | FUSE | 6599 | 20190215 | 3 | 311057 | 661 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 27762 | 37.899 | -122.1257 | 3691NORDSTROMLANE | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023808 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416958 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025051&numberofmonths=24&showchangehistorylog=1 | 19-0025051 | DIABLO | FIELD OPS CENTRAL | Tier 3 | CLAYTON-2212 | 12022212 | FUSE | 9264 | 20190217 | 753 | 315343 | 302 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 4530 | 37.8918 | -121.8506 | 1255MARSHCREEKRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025051 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1418127 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028748&numberofmonths=24&showchangehistorylog=1 | 19-0028748 | DIABLO | FIELD OPS CENTRAL | Tier 2 | SOBRANTE-1102 | 14671102 | FUSE | 6597 | 20190227 | 40 | 325950 | 693 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 28413 | 37.8949 | -122.1343 | 2spansLDsideofFUCO6597 | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028748 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1420657 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0018960&numberofmonths=24&showchangehistorylog=1 | 20-0018960 | DIABLO | FIELD OPS CENTRAL | Tier 2 | ALHAMBRA-1105 | 14101105 | FUSE | 7646 | 20200209 | 808 | 781136 | 411 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 7398 | 37.9797 | -122.125 | BET124175SHERIDAN | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0018960 | OH | Sus | 0 | yes | 2020 | FEB | Yes | Line to Ground | 1512972 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0102102&numberofmonths=24&showchangehistorylog=1 | 20-0102102 | DIABLO | FIELD OPS CENTRAL | Tier 2 | ALHAMBRA-1105 | 14101105 | OTHER | WIREDOWN1175GARCIARANCHRD | 20200927 | 1329 | 1095205 | 547 | Distribution Circuit | Vegetation | Tree - branch fell on line | 402 | 25980 | 37.9505 | -122.1764 | 1175GARCIARANCHRD | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 20-0102102 | OH | Sus | 31514676 | yes | 2020 | SEP | Yes | Line to Ground | 1566518 | CAW | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0135726&numberofmonths=24&showchangehistorylog=1 | 21-0135726 | DIABLO | FIELD OPS CENTRAL | Tier 2 | CLAYTON-2215 | 12022215 | RECLOSER | 812394 | 20211024 | 758 | 1508525 | 600 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 17400 | 37.9025 | -122.0019 | 1150CASTLEROCKRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0135726 | OH | Sus | 0 | No | 2021 | OCT | Yes | Force Out | 1677201 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0136039&numberofmonths=24&showchangehistorylog=1 | 21-0136039 | DIABLO | FIELD OPS CENTRAL | Tier 3 | ORINDA-0402 | 12350402 | FUSE | 275689 | 20211024 | 1036 | 1510041 | 273 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 16653 | 37.8852 | -122.1952 | 32LomaVista | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0136039 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Ground | 1677507 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0012606&numberofmonths=24&showchangehistorylog=1 | 23-0012606 | DIABLO | FIELD OPS CENTRAL | Tier 2 | SOBRANTE-1102 | 14671102 | FUSE | 1151 | 20230110 | 230 | 1940798 | 1067 | Distribution Circuit | Vegetation | Tree - fell into line | 71 | 75757 | 37.9045 | -122.153 | 4015CANYONRD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0012606 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1802276 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0012141&numberofmonths=24&showchangehistorylog=1 | 23-0012141 | DIABLO | FIELD OPS CENTRAL | Tier 2 | SOBRANTE-1103 | 14671103 | FUSE | 1160 | 20230110 | 225 | 1944248 | 1296 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 103680 | 37.8974 | -122.1696 | POLE110202501 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0012141 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1801911 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0031574&numberofmonths=24&showchangehistorylog=1 | 23-0031574 | DIABLO | FIELD OPS CENTRAL | Tier 2 | ROSSMOOR-1101 | 14161101 | FUSE | 6599 | 20230221 | 1618 | 1993081 | 449 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 18409 | 37.899 | -122.1256 | CORNEROFNORDSTROMLNHILLTOPNDR | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0031574 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Line | 1815198 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078749&numberofmonths=24&showchangehistorylog=1 | 13-0078749 | EAST BAY | FIELD OPS CENTRAL | Tier 3 | BERKELEY F-1103 | 12061103 | FUSE | 8029 | 20131121 | 1949 | 908830 | 2608 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 28688 | 37.8695 | -122.2449 | 850PANAROMICWAY | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0078749 | OH | Sus | 0 | yes | 2013 | NOV | Yes |  | 99251200 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078278&numberofmonths=24&showchangehistorylog=1 | 13-0078278 | EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND K-1102 | 12101102 | FUSE | 172497 | 20131121 | 1849 | 908059 | 843 | Distribution Circuit | Vegetation | Tree - branch fell on line | 26 | 21918 | 37.8466 | -122.1992 | STEPHENSK827721687505433SAME | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0078278 | OH | Sus | 0 | yes | 2013 | NOV | Yes | Line to Ground | 99251249 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078341&numberofmonths=24&showchangehistorylog=1 | 13-0078341 | EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND K-1104 | 12101104 | FUSE | 9428 | 20131121 | 2032 | 909208 | 804 | Distribution Circuit | Vegetation | Tree - bark fell into line | 44 | 35376 | 37.8348 | -122.1951 | 7158SAYREDR | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078341 | OH | Sus | 0 | yes | 2013 | NOV | Yes | Line to Ground | 99251681 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078070&numberofmonths=24&showchangehistorylog=1 | 13-0078070 | EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND X-1104 | 12541104 | RECLOSER | CR214 | 20131121 | 1857 | 908099 | 1697 | Distribution Circuit | Vegetation | Tree - fell into line | 422 | 225292 | 37.8188 | -122.1997 | MOUNTAINGATE1EOFCR214 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078070 | OH | Sus | 31038174 | yes | 2013 | NOV | Yes | None | 99251276 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078427&numberofmonths=24&showchangehistorylog=1 | 13-0078427 | EAST BAY | FIELD OPS CENTRAL | Tier 2 | OAKLAND K-1103 | 12101103 | FUSE | 6533 | 20131122 | 311 | 910794 | 1809 | Distribution Circuit | Vegetation | Tree - fell into line | 141 | 136069 | 37.8378 | -122.2124 | FLORENCETERRACECAPRICORN | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078427 | OH | Sus | 0 | yes | 2013 | NOV | Yes | Line to Ground | 99251230 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078446&numberofmonths=24&showchangehistorylog=1 | 13-0078446 | EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND X-1104 | 12541104 | FUSE | 9024 | 20131122 | 641 | 911048 | 1611 | Distribution Circuit | Vegetation | Tree - fell into line | 133 | 105823 | 37.8262 | -122.1939 | CHELSEATHACKERAY | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078446 | OH | Sus | 0 | yes | 2013 | NOV | Yes | Line to Ground | 99251228 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078764&numberofmonths=24&showchangehistorylog=1 | 13-0078764 | EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND X-1104 | 12541104 | OTHER |  | 20131122 | 1857 | 912995 | 254 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1200 | 53781 | 37.8175 | -122.1921 | CALENDARKEN8316821739StonebridgeChelsea | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078764 | OH | Sus | 0 | yes | 2013 | NOV | Yes | None | 99251446 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0073553&numberofmonths=24&showchangehistorylog=1 | 14-0073553 | EAST BAY | FIELD OPS CENTRAL | Tier 2 | OAKLAND X-1106 | 12541106 | FUSE | 6639 | 20141203 | 1407 | 1123348 | 674 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 674 | 37.7922 | -122.1575 | 12667SKYLINEDRATDRIVEWAY | Clear-32 - 90 F | Conductor, Overhead | On Ground | 14-0073553 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99196712 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0074841&numberofmonths=24&showchangehistorylog=1 | 14-0074841 | EAST BAY | FIELD OPS CENTRAL | Tier 2 | OAK-0401 | 12600401 | OCB | OCB | 20141211 | 342 | 1128964 | 998 | Distribution Circuit | Equipment Failure/Involved | Other | 1011 | 150431 | 37.9012 | -122.2867 | STATFORDANDCOVENTRY | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 14-0074841 | OH | Sus | 31120520 | yes | 2014 | DEC | Yes | Line to Ground | 99195305 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079107&numberofmonths=24&showchangehistorylog=1 | 14-0079107 | EAST BAY | FIELD OPS CENTRAL | Tier 2 | EDES-1112 | 13681112 | RECLOSER | CR282 | 20141230 | 1355 | 1152491 | 409 | Distribution Circuit | Vegetation | Tree - fell into line | 1022 | 78068 | 37.7543 | -122.148 | 145ELYSIANFIELDSANDLDSIDECR297 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079107 | OH | Sus | 31123832 | yes | 2014 | DEC | Yes | Line to Ground | 99190201 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079485&numberofmonths=24&showchangehistorylog=1 | 14-0079485 | EAST BAY | FIELD OPS CENTRAL | Tier 2 | SAN LEANDRO-1109 | 13111109 | FUSE | 9077 | 20141230 | 1739 | 1154510 | 544 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 24480 | 37.752 | -122.1308 | ETTRICKSTSOMALCOLMAVE | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079485 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99190312 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010355&numberofmonths=24&showchangehistorylog=1 | 15-0010355 | EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND K-1104 | 12101104 | FUSE | 8940 | 20150206 | 1428 | 1175827 | 543 | Distribution Circuit | Vegetation | Tree - branch fell on line | 24 | 13032 | 37.8359 | -122.1928 | WebsterJ13121737295SAYRS | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010355 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99185021 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010057&numberofmonths=24&showchangehistorylog=1 | 15-0010057 | EAST BAY | FIELD OPS CENTRAL | Tier 2 | SAN LEANDRO-1109 | 13111109 | FUSE | 9859 | 20150206 | 1021 | 1174507 | 376 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 14664 | 37.7474 | -122.1196 | SUNVALLEY | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010057 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99185185 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0084558&numberofmonths=24&showchangehistorylog=1 | 15-0084558 | EAST BAY | FIELD OPS CENTRAL | Tier 2 | FLORENCE-0401 | 12690401 | OCB | OCB | 20151213 | 743 | 1360231 | 280 | Distribution Circuit | Vegetation | Tree - fell into line | 479 | 35020 | 37.8361 | -122.2202 | WIREDOWNAT5566MORAGA8SOF5521SNAPPEDPOLECOMORAGAANDMAXWELLINGTON | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 15-0084558 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1174220 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0084701&numberofmonths=24&showchangehistorylog=1 | 15-0084701 | EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND X-1104 | 12541104 | OTHER | CR022 | 20151213 | 923 | 1360762 | 597 | Distribution Circuit | Vegetation | Tree - fell into line | 676 | 67870 | 37.8218 | -122.1999 | SKYLINE2SOFEVERGREEN | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084701 | OH | Sus | 31205544 | yes | 2015 | DEC | Yes | Open Circuit | 1174367 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0013482&numberofmonths=24&showchangehistorylog=1 | 16-0013482 | EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND K-1102 | 12101102 | FUSE | 6589 | 20160217 | 2151 | 1407396 | 634 | Distribution Circuit | Vegetation | Tree - branch fell on line | 59 | 19107 | 37.8427 | -122.2046 | 6581HeatherRidgeWay | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013482 | OH | Sus | 31219888 | yes | 2016 | FEB | Yes | Line to Ground | 1186570 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0013324&numberofmonths=24&showchangehistorylog=1 | 16-0013324 | EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND K-1104 | 12101104 | JUMPER | WIREDOWNWESTOVERANDSHELTERWOOD | 20160217 | 1757 | 1406157 | 663 | Distribution Circuit | Vegetation | Tree - bark fell into line | 117 | 32864 | 37.8303 | -122.1961 | WebsterJ13121736460SHELTERWOOD | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013324 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Line to Line | 1186408 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0018006&numberofmonths=24&showchangehistorylog=1 | 16-0018006 | EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND X-1104 | 12541104 | JUMPER | WIREDOWN2NO9024 | 20160305 | 2058 | 1419340 | 474 | Distribution Circuit | Vegetation | Tree - fell into line | 133 | 29762 | 37.827 | -122.1945 | ChelseaDrive2NO9024 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018006 | OH | Sus | 31222882 | yes | 2016 | MAR | Yes | Line to Ground | 1189877 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0018093&numberofmonths=24&showchangehistorylog=1 | 16-0018093 | EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND X-1104 | 12541104 | FUSE | 9089 | 20160305 | 2259 | 1420616 | 818 | Distribution Circuit | Vegetation | Tree - fell into line | 233 | 51016 | 37.819 | -122.1889 | MELVILLEDRANDASCOT | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018093 | OH | Sus | 31222882 | yes | 2016 | MAR | Yes | Line to Ground | 1189965 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017860&numberofmonths=24&showchangehistorylog=1 | 16-0017860 | EAST BAY | FIELD OPS CENTRAL | Tier 2 | SAN LEANDRO-1109 | 13111109 | RECLOSER | CR182 | 20160305 | 2100 | 1419339 | 840 | Distribution Circuit | Vegetation | Tree - fell into line | 419 | 83790 | 37.7521 | -122.1265 | SUNVALLEYDR1WO9859AND1EO9859 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017860 | OH | Sus | 31222882 | yes | 2016 | MAR | Yes | Multi-Fault | 1189714 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005469&numberofmonths=24&showchangehistorylog=1 | 17-0005469 | EAST BAY | FIELD OPS CENTRAL | Tier 2 | EL CERRITO G-1105 | 12501105 | RECLOSER | BR160 | 20170108 | 1544 | 1627794 | 1481 | Distribution Circuit | Vegetation | Tree - fell into line | 2152 | 143997 | 37.8981 | -122.2615 | LDSIDER9359TWDR7302 | Overcast-Rain-32-90 F | Conductor, Overhead | On Ground | 17-0005469 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1245253 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005216&numberofmonths=24&showchangehistorylog=1 | 17-0005216 | EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND K-1102 | 12101102 | FUSE | 1369 | 20170108 | 1041 | 1625023 | 1579 | Distribution Circuit | Vegetation | Tree - fell into line | 152 | 93062 | 37.8425 | -122.209 | VILLALOBOSCARLOS6931PINEHAVENRDOAKLAND | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005216 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245005 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005230&numberofmonths=24&showchangehistorylog=1 | 17-0005230 | EAST BAY | FIELD OPS CENTRAL | Tier 2 | SAN LEANDRO-1109 | 13111109 | FUSE | 9166 | 20170108 | 957 | 1624525 | 353 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 6707 | 37.7515 | -122.1277 | MONANSTEOMALCOLM | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005230 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245019 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006655&numberofmonths=24&showchangehistorylog=1 | 17-0006655 | EAST BAY | FIELD OPS CENTRAL | Tier 2 | OAKLAND J-1102 | 12091102 | FUSE | 6651 | 20170110 | 1317 | 1633358 | 919 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 42274 | 37.783 | -122.1757 | LDSIDEOF6651FUCOMountainBlvdRustlingAve | Heavy Rain-Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006655 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246284 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006685&numberofmonths=24&showchangehistorylog=1 | 17-0006685 | EAST BAY | FIELD OPS CENTRAL | Tier 2 | OAKLAND K-1103 | 12101103 | FUSE | 7970 | 20170110 | 1334 | 1633406 | 366 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 8784 | 37.8358 | -122.2186 | FERWOODDR50SOFLORENCETERR | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006685 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246305 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006860&numberofmonths=24&showchangehistorylog=1 | 17-0006860 | EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND K-1104 | 12101104 | FUSE | 6465 | 20170110 | 1623 | 1634295 | 1138 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 39830 | 37.8357 | -122.1847 | LDSIDEOF6465 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006860 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246440 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006634&numberofmonths=24&showchangehistorylog=1 | 17-0006634 | EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND X-1104 | 12541104 | FUSE | 81195 | 20170110 | 1228 | 1633278 | 1006 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 14084 | 37.8206 | -122.2007 | TREEDOWN2PNOF81195FUCO | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0006634 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246266 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007370&numberofmonths=24&showchangehistorylog=1 | 17-0007370 | EAST BAY | FIELD OPS CENTRAL | Tier 2 | OAKLAND X-1106 | 12541106 | FUSE | 2457 | 20170111 | 19 | 1638166 | 1195 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 10755 | 37.7852 | -122.145 | PAVANAPHILsw2457Cathyandskyline | Overcast-Fog-Rain-Lightning-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007370 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246957 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013605&numberofmonths=24&showchangehistorylog=1 | 17-0013605 | EAST BAY | FIELD OPS CENTRAL | Tier 2 | OAKLAND X-1106 | 12541106 | FUSE | 9749 | 20170123 | 433 | 1662783 | 375 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 10875 | 37.81 | -122.1975 | 3118Monterey | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013605 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Multi-Fault | 1252427 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018118&numberofmonths=24&showchangehistorylog=1 | 17-0018118 | EAST BAY | FIELD OPS CENTRAL | Tier 2 | OAKLAND J-1102 | 12091102 | FUSE | 6673 | 20170207 | 304 | 1677526 | 610 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 17962 | 37.7973 | -122.1847 | STEPHENSKEVINredwoodrdandmountian | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018118 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1255980 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018169&numberofmonths=24&showchangehistorylog=1 | 17-0018169 | EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND K-1104 | 12101104 | RECLOSER | CR206 | 20170207 | 604 | 1678074 | 506 | Distribution Circuit | Vegetation | Tree - branch fell on line | 221 | 27636 | 37.8317 | -122.197 | STEPHENSKEVIN3pnocr206 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018169 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1256032 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0022917&numberofmonths=24&showchangehistorylog=1 | 17-0022917 | EAST BAY | FIELD OPS CENTRAL | Tier 2 | OAKLAND X-1106 | 12541106 | FUSE | 6935 | 20170218 | 619 | 1698965 | 1686 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 40464 | 37.8055 | -122.1849 | TRINIDADSSDOF6935FUCO | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022917 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1259932 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024836&numberofmonths=24&showchangehistorylog=1 | 17-0024836 | EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND K-1102 | 12101102 | OTHER | WIREDOWN6995ELVERTONDR | 20170221 | 33 | 1706964 | 1029 | Distribution Circuit | Vegetation | Tree - fell into line | 1323 | 345024 | 37.8453 | -122.1989 | PAGANMICHAEL41576012936995ELVERTONDR | Overcast-Fog-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024836 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1261805 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025740&numberofmonths=24&showchangehistorylog=1 | 17-0025740 | EAST BAY | FIELD OPS CENTRAL | Tier 2 | OAKLAND X-1106 | 12541106 | SWITCH | CR21 | 20170222 | 1705 | 1711077 | 609 | Distribution Circuit | Vegetation | Tree - fell into line | 1658 | 36593 | 37.8102 | -122.1995 | HAMILLMIKE51068111482pno9790FUCO | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025740 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1262527 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037714&numberofmonths=24&showchangehistorylog=1 | 17-0037714 | EAST BAY | FIELD OPS CENTRAL | Tier 3 | BERKELEY F-1103 | 12061103 | FUSE | R8029 | 20170406 | 2052 | 1746827 | 1725 | Distribution Circuit | Vegetation | Tree - fell into line | 1931 | 22619 | 37.8695 | -122.245 | PASTR8029 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037714 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1271912 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037545&numberofmonths=24&showchangehistorylog=1 | 17-0037545 | EAST BAY | FIELD OPS CENTRAL | Tier 2 | FRANKLIN-1104 | 13921104 | OTHER | P136 | 20170406 | 2113 | 1749290 | 837 | Distribution Circuit | Equipment Failure/Involved | Overhead | 82 | 67233 | 38.0355 | -122.2583 | LDSDOFP136UNOCALPROPSOTULLIBEERDNO4THST | Overcast-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037545 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Line | 1271765 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037451&numberofmonths=24&showchangehistorylog=1 | 17-0037451 | EAST BAY | FIELD OPS CENTRAL | Tier 2 | OAKLAND K-1104 | 12101104 | RECLOSER | CR210 | 20170406 | 2131 | 1747837 | 1084 | Distribution Circuit | Equipment Failure/Involved | Overhead | 417 | 97411 | 37.8299 | -122.2106 | JENSONRYANCOLTONBLVDNODIAZPL | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037451 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1271665 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037583&numberofmonths=24&showchangehistorylog=1 | 17-0037583 | EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND X-1104 | 12541104 | OTHER | WIREDOWNCORNERCHELTONLNBAGSSMTR100 | 20170406 | 2025 | 1747442 | 505 | Distribution Circuit | Vegetation | Tree - branch fell on line | 154 | 67942 | 37.8232 | -122.1997 | CORNEROFCHELTONLNANDBAGSHOTTEDRSSMTR1009211298 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037583 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1271806 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0038059&numberofmonths=24&showchangehistorylog=1 | 17-0038059 | EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND X-1104 | 12541104 | FUSE | 1353 | 20170406 | 2327 | 1748783 | 1873 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 91176 | 37.8243 | -122.1897 | TWAROWSKICHRIS6508266246LONGWALKDR1NOASCOTDR | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0038059 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1272127 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037609&numberofmonths=24&showchangehistorylog=1 | 17-0037609 | EAST BAY | FIELD OPS CENTRAL | Tier 2 | OAKLAND X-1106 | 12541106 | SWITCH | 1454 | 20170407 | 623 | 1749549 | 796 | Distribution Circuit | Equipment Failure/Involved | Overhead | 204 | 29614 | 37.7863 | -122.1473 | BET1454699301 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037609 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1271836 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037629&numberofmonths=24&showchangehistorylog=1 | 17-0037629 | EAST BAY | FIELD OPS CENTRAL | Tier 2 | SAN LEANDRO-1109 | 13111109 | RECLOSER | CR182 | 20170407 | 114 | 1749128 | 1064 | Distribution Circuit | Equipment Failure/Involved | Overhead | 420 | 300305 | 37.7522 | -122.1267 | BEHINDFIRESTATION9531 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037629 | OH | Sus | 0 | yes | 2017 | APR | Yes | Three Phase Fault | 1271852 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0102194&numberofmonths=24&showchangehistorylog=1 | 17-0102194 | EAST BAY | FIELD OPS CENTRAL | Tier 2 | FLORENCE-0401 | 12690401 | OCB | 4012 | 20171216 | 1622 | 1945670 | 414 | Distribution Circuit | Equipment Failure/Involved | Overhead | 492 | 63550 | 37.8359 | -122.2201 | 1SOF3546 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0102194 | OH | Sus | 0 | yes | 2017 | DEC | Yes | Line to Ground | 1320104 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005153&numberofmonths=24&showchangehistorylog=1 | 19-0005153 | EAST BAY | FIELD OPS CENTRAL | Tier 3 | BERKELEY F-1103 | 12061103 | FUSE | R8029 | 20190106 | 1440 | 255424 | 714 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 9282 | 37.8695 | -122.245 | EOFCGC314973850342 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005153 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1403624 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0009986&numberofmonths=24&showchangehistorylog=1 | 19-0009986 | EAST BAY | FIELD OPS CENTRAL | Tier 2 | OAK SUB | 1260 | OCB | 4012 | 20190116 | 1713 | 268446 | 654 | Distribution Circuit | Vegetation | Tree - fell into line | 1012 | 351822 | 37.9013 | -122.287 | 94StratfordArlingtonCovingtonEofR3649 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009986 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1406852 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011128&numberofmonths=24&showchangehistorylog=1 | 19-0011128 | EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND K-1104 | 12101104 | FUSE | 9151 | 20190117 | 1237 | 273989 | 228 | Distribution Circuit | Vegetation | Tree - fell into line | 71 | 16188 | 37.8309 | -122.1954 | TWAROWSKICHRIS6508266246WESTOVERDRIVEEOSHELTERWOODDRIVE | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011128 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407747 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0016981&numberofmonths=24&showchangehistorylog=1 | 19-0016981 | EAST BAY | FIELD OPS CENTRAL | Tier 2 | RIDGE-0401 | 12840401 | FUSE | R7941 | 20190202 | 602 | 286601 | 891 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 53460 | 37.8879 | -122.2544 | ONSHASTAEOFQUEENSSHASTAINTERSECTION | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0016981 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1411440 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023258&numberofmonths=24&showchangehistorylog=1 | 19-0023258 | EAST BAY | FIELD OPS CENTRAL | Tier 2 | OAKLAND K SUB | 1210 | OCB | 172 | 20190214 | 1113 | 308726 | 489 | Distribution Circuit | Vegetation | Tree - fell into line | 10992 | 808191 | 37.8481 | -122.2286 | 7070pasorobles | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023258 | OH | Sus | 31425494 | yes | 2019 | FEB | Yes | Line to Line | 1416450 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0064773&numberofmonths=24&showchangehistorylog=1 | 19-0064773 | EAST BAY | FIELD OPS CENTRAL | Tier 2 | SAN LEANDRO-1109 | 13111109 | FUSE | 9166 | 20190608 | 2045 | 401833 | 1094 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 20786 | 37.7515 | -122.1277 | 3SOF9166 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0064773 | OH | Sus | 31452134 | yes | 2019 | JUN | Yes | Line to Ground | 1447031 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0018981&numberofmonths=24&showchangehistorylog=1 | 20-0018981 | EAST BAY | FIELD OPS CENTRAL | Tier 2 | OAKLAND J-1106 | 12091106 | FUSE | 67575 | 20200209 | 819 | 781217 | 597 | Distribution Circuit | Vegetation | Tree - fell into line | 122 | 72834 | 37.7604 | -122.1577 | 2POLESSOUTH67575 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0018981 | OH | Sus | 31490427 | yes | 2020 | FEB | Yes | Three Phase Fault | 1512993 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0010158&numberofmonths=24&showchangehistorylog=1 | 21-0010158 | EAST BAY | FIELD OPS CENTRAL | Tier 2 | BOSTON-0401 | 13320401 | OTHER | 1PHASEDOWNCOLEIMERTMONTEREY | 20210119 | 322 | 1214410 | 437 | Distribution Circuit | Equipment Failure/Involved | Overhead | 314 | 124442 | 37.8152 | -122.2026 | COLEIMERTMONTEREY | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0010158 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1594124 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0010425&numberofmonths=24&showchangehistorylog=1 | 21-0010425 | EAST BAY | FIELD OPS CENTRAL | Tier 2 | EL CERRITO G-1105 | 12501105 | FUSE | R8474 | 20210119 | 648 | 1215170 | 430 | Distribution Circuit | Company Initiated | Improper Construction | 136 | 58480 | 37.9154 | -122.282 | 101KINGSINGTON | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0010425 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1594383 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0010755&numberofmonths=24&showchangehistorylog=1 | 21-0010755 | EAST BAY | FIELD OPS CENTRAL | Tier 2 | EL CERRITO G-1105 | 12501105 | FUSE | R8236 | 20210119 | 1215 | 1217017 | 442 | Distribution Circuit | Equipment Failure/Involved | Overhead | 117 | 51714 | 37.9213 | -122.2911 | 1015HavensPl | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0010755 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1594630 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0010280&numberofmonths=24&showchangehistorylog=1 | 21-0010280 | EAST BAY | FIELD OPS CENTRAL | Tier 2 | OAKLAND K-1102 | 12101102 | OCB | 11022 | 20210119 | 646 | 1215189 | 411 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1340 | 357711 | 37.848 | -122.2286 | THORNHILLANDOAKWOOD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0010280 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1594264 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0010704&numberofmonths=24&showchangehistorylog=1 | 21-0010704 | EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND K-1104 | 12101104 | OTHER | WIREDOWNLOADSIDEOF9880 | 20210119 | 946 | 1216517 | 422 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 1266 | 37.8328 | -122.1977 | 6840BALBOADR | Clear-32-90 F | Conductor, Overhead | On Ground | 21-0010704 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1594594 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0010529&numberofmonths=24&showchangehistorylog=1 | 21-0010529 | EAST BAY | FIELD OPS CENTRAL | Tier 2 | SPRUCE-0402 | 13340402 | FUSE | R3383 | 20210119 | 726 | 1215589 | 591 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 12411 | 37.9025 | -122.2642 | CARTERDAVID5103855868609Vistamont | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0010529 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1594468 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0136022&numberofmonths=24&showchangehistorylog=1 | 21-0136022 | EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND K-1104 | 12101104 | FUSE | 9541 | 20211024 | 907 | 1509040 | 527 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 13608 | 37.8347 | -122.1903 | 6869MOOREDR | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0136022 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Ground | 1677491 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0157820&numberofmonths=24&showchangehistorylog=1 | 21-0157820 | EAST BAY | FIELD OPS CENTRAL | Tier 2 | EDES-1112 | 13681112 | FUSE | 6787 | 20211214 | 530 | 1569702 | 596 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2384 | 37.7657 | -122.1362 | NOF8739 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0157820 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1694719 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0044645&numberofmonths=24&showchangehistorylog=1 | 23-0044645 | EAST BAY | FIELD OPS CENTRAL | Tier 2 | PALO SECO-0401 | 13180401 | FUSE | 4137 | 20230314 | 850 | 2035370 | 309 | Distribution Circuit | Vegetation | Tree - fell into line | 307 | 87130 | 37.8152 | -122.2028 | LDSIDEOF4137 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0044645 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1824809 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0022304&numberofmonths=24&showchangehistorylog=1 | 13-0022304 | FRESNO | FIELD OPS SOUTH | Tier 2 | AUBERRY-1101 | 254151101 | FUSE | D133 | 20130408 | 741 | 769174 | 464 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 5104 | 37.0089 | -119.413 | 1SPANFROMD133 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0022304 | OH | Sus | 0 | yes | 2013 | APR | Yes | Line to Ground | 99292239 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017870&numberofmonths=24&showchangehistorylog=1 | 16-0017870 | FRESNO | FIELD OPS SOUTH | Tier 2 | AUBERRY-1101 | 254151101 | FUSE | D13006 | 20160305 | 2022 | 1418915 | 459 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2295 | 37.0952 | -119.4291 | 41470ACORN | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017870 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1189724 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007485&numberofmonths=24&showchangehistorylog=1 | 17-0007485 | FRESNO | FIELD OPS SOUTH | Tier 2 | DUNLAP-1103 | 254061103 | RECLOSER | 7080 | 20170111 | 20 | 1638345 | 854 | Distribution Circuit | Vegetation | Tree - fell into line | 282 | 240828 | 36.7433 | -118.9608 | TREECONNECT26POLE4TOPOLE7BEWYOND7629D | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007485 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1247042 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011753&numberofmonths=24&showchangehistorylog=1 | 17-0011753 | FRESNO | FIELD OPS SOUTH | Tier 2 | DUNLAP-1103 | 254061103 | RECLOSER | 7080 | 20170120 | 1825 | 1653783 | 1523 | Distribution Circuit | Vegetation | Tree - branch fell on line | 282 | 426086 | 36.7433 | -118.9608 | LDSIDE7964DBETTREE1920 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0011753 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Three Phase Fault | 1250584 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011886&numberofmonths=24&showchangehistorylog=1 | 17-0011886 | FRESNO | FIELD OPS SOUTH | Tier 2 | SAND CREEK-1103 | 254601103 | FUSE | 7995F | 20170121 | 101 | 1655384 | 481 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 40885 | 36.6391 | -118.9547 | MTR1005161958 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0011886 | OH | Sus | 42930433 | yes | 2017 | JAN | Yes | Line to Ground | 1250712 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013060&numberofmonths=24&showchangehistorylog=1 | 17-0013060 | FRESNO | FIELD OPS SOUTH | Tier 3 | AUBERRY-1101 | 254151101 | FUSE | D5467 | 20170122 | 427 | 1658745 | 1938 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 6971 | 37.0475 | -119.3222 | MARKARIANFRED55928940682LOCATIONS | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013060 | OH | Sus | 31297701 | yes | 2017 | JAN | Yes | Line to Ground | 1251880 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013127&numberofmonths=24&showchangehistorylog=1 | 17-0013127 | FRESNO | FIELD OPS SOUTH | Tier 2 | AUBERRY-1101 | 254151101 | RECLOSER | R314 | 20170122 | 1140 | 1660681 | 204 | Distribution Circuit | Vegetation | Tree - fell into line | 421 | 43624 | 36.9954 | -119.4087 | MCKINNEYRICHARD4083095478MAINLINEATD12547 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013127 | OH | Sus | 42930604 | yes | 2017 | JAN | Yes | Line to Ground | 1251945 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012500&numberofmonths=24&showchangehistorylog=1 | 17-0012500 | FRESNO | FIELD OPS SOUTH | Tier 2 | DUNLAP-1102 | 254061102 | SWITCH | 3084D | 20170122 | 1453 | 1661368 | 123 | Distribution Circuit | Vegetation | Tree - fell into line | 65 | 7995 | 36.7235 | -118.9828 | BETWEEN8TH9THSPANLOADSIDE3084DCENTERPHASE | Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0012500 | OH | Sus | 42930533 | yes | 2017 | JAN | Yes | Line to Ground | 1252053 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013043&numberofmonths=24&showchangehistorylog=1 | 17-0013043 | FRESNO | FIELD OPS SOUTH | Tier 2 | DUNLAP-1103 | 254061103 | RECLOSER | 7080 | 20170122 | 1048 | 1660448 | 1494 | Distribution Circuit | Vegetation | Tree - fell into line | 282 | 413458 | 36.7433 | -118.9608 | 4SPANSLOADSIDEOF7629D | Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0013043 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1251862 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013985&numberofmonths=24&showchangehistorylog=1 | 17-0013985 | FRESNO | FIELD OPS SOUTH | Tier 3 | AUBERRY-1101 | 254151101 | FUSE | 37429 | 20170123 | 1715 | 1664724 | 155 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 310 | 37.0582 | -119.3432 | 1SPANNOF37429 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0013985 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1252737 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013043&numberofmonths=24&showchangehistorylog=1 | 17-0013043 | FRESNO | FIELD OPS SOUTH | Tier 2 | DUNLAP-1102 | 254061102 | FUSE | 7997F | 20170123 | 1620 | 1664590 | 1232 | Distribution Circuit | Environmental/External | Ice or snow | 61 | 75152 | 36.7284 | -118.9576 | 7SPANSNOFFUCO | Overcast-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0013043 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1252706 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037721&numberofmonths=24&showchangehistorylog=1 | 17-0037721 | FRESNO | FIELD OPS SOUTH | Tier 3 | AUBERRY-1101 | 254151101 | JUMPER | WIREDOWN1WOFMTR1004704399 | 20170407 | 542 | 1749536 | 453 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1812 | 37.0759 | -119.346 | SpahShannon5596330251woodlandrd | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037721 | OH | Sus | 0 | yes | 2017 | APR | Yes | None | 1271918 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005476&numberofmonths=24&showchangehistorylog=1 | 19-0005476 | FRESNO | FIELD OPS SOUTH | Tier 2 | AUBERRY-1102 | 254151102 | FUSE | D2748 | 20190106 | 2018 | 257577 | 363 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 21054 | 37.017 | -119.5136 | POLSGROVEJUSTINpennyroyalln | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005476 | OH | Sus | 43626773 | yes | 2019 | JAN | Yes | Line to Ground | 1403924 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018005&numberofmonths=24&showchangehistorylog=1 | 19-0018005 | FRESNO | FIELD OPS SOUTH | Tier 2 | DUNLAP-1102 | 254061102 | RECLOSER | 7173 | 20190204 | 1359 | 290490 | 7414 | Distribution Circuit | Equipment Failure/Involved | Overhead | 303 | 1040880 | 36.6985 | -119.0118 | LOADSIDEOF7167AND6SPANSOFWIRE3201FAND6SPANSOFWIRE | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0018005 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Multi-Fault | 1412291 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018401&numberofmonths=24&showchangehistorylog=1 | 19-0018401 | FRESNO | FIELD OPS SOUTH | Tier 2 | DUNLAP-1102 | 254061102 | FUSE | 7684F | 20190204 | 506 | 289478 | 3701 | Distribution Circuit | Vegetation | Tree - branch fell on line | 30 | 111030 | 36.7365 | -118.9596 | OKAMURADALE5599033864VARIOUSLOCATIONS | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018401 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1412605 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018005&numberofmonths=24&showchangehistorylog=1 | 19-0018005 | FRESNO | FIELD OPS SOUTH | Tier 2 | DUNLAP-1102 | 254061102 | FUSE | 3201F | 20190204 | 1359 | 296545 | 8250 | Distribution Circuit | Environmental/External | Ice or snow | 4 | 40636 | 36.722 | -118.9782 | NEARMTR1009435787 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0018005 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1413830 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0017740&numberofmonths=24&showchangehistorylog=1 | 19-0017740 | FRESNO | FIELD OPS SOUTH | Tier 2 | DUNLAP-1103 | 254061103 | RECLOSER | 7170 | 20190204 | 256 | 289407 | 10624 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 150788 | 36.7263 | -118.9956 | 3RD4THPOLESSOF3418F | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017740 | OH | Sus | 43669499 | yes | 2019 | FEB | Yes | Line to Line | 1412142 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0017740&numberofmonths=24&showchangehistorylog=1 | 19-0017740 | FRESNO | FIELD OPS SOUTH | Tier 2 | DUNLAP-1103 | 254061103 | RECLOSER | 7080 | 20190204 | 256 | 292038 | 3518 | Distribution Circuit | Environmental/External | Ice or snow | 354 | 969928 | 36.7404 | -118.9616 | BEYOND7989FINNEIGHBORHOOD | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017740 | OH | Sus | 43669499 | yes | 2019 | FEB | Yes | Line to Ground | 1412545 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020277&numberofmonths=24&showchangehistorylog=1 | 19-0020277 | FRESNO | FIELD OPS SOUTH | Tier 2 | DUNLAP-1103 | 254061103 | FUSE | 3767F | 20190209 | 955 | 296826 | 375 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 375 | 36.7416 | -118.9589 | EOLDEPOLE2SPOFWIREATEOL | Overcast-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0020277 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1413983 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023635&numberofmonths=24&showchangehistorylog=1 | 19-0023635 | FRESNO | FIELD OPS SOUTH | Tier 3 | AUBERRY-1101 | 254151101 | FUSE | D325 | 20190214 | 1357 | 309515 | 1625 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 63402 | 37.0401 | -119.3375 | MULTIPLEDUETOSTORM | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0023635 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416783 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025522&numberofmonths=24&showchangehistorylog=1 | 19-0025522 | FRESNO | FIELD OPS SOUTH | Tier 2 | AUBERRY-1102 | 254151102 | FUSE | D9404 | 20190217 | 2247 | 317102 | 693 | Distribution Circuit | Equipment Failure/Involved | Overhead | 35 | 24255 | 36.9875 | -119.5309 | CGC41816260425AMARALRANCH15488SKYLANLN | Partly Cloudy-Fog-Below 32 F | Connector or Splice (OH) | Broken, wire on ground | 19-0025522 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1418579 | CSO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0086152&numberofmonths=24&showchangehistorylog=1 | 20-0086152 | FRESNO | FIELD OPS SOUTH | Tier 2 | DUNLAP-0001 | 254060001 | FUSE | 7985F | 20200817 | 1452 | 1017281 | 370 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 5507 | 36.7088 | -119.005 | TREVINOVINCENT559356280151756CALIFORNIA245PINEHURST | Partly Cloudy-Heat Wave-Above 90 | Crossarm, Wood | Broken, wire on ground | 20-0086152 | OH | Sus | 0 | yes | 2020 | AUG | Yes | Line to Ground | 1556327 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0129469&numberofmonths=24&showchangehistorylog=1 | 21-0129469 | FRESNO | FIELD OPS SOUTH | Tier 2 | AUBERRY-1101 | 254151101 | RECLOSER | R2845 | 20211011 | 2112 | 1495296 | 1171 | Distribution Circuit | Vegetation | Tree - fell into line | 823 | 842904 | 37.0539 | -119.4608 | WEOFMTR1008950111 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0129469 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Line | 1673363 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0157266&numberofmonths=24&showchangehistorylog=1 | 21-0157266 | FRESNO | FIELD OPS SOUTH | Tier 2 | AUBERRY-1102 | 254151102 | FUSE | D10394 | 20211213 | 1217 | 1567063 | 214 | Distribution Circuit | 3rd Party | Other | 20 | 4280 | 37.0272 | -119.5024 | 1WOFMTR1004760990 | Clear-32-90F | Conductor, Overhead | On Ground | 21-0157266 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Line | 1694172 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0010866&numberofmonths=24&showchangehistorylog=1 | 23-0010866 | FRESNO | FIELD OPS SOUTH | Tier 2 | AUBERRY-1101 | 254151101 | RECLOSER | R2838 | 20230109 | 755 | 1936604 | 754 | Distribution Circuit | Vegetation | Tree - fell into line | 418 | 255427 | 37.0877 | -119.4677 | PATTONLANDON5595735990AuberryrdWOFD4138 | Overcast-Fog-Heavy Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 23-0010866 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Line | 1800718 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0017068&numberofmonths=24&showchangehistorylog=1 | 23-0017068 | FRESNO | FIELD OPS SOUTH | Tier 2 | AUBERRY-1102 | 254151102 | OTHER | D8323 | 20230116 | 708 | 1957161 | 664 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 3016 | 37.0126 | -119.5615 | 1NOFCGC418350461083 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 23-0017068 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1805766 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0034521&numberofmonths=24&showchangehistorylog=1 | 23-0034521 | FRESNO | FIELD OPS SOUTH | Tier 2 | AUBERRY-1101 | 254151101 | RECLOSER | 49122 | 20230224 | 2120 | 2007220 | 1100 | Distribution Circuit | Environmental/External | Ice or snow | 1 | 1100 | 37.0812 | -119.4864 | NA | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 23-0034521 | OH | Sus | 0 | No | 2023 | FEB | Yes | Force Out | 1817531 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0035155&numberofmonths=24&showchangehistorylog=1 | 23-0035155 | FRESNO | FIELD OPS SOUTH | Tier 2 | KERCKHOFF-1101 | 252561101 | FUSE | D2818 | 20230225 | 119 | 2007461 | 1080 | Distribution Circuit | Environmental/External | Ice or snow | 49 | 52920 | 37.0936 | -119.4974 | PATTONLANDON5595735990Mountaintopranchrd | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0035155 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Line | 1818011 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0035280&numberofmonths=24&showchangehistorylog=1 | 23-0035280 | FRESNO | FIELD OPS SOUTH | Tier 2 | SAND CREEK-1103 | 254601103 | FUSE | 7485F | 20230225 | 211 | 2008658 | 922 | Distribution Circuit | Environmental/External | Ice or snow | 51 | 47022 | 36.6893 | -119.1039 | CGC419683348947CGC419686049230 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0035280 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Ground | 1818118 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0044810&numberofmonths=24&showchangehistorylog=1 | 23-0044810 | FRESNO | FIELD OPS SOUTH | Tier 2 | AUBERRY-1102 | 254151102 | OCB | 11022 | 20230314 | 1122 | 2036982 | 563 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1656 | 127091 | 37.0682 | -119.4963 | CGC4184538638901POLESOUTH | Strong Winds-Clear-32-90F | Pole-Wood | Broken, wire on ground | 23-0044810 | OH | Sus | 35431654 | No | 2023 | MAR | Yes | Line to Ground | 1824929 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0022464&numberofmonths=24&showchangehistorylog=1 | 13-0022464 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 3283 | 20130408 | 648 | 768993 | 602 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 3817 | 39.3122 | -123.7829 | 4PASTFUSES | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0022464 | OH | Sus | 0 | yes | 2013 | APR | Yes | Line to Ground | 99292111 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0022150&numberofmonths=24&showchangehistorylog=1 | 13-0022150 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 3975 | 20130408 | 112 | 768222 | 918 | Distribution Circuit | Vegetation | Tree - branch fell on line | 68 | 41827 | 39.2093 | -123.7102 | 6PASTOJS | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0022150 | OH | Sus | 0 | yes | 2013 | APR | Yes | Line to Ground | 99292339 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0022485&numberofmonths=24&showchangehistorylog=1 | 13-0022485 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 2525 | 20130408 | 948 | 769568 | 528 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 651 | 39.0978 | -123.7045 | 4AND5SPANSFROM98555 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0022485 | OH | Sus | 0 | yes | 2013 | APR | Yes | Line to Line | 99292098 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0022531&numberofmonths=24&showchangehistorylog=1 | 13-0022531 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | RECLOSER | 1260 | 20130408 | 1138 | 769912 | 527 | Distribution Circuit | Vegetation | Tree - fell into line | 94 | 14670 | 39.1295 | -123.7111 | 2AND3SPANSFROM2605TWDLR1260 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0022531 | OH | Sus | 0 | yes | 2013 | APR | Yes | Line to Line | 99292067 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0022575&numberofmonths=24&showchangehistorylog=1 | 13-0022575 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 1273 | 20130408 | 1158 | 770205 | 752 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 752 | 39.0238 | -123.6747 | 1STSPANLDSIDEOF1273 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0022575 | OH | Sus | 0 | yes | 2013 | APR | Yes | Line to Line | 99292032 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0022453&numberofmonths=24&showchangehistorylog=1 | 13-0022453 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 8547 | 20130408 | 607 | 769799 | 578 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1156 | 39.5065 | -123.7572 | 2PSANSPASTFUSES | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0022453 | OH | Sus | 0 | yes | 2013 | APR | Yes | Line to Line | 99292117 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0022757&numberofmonths=24&showchangehistorylog=1 | 13-0022757 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 3163 | 20130408 | 1645 | 770959 | 1181 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 44878 | 39.6527 | -123.7828 | ATFUCO3157ONSS | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0022757 | OH | Sus | 0 | yes | 2013 | APR | Yes | Three Phase Fault | 99291773 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0022231&numberofmonths=24&showchangehistorylog=1 | 13-0022231 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 1677 | 20130408 | 550 | 768874 | 425 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 6375 | 39.4154 | -123.7817 | 5SPANSPASTFUSESTOTHENORTH | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0022231 | OH | Sus | 0 | yes | 2013 | APR | Yes | Line to Ground | 99292300 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0022646&numberofmonths=24&showchangehistorylog=1 | 13-0022646 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 8769 | 20130408 | 859 | 769414 | 646 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 3876 | 39.3718 | -123.7697 | 15080MITCHELCRK | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0022646 | OH | Sus | 0 | yes | 2013 | APR | Yes | Line to Line | 99291984 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0022562&numberofmonths=24&showchangehistorylog=1 | 13-0022562 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | RIO DELL-1102 | 192251102 | FUSE | 1997 | 20130408 | 834 | 769769 | 621 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 4347 | 40.2843 | -124.0598 | 114279035074 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0022562 | OH | Sus | 0 | yes | 2013 | APR | Yes | Line to Line | 99292043 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0022207&numberofmonths=24&showchangehistorylog=1 | 13-0022207 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER | 2500 | 20130408 | 318 | 768751 | 574 | Distribution Circuit | Vegetation | Tree - fell into line | 116 | 66584 | 39.4487 | -123.3143 | 7701HEARSTWILLITSROADAND8SPANSPASTLR2500 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0022207 | OH | Sus | 0 | yes | 2013 | APR | Yes | Line to Ground | 99292310 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078055&numberofmonths=24&showchangehistorylog=1 | 13-0078055 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 1709 | 20131121 | 1626 | 908219 | 1574 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 6296 | 39.878 | -123.7264 | 115176121002 | Strong winds-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 13-0078055 | OH | Sus | 0 | yes | 2013 | NOV | Yes | Line to Line | 99251782 | CAW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078065&numberofmonths=24&showchangehistorylog=1 | 13-0078065 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LUCERNE-1103 | 43351103 | OCB | OCB | 20131121 | 1904 | 908530 | 2720 | Distribution Circuit | Vegetation | Tree - fell into line | 2885 | 1301516 | 39.1105 | -122.813 | ATMTR10083908543628LAKESHOREBLVDNICE | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on object | 13-0078065 | OH | Sus | 0 | yes | 2013 | NOV | Yes | Three Phase Fault | 99251277 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078266&numberofmonths=24&showchangehistorylog=1 | 13-0078266 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LUCERNE-1103 | 43351103 | FUSE | 4873 | 20131121 | 2114 | 910446 | 2379 | Distribution Circuit | Vegetation | Tree - branch fell on line | 39 | 92781 | 39.1289 | -122.8566 | 2SPANSSSMTR1008153102 | Strong winds-32 - 90 F | Conductor, Underground | Broken, wire on ground | 13-0078266 | OH | Sus | 0 | yes | 2013 | NOV | Yes | None | 99251252 | CU | UG | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078100&numberofmonths=24&showchangehistorylog=1 | 13-0078100 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | POTTER VALLEY P H-1105 | 42281105 | RECLOSER | 1904 | 20131121 | 1921 | 908604 | 1703 | Distribution Circuit | Vegetation | Tree - branch fell on line | 347 | 590941 | 39.3193 | -123.0943 | SILVER346112SPANSFROM4373TOWARDS1904 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0078100 | OH | Sus | 0 | yes | 2013 | NOV | Yes |  | 99251770 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078220&numberofmonths=24&showchangehistorylog=1 | 13-0078220 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | POTTER VALLEY P H-1105 | 42281105 | RECLOSER | 64118 | 20131121 | 2006 | 908967 | 2659 | Distribution Circuit | Vegetation | Tree - branch fell on line | 135 | 358965 | 39.362 | -123.1285 | SILVER346110552MAINST | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0078220 | OH | Sus | 0 | yes | 2013 | NOV | Yes |  | 99251259 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078985&numberofmonths=24&showchangehistorylog=1 | 13-0078985 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | UPPER LAKE-1101 | 42871101 | FUSE | 2335 | 20131121 | 2129 | 911058 | 2881 | Distribution Circuit | Equipment Failure/Involved | Other | 27 | 77787 | 39.1926 | -122.9706 | 8SPANSLOADSIDEOF2335 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0078985 | OH | Sus | 0 | yes | 2013 | NOV | Yes | None | 99250901 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078139&numberofmonths=24&showchangehistorylog=1 | 13-0078139 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1103 | 42661103 | FUSE | 8301 | 20131121 | 1907 | 908325 | 686 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 18585 | 39.4882 | -123.4221 | GALLETTITIMTREETHROUGHLINEBROKENPOLERISERCUTOUTS6457 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0078139 | OH | Sus | 0 | yes | 2013 | NOV | Yes |  | 99251761 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078282&numberofmonths=24&showchangehistorylog=1 | 13-0078282 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOPLAND-1101 | 42251101 | FUSE | 9395 | 20131122 | 133 | 910379 | 1013 | Distribution Circuit | Equipment Failure/Involved | Other | 9 | 9117 | 38.9475 | -123.1655 | ESPINOLACHRISTOPHER2SPANSsssideofmeter1009671352 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078282 | OH | Sus | 0 | yes | 2013 | NOV | Yes | Line to Line | 99251708 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078480&numberofmonths=24&showchangehistorylog=1 | 13-0078480 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LOW GAP-1101 | 192411101 | RECLOSER | 4086 | 20131122 | 919 | 911595 | 388 | Distribution Circuit | Vegetation | Tree - branch fell on line | 56 | 19853 | 40.3029 | -123.3534 | WALPOLEJIMZENIARD | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078480 | OH | Sus | 0 | yes | 2013 | NOV | Yes | Line to Line | 99251599 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078968&numberofmonths=24&showchangehistorylog=1 | 13-0078968 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LOW GAP-1101 | 192411101 | FUSE | 4139 | 20131122 | 1545 | 912607 | 1525 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 28975 | 40.4651 | -123.5279 | 1SPANLDSIDEOFFUCO4139 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0078968 | OH | Sus | 0 | yes | 2013 | NOV | Yes | Line to Line | 99251099 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078827&numberofmonths=24&showchangehistorylog=1 | 13-0078827 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LUCERNE-1103 | 43351103 | FUSE | 7205 | 20131122 | 9 | 913272 | 3821 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 106492 | 39.1227 | -122.8396 | 1CORNEROFBURPEEANDLAKEVIEWDRIVETREETHROUGHLINE2TX1007973337WIREONGROUND | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078827 | OH | Sus | 0 | yes | 2013 | NOV | Yes | Line to Ground | 99250910 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0079011&numberofmonths=24&showchangehistorylog=1 | 13-0079011 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LUCERNE-1106 | 43351106 | FUSE | 8955 | 20131122 | 1820 | 912867 | 1773 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 5319 | 39.1061 | -122.8125 | 1POLESOUTHOF8955 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0079011 | OH | Sus | 0 | yes | 2013 | NOV | Yes | None | 99251063 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078486&numberofmonths=24&showchangehistorylog=1 | 13-0078486 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | POTTER VALLEY P H-1102 | 42281102 | RECLOSER | 95878 | 20131122 | 446 | 910836 | 794 | Distribution Circuit | Equipment Failure/Involved | Other | 140 | 111160 | 39.3617 | -123.1266 | CAP726WIREDOWN | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078486 | OH | Sus | 0 | yes | 2013 | NOV | Yes | Line to Ground | 99251596 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078777&numberofmonths=24&showchangehistorylog=1 | 13-0078777 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | REDBUD-1101 | 43191101 | RECLOSER | 400 | 20131122 | 1204 | 912235 | 1659 | Distribution Circuit | Vegetation | Tree - fell into line | 673 | 560037 | 39.0262 | -122.7314 | MTR10097379771SPANFROMMTR1009737977TWDFUCO81239AND1SPANSSOF48895 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078777 | OH | Sus | 0 | yes | 2013 | NOV | Yes | Line to Line | 99251192 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078913&numberofmonths=24&showchangehistorylog=1 | 13-0078913 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | UPPER LAKE-1101 | 42871101 | FUSE | 6663 | 20131122 | 2354 | 913310 | 2461 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 22058 | 39.2125 | -122.9316 | MTR1007978165 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on object | 13-0078913 | OH | Sus | 0 | yes | 2013 | NOV | Yes |  | 99250908 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078846&numberofmonths=24&showchangehistorylog=1 | 13-0078846 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER | 91810 | 20131122 | 1357 | 912370 | 811 | Distribution Circuit | Vegetation | Tree - branch fell on line | 860 | 576690 | 39.4456 | -123.3807 | 1SPANLOADSIDEOFMTR1009230035ONMAINLINE | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078846 | OH | Sus | 0 | yes | 2013 | NOV | Yes | Open Circuit | 99251176 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0073664&numberofmonths=24&showchangehistorylog=1 | 14-0073664 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 3173 | 20141203 | 2138 | 1123974 | 962 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1924 | 39.6337 | -123.7826 | APPROXIMATELY3spansbeyondFUCO3173 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073664 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99196552 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075914&numberofmonths=24&showchangehistorylog=1 | 14-0075914 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE | 4577 | 20141211 | 1841 | 1135402 | 919 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 18052 | 38.7167 | -123.3538 | JONESMICHAELTXNEXTPOLELOADSIDE | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075914 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194557 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075943&numberofmonths=24&showchangehistorylog=1 | 14-0075943 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE | 9497 | 20141211 | 1841 | 1136409 | 1229 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 43015 | 38.7209 | -123.3584 | MTR1008394795 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075943 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194232 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0074826&numberofmonths=24&showchangehistorylog=1 | 14-0074826 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | RECLOSER | 69032 | 20141211 | 58 | 1128814 | 892 | Distribution Circuit | Vegetation | Tree - fell into line | 120 | 101712 | 39.2998 | -123.7901 | ATFUCO7737ONMAINLINE | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074826 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Multi-Fault | 99195313 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0074868&numberofmonths=24&showchangehistorylog=1 | 14-0074868 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 5065 | 20141211 | 312 | 1128977 | 1700 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 91800 | 39.3645 | -123.7973 | 2SPANSPASTFUCO | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074868 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194403 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075069&numberofmonths=24&showchangehistorylog=1 | 14-0075069 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 3283 | 20141211 | 520 | 1131093 | 1045 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 7315 | 39.3122 | -123.7829 | 3SPANSLDOFFUCO3283 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075069 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99195170 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075198&numberofmonths=24&showchangehistorylog=1 | 14-0075198 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 5009 | 20141211 | 850 | 1131843 | 1120 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 7840 | 39.3108 | -123.7725 | 43401SURFWOODDR | Clear-32 - 90 F | Conductor, Overhead | On Ground | 14-0075198 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99195067 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075265&numberofmonths=24&showchangehistorylog=1 | 14-0075265 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 7339 | 20141211 | 756 | 1131143 | 394 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 5550 | 39.3176 | -123.7863 | 10871MERRILLLN | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075265 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99195014 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075648&numberofmonths=24&showchangehistorylog=1 | 14-0075648 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 3287 | 20141211 | 1439 | 1132161 | 731 | Distribution Circuit | Vegetation | Tree - branch fell on line | 62 | 16937 | 39.3137 | -123.7463 | LOMASADRIAN3SO40530LITTLELAKERD | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075648 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194719 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075694&numberofmonths=24&showchangehistorylog=1 | 14-0075694 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 3151 | 20141211 | 1651 | 1135010 | 130 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 1950 | 39.3417 | -123.8114 | SEVERALSPANSPASTFUSES | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075694 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99194684 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075750&numberofmonths=24&showchangehistorylog=1 | 14-0075750 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 5651 | 20141211 | 1448 | 1135353 | 1797 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 14376 | 39.2774 | -123.7905 | VANDAMMESTATEPARK | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075750 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194288 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075762&numberofmonths=24&showchangehistorylog=1 | 14-0075762 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 5187 | 20141211 | 1452 | 1134484 | 626 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 5634 | 39.2862 | -123.7794 | 44221GORDONLANE | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075762 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194646 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075768&numberofmonths=24&showchangehistorylog=1 | 14-0075768 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 5173 | 20141211 | 1452 | 1134455 | 935 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 12155 | 39.2862 | -123.7802 | 44360GORDONLANE | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075768 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194284 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075843&numberofmonths=24&showchangehistorylog=1 | 14-0075843 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 2223 | 20141211 | 747 | 1131092 | 953 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 3812 | 39.3737 | -123.8154 | 2SPANSPASTFUCO | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075843 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194608 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0074833&numberofmonths=24&showchangehistorylog=1 | 14-0074833 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | EEL RIVER 1101 | 192381101 | RECLOSER | 4814 | 20141211 | 322 | 1128944 | 3546 | Distribution Circuit | Vegetation | Tree - fell into line | 78 | 276588 | 40.4821 | -124.2291 | 3spanssourcesideof4814 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on object | 14-0074833 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99193587 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0074837&numberofmonths=24&showchangehistorylog=1 | 14-0074837 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | RECLOSER | 1260 | 20141211 | 58 | 1128908 | 852 | Distribution Circuit | Vegetation | Tree - branch fell on line | 95 | 80652 | 39.1295 | -123.7111 | ONMAINLINEATFUCO8641 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074837 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194411 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075128&numberofmonths=24&showchangehistorylog=1 | 14-0075128 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | OTHER |  | 20141211 | 420 | 1129440 | 1016 | Distribution Circuit | Vegetation | Tree - branch fell on line | 62 | 60768 | 39.227 | -123.7378 | 2SPANSLDSIDEOFFUCO3903 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075128 | OH | Sus | 0 | yes | 2014 | DEC | Yes | None | 99195128 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075457&numberofmonths=24&showchangehistorylog=1 | 14-0075457 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 3975 | 20141211 | 720 | 1131282 | 378 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 25471 | 39.2093 | -123.7102 | 4SPANSLDSIDEOF79817 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075457 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99194343 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075495&numberofmonths=24&showchangehistorylog=1 | 14-0075495 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 5533 | 20141211 | 548 | 1129593 | 837 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 17718 | 39.1895 | -123.7553 | 1FROM1600CAMERON | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075495 | OH | Sus | 0 | yes | 2014 | DEC | Yes |  | 99194829 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075929&numberofmonths=24&showchangehistorylog=1 | 14-0075929 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 1905 | 20141211 | 258 | 1128914 | 1687 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 38801 | 39.2278 | -123.7411 | SPANPASTFUCO | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075929 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194237 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075986&numberofmonths=24&showchangehistorylog=1 | 14-0075986 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 3273 | 20141211 | 1023 | 1132834 | 1981 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 13867 | 39.1938 | -123.7233 | MTR5000125810 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075986 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194218 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076256&numberofmonths=24&showchangehistorylog=1 | 14-0076256 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 5233 | 20141211 | 231 | 1131630 | 2374 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 78174 | 39.2282 | -123.7661 | 1STHARDTAPPASTFUSES | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076256 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99194059 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075001&numberofmonths=24&showchangehistorylog=1 | 14-0075001 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | RECLOSER | 4622 | 20141211 | 428 | 1129538 | 842 | Distribution Circuit | Vegetation | Tree - fell into line | 371 | 312382 | 39.5149 | -123.764 | 27100NHIGHWAY1 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075001 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99195218 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075970&numberofmonths=24&showchangehistorylog=1 | 14-0075970 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 5985 | 20141211 | 2143 | 1136223 | 786 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 11004 | 39.5621 | -123.7652 | 1SPANPASTFUCO | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075970 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194224 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075975&numberofmonths=24&showchangehistorylog=1 | 14-0075975 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 1497 | 20141211 | 440 | 1129126 | 2055 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 28770 | 39.4878 | -123.7764 | 6SPANSPASTFUCO | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075975 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194222 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076152&numberofmonths=24&showchangehistorylog=1 | 14-0076152 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 979 | 20141211 | 1917 | 1135604 | 1324 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 9326 | 39.6552 | -123.7627 | 9PASTFUSES | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076152 | OH | Sus | 0 | yes | 2014 | DEC | Yes |  | 99194146 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0074900&numberofmonths=24&showchangehistorylog=1 | 14-0074900 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3341 | 20141211 | 309 | 1129115 | 931 | Distribution Circuit | Vegetation | Tree - fell into line | 142 | 31288 | 39.3942 | -123.773 | 30171SIMPSONLN | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074900 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99195284 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075156&numberofmonths=24&showchangehistorylog=1 | 14-0075156 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | RECLOSER | 31304 | 20141211 | 426 | 1129098 | 497 | Distribution Circuit | Vegetation | Tree - fell into line | 131 | 59908 | 39.4147 | -123.7702 | 17PASTLR | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075156 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99195104 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075253&numberofmonths=24&showchangehistorylog=1 | 14-0075253 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3941 | 20141211 | 653 | 1130303 | 1072 | Distribution Circuit | Vegetation | Tree - fell into line | 76 | 37692 | 39.3943 | -123.7712 | 16600FRANKLINRD | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075253 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99195023 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075271&numberofmonths=24&showchangehistorylog=1 | 14-0075271 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3099 | 20141211 | 425 | 1129072 | 670 | Distribution Circuit | Vegetation | Tree - fell into line | 86 | 38639 | 39.4211 | -123.7804 | 31470CAMILLELN | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075271 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99195010 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075281&numberofmonths=24&showchangehistorylog=1 | 14-0075281 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 8573 | 20141211 | 514 | 1129329 | 841 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 9251 | 39.4207 | -123.7778 | 19293BENSONLN | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075281 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99195000 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075351&numberofmonths=24&showchangehistorylog=1 | 14-0075351 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 94575 | 20141211 | 653 | 1133065 | 868 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 10416 | 39.3865 | -123.7711 | 30270ROBINRD | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075351 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194938 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075356&numberofmonths=24&showchangehistorylog=1 | 14-0075356 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | OTHER |  | 20141211 | 653 | 1133090 | 643 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 643 | 39.3897 | -123.7707 | 16701FRANKLINRD | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 14-0075356 | OH | Sus | 0 | yes | 2014 | DEC | Yes | None | 99194934 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075418&numberofmonths=24&showchangehistorylog=1 | 14-0075418 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | OTHER |  | 20141211 | 653 | 1133407 | 475 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 5225 | 39.3885 | -123.7712 | SEVERALSPANSPASTOJS | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075418 | OH | Sus | 0 | yes | 2014 | DEC | Yes | None | 99194885 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075899&numberofmonths=24&showchangehistorylog=1 | 14-0075899 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3979 | 20141211 | 656 | 1130203 | 1111 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 14443 | 39.3927 | -123.7609 | 4SPANSLOADSIDEFUCO | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075899 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99194567 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076054&numberofmonths=24&showchangehistorylog=1 | 14-0076054 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 8505 | 20141211 | 2041 | 1135977 | 797 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 10361 | 39.378 | -123.7983 | 3SPANSLOADSIDEOF8505 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076054 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99194194 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076237&numberofmonths=24&showchangehistorylog=1 | 14-0076237 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3969 | 20141211 | 1811 | 1135291 | 1162 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 66234 | 39.3819 | -123.7744 | 15183MITCHELCRKRD | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076237 | OH | Sus | 0 | yes | 2014 | DEC | Yes | None | 99194071 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075020&numberofmonths=24&showchangehistorylog=1 | 14-0075020 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 411 | 20141211 | 433 | 1129100 | 512 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 7168 | 39.447 | -123.7526 | 2PASTFUSES | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075020 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Three Phase Fault | 99195203 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075311&numberofmonths=24&showchangehistorylog=1 | 14-0075311 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 3295 | 20141211 | 637 | 1129998 | 752 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 9024 | 39.4427 | -123.7706 | SUTTONJASON1spanloadside3295 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075311 | OH | Sus | 0 | yes | 2014 | DEC | Yes |  | 99194974 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0074908&numberofmonths=24&showchangehistorylog=1 | 14-0074908 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT SEWARD-1121 | 192321121 | RECLOSER | 1690 | 20141211 | 510 | 1129409 | 2410 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 52229 | 40.1679 | -123.6112 | 115432129299 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074908 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Three Phase Fault | 99194398 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0074878&numberofmonths=24&showchangehistorylog=1 | 14-0074878 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | RECLOSER | 6054 | 20141211 | 441 | 1129160 | 1389 | Distribution Circuit | Vegetation | Tree - fell into line | 593 | 704376 | 40.2857 | -123.8373 | 114886033625 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074878 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99195296 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075272&numberofmonths=24&showchangehistorylog=1 | 14-0075272 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 1587 | 20141211 | 535 | 1132583 | 1360 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1360 | 40.2961 | -123.8303 | 114896635697 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075272 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99195009 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0074827&numberofmonths=24&showchangehistorylog=1 | 14-0074827 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 56048 | 20141211 | 305 | 1128850 | 2538 | Distribution Circuit | Vegetation | Tree - fell into line | 118 | 298569 | 40.1476 | -124.0197 | 114331630449 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074827 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99194413 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0074918&numberofmonths=24&showchangehistorylog=1 | 14-0074918 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 8652 | 20141211 | 152 | 1129431 | 2184 | Distribution Circuit | Vegetation | Tree - fell into line | 244 | 432315 | 40.1065 | -123.928 | 114582928220 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074918 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99194395 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075778&numberofmonths=24&showchangehistorylog=1 | 14-0075778 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | OTHER |  | 20141211 | 152 | 1135483 | 2184 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 4368 | 40.0917 | -123.9384 | INTHESPANSSSOF8209 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075778 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194280 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075925&numberofmonths=24&showchangehistorylog=1 | 14-0075925 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 2581 | 20141211 | 1247 | 1133677 | 1511 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 4533 | 40.1198 | -123.8845 | 114728729348 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075925 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99194238 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0074955&numberofmonths=24&showchangehistorylog=1 | 14-0074955 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 561 | 20141211 | 357 | 1128996 | 614 | Distribution Circuit | Vegetation | Tree - fell into line | 106 | 65084 | 38.7885 | -123.5251 | 46125PACIFICWOODSRD | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074955 | OH | Sus | 0 | yes | 2014 | DEC | Yes |  | 99195253 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075092&numberofmonths=24&showchangehistorylog=1 | 14-0075092 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 6693 | 20141211 | 346 | 1128973 | 556 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1112 | 38.6459 | -123.397 | SOFMTR47K320 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075092 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Three Phase Fault | 99195151 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075570&numberofmonths=24&showchangehistorylog=1 | 14-0075570 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 561 | 20141211 | 1420 | 1134356 | 22 | Distribution Circuit | Vegetation | Tree - branch fell on line | 106 | 2332 | 38.7885 | -123.5251 | 45400PACIFICWOODSRD | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075570 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Three Phase Fault | 99194772 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075244&numberofmonths=24&showchangehistorylog=1 | 14-0075244 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1112 | 42841112 | FUSE | 8167 | 20141211 | 743 | 1131034 | 475 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 5225 | 38.845 | -123.5743 | 1SS2321 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075244 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99195028 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075644&numberofmonths=24&showchangehistorylog=1 | 14-0075644 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1112 | 42841112 | FUSE | 7325 | 20141211 | 1028 | 1132876 | 1792 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3584 | 38.8052 | -123.5865 | SEVERALSPANSPASTFUSES | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075644 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99194311 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0074888&numberofmonths=24&showchangehistorylog=1 | 14-0074888 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | KONOCTI-1102 | 43311102 | FUSE | 4205 | 20141211 | 402 | 1129049 | 458 | Distribution Circuit | Vegetation | Tree - fell into line | 286 | 130988 | 38.8369 | -122.7261 | CORNEROFSHASTAANDTRINITYRD | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074888 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Three Phase Fault | 99195291 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075320&numberofmonths=24&showchangehistorylog=1 | 14-0075320 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | KONOCTI-1102 | 43311102 | FUSE | 4213 | 20141211 | 702 | 1130255 | 458 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 10076 | 38.8305 | -122.7267 | 5PASTFUSES | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075320 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99194966 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075191&numberofmonths=24&showchangehistorylog=1 | 14-0075191 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE | 2749 | 20141211 | 708 | 1130322 | 398 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 8756 | 39.6732 | -123.5062 | 1951NORRISRD | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075191 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99195071 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0074812&numberofmonths=24&showchangehistorylog=1 | 14-0074812 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | RIO DELL-1102 | 192251102 | RECLOSER | 4230 | 20141211 | 217 | 1128884 | 3701 | Distribution Circuit | Equipment Failure/Involved | Other | 25 | 86504 | 40.4175 | -124.0895 | 114076534149 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0074812 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99193589 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075651&numberofmonths=24&showchangehistorylog=1 | 14-0075651 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | UKIAH-1114 | 42771114 | FUSE | 3371 | 20141211 | 1430 | 1134793 | 1250 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 7500 | 39.0897 | -123.1624 | GALLETTITIMTREETHROUGHLINEONHARDTAP4POLESLSOF3371 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075651 | OH | Sus | 0 | yes | 2014 | DEC | Yes |  | 99194309 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076378&numberofmonths=24&showchangehistorylog=1 | 14-0076378 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | SWITCH | 3053 | 20141212 | 1000 | 1137967 | 1595 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 17545 | 39.2759 | -123.687 | 3PASTSBCO | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076378 | OH | Sus | 0 | yes | 2014 | DEC | Yes | None | 99193474 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076302&numberofmonths=24&showchangehistorylog=1 | 14-0076302 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3911 | 20141212 | 1045 | 1138029 | 366 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 1830 | 39.3598 | -123.656 | 14AND14SPANSPASTFUSES | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076302 | OH | Sus | 0 | yes | 2014 | DEC | Yes |  | 99194023 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076297&numberofmonths=24&showchangehistorylog=1 | 14-0076297 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 1815 | 20141212 | 612 | 1137161 | 986 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 28594 | 39.868 | -123.717 | 115173019920 | Fog-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0076297 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99194024 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076558&numberofmonths=24&showchangehistorylog=1 | 14-0076558 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 1799 | 20141212 | 816 | 1138674 | 981 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 4905 | 40.0468 | -123.9617 | 151SIMPSONLN | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076558 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99193841 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0074827&numberofmonths=24&showchangehistorylog=1 | 14-0074827 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 37054 | 20141212 | 2150 | 1139284 | 29 | Distribution Circuit | Equipment Failure/Involved | Other | 102 | 2958 | 40.1642 | -124.0812 | MTR1009229768 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074827 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99193822 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0074827&numberofmonths=24&showchangehistorylog=1 | 14-0074827 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | OTHER |  | 20141212 | 2123 | 1139299 | 118 | Distribution Circuit | Equipment Failure/Involved | Other | 1 | 118 | 40.2218 | -124.1156 | 114094733070 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074827 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99193820 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0078927&numberofmonths=24&showchangehistorylog=1 | 14-0078927 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 68415 | 20141230 | 846 | 1150568 | 339 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 339 | 40.2607 | -123.8299 | 114895034328 | Fog-32 - 90 F | Cutout, fuse holder | Broken, wire on ground | 14-0078927 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99190736 | CFH | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0009900&numberofmonths=24&showchangehistorylog=1 | 15-0009900 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE | 4583 | 20150206 | 335 | 1173712 | 850 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 11900 | 38.7195 | -123.3701 | 6SPANSLOADSIDEOF4583 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0009900 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99185283 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0009896&numberofmonths=24&showchangehistorylog=1 | 15-0009896 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 1265 | 20150206 | 830 | 1173680 | 3243 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 3243 | 39.2703 | -123.778 | 1SPANLOADSIDEOF1265 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0009896 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99183961 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010339&numberofmonths=24&showchangehistorylog=1 | 15-0010339 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 3281 | 20150206 | 1353 | 1176004 | 1412 | Distribution Circuit | Vegetation | Tree - fell into line | 83 | 30158 | 39.3129 | -123.7848 | WILDWOODGURLEYLN | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010339 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99184631 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010416&numberofmonths=24&showchangehistorylog=1 | 15-0010416 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 2431 | 20150206 | 937 | 1176443 | 1941 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 67935 | 39.3448 | -123.7791 | LDSIDEOF2431 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010416 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99184619 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010417&numberofmonths=24&showchangehistorylog=1 | 15-0010417 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 5065 | 20150206 | 937 | 1176460 | 1698 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 91692 | 39.3645 | -123.7973 | LDSIDEOF5065 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010417 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99184618 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010434&numberofmonths=24&showchangehistorylog=1 | 15-0010434 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 3033 | 20150206 | 952 | 1173969 | 1640 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 23272 | 39.2856 | -123.7893 | 9485HARDTAP | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010434 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183949 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010956&numberofmonths=24&showchangehistorylog=1 | 15-0010956 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 3151 | 20150206 | 937 | 1180028 | 2260 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 33900 | 39.3417 | -123.8114 | LDSIDEOFFU3151 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010956 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99184486 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011064&numberofmonths=24&showchangehistorylog=1 | 15-0011064 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 6543 | 20150206 | 2050 | 1180637 | 1000 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 3000 | 39.3125 | -123.7855 | 1SPANLDSIDEOF6543 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 15-0011064 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183898 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011350&numberofmonths=24&showchangehistorylog=1 | 15-0011350 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 3967 | 20150206 | 1719 | 1178233 | 2506 | Distribution Circuit | Equipment Failure/Involved | Other | 65 | 162890 | 39.2864 | -123.7529 | 40751COMPTCHERD | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011350 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182852 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010380&numberofmonths=24&showchangehistorylog=1 | 15-0010380 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 87163 | 20150206 | 1141 | 1174550 | 1666 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 36652 | 39.2257 | -123.7477 | 1SPANLOADSIDE3901 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010380 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99184626 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010536&numberofmonths=24&showchangehistorylog=1 | 15-0010536 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 5533 | 20150206 | 924 | 1173906 | 1896 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 54984 | 39.1895 | -123.7553 | 3SPANSLOADSIDEOF5533 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010536 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99184597 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010596&numberofmonths=24&showchangehistorylog=1 | 15-0010596 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | RECLOSER | 1298 | 20150206 | 1921 | 1179285 | 1539 | Distribution Circuit | Vegetation | Tree - fell into line | 501 | 642067 | 39.1426 | -123.7286 | Stone3466multiplelocations1SPANSSIDEOFR8315 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010596 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183402 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010883&numberofmonths=24&showchangehistorylog=1 | 15-0010883 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 3921 | 20150206 | 1921 | 1179792 | 1614 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 111366 | 39.2062 | -123.7072 | LDSIDEOF3921 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010883 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99184515 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011147&numberofmonths=24&showchangehistorylog=1 | 15-0011147 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 5233 | 20150206 | 1921 | 1180961 | 2464 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 101024 | 39.2282 | -123.7661 | 5301ALBIANLITTLERIVERRD | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011147 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183888 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011181&numberofmonths=24&showchangehistorylog=1 | 15-0011181 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 94127 | 20150206 | 1921 | 1181087 | 2430 | Distribution Circuit | Equipment Failure/Involved | Other | 5 | 12150 | 39.2272 | -123.742 | 3320ALBIONRIDGERD | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011181 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183881 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011215&numberofmonths=24&showchangehistorylog=1 | 15-0011215 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 1319 | 20150206 | 1921 | 1181210 | 5571 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 16713 | 39.2176 | -123.6794 | 1LDSIDEOF1319 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 15-0011215 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182854 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011272&numberofmonths=24&showchangehistorylog=1 | 15-0011272 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 3919 | 20150206 | 1921 | 1181383 | 2859 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 71475 | 39.2153 | -123.7297 | 31515ALBEANRIDGERD | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011272 | OH | Sus | 0 | yes | 2015 | FEB | Yes | None | 99183371 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0009853&numberofmonths=24&showchangehistorylog=1 | 15-0009853 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | RECLOSER | 31304 | 20150206 | 604 | 1173268 | 2403 | Distribution Circuit | Vegetation | Tree - branch fell on line | 131 | 171322 | 39.4147 | -123.7702 | 29200HWY20 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0009853 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183430 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010016&numberofmonths=24&showchangehistorylog=1 | 15-0010016 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | RECLOSER | 816 | 20150206 | 935 | 1173905 | 279 | Distribution Circuit | Vegetation | Tree - fell into line | 72 | 15419 | 39.4118 | -123.7982 | 4SPANSFROM1687TWDS6079 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010016 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182892 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010526&numberofmonths=24&showchangehistorylog=1 | 15-0010526 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 1603 | 20150206 | 1656 | 1176920 | 1289 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 79918 | 39.3904 | -123.8004 | 16296GIBNEYLN | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010526 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99184599 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010612&numberofmonths=24&showchangehistorylog=1 | 15-0010612 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 6081 | 20150206 | 1241 | 1177383 | 1633 | Distribution Circuit | Vegetation | Tree - fell into line | 469 | 758707 | 39.3922 | -123.7991 | betweensws5229578730570TURNERRD | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010612 | OH | Sus | 0 | yes | 2015 | FEB | Yes | None | 99182880 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011375&numberofmonths=24&showchangehistorylog=1 | 15-0011375 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3969 | 20150206 | 1241 | 1181873 | 2025 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 115425 | 39.3819 | -123.7744 | 12SPLS3969 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011375 | OH | Sus | 0 | yes | 2015 | FEB | Yes | None | 99182851 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010605&numberofmonths=24&showchangehistorylog=1 | 15-0010605 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 1987 | 20150206 | 1838 | 1177568 | 2449 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 17143 | 39.4447 | -123.7886 | 20750RASSMUSENLN | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010605 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183941 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010206&numberofmonths=24&showchangehistorylog=1 | 15-0010206 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1141 | 192311141 | OCB | OCB | 20150206 | 1006 | 1174140 | 582 | Distribution Circuit | Vegetation | Tree - fell into line | 370 | 158397 | 40.2863 | -123.8376 | 114708436541 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010206 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99185108 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010792&numberofmonths=24&showchangehistorylog=1 | 15-0010792 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | RECLOSER | 1770 | 20150206 | 2240 | 1179355 | 760 | Distribution Circuit | Vegetation | Tree - fell into line | 389 | 295877 | 39.9155 | -123.7638 | 115076421444 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010792 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183400 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010794&numberofmonths=24&showchangehistorylog=1 | 15-0010794 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | RECLOSER | 1750 | 20150206 | 2252 | 1179359 | 952 | Distribution Circuit | Vegetation | Tree - fell into line | 117 | 111384 | 40.0848 | -123.8079 | SSMTR1008672254 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 15-0010794 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183399 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011224&numberofmonths=24&showchangehistorylog=1 | 15-0011224 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 1717 | 20150206 | 2240 | 1181233 | 2809 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 53371 | 39.8492 | -123.7058 | 115212119127 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0011224 | OH | Sus | 0 | yes | 2015 | FEB | Yes | None | 99183872 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010098&numberofmonths=24&showchangehistorylog=1 | 15-0010098 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 8652 | 20150206 | 1211 | 1174721 | 4996 | Distribution Circuit | Equipment Failure/Involved | Other | 181 | 0 | 40.1065 | -123.928 | FLECKLINPAUL623530906314216565BRICELANDTHORNRD | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010098 | OH | Sus | 0 | yes | 2015 | FEB | Yes |  | 99182890 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011045&numberofmonths=24&showchangehistorylog=1 | 15-0011045 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 3759 | 20150206 | 2302 | 1180532 | 3858 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 46730 | 40.1082 | -123.7952 | 324ALDERPOINTRD | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0011045 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183388 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011404&numberofmonths=24&showchangehistorylog=1 | 15-0011404 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 2505 | 20150206 | 127 | 1181957 | 5359 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 182206 | 40.307 | -124.2967 | 113587335996 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011404 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182849 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0009837&numberofmonths=24&showchangehistorylog=1 | 15-0009837 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 3433 | 20150206 | 522 | 1173199 | 3233 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 85190 | 38.8103 | -123.5412 | 36200OLDSTAGERD | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0009837 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183963 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010247&numberofmonths=24&showchangehistorylog=1 | 15-0010247 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | RECLOSER | 445166 | 20150206 | 806 | 1173546 | 1644 | Distribution Circuit | Vegetation | Tree - fell into line | 261 | 425914 | 38.6936 | -123.4237 | JONESMICHAEL | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 15-0010247 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Three Phase Fault | 99182887 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010399&numberofmonths=24&showchangehistorylog=1 | 15-0010399 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 561 | 20150206 | 654 | 1173411 | 1593 | Distribution Circuit | Vegetation | Tree - fell into line | 106 | 128380 | 38.7885 | -123.5251 | 1SPANPASTFUCO | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010399 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183415 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011195&numberofmonths=24&showchangehistorylog=1 | 15-0011195 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 4451 | 20150206 | 837 | 1181135 | 4703 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 27681 | 38.7905 | -123.5103 | 44500GUALALARD | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011195 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99182855 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0009808&numberofmonths=24&showchangehistorylog=1 | 15-0009808 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1112 | 42841112 | FUSE | 4437 | 20150206 | 3 | 1173196 | 2367 | Distribution Circuit | Vegetation | Tree - branch fell on line | 23 | 54441 | 38.825 | -123.5765 | 4SPANSLOADSIDE6061 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0009808 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99184665 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010933&numberofmonths=24&showchangehistorylog=1 | 15-0010933 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1112 | 42841112 | FUSE | 4429 | 20150206 | 613 | 1173310 | 2204 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 37468 | 38.8136 | -123.5776 | IRO44780TANBARKRD | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010933 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99184497 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011027&numberofmonths=24&showchangehistorylog=1 | 15-0011027 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1112 | 42841112 | FUSE | 6487 | 20150206 | 702 | 1173418 | 3391 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 9437 | 38.8358 | -123.5674 | OJS5SPANSLOADSIDEOF6487 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011027 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99183900 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010829&numberofmonths=24&showchangehistorylog=1 | 15-0010829 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | HARTLEY-1101 | 43211101 | FUSE | 58095 | 20150206 | 2206 | 1179022 | 4129 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 12792 | 39.0403 | -122.9364 | 1573MARTINSTLAKEPORT | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010829 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99183398 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010876&numberofmonths=24&showchangehistorylog=1 | 15-0010876 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE | 2577 | 20150206 | 2327 | 1179466 | 1277 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 58742 | 39.6879 | -123.4953 | 1050BAUERRD | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010876 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99184520 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011282&numberofmonths=24&showchangehistorylog=1 | 15-0011282 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE | 5259 | 20150206 | 2303 | 1179382 | 1437 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 27303 | 39.6515 | -123.4845 | LDSIDEOF5259 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011282 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183858 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0009903&numberofmonths=24&showchangehistorylog=1 | 15-0009903 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LUCERNE-1106 | 43351106 | RECLOSER | 38632 | 20150206 | 808 | 1173540 | 312 | Distribution Circuit | Vegetation | Tree - fell into line | 257 | 24814 | 38.9912 | -122.7479 | 2SPANSLOADSIDEOFMTR1008034843 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0009903 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182897 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0009878&numberofmonths=24&showchangehistorylog=1 | 15-0009878 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | OTHER |  | 20150206 | 803 | 1173629 | 547 | Distribution Circuit | Vegetation | Tree - fell into line | 216 | 112716 | 38.9144 | -123.6616 | 9SPANSLOADSIDE474 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0009878 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99185300 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010193&numberofmonths=24&showchangehistorylog=1 | 15-0010193 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE | 2653 | 20150206 | 648 | 1173398 | 1861 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 14888 | 38.931 | -123.6917 | 4SPANSLOADSIDEOF2653 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010193 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99184639 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010860&numberofmonths=24&showchangehistorylog=1 | 15-0010860 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE | 8989 | 20150206 | 1900 | 1178783 | 2580 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 15480 | 38.8861 | -123.6366 | 2SPANSSSFROMEOL | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010860 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99183915 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011364&numberofmonths=24&showchangehistorylog=1 | 15-0011364 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE | 1363 | 20150206 | 1819 | 1178748 | 1536 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 87552 | 38.9158 | -123.6385 | 1SPFROM980999TWD6799 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011364 | OH | Sus | 0 | yes | 2015 | FEB | Yes | None | 99184249 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0009940&numberofmonths=24&showchangehistorylog=1 | 15-0009940 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | RIO DELL-1102 | 192251102 | RECLOSER | 4230 | 20150206 | 938 | 1173932 | 4799 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 119975 | 40.4175 | -124.0895 | 114237638714 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0009940 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99182895 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0009869&numberofmonths=24&showchangehistorylog=1 | 15-0009869 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER | 37506 | 20150206 | 623 | 1173389 | 436 | Distribution Circuit | Vegetation | Tree - fell into line | 90 | 34148 | 39.4832 | -123.3603 | GALLETTITIMTREETHROUGHLINE30000NHWY101 | Strong winds-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 15-0009869 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99185307 | CAW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010215&numberofmonths=24&showchangehistorylog=1 | 15-0010215 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | FUSE | 3811 | 20150206 | 910 | 1173752 | 560 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 10640 | 39.4947 | -123.2099 | 2SPANSPASTFUCO | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010215 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99185102 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010995&numberofmonths=24&showchangehistorylog=1 | 15-0010995 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1103 | 42661103 | FUSE | 2813 | 20150206 | 2332 | 1180166 | 868 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 51212 | 39.4542 | -123.3779 | 4PASTFUSES | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010995 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99184466 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0009819&numberofmonths=24&showchangehistorylog=1 | 15-0009819 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1104 | 42661104 | FUSE | 8467 | 20150206 | 511 | 1173191 | 596 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 17284 | 39.3474 | -123.3376 | 5SPANSLOADSIDEOF8467 | Strong winds-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 15-0009819 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99185331 | CAW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010821&numberofmonths=24&showchangehistorylog=1 | 15-0010821 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1104 | 42661104 | FUSE | 3769 | 20150206 | 2217 | 1179196 | 1033 | Distribution Circuit | Vegetation | Tree - fell into line | 111 | 114663 | 39.4348 | -123.3795 | 24949COBBDRWILLITS | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010821 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182873 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010597&numberofmonths=24&showchangehistorylog=1 | 15-0010597 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE | 2981 | 20150206 | 1540 | 1176256 | 4235 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 8470 | 40.7875 | -123.4255 | 116060553274 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010597 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183410 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011311&numberofmonths=24&showchangehistorylog=1 | 15-0011311 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE | 6073 | 20150207 | 1629 | 1181535 | 2026 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 12156 | 38.6577 | -123.2886 | 10SPANSFROM4611TWD3731 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011311 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99183366 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011231&numberofmonths=24&showchangehistorylog=1 | 15-0011231 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 4987 | 20150207 | 731 | 1180319 | 721 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 7210 | 39.4985 | -123.7763 | 5PASTFUSES | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0011231 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Multi-Fault | 99184321 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011263&numberofmonths=24&showchangehistorylog=1 | 15-0011263 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 3173 | 20150207 | 1451 | 1181372 | 1629 | Distribution Circuit | Equipment Failure/Involved | Other | 2 | 3258 | 39.6337 | -123.7826 | 3SPANSLOADSIDE | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011263 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183862 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011491&numberofmonths=24&showchangehistorylog=1 | 15-0011491 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 5985 | 20150207 | 1030 | 1180918 | 1530 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 21420 | 39.5621 | -123.7652 | 2SPANSPASTFUSES | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011491 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99183779 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011512&numberofmonths=24&showchangehistorylog=1 | 15-0011512 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 1767 | 20150207 | 1126 | 1181031 | 1724 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 13792 | 39.6705 | -123.7785 | 11SPANLDSIDEOF1767 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011512 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183760 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011041&numberofmonths=24&showchangehistorylog=1 | 15-0011041 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | OTHER |  | 20150207 | 123 | 1180149 | 874 | Distribution Circuit | Vegetation | Tree - fell into line | 186 | 149914 | 40.2954 | -123.8327 | 114898035608 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011041 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183389 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011153&numberofmonths=24&showchangehistorylog=1 | 15-0011153 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 8279 | 20150207 | 721 | 1180710 | 3224 | Distribution Circuit | Vegetation | Tree - branch fell on line | 18 | 58032 | 40.089 | -123.8094 | 1880SPROWLCREEKRD | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011153 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183378 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010794&numberofmonths=24&showchangehistorylog=1 | 15-0010794 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | SWITCH | 1869 | 20150207 | 1512 | 1181387 | 3375 | Distribution Circuit | Equipment Failure/Involved | Other | 16 | 54000 | 40.018 | -123.9312 | FOUNDHOTWIREONGRDSSOFMTR1008672254 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010794 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Open Circuit | 99183365 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011336&numberofmonths=24&showchangehistorylog=1 | 15-0011336 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 1771 | 20150207 | 1539 | 1181508 | 1873 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 14984 | 40.0717 | -123.8299 | ONTAP1SPANWOSPROWLCREEKRD | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 15-0011336 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183845 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011333&numberofmonths=24&showchangehistorylog=1 | 15-0011333 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 8207 | 20150207 | 1501 | 1181648 | 3089 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 27801 | 39.9943 | -123.9263 | BRICELANDRD9PSOFCOUNTYLINE | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 15-0011333 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99183364 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011167&numberofmonths=24&showchangehistorylog=1 | 15-0011167 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | KONOCTI-1102 | 43311102 | FUSE | 431 | 20150207 | 907 | 1180682 | 4798 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 43182 | 38.9216 | -122.7138 | 2SPANSLOADSIDEOF431 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011167 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99182857 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011102&numberofmonths=24&showchangehistorylog=1 | 15-0011102 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LOW GAP-1101 | 192411101 | OCB | OCB | 20150207 | 200 | 1180393 | 1122 | Distribution Circuit | Vegetation | Tree - fell into line | 739 | 679197 | 40.4333 | -123.4727 | 115878940209 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011102 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Three Phase Fault | 99183384 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011390&numberofmonths=24&showchangehistorylog=1 | 15-0011390 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LOW GAP-1101 | 192411101 | OTHER |  | 20150207 | 1838 | 1181885 | 2809 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 7691 | 40.4581 | -123.6517 | 2SPANSFROM4127TWD7869 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011390 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183358 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0012327&numberofmonths=24&showchangehistorylog=1 | 15-0012327 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1101 | 42601101 | RECLOSER | 37222 | 20150207 | 901 | 1187254 | 4900 | Distribution Circuit | Vegetation | Tree - fell into line | 146 | 715400 | 38.914 | -123.2725 | 2SPANSLOADSIDE | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012327 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182737 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011100&numberofmonths=24&showchangehistorylog=1 | 15-0011100 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1102 | 42601102 | RECLOSER | 1308 | 20150207 | 158 | 1179796 | 3591 | Distribution Circuit | Vegetation | Tree - fell into line | 292 | 444437 | 39.1869 | -123.5808 | MTR23161R | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011100 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99182858 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011075&numberofmonths=24&showchangehistorylog=1 | 15-0011075 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | RIO DELL-1102 | 192251102 | FUSE | 3909 | 20150207 | 221 | 1180697 | 3764 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 11292 | 40.404 | -123.9522 | 114559639573 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011075 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183385 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011699&numberofmonths=24&showchangehistorylog=1 | 15-0011699 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | UKIAH-1114 | 42771114 | FUSE | 1711 | 20150207 | 2056 | 1180643 | 2399 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 9596 | 39.1146 | -123.1175 | 2SPANSLDSIDEOF1711 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011699 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183330 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010931&numberofmonths=24&showchangehistorylog=1 | 15-0010931 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1101 | 192171101 | FUSE | 3021 | 20150207 | 343 | 1179969 | 662 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 25818 | 40.9628 | -123.8377 | 114881161144 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010931 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Three Phase Fault | 99184499 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011377&numberofmonths=24&showchangehistorylog=1 | 15-0011377 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE | 3079 | 20150207 | 1356 | 1181284 | 2764 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 96740 | 40.7987 | -123.4049 | 116259253742 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011377 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99183359 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0012201&numberofmonths=24&showchangehistorylog=1 | 15-0012201 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE | 8483 | 20150208 | 2042 | 1185254 | 2568 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 43059 | 38.7335 | -123.374 | CRAMERCHRISCutouts352975notmappedTwds42555BrushyRidgeLoop | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012201 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182772 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011615&numberofmonths=24&showchangehistorylog=1 | 15-0011615 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ARCATA-1122 | 192021122 | FUSE | 6785 | 20150208 | 1452 | 1182767 | 91 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 637 | 40.7976 | -124.0497 | 134HISLANEGREENWOODHEIGHTS | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 15-0011615 | OH | Sus | 0 | yes | 2015 | FEB | Yes | None | 99183683 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011715&numberofmonths=24&showchangehistorylog=1 | 15-0011715 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 7339 | 20150208 | 1552 | 1183171 | 155 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 6975 | 39.3176 | -123.7863 | LAWRDQURLEYLN | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011715 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183617 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011805&numberofmonths=24&showchangehistorylog=1 | 15-0011805 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | RECLOSER | 79628 | 20150208 | 1927 | 1183900 | 2094 | Distribution Circuit | Vegetation | Tree - fell into line | 365 | 764310 | 39.3123 | -123.7861 | SEVERALLOCATIONS | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011805 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182820 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011533&numberofmonths=24&showchangehistorylog=1 | 15-0011533 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 5061 | 20150208 | 811 | 1182137 | 484 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 9196 | 39.4994 | -123.7742 | SUTTONJASON32500namelesslane | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011533 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183742 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011466&numberofmonths=24&showchangehistorylog=1 | 15-0011466 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3069 | 20150208 | 809 | 1182153 | 294 | Distribution Circuit | Vegetation | Tree - fell into line | 172 | 50568 | 39.4157 | -123.7782 | 4POLESPASTFUSES | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011466 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Three Phase Fault | 99183797 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011508&numberofmonths=24&showchangehistorylog=1 | 15-0011508 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3969 | 20150208 | 807 | 1182144 | 498 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 19966 | 39.3819 | -123.7744 | 15007MITCHELLCREEKRD | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011508 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183763 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011649&numberofmonths=24&showchangehistorylog=1 | 15-0011649 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 1607 | 20150208 | 739 | 1182795 | 646 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2584 | 39.442 | -123.7731 | 30940SHERWOODRD | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011649 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183660 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011463&numberofmonths=24&showchangehistorylog=1 | 15-0011463 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT SEWARD-1121 | 192321121 | RECLOSER | 1602 | 20150208 | 839 | 1182183 | 3295 | Distribution Circuit | Equipment Failure/Involved | Other | 87 | 259017 | 40.1833 | -123.5761 | RIGBYSTEVENLAKEMOUNTAINRD | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011463 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182844 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0012266&numberofmonths=24&showchangehistorylog=1 | 15-0012266 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT SEWARD-1122 | 192321122 | FUSE | 1651 | 20150208 | 1433 | 1185122 | 2867 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 17202 | 40.2374 | -123.604 | 2MILESPAST1651 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012266 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182761 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011579&numberofmonths=24&showchangehistorylog=1 | 15-0011579 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 2571 | 20150208 | 912 | 1182208 | 1938 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 19380 | 40.136 | -123.9842 | CROOKEDPRAIRIERD | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0011579 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99183345 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011878&numberofmonths=24&showchangehistorylog=1 | 15-0011878 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | SWITCH | 6084 | 20150208 | 2356 | 1185303 | 1254 | Distribution Circuit | Vegetation | Tree - branch fell on line | 63 | 0 | 40.0619 | -123.9619 | BradleyGERALDINE13295BRICELANDTHORNRD | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011878 | OH | Sus | 0 | yes | 2015 | FEB | Yes |  | 99182810 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011784&numberofmonths=24&showchangehistorylog=1 | 15-0011784 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | RECLOSER | 445166 | 20150208 | 1954 | 1183953 | 1256 | Distribution Circuit | Vegetation | Tree - fell into line | 261 | 322458 | 38.6936 | -123.4237 | CRAMERCHRISHwy1southofAnnapolisRd2Spansfrom1367 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011784 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182825 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0012272&numberofmonths=24&showchangehistorylog=1 | 15-0012272 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | HIGHLANDS-1103 | 43361103 | FUSE | 61699 | 20150208 | 2151 | 1185637 | 3929 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 43219 | 38.8474 | -122.557 | 14202SPRUCEGROVERD | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0012272 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99182515 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011469&numberofmonths=24&showchangehistorylog=1 | 15-0011469 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 3247 | 20150208 | 910 | 1181995 | 3248 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 3248 | 41.1046 | -123.6892 | MELLOADAM9SPANSDOWNFRM33373SPANSUPFRM3304WILDMANOFFOFDOWDRDATCONES | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011469 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182843 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011973&numberofmonths=24&showchangehistorylog=1 | 15-0011973 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | KONOCTI-1102 | 43311102 | OTHER |  | 20150208 | 2124 | 1184578 | 1867 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1867 | 38.9189 | -122.8013 | ATFUCO9869 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011973 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183250 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011985&numberofmonths=24&showchangehistorylog=1 | 15-0011985 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1101 | 42681101 | RECLOSER | 402 | 20150208 | 2223 | 1185631 | 3117 | Distribution Circuit | Equipment Failure/Involved | Other | 684 | 688758 | 39.7038 | -123.4874 | HARDTAPMETER100839164021SPANSFROM1723TWD1889 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011985 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182790 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011997&numberofmonths=24&showchangehistorylog=1 | 15-0011997 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE | 2577 | 20150208 | 706 | 1185678 | 2089 | Distribution Circuit | Vegetation | Tree - branch fell on line | 46 | 87734 | 39.6879 | -123.4953 | 2SPANSLDSIDETO2579 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011997 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183238 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0012582&numberofmonths=24&showchangehistorylog=1 | 15-0012582 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE | 3789 | 20150208 | 2153 | 1184870 | 2644 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 15864 | 39.649 | -123.6124 | MUDCRKRD | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012582 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182592 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0012139&numberofmonths=24&showchangehistorylog=1 | 15-0012139 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1102 | 42601102 | FUSE | 3705 | 20150208 | 2129 | 1185839 | 1744 | Distribution Circuit | Vegetation | Tree - branch fell on line | 52 | 90688 | 39.1357 | -123.5113 | 600EO1300SMITHHILLSRDPHILO | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012139 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183153 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011819&numberofmonths=24&showchangehistorylog=1 | 15-0011819 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE | 2637 | 20150208 | 1831 | 1184062 | 1269 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 39339 | 38.9548 | -123.6433 | 40101MOUNTAINVIEWRD | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011819 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183302 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011870&numberofmonths=24&showchangehistorylog=1 | 15-0011870 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1103 | 42661103 | FUSE | 2813 | 20150208 | 2153 | 1185281 | 1330 | Distribution Circuit | Vegetation | Tree - fell into line | 141 | 120152 | 39.4542 | -123.3779 | 2SPANSLDSIDEOF2813 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011870 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182812 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011879&numberofmonths=24&showchangehistorylog=1 | 15-0011879 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1103 | 42661103 | FUSE | 8301 | 20150208 | 8 | 1184756 | 4159 | Distribution Circuit | Vegetation | Tree - fell into line | 118 | 324438 | 39.4882 | -123.4221 | 2SPANSLDSIDEOF9301 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011879 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182809 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011957&numberofmonths=24&showchangehistorylog=1 | 15-0011957 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | FUSE | 2117 | 20150208 | 2132 | 1184681 | 536 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 22512 | 39.4567 | -123.3861 | 7SPANSLOADSIDEAND1POLEEAST | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011957 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183256 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0012336&numberofmonths=24&showchangehistorylog=1 | 15-0012336 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1103 | 42661103 | FUSE | 8049 | 20150208 | 2216 | 1187271 | 1709 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 8545 | 39.5037 | -123.4558 | 3SPANSLDSIDEOF8049 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012336 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183043 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011981&numberofmonths=24&showchangehistorylog=1 | 15-0011981 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1104 | 42661104 | FUSE | 1429 | 20150208 | 2144 | 1185613 | 716 | Distribution Circuit | Vegetation | Tree - fell into line | 116 | 57082 | 39.3581 | -123.332 | 2SPANSSSOFMTR1009770013 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011981 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99183244 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0024650&numberofmonths=24&showchangehistorylog=1 | 15-0024650 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 2540 | 20150406 | 2232 | 1214427 | 790 | Distribution Circuit | Vegetation | Tree - fell into line | 311 | 180026 | 40.2431 | -124.1271 | 114070933929 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0024650 | OH | Sus | 0 | No | 2015 | APR | Yes | Multi-Fault | 99175098 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0039293&numberofmonths=24&showchangehistorylog=1 | 15-0039293 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | UKIAH-1115 | 42771115 | FUSE | 3405 | 20150608 | 1123 | 1245614 | 196 | Distribution Circuit | 3rd Party | Vehicle | 128 | 17408 | 39.1428 | -123.1728 | REGEROBERTINTWATSONANDKNOBHILL | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0039293 | OH | Sus | 42401929 | yes | 2015 | JUN | Yes | Line to Line | 99164944 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0048410&numberofmonths=24&showchangehistorylog=1 | 15-0048410 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | COVELO-1101 | 43061101 | FUSE | 2719 | 20150718 | 1859 | 1270312 | 411 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2466 | 39.7086 | -123.3294 | 5800COVELORD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0048410 | OH | Sus | 0 | yes | 2015 | JUL | Yes | Line to Line | 1145889 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0048394&numberofmonths=24&showchangehistorylog=1 | 15-0048394 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1112 | 42841112 | JUMPER | 2SPANSSS4487 | 20150718 | 1700 | 1270334 | 894 | Distribution Circuit | Vegetation | Tree - fell into line | 250 | 51806 | 38.8377 | -123.6291 | 2SPANSSS4487 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0048394 | OH | Sus | 0 | yes | 2015 | JUL | Yes | Three Phase Fault | 1145885 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0048315&numberofmonths=24&showchangehistorylog=1 | 15-0048315 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | KONOCTI-1102 | 43311102 | FUSE | 4103 | 20150718 | 139 | 1269867 | 531 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 23364 | 38.9475 | -122.6886 | 1SPANPA5T4103 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0048315 | OH | Sus | 31170009 | yes | 2015 | JUL | Yes | Line to Ground | 1145797 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0048331&numberofmonths=24&showchangehistorylog=1 | 15-0048331 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1101 | 42601101 | FUSE | 3737 | 20150718 | 634 | 1269890 | 630 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 3150 | 38.8966 | -123.2026 | ATMTR1009745076 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0048331 | OH | Sus | 31170011 | yes | 2015 | JUL | Yes | Line to Line | 1145819 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0084681&numberofmonths=24&showchangehistorylog=1 | 15-0084681 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE | 4597 | 20151213 | 542 | 1359974 | 1085 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 9765 | 38.729 | -123.3499 | 6SPANSSOURCESIDEOF4599 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084681 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Three Phase Fault | 1174347 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0084657&numberofmonths=24&showchangehistorylog=1 | 15-0084657 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | RECLOSER | 1052 | 20151213 | 716 | 1360154 | 492 | Distribution Circuit | Vegetation | Tree - branch fell on line | 582 | 131494 | 39.3098 | -123.7938 | 3SPANSFROM3031TWD1052 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084657 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Line | 1174323 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0084969&numberofmonths=24&showchangehistorylog=1 | 15-0084969 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | RECLOSER | 79628 | 20151213 | 1312 | 1362196 | 254 | Distribution Circuit | Vegetation | Tree - fell into line | 366 | 76479 | 39.3123 | -123.7861 | 20SPANSLDSIDEOF7383 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084969 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Line | 1174642 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0084977&numberofmonths=24&showchangehistorylog=1 | 15-0084977 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 3967 | 20151213 | 716 | 1362680 | 1036 | Distribution Circuit | Vegetation | Tree - fell into line | 65 | 67340 | 39.2864 | -123.7529 | SPAHSHANNON2eo2927 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084977 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1174650 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0084833&numberofmonths=24&showchangehistorylog=1 | 15-0084833 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BRIDGEVILLE-1102 | 192461102 | FUSE | 3455 | 20151213 | 753 | 1360262 | 568 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 32376 | 40.4953 | -123.9906 | 2spansbeyondFUCO3455 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084833 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1174501 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0084576&numberofmonths=24&showchangehistorylog=1 | 15-0084576 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | EEL RIVER 1101 | 192381101 | FUSE | 1909 | 20151213 | 514 | 1359857 | 536 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 12864 | 40.5118 | -124.1601 | 4SPANSLOADSIDE | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084576 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1174238 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0084853&numberofmonths=24&showchangehistorylog=1 | 15-0084853 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | RECLOSER | 1300 | 20151213 | 1017 | 1361284 | 638 | Distribution Circuit | Vegetation | Tree - fell into line | 424 | 74987 | 39.1287 | -123.7106 | 3SPANSSSOF9763ONMAINLINETWD1300 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084853 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1174520 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0085022&numberofmonths=24&showchangehistorylog=1 | 15-0085022 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 3945 | 20151213 | 1353 | 1362477 | 1467 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 8652 | 39.2895 | -123.7943 | SPAHSHANNON1wometer1008700981 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0085022 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1174696 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0085026&numberofmonths=24&showchangehistorylog=1 | 15-0085026 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | JUMPER | OJ5SPANSLOADSIDEFUCO5187 | 20151213 | 1332 | 1362297 | 793 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 6533 | 39.2856 | -123.7747 | 5spansloadsideofFUCO5187 | Clear-32-90 F | Conductor, Overhead | On Ground | 15-0085026 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1174700 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0085196&numberofmonths=24&showchangehistorylog=1 | 15-0085196 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 3137 | 20151213 | 1331 | 1362244 | 776 | Distribution Circuit | Vegetation | Tree - fell into line | 154 | 119504 | 39.2612 | -123.7296 | 3SPANSLDSIDEOF3045 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0085196 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1174871 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0085197&numberofmonths=24&showchangehistorylog=1 | 15-0085197 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 3975 | 20151213 | 1322 | 1362218 | 763 | Distribution Circuit | Equipment Failure/Involved | Overhead | 69 | 52647 | 39.2093 | -123.7102 | 1SPANPAST31200MIDDLRDGRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0085197 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1174872 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0085210&numberofmonths=24&showchangehistorylog=1 | 15-0085210 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 1905 | 20151213 | 1021 | 1361267 | 1146 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 29796 | 39.2276 | -123.7414 | 3881ABLIONRIDGERD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0085210 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1174886 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0084488&numberofmonths=24&showchangehistorylog=1 | 15-0084488 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 3115 | 20151213 | 435 | 1359783 | 306 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2448 | 39.5054 | -123.7503 | 26200SPRUCELN | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084488 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Line | 1174146 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0084591&numberofmonths=24&showchangehistorylog=1 | 15-0084591 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | SWITCH | 91017 | 20151213 | 600 | 1359981 | 413 | Distribution Circuit | Vegetation | Tree - branch fell on line | 176 | 72688 | 39.6212 | -123.7825 | 1PASIFIC | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084591 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1174254 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0084543&numberofmonths=24&showchangehistorylog=1 | 15-0084543 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 7365 | 20151213 | 713 | 1359994 | 467 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 4203 | 39.4153 | -123.7805 | 4SPANSLOADSIDEOF7365 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084543 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1174202 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0084934&numberofmonths=24&showchangehistorylog=1 | 15-0084934 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | RECLOSER | 816 | 20151213 | 1304 | 1362179 | 416 | Distribution Circuit | Vegetation | Tree - branch fell on line | 439 | 172554 | 39.4119 | -123.7982 | 31900simpsonlnatsw6079 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084934 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1174607 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0084740&numberofmonths=24&showchangehistorylog=1 | 15-0084740 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 3109 | 20151213 | 603 | 1361545 | 858 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 64835 | 39.4628 | -123.7932 | 7SPANSLDSIDEOF3109 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084740 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1174407 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0084910&numberofmonths=24&showchangehistorylog=1 | 15-0084910 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1141 | 192311141 | FUSE | 3931 | 20151213 | 917 | 1362083 | 449 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 7189 | 40.3386 | -123.9132 | BRYANJOSEPH7072981053DYERVILLELOOPRDEOLBOYSCOUTCAMPRDEOL | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084910 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1174578 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0084489&numberofmonths=24&showchangehistorylog=1 | 15-0084489 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | OCB | OCB | 20151213 | 523 | 1359885 | 2202 | Distribution Circuit | Equipment Failure/Involved | Overhead | 682 | 361679 | 40.2865 | -123.8374 | CRINERRUSSELL53068156742403ELKCREEKRD | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084489 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1174147 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0084912&numberofmonths=24&showchangehistorylog=1 | 15-0084912 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 3769 | 20151213 | 1001 | 1361112 | 746 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 6246 | 40.2643 | -123.8276 | Meter1008671689 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084912 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1174582 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0085352&numberofmonths=24&showchangehistorylog=1 | 15-0085352 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | SWITCH | 1687 | 20151213 | 523 | 1363666 | 2279 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 22790 | 40.3085 | -123.8176 | ONMAINLINE4SPSOURCESIDEOFMTR1008798417 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0085352 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1175032 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0084515&numberofmonths=24&showchangehistorylog=1 | 15-0084515 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | RECLOSER | 1514 | 20151213 | 640 | 1360038 | 579 | Distribution Circuit | Vegetation | Tree - fell into line | 220 | 123430 | 40.0478 | -123.79 | ONMAINLINE1SPANFROM1891TWD7201 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084515 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1174174 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0084908&numberofmonths=24&showchangehistorylog=1 | 15-0084908 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | RECLOSER | 1770 | 20151213 | 532 | 1362412 | 1348 | Distribution Circuit | Vegetation | Tree - fell into line | 332 | 229513 | 39.9155 | -123.7638 | HWY101BETSB624583FLYINGBELLSONMAINLINE1SP5659 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084908 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1174576 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0084503&numberofmonths=24&showchangehistorylog=1 | 15-0084503 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 56048 | 20151213 | 450 | 1359909 | 676 | Distribution Circuit | Vegetation | Tree - fell into line | 332 | 160358 | 40.1476 | -124.0197 | MTR1007717585 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084503 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1174160 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0084816&numberofmonths=24&showchangehistorylog=1 | 15-0084816 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 2505 | 20151213 | 450 | 1362029 | 970 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 33950 | 40.307 | -124.2967 | 9spansloadsideofFUCO2505 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084816 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1174484 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0085050&numberofmonths=24&showchangehistorylog=1 | 15-0085050 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 8223 | 20151213 | 1904 | 1362915 | 473 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1892 | 38.6996 | -123.4246 | 4SPANSLOADSIDEOF8223 | Partly Cloudy-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 15-0085050 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1174724 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0084616&numberofmonths=24&showchangehistorylog=1 | 15-0084616 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | HARRIS-1109 | 192431109 | FUSE | 5577 | 20151213 | 734 | 1360205 | 394 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 4728 | 40.7589 | -124.0511 | 7SPLDSIDEOF5577 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084616 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Line | 1174280 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0085003&numberofmonths=24&showchangehistorylog=1 | 15-0085003 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 6795 | 20151213 | 1617 | 1362253 | 453 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2265 | 41.2586 | -123.6007 | LDSIDEMETER1008025433 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0085003 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1174678 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0084774&numberofmonths=24&showchangehistorylog=1 | 15-0084774 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | KONOCTI-1102 | 43311102 | FUSE | 4613 | 20151213 | 1035 | 1361376 | 265 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 4505 | 38.8939 | -122.7074 | 10235SEIGLERSPRINGSNORTHMTR1008206729 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084774 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1174442 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0084857&numberofmonths=24&showchangehistorylog=1 | 15-0084857 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE | 7527 | 20151213 | 1039 | 1361403 | 387 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 774 | 38.9094 | -123.6341 | JONESMICHAELCOs7527 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084857 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1174524 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0084696&numberofmonths=24&showchangehistorylog=1 | 15-0084696 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | POTTER VALLEY P H-1105 | 42281105 | JUMPER | WIREDOWN | 20151213 | 714 | 1361225 | 293 | Distribution Circuit | Equipment Failure/Involved | Overhead | 670 | 168198 | 39.3617 | -123.1288 | 2SPANSLDSIDEOF64118 | Overcast-Heavy Rain-32-90 F | PGs, Kearneys | Broken, wire on ground | 15-0084696 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1174362 | PGK | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0085044&numberofmonths=24&showchangehistorylog=1 | 15-0085044 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | RIO DELL-1102 | 192251102 | FUSE | 7017 | 20151213 | 1759 | 1362856 | 361 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 5415 | 40.4357 | -123.9967 | 6SPANSSSOF3941 | Clear-Lightning-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0085044 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1174718 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0084887&numberofmonths=24&showchangehistorylog=1 | 15-0084887 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | FUSE | 2415 | 20151213 | 719 | 1360144 | 541 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1082 | 39.4866 | -123.3526 | 8SPANSLDSIDEOF2415 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084887 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Line | 1174555 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0084479&numberofmonths=24&showchangehistorylog=1 | 15-0084479 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | RECLOSER | 3090 | 20151213 | 514 | 1359863 | 847 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 38962 | 40.889 | -123.5934 | 2SPANSLOADSIDEOF3090 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084479 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Multi-Fault | 1174137 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0087101&numberofmonths=24&showchangehistorylog=1 | 15-0087101 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BRIDGEVILLE-1101 | 192461101 | RECLOSER | 37484 | 20151224 | 1135 | 1370806 | 3104 | Distribution Circuit | Environmental/External | Ice or snow | 38 | 42349 | 40.4524 | -123.6542 | ONMAINLINE1SPANEASTOF6697 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0087101 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Line | 1177173 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0087118&numberofmonths=24&showchangehistorylog=1 | 15-0087118 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BRIDGEVILLE-1101 | 192461101 | JUMPER | WIREDOWN2SPSSIDEOFFUSE4087 | 20151224 | 445 | 1371067 | 3628 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 112690 | 40.2888 | -123.4315 | MTR1007962494FUCO4087AND2SPANSSOURCESIDEOFFUCO4087 | Overcast-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on ground | 15-0087118 | OH | Sus | 0 | yes | 2015 | DEC | Yes | None | 1177190 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0087079&numberofmonths=24&showchangehistorylog=1 | 15-0087079 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 5233 | 20151224 | 839 | 1370809 | 313 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 11369 | 39.2282 | -123.7661 | THORPETIM4651AlbionLittleRiverRd | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0087079 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Line | 1177151 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0087176&numberofmonths=24&showchangehistorylog=1 | 15-0087176 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 1381 | 20151224 | 1850 | 1371354 | 229 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 458 | 39.0148 | -123.6806 | 16003SHWY1 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0087176 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1177255 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0087120&numberofmonths=24&showchangehistorylog=1 | 15-0087120 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3909 | 20151224 | 1306 | 1371037 | 109 | Distribution Circuit | Vegetation | Tree - branch fell on line | 30 | 3270 | 39.3998 | -123.7151 | 5SLOADSIDEOF3909 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0087120 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Line | 1177192 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0087414&numberofmonths=24&showchangehistorylog=1 | 15-0087414 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT SEWARD-1121 | 192321121 | FUSE | 1673 | 20151224 | 1619 | 1371732 | 4025 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 44275 | 40.2029 | -123.492 | 1SPAN4SPANSLDSIDEOF1673 | Overcast-Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 15-0087414 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1177493 | CAW | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0087119&numberofmonths=24&showchangehistorylog=1 | 15-0087119 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 7287 | 20151224 | 950 | 1370858 | 684 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 684 | 41.3719 | -123.4981 | 5SPANSLDSIDEOF7287 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0087119 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1177191 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0087061&numberofmonths=24&showchangehistorylog=1 | 15-0087061 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LOW GAP-1101 | 192411101 | RECLOSER | 4160 | 20151224 | 656 | 1370702 | 3497 | Distribution Circuit | Vegetation | Tree - fell into line | 379 | 1236891 | 40.4268 | -123.4807 | MTR1008025552SHERRIFCOVE | Overcast-Fog-32-90 F | Crossarm, Wood | Broken, wire on ground | 15-0087061 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1177130 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0087111&numberofmonths=24&showchangehistorylog=1 | 15-0087111 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LOW GAP-1101 | 192411101 | RECLOSER | 2094 | 20151224 | 1253 | 1370999 | 4432 | Distribution Circuit | Environmental/External | Ice or snow | 326 | 1281395 | 40.4361 | -123.488 | 2SPANSSSOF91983multiplebrokenpolesandwireongroundatandnearSW4107mainllinewiredownat7255 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 15-0087111 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Line | 1177183 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0087108&numberofmonths=24&showchangehistorylog=1 | 15-0087108 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | REDBUD-1101 | 43191101 | JUMPER | HOTWIREDOWN1SOF8263TWD83975 | 20151224 | 1233 | 1370995 | 274 | Distribution Circuit | Vegetation | Tree - fell into line | 1593 | 146925 | 39.0226 | -122.6764 | 1SOF8263TWD8263 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0087108 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Open Circuit | 1177180 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0087115&numberofmonths=24&showchangehistorylog=1 | 15-0087115 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | REDBUD-1101 | 43191101 | RECLOSER | 91960 | 20151224 | 1211 | 1371041 | 541 | Distribution Circuit | Vegetation | Tree - fell into line | 533 | 125745 | 39.0242 | -122.7213 | MTR1008659201CORNEROFPINTREESWANSON | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0087115 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1177187 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0087223&numberofmonths=24&showchangehistorylog=1 | 15-0087223 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLOW CREEK-1101 | 192171101 | FUSE | 3053 | 20151224 | 1943 | 1371413 | 4001 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 106920 | 40.9504 | -123.6536 | APPROX7SPANSLDSIDE30533milesupBrannonMTRD | Snow-Sleet or Ice-Rain-Hail-Combination-Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 15-0087223 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Line | 1177303 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0087227&numberofmonths=24&showchangehistorylog=1 | 15-0087227 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLOW CREEK-1101 | 192171101 | RECLOSER | 4904 | 20151224 | 2202 | 1371438 | 1713 | Distribution Circuit | Vegetation | Tree - branch fell on line | 151 | 230322 | 40.947 | -123.6423 | 8spansSSof68569 | Snow-Sleet or Ice-Rain-Hail-Combination-Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 15-0087227 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Multi-Fault | 1177308 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0087248&numberofmonths=24&showchangehistorylog=1 | 15-0087248 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLOW CREEK-1102 | 192171102 | OCB | OCB | 20151224 | 2309 | s1177329 | 3101 | Distribution Circuit | Vegetation | Tree - fell into line | 146 | 92054 | 40.9477 | -123.6396 | TRANSPOLE2210HWY96MM340 | Snow-Sleet or Ice-Rain-Combination-Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 15-0087248 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Multi-Fault | 1177329 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0087230&numberofmonths=24&showchangehistorylog=1 | 15-0087230 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | RECLOSER | 3090 | 20151224 | 2223 | 1371460 | 3301 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 151846 | 40.889 | -123.5934 | 7polesloadsideof3090 | Overcast-Fog-Below 32 F | Pole-Wood | Broken, wire on ground | 15-0087230 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Multi-Fault | 1177311 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0087306&numberofmonths=24&showchangehistorylog=1 | 15-0087306 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE | 7881 | 20151224 | 2130 | 1371813 | 2630 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 31560 | 40.8779 | -123.5129 | MTR1008025649 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 15-0087306 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Line | 1177388 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0012987&numberofmonths=24&showchangehistorylog=1 | 16-0012987 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | MENDOCINO-1101 | 42951101 | FUSE | 3443 | 20160217 | 841 | 1404619 | 155 | Distribution Circuit | Animal | Bird found | 134 | 20770 | 39.267 | -123.2042 | INTERSECTIONOFHARRISCTANDROADDWHICHIS1SPANEOFUCO8311 | Strong Winds-Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0012987 | OH | Sus | 42632252 | yes | 2016 | FEB | Yes | Line to Ground | 1186136 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017769&numberofmonths=24&showchangehistorylog=1 | 16-0017769 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 3045 | 20160305 | 1748 | 1417769 | 852 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 20956 | 39.2603 | -123.7237 | SMITHJOSEPH6811RD18WEST | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017769 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1189622 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017789&numberofmonths=24&showchangehistorylog=1 | 16-0017789 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BRIDGEVILLE-1101 | 192461101 | JUMPER | 3PHASESWIREDOWNATSW4101 | 20160305 | 1811 | 1418018 | 607 | Distribution Circuit | Vegetation | Tree - fell into line | 96 | 23408 | 40.4786 | -123.7781 | ATSW4101 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017789 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1189641 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017610&numberofmonths=24&showchangehistorylog=1 | 16-0017610 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | CALPELLA-1101 | 43411101 | FUSE | 7493 | 20160305 | 1708 | 1417544 | 640 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 6400 | 39.2505 | -123.2104 | ESPINOLACHRISTOPHER7406semslane | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0017610 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1189464 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017648&numberofmonths=24&showchangehistorylog=1 | 16-0017648 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | EEL RIVER 1101 | 192381101 | FUSE | 1907 | 20160305 | 1559 | 1417041 | 317 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 4353 | 40.4872 | -124.2599 | 2SPANSSOURCESIDEOF1987 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017648 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1189503 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017657&numberofmonths=24&showchangehistorylog=1 | 16-0017657 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 3975 | 20160305 | 1636 | 1417367 | 418 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 28842 | 39.2083 | -123.7105 | 31200MIDDLERIDGERDALBION | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017657 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1189513 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017977&numberofmonths=24&showchangehistorylog=1 | 16-0017977 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | SWITCH | 427 | 20160305 | 1831 | 1418141 | 864 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 40608 | 39.1374 | -123.6626 | ATFUCO5931 | Partly Cloudy-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017977 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1189848 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017626&numberofmonths=24&showchangehistorylog=1 | 16-0017626 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 2857 | 20160305 | 1550 | 1417010 | 250 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 7500 | 39.3912 | -123.7745 | METER1008392791 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017626 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1189480 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017717&numberofmonths=24&showchangehistorylog=1 | 16-0017717 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3969 | 20160305 | 1752 | 1417862 | 325 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 19175 | 39.3811 | -123.7737 | ATMTR1009653196 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017717 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1189572 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017818&numberofmonths=24&showchangehistorylog=1 | 16-0017818 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | OTHER | WIREDOWN | 20160305 | 1811 | 1417980 | 581 | Distribution Circuit | Vegetation | Tree - branch fell on line | 131 | 56128 | 39.4038 | -123.7404 | 29101HWY20 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017818 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1189671 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017757&numberofmonths=24&showchangehistorylog=1 | 16-0017757 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1141 | 192311141 | RECLOSER | 3902 | 20160305 | 1942 | 1418672 | 1200 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 1934 | 40.3428 | -123.9157 | 1SPANSSOF3939 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017757 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1189611 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017678&numberofmonths=24&showchangehistorylog=1 | 16-0017678 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 47739 | 20160305 | 1612 | 1417127 | 467 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 934 | 40.2279 | -123.8234 | 2SPANSLOADSIDEOF47739 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017678 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1189534 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017702&numberofmonths=24&showchangehistorylog=1 | 16-0017702 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | OTHER | 7449 | 20160305 | 1625 | 1417218 | 487 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2642 | 40.2155 | -123.8344 | 24SPANSLOADSIDEOF7449 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017702 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1189558 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017426&numberofmonths=24&showchangehistorylog=1 | 16-0017426 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | OTHER | WIREDOWN | 20160305 | 638 | 1416467 | 1140 | Distribution Circuit | Vegetation | Tree - fell into line | 439 | 187153 | 40.1143 | -123.9443 | 5SPANSFROM5763TWD2585ONMAINLINE | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017426 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1189316 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017558&numberofmonths=24&showchangehistorylog=1 | 16-0017558 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | JUMPER | WIREDOWN4SPLDSIDEOF1510 | 20160305 | 1528 | 1416920 | 690 | Distribution Circuit | Vegetation | Tree - fell into line | 372 | 177661 | 40.1232 | -123.8373 | 4SPANSLDSIDEOF1510 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017558 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Three Phase Fault | 1189416 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017549&numberofmonths=24&showchangehistorylog=1 | 16-0017549 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | RIO DELL-1102 | 192251102 | RECLOSER | 4230 | 20160305 | 1410 | 1416493 | 922 | Distribution Circuit | Vegetation | Tree - fell into line | 327 | 286241 | 40.4173 | -124.0895 | APPROX9SPANSLDSIDEOFSW7719 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0017549 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1189407 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0018474&numberofmonths=24&showchangehistorylog=1 | 16-0018474 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | RIO DELL-1102 | 192251102 | FUSE | 1997 | 20160305 | 1410 | 1421227 | 1577 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 11039 | 40.2852 | -124.0595 | 10SPANSLOADSIDEOF1997 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018474 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1190313 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0072159&numberofmonths=24&showchangehistorylog=1 | 16-0072159 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | EEL RIVER-1102 | 192381102 | FUSE | 1903 | 20161014 | 1113 | 1559350 | 400 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 2800 | 40.5282 | -124.1667 | 3SLSOF1903 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0072159 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Three Phase Fault | 1229283 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0072393&numberofmonths=24&showchangehistorylog=1 | 16-0072393 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT SEWARD-1121 | 192321121 | FUSE | 1637 | 20161014 | 2312 | 1560488 | 868 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 15932 | 40.1473 | -123.6358 | BRYANJOSEPH7072981053alderpointrd2spldsideco1637 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0072393 | OH | Sus | 42815227 | yes | 2016 | OCT | Yes | Line to Line | 1229455 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0071846&numberofmonths=24&showchangehistorylog=1 | 16-0071846 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | RECLOSER | 97300 | 20161014 | 335 | 1558105 | 751 | Distribution Circuit | Vegetation | Tree - fell into line | 442 | 35593 | 39.9723 | -123.8008 | BRYANJOSEPH70729810535SPNOFLR1770 | Clear-32-90 F | Conductor, Overhead | On Ground | 16-0071846 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Three Phase Fault | 1229024 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0072089&numberofmonths=24&showchangehistorylog=1 | 16-0072089 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 2571 | 20161014 | 828 | 1558710 | 622 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 6220 | 40.1348 | -123.9846 | 3SPANSNEOF2571 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0072089 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Ground | 1229242 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0003288&numberofmonths=24&showchangehistorylog=1 | 17-0003288 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3969 | 20170103 | 1959 | 1616676 | 460 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 27140 | 39.3811 | -123.7737 | 15001MITCHELLCREEKDR | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | On Ground | 17-0003288 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Multi-Fault | 1243460 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0003620&numberofmonths=24&showchangehistorylog=1 | 17-0003620 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT SEWARD-1121 | 192321121 | FUSE | 1659 | 20170103 | 1106 | 1615658 | 3194 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 12776 | 40.1631 | -123.616 | BYMTR115375730664STEELHEADEND | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003620 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1243744 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0002980&numberofmonths=24&showchangehistorylog=1 | 17-0002980 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 3775 | 20170103 | 719 | 1615363 | 1181 | Distribution Circuit | Vegetation | Tree - branch fell on line | 10 | 11810 | 40.2268 | -123.7887 | 10SPANSLDSIDEOF3775MULTIPLELOCATIONSOFWIREDOWNBROKENPOLETREELIMBSACROSSWIRES | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0002980 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1243267 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0002947&numberofmonths=24&showchangehistorylog=1 | 17-0002947 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 6635 | 20170103 | 629 | 1615340 | 9461 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 37844 | 41.2554 | -123.649 | 10SPANSLDSIDEOF6635 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0002947 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1243247 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0003117&numberofmonths=24&showchangehistorylog=1 | 17-0003117 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 3259 | 20170103 | 1423 | 1615837 | 8580 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 154440 | 41.3048 | -123.5346 | MTR1008022069 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003117 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1243312 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0003166&numberofmonths=24&showchangehistorylog=1 | 17-0003166 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | RECLOSER | 3304 | 20170103 | 1722 | 1615913 | 8978 | Distribution Circuit | Vegetation | Tree - fell into line | 531 | 3365902 | 41.1053 | -123.6888 | treeintolineuphillfrom595owlcreekrd6SPANSSSOF6325 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0003166 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1243335 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0003545&numberofmonths=24&showchangehistorylog=1 | 17-0003545 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | SWITCH | 3231 | 20170103 | 1711 | 1618211 | 5822 | Distribution Circuit | Vegetation | Tree - fell into line | 172 | 948974 | 41.0606 | -123.6809 | COUTPOLE4677 | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0003545 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1243700 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0003662&numberofmonths=24&showchangehistorylog=1 | 17-0003662 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | HOOPA-1101 | 192401101 | JUMPER | WIREDOWN2NDHARDTAPBEYOND3243 | 20170103 | 1854 | 1618495 | 4213 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 45209 | 41.0338 | -123.6714 | 2SPANSLDSIDEOF2NDHARDTAPBEYOND3243 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003662 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1243760 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0003722&numberofmonths=24&showchangehistorylog=1 | 17-0003722 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 4679 | 20170103 | 1627 | 1618621 | 4370 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 30590 | 41.0785 | -123.6984 | 3SPANSLDSIDEOF4679 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003722 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1243784 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0003723&numberofmonths=24&showchangehistorylog=1 | 17-0003723 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | OTHER | WIREDOWNLDSIDE3073 | 20170103 | 1627 | 1618624 | 4370 | Distribution Circuit | Vegetation | Tree - fell into line | 164 | 716680 | 41.0622 | -123.6944 | 1ST6SPANSIMMEDIATELYLDSIDEOF3073 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003723 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1243785 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0004114&numberofmonths=24&showchangehistorylog=1 | 17-0004114 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 3239 | 20170103 | 1854 | 1619843 | 5634 | Distribution Circuit | Vegetation | Tree - fell into line | 66 | 233712 | 41.0765 | -123.6874 | 5SLSOFSINGLEPHASETAP | Overcast-Fog-32-90 F | Pole-Wood | Broken, wire on ground | 17-0004114 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1244044 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0004117&numberofmonths=24&showchangehistorylog=1 | 17-0004117 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 5209 | 20170103 | 1809 | 1619858 | 5265 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 101438 | 41.0952 | -123.6956 | 3SPANSLDSIDEOFMTR1008282831 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004117 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1244048 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0004142&numberofmonths=24&showchangehistorylog=1 | 17-0004142 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 3277 | 20170103 | 1254 | 1619903 | 8871 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 62097 | 41.2598 | -123.6075 | 1STSPANLDSIDEOF3277AND3SPANSLDSIDEOF6795 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004142 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1244072 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006364&numberofmonths=24&showchangehistorylog=1 | 17-0006364 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 3369 | 20170103 | 1722 | 1632442 | 10021 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 190399 | 41.3725 | -123.5016 | 5SPANSLDSIDEOF3369 | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0006364 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246071 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0003334&numberofmonths=24&showchangehistorylog=1 | 17-0003334 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | KONOCTI-1102 | 43311102 | RECLOSER | 532 | 20170103 | 2232 | 1617141 | 916 | Distribution Circuit | Vegetation | Tree - fell into line | 302 | 52372 | 38.8576 | -122.7221 | 1SPANLDSIDEOFFUCO2169ONMAINLINE | Overcast-Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0003334 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Multi-Fault | 1243507 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0002897&numberofmonths=24&showchangehistorylog=1 | 17-0002897 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1103 | 42661103 | FUSE | 2853 | 20170103 | 23 | 1615253 | 979 | Distribution Circuit | Vegetation | Tree - fell into line | 122 | 98096 | 39.4683 | -123.3974 | RegeRobert110228970SHERWOODRDOHFEEDING7069 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0002897 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1243214 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0003212&numberofmonths=24&showchangehistorylog=1 | 17-0003212 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLOW CREEK-1101 | 192171101 | RECLOSER | 5002 | 20170103 | 1918 | 1616446 | 2353 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 108238 | 40.9462 | -123.6409 | 4SPANSSSOF6283 | Overcast-Fog-Strong Winds-Below 32 F | Pole-Wood | Broken, wire on ground | 17-0003212 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1243381 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0003212&numberofmonths=24&showchangehistorylog=1 | 17-0003212 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1101 | 192171101 | JUMPER | OJS1SOF2905 | 20170103 | 1918 | 1618098 | 2353 | Distribution Circuit | Vegetation | Tree - fell into line | 424 | 997672 | 40.9441 | -123.6266 | COUTPOLE2905 | Clear-Strong Winds-Below 32 F | Pole-Wood | Broken, wire on ground | 17-0003212 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1243682 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0003576&numberofmonths=24&showchangehistorylog=1 | 17-0003576 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1101 | 192171101 | FUSE | 3059 | 20170103 | 1914 | 1618290 | 2790 | Distribution Circuit | Vegetation | Tree - fell into line | 65 | 181350 | 40.9407 | -123.614 | 4SPANSLDSIDEOF3059 | Clear-Strong Winds-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0003576 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1243718 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0003705&numberofmonths=24&showchangehistorylog=1 | 17-0003705 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLOW CREEK-1101 | 192171101 | FUSE | 3009 | 20170103 | 1417 | 1618586 | 4463 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 17852 | 40.9055 | -123.7467 | 4SPANSLDSIDEOF3009 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0003705 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1243776 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0003760&numberofmonths=24&showchangehistorylog=1 | 17-0003760 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1101 | 192171101 | FUSE | 2985 | 20170103 | 1918 | 1618737 | 2786 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 153230 | 40.9442 | -123.621 | 10LDSIDEOFFUCO2985 | Clear-Strong Winds-Below 32 F | Pole-Wood | Broken, wire on ground | 17-0003760 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Open Circuit | 1243802 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0003227&numberofmonths=24&showchangehistorylog=1 | 17-0003227 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLOW CREEK-1102 | 192171102 | OCB | 11022 | 20170103 | 1957 | 1616369 | 1705 | Distribution Circuit | Vegetation | Tree - fell into line | 131 | 223355 | 40.9479 | -123.6402 | 3NOF335385 | Overcast-Fog-Strong Winds-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0003227 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1243396 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0003223&numberofmonths=24&showchangehistorylog=1 | 17-0003223 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | RECLOSER | 3090 | 20170103 | 1956 | 1616675 | 2126 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 99922 | 40.8889 | -123.5927 | 15SPANSLDSIDEOF309011SPANSLDSIDEOF3090 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003223 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1243392 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0003607&numberofmonths=24&showchangehistorylog=1 | 17-0003607 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE | 3119 | 20170103 | 2001 | 1618353 | 2686 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 75208 | 40.923 | -123.6241 | 2SPANSLDSIDEOF3119 | Clear-Strong Winds-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0003607 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1243734 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0003735&numberofmonths=24&showchangehistorylog=1 | 17-0003735 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | JUMPER | OJ1EOFMTR1008027868 | 20170103 | 1853 | 1618674 | 2924 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 55556 | 40.9397 | -123.6249 | SINGLEPHASETAP1EOFMTR1008027868 | Clear-Strong Winds-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0003735 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Open Circuit | 1243791 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0003770&numberofmonths=24&showchangehistorylog=1 | 17-0003770 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE | 6775 | 20170103 | 1650 | 1618816 | 4136 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 62040 | 40.8852 | -123.6249 | 16SPANSLDSIDEOFFUCO6775 | Clear-Strong Winds-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0003770 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1243809 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005127&numberofmonths=24&showchangehistorylog=1 | 17-0005127 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE | 5113 | 20170108 | 921 | 1624138 | 4839 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 5289 | 38.7189 | -123.38 | WIREDNONLINEANDBUCKLDSIDEOF51133SPANSLDSIDEOFBUCK | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005127 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1244926 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005452&numberofmonths=24&showchangehistorylog=1 | 17-0005452 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ANNAPOLIS-1101 | 42861101 | JUMPER | UNNUMBEREDFUSES | 20170108 | 1427 | 1627324 | 4293 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 4293 | 38.7136 | -123.341 | MTR1009672636 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005452 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245236 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0004982&numberofmonths=24&showchangehistorylog=1 | 17-0004982 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | RECLOSER | 79628 | 20170108 | 633 | 1622773 | 2228 | Distribution Circuit | Vegetation | Tree - fell into line | 328 | 751702 | 39.312 | -123.7861 | 44000LITTLELAKERD1SPANLDSIDEOF7343 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004982 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1244783 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005035&numberofmonths=24&showchangehistorylog=1 | 17-0005035 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 3283 | 20170108 | 630 | 1623848 | 4666 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 32662 | 39.3122 | -123.7829 | LDSIDEOF3283 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005035 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1244833 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005099&numberofmonths=24&showchangehistorylog=1 | 17-0005099 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 3291 | 20170108 | 633 | 1624724 | 4502 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 81036 | 39.3097 | -123.7501 | CORNEROFLITTLELAKERD3MILEYRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005099 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Open Circuit | 1244897 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005320&numberofmonths=24&showchangehistorylog=1 | 17-0005320 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 5731 | 20170108 | 910 | 1626791 | 2093 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 102557 | 39.2692 | -123.7817 | HWY1ATLITTLERIVERRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005320 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Multi-Fault | 1245110 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005813&numberofmonths=24&showchangehistorylog=1 | 17-0005813 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 5173 | 20170108 | 758 | 1629882 | 3616 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 47008 | 39.2859 | -123.7801 | LOADSIDEOF5173 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005813 | OH | Sus | 0 | yes | 2017 | JAN | Yes | None | 1245598 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006277&numberofmonths=24&showchangehistorylog=1 | 17-0006277 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | JUMPER | OPENJUMPERSSOURCESIDEOFMETER1009653056 | 20170108 | 633 | 1632081 | 4850 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 14550 | 39.3173 | -123.7881 | SOUTHOFMTR1009653056 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006277 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245974 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005481&numberofmonths=24&showchangehistorylog=1 | 17-0005481 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BRIDGEVILLE-1101 | 192461101 | RECLOSER | 37484 | 20170108 | 1006 | 1625400 | 3324 | Distribution Circuit | Vegetation | Tree - fell into line | 399 | 164480 | 40.4523 | -123.6539 | 4SPANSLDSIDEOF4737WIREDOWNBET37484AND39288MULTIPLELOCATIONSLIMBSONLINES2SEOF59535BROKENCROSSARMANDWI | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0005481 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245264 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006463&numberofmonths=24&showchangehistorylog=1 | 17-0006463 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | EEL RIVER-1102 | 192381102 | FUSE | 1899 | 20170108 | 852 | 1623812 | 3054 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 33594 | 40.5106 | -124.1608 | 5SPANSSOUTHOF1899 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006463 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246145 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005393&numberofmonths=24&showchangehistorylog=1 | 17-0005393 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 5931 | 20170108 | 1426 | 1627318 | 2877 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 5754 | 39.1338 | -123.6296 | 1SPANLDSIDEOF59311SPANEASTOF5931ON3PHASEMAINLINE | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005393 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1245178 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005459&numberofmonths=24&showchangehistorylog=1 | 17-0005459 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | RECLOSER | 1260 | 20170108 | 1043 | 1625132 | 3060 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 278301 | 39.1293 | -123.7112 | MAINLINEATFUCO5873 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005459 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245243 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005521&numberofmonths=24&showchangehistorylog=1 | 17-0005521 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 5781 | 20170108 | 804 | 1628114 | 4741 | Distribution Circuit | Equipment Failure/Involved | Overhead | 194 | 373423 | 39.2263 | -123.7286 | LDSIDEDOWN5781 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0005521 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Force Out | 1245304 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006223&numberofmonths=24&showchangehistorylog=1 | 17-0006223 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | JUMPER | OJ1SPANLDSIDEOF17012 | 20170108 | 1211 | 1631719 | 4683 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 4683 | 39.2233 | -123.748 | MTR207670 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006223 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1245925 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005173&numberofmonths=24&showchangehistorylog=1 | 17-0005173 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 6069 | 20170108 | 931 | 1624355 | 1895 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 75800 | 39.6578 | -123.7827 | 6SPANSLDSIDEOF6069 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005173 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1244967 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005554&numberofmonths=24&showchangehistorylog=1 | 17-0005554 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 5681 | 20170108 | 835 | 1628402 | 2294 | Distribution Circuit | Vegetation | Tree - branch fell on line | 10 | 22940 | 39.4801 | -123.7868 | 1WIREDN6SPANSLDSIDEOF5681 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005554 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1245336 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0004949&numberofmonths=24&showchangehistorylog=1 | 17-0004949 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 5561 | 20170108 | 543 | 1622949 | 3482 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 141424 | 39.381 | -123.8003 | 2SPANSSOF5561 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004949 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1244751 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005181&numberofmonths=24&showchangehistorylog=1 | 17-0005181 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 8575 | 20170108 | 752 | 1625350 | 740 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 17760 | 39.4207 | -123.7804 | 19620BENSON | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005181 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1244975 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005378&numberofmonths=24&showchangehistorylog=1 | 17-0005378 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 5661 | 20170108 | 904 | 1627222 | 2082 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 52050 | 39.392 | -123.7986 | LDSIDEOF5661FUCO | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005378 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1245164 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005525&numberofmonths=24&showchangehistorylog=1 | 17-0005525 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | SWITCH | 5989 | 20170108 | 752 | 1628133 | 2174 | Distribution Circuit | Vegetation | Tree - branch fell on line | 48 | 104352 | 39.4077 | -123.7333 | 27917HWY20 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005525 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245308 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005676&numberofmonths=24&showchangehistorylog=1 | 17-0005676 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 503683 | 20170108 | 754 | 1623345 | 2376 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 21384 | 39.3876 | -123.7714 | 1SPANLDSIDEOF503683 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005676 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245457 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005679&numberofmonths=24&showchangehistorylog=1 | 17-0005679 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3969 | 20170108 | 752 | 1629170 | 2963 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 174817 | 39.3811 | -123.7737 | 9SPANSLDSIDEOF3969 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005679 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245460 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005731&numberofmonths=24&showchangehistorylog=1 | 17-0005731 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 1513 | 20170108 | 752 | 1629027 | 3293 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 125134 | 39.4165 | -123.7889 | havewiredown6plsof1513 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005731 | OH | Sus | 0 | yes | 2017 | JAN | Yes | None | 1245515 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005906&numberofmonths=24&showchangehistorylog=1 | 17-0005906 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | JUMPER | OJSSSOFMTR1009672629 | 20170108 | 2029 | 1630364 | 2671 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2671 | 39.4188 | -123.7792 | SSOFMTR1009672629 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005906 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245689 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005953&numberofmonths=24&showchangehistorylog=1 | 17-0005953 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 7253 | 20170108 | 2029 | 1630596 | 1505 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 18060 | 39.4188 | -123.778 | MTR1009202244 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005953 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245725 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006009&numberofmonths=24&showchangehistorylog=1 | 17-0006009 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3321 | 20170108 | 733 | 1630767 | 4977 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 19908 | 39.4049 | -123.7415 | FELICICHDAVIDat29501hwy20 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006009 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245757 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006089&numberofmonths=24&showchangehistorylog=1 | 17-0006089 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 2275 | 20170108 | 959 | 1624699 | 1691 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 40584 | 39.3877 | -123.7744 | 4SPANSLDSIDEOF2275 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006089 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245818 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0004949&numberofmonths=24&showchangehistorylog=1 | 17-0004949 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 5601 | 20170108 | 810 | 1633163 | 3311 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 16555 | 39.3853 | -123.7993 | LEEDSWAY | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004949 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1246215 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0004949&numberofmonths=24&showchangehistorylog=1 | 17-0004949 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 5579 | 20170108 | 850 | 1633166 | 3315 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 13260 | 39.386 | -123.7993 | OLDCASPARRR2800NOGIBNEYLN | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004949 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1246217 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0004949&numberofmonths=24&showchangehistorylog=1 | 17-0004949 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 5593 | 20170108 | 850 | 1633168 | 3400 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 23800 | 39.3871 | -123.7992 | FIRDR | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004949 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1246218 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0004949&numberofmonths=24&showchangehistorylog=1 | 17-0004949 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 5589 | 20170108 | 850 | 1633172 | 3430 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 10290 | 39.388 | -123.7997 | ENDOFMCDONALDLANE | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004949 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1246219 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0004949&numberofmonths=24&showchangehistorylog=1 | 17-0004949 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 5583 | 20170108 | 850 | 1633178 | 4511 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 9022 | 39.3898 | -123.8007 | 60KVRW800SOUTHOFPEARL | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004949 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1246220 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007706&numberofmonths=24&showchangehistorylog=1 | 17-0007706 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 1687 | 20170108 | 959 | 1624538 | 4660 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 27960 | 39.3965 | -123.7815 | NSSIMPSONLNHILLSOHOMELNFORTBRAGG | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007706 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247198 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005184&numberofmonths=24&showchangehistorylog=1 | 17-0005184 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 6545 | 20170108 | 833 | 1623560 | 4487 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 21980 | 39.4631 | -123.8002 | MTR1009765125 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005184 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1244978 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005366&numberofmonths=24&showchangehistorylog=1 | 17-0005366 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 1607 | 20170108 | 1110 | 1627166 | 3565 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 14260 | 39.4419 | -123.773 | FELICICHDAVIDtwospansloadsideco1607 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005366 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245152 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005370&numberofmonths=24&showchangehistorylog=1 | 17-0005370 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 1477 | 20170108 | 1038 | 1627181 | 3509 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 10527 | 39.4422 | -123.7717 | 2SPANSLDSIDEOF1477 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005370 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245156 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005446&numberofmonths=24&showchangehistorylog=1 | 17-0005446 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1141 | 192311141 | FUSE | 3965 | 20170108 | 924 | 1627686 | 4592 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 4592 | 40.3417 | -123.8803 | 7SPANSLDSIDEOF3965 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005446 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1245230 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005153&numberofmonths=24&showchangehistorylog=1 | 17-0005153 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | RECLOSER | 6054 | 20170108 | 905 | 1624053 | 4792 | Distribution Circuit | Vegetation | Tree - branch fell on line | 579 | 758109 | 40.2854 | -123.8367 | 3SPANSLDSIDEOF37541BRANCHONLINE15SPANSLDSIDE93234MAINLINEDOWN8SLDSIDE93234MUDSLIDETREEINTOLINE | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005153 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1244948 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005236&numberofmonths=24&showchangehistorylog=1 | 17-0005236 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | RECLOSER | 6064 | 20170108 | 851 | 1623842 | 1497 | Distribution Circuit | Equipment Failure/Involved | Overhead | 66 | 98802 | 40.2942 | -123.8196 | SSOFFUCO8055 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005236 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1245025 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005334&numberofmonths=24&showchangehistorylog=1 | 17-0005334 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 7359 | 20170108 | 905 | 1626914 | 4760 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 9520 | 40.2394 | -123.8167 | TrumboMauriceK1911T1202911LOGAN | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005334 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245124 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006014&numberofmonths=24&showchangehistorylog=1 | 17-0006014 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 1679 | 20170108 | 942 | 1630783 | 4427 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 203642 | 40.2781 | -123.7929 | 2SPANSSSOF8055 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006014 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245761 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006845&numberofmonths=24&showchangehistorylog=1 | 17-0006845 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 7215 | 20170108 | 905 | 1634644 | 4647 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 88293 | 40.2256 | -123.8687 | LASTSPANLDSIDEOF72515 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006845 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246426 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007672&numberofmonths=24&showchangehistorylog=1 | 17-0007672 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 1523 | 20170108 | 1247 | 1626410 | 4393 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 52716 | 40.2899 | -123.8126 | 1285TSARNASGOODRD | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007672 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247177 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0004963&numberofmonths=24&showchangehistorylog=1 | 17-0004963 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | RECLOSER | 1514 | 20170108 | 716 | 1623071 | 3397 | Distribution Circuit | Vegetation | Tree - fell into line | 248 | 532194 | 40.0478 | -123.7896 | 1PSOCO1873MTR1008693562REG7833BROKENPOLE1SPANSSOFSBCO864261WIREONGROUND | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0004963 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1244765 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005392&numberofmonths=24&showchangehistorylog=1 | 17-0005392 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 1569 | 20170108 | 716 | 1627314 | 2116 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 12696 | 40.0193 | -123.796 | RICHARDSONGROVE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005392 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Force Out | 1245177 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005277&numberofmonths=24&showchangehistorylog=1 | 17-0005277 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 2529 | 20170108 | 717 | 1626362 | 2238 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 11190 | 40.0889 | -123.9445 | BryanJoeK3426T20673spldsdco2529ettersburgrd | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0005277 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245067 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005420&numberofmonths=24&showchangehistorylog=1 | 17-0005420 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 2523 | 20170108 | 716 | 1627478 | 6253 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 68783 | 40.237 | -124.1567 | 1SPANLDSIDEOF2523 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005420 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245203 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005565&numberofmonths=24&showchangehistorylog=1 | 17-0005565 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 3791 | 20170108 | 746 | 1628465 | 4899 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 4899 | 40.1243 | -123.8303 | 1SPANLDSIDEOF3791 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005565 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245348 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005572&numberofmonths=24&showchangehistorylog=1 | 17-0005572 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 1965 | 20170108 | 746 | 1628478 | 1900 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 74100 | 40.1219 | -123.834 | 1008024346 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005572 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245354 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006824&numberofmonths=24&showchangehistorylog=1 | 17-0006824 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | JUMPER | OJSONHARDTAPFEEDINGTRANSF114418827490 | 20170108 | 717 | s1246410 | 4743 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 18309 | 40.0623 | -123.9944 | TRANSF114418827490EOL | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006824 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246410 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005226&numberofmonths=24&showchangehistorylog=1 | 17-0005226 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | OTHER | 481 | 20170108 | 1022 | 1625185 | 1708 | Distribution Circuit | Vegetation | Tree - fell into line | 408 | 657236 | 38.6963 | -123.4315 | 2SPANSLDSIDE481 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005226 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245015 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005299&numberofmonths=24&showchangehistorylog=1 | 17-0005299 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 9407 | 20170108 | 1037 | 1624980 | 3171 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 19026 | 38.8171 | -123.5599 | 4SPANSLDSIDEOF9407 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005299 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245088 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005089&numberofmonths=24&showchangehistorylog=1 | 17-0005089 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 3319 | 20170108 | 1008 | 1624651 | 375 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 4125 | 41.0492 | -123.6656 | 3SPANSLDSIDEOF3319 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005089 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1244887 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005164&numberofmonths=24&showchangehistorylog=1 | 17-0005164 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 3153 | 20170108 | 1106 | 1625243 | 317 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2536 | 41.061 | -123.6774 | MTR1008022328 | Overcast-Fog-Heavy Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0005164 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1244959 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005055&numberofmonths=24&showchangehistorylog=1 | 17-0005055 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | KONOCTI-1102 | 43311102 | RECLOSER | 532 | 20170108 | 754 | 1623559 | 542 | Distribution Circuit | Vegetation | Tree - fell into line | 302 | 32722 | 38.8576 | -122.7221 | GROUSERDCORNEROFGROUSEENTRANCE | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005055 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Multi-Fault | 1244853 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005356&numberofmonths=24&showchangehistorylog=1 | 17-0005356 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | KONOCTI-1102 | 43311102 | OTHER | WIREDOWN2SPANSFROM2311 | 20170108 | 1034 | 1625492 | 1934 | Distribution Circuit | Vegetation | Tree - fell into line | 762 | 169590 | 38.8895 | -122.737 | 2spansfrom2311TWDSLR4300 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005356 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Force Out | 1245144 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005602&numberofmonths=24&showchangehistorylog=1 | 17-0005602 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | KONOCTI-1102 | 43311102 | OTHER | WIREDOWN | 20170108 | 1708 | 1628373 | 1104 | Distribution Circuit | Vegetation | Tree - fell into line | 304 | 328917 | 38.8327 | -122.7358 | SmithCody15780BOTTLEROCKRD | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005602 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245380 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006842&numberofmonths=24&showchangehistorylog=1 | 17-0006842 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE | 6467 | 20170108 | 922 | 1634625 | 4883 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 24415 | 39.8486 | -123.7097 | MTR5000008242 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006842 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Force Out | 1246423 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005260&numberofmonths=24&showchangehistorylog=1 | 17-0005260 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE | 2463 | 20170108 | 930 | 1624230 | 672 | Distribution Circuit | Vegetation | Tree - fell into line | 71 | 47712 | 39.749 | -123.5106 | ESPINOLACHRISTOPHER5loadside2463 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005260 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Three Phase Fault | 1245050 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005310&numberofmonths=24&showchangehistorylog=1 | 17-0005310 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE | 7093 | 20170108 | 1223 | 1626168 | 1627 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 42302 | 39.6446 | -123.4783 | 42501TWINPINESCIR | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005310 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245100 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005156&numberofmonths=24&showchangehistorylog=1 | 17-0005156 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1101 | 42601101 | FUSE | 7071 | 20170108 | 923 | 1624170 | 2081 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 45782 | 39.0325 | -123.37 | 7SPANSLDSIDEOF7071 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005156 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1244951 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005547&numberofmonths=24&showchangehistorylog=1 | 17-0005547 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1102 | 42601102 | SWITCH | 625 | 20170108 | 1645 | 1627779 | 2655 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 76995 | 39.0856 | -123.5336 | ONPHILOSIDEOF2605 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005547 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245329 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006107&numberofmonths=24&showchangehistorylog=1 | 17-0006107 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1102 | 42601102 | FUSE | 2919 | 20170108 | 1011 | 1625129 | 1863 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 44712 | 39.0594 | -123.5168 | PANORAMAANDSIGNALRIDGE | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0006107 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245832 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005038&numberofmonths=24&showchangehistorylog=1 | 17-0005038 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | RECLOSER | 83354 | 20170108 | 452 | 1622539 | 844 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 21100 | 38.8808 | -123.6621 | 5139 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005038 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1244836 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005092&numberofmonths=24&showchangehistorylog=1 | 17-0005092 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE | 7871 | 20170108 | 524 | 1622556 | 2018 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 10090 | 38.922 | -123.6227 | LASTSPANONTAP | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005092 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1244890 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005416&numberofmonths=24&showchangehistorylog=1 | 17-0005416 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | JUMPER | WIREDOWN2SPLDSIDEOF97045 | 20170108 | 920 | 1624135 | 2981 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 8943 | 38.9011 | -123.6772 | 2SPANSLDSIDEOF97045 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005416 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Three Phase Fault | 1245199 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0008416&numberofmonths=24&showchangehistorylog=1 | 17-0008416 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE | 6415 | 20170108 | 949 | 1624384 | 5826 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 5826 | 38.9159 | -123.6536 | LDSIDEOF6415 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0008416 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1247805 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005307&numberofmonths=24&showchangehistorylog=1 | 17-0005307 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | RIO DELL-1102 | 192251102 | RECLOSER | 4230 | 20170108 | 919 | 1626741 | 4835 | Distribution Circuit | Environmental/External | Water | 324 | 1130611 | 40.4173 | -124.0895 | 40SLDOFLR42302SOFMTR1009022882 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0005307 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245096 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005759&numberofmonths=24&showchangehistorylog=1 | 17-0005759 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLOW CREEK-1101 | 192171101 | RECLOSER | 5002 | 20170108 | 2139 | 1629613 | 1158 | Distribution Circuit | Vegetation | Tree - fell into line | 590 | 683220 | 40.9462 | -123.6409 | 4SLSOF6283 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005759 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245544 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005890&numberofmonths=24&showchangehistorylog=1 | 17-0005890 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ARCATA-1121 | 192021121 | FUSE | 1217 | 20170109 | 125 | 1630127 | 510 | Distribution Circuit | Vegetation | Tree - fell into line | 65 | 33150 | 40.8388 | -124.0229 | 1SPANSO8815 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005890 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245675 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006269&numberofmonths=24&showchangehistorylog=1 | 17-0006269 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 551 | 20170109 | 1656 | 1632051 | 3060 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 52020 | 39.3266 | -123.7929 | 5SPANSLDSIDEOF551 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006269 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245966 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006281&numberofmonths=24&showchangehistorylog=1 | 17-0006281 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 7719 | 20170109 | 1638 | 1632115 | 1649 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3298 | 39.2613 | -123.7205 | 1SPANLDSIDEOF7719 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006281 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245979 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006290&numberofmonths=24&showchangehistorylog=1 | 17-0006290 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | RECLOSER | 69032 | 20170109 | 1633 | 1631858 | 1111 | Distribution Circuit | Vegetation | Tree - fell into line | 122 | 135542 | 39.2995 | -123.789 | MAINLINEAT41651FUCO | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006290 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1245989 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006466&numberofmonths=24&showchangehistorylog=1 | 17-0006466 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 3287 | 20170109 | 2031 | 1632509 | 1146 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 69906 | 39.3135 | -123.747 | LITTLELAKEROAD3MILESEOMENDOCINO | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006466 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246148 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006922&numberofmonths=24&showchangehistorylog=1 | 17-0006922 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 7273 | 20170109 | 2029 | 1635771 | 2559 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 115155 | 39.2719 | -123.6978 | 39475COMPTCHERDMENDOCINO | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006922 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246504 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006162&numberofmonths=24&showchangehistorylog=1 | 17-0006162 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 5233 | 20170109 | 1412 | 1631461 | 1487 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 60967 | 39.2282 | -123.7663 | GarciaDan12609spansbeyond5233albionlittleriverrd | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0006162 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245874 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006228&numberofmonths=24&showchangehistorylog=1 | 17-0006228 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | OTHER | WIREDOWNMTR1009140678 | 20170109 | 3 | 1631738 | 3902 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 10813 | 39.219 | -123.7465 | MTR1009140678 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006228 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1245928 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007604&numberofmonths=24&showchangehistorylog=1 | 17-0007604 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 3183 | 20170109 | 1330 | 1639668 | 3101 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 6202 | 39.552 | -123.7226 | 6SPANSLDSIDEOF3183 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007604 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Three Phase Fault | 1247119 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005974&numberofmonths=24&showchangehistorylog=1 | 17-0005974 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3099 | 20170109 | 913 | 1630647 | 2155 | Distribution Circuit | Vegetation | Tree - fell into line | 88 | 53710 | 39.4209 | -123.78 | 1SO3103 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005974 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245739 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006183&numberofmonths=24&showchangehistorylog=1 | 17-0006183 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 5153 | 20170109 | 1014 | 1630823 | 2294 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 4588 | 39.3925 | -123.7662 | FelicichDavid5spansloadsideco5153 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006183 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245884 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006207&numberofmonths=24&showchangehistorylog=1 | 17-0006207 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1141 | 192311141 | OTHER | WIREDOWN4SPLDSIDEOF1595 | 20170109 | 1002 | 1630946 | 3704 | Distribution Circuit | Vegetation | Tree - fell into line | 221 | 222140 | 40.3114 | -123.9011 | 4SPANSLDSIDEOFSW1595 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006207 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245898 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005896&numberofmonths=24&showchangehistorylog=1 | 17-0005896 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 3283 | 20170109 | 706 | 1630298 | 1952 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 9760 | 41.2959 | -123.5644 | 200SOHWY96ATCRAWFORDCRORLEANS | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005896 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Open Circuit | 1245681 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005923&numberofmonths=24&showchangehistorylog=1 | 17-0005923 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 654897 | 20170109 | 759 | 1630434 | 731 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 5117 | 41.1882 | -123.7056 | 9SPANSLDSIDETOEOL | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005923 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245701 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006079&numberofmonths=24&showchangehistorylog=1 | 17-0006079 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 3127 | 20170109 | 1135 | 1631069 | 287 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 861 | 41.2808 | -123.5873 | 2SPANSLDSIDEOF3127 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006079 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245810 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006339&numberofmonths=24&showchangehistorylog=1 | 17-0006339 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LOW GAP-1101 | 192411101 | RECLOSER | 4160 | 20170109 | 2215 | 1632328 | 2570 | Distribution Circuit | Vegetation | Tree - fell into line | 416 | 626894 | 40.4272 | -123.481 | 6POLESSSOFLBFEEDING4086 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006339 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246044 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005930&numberofmonths=24&showchangehistorylog=1 | 17-0005930 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LUCERNE-1106 | 43351106 | FUSE | 571 | 20170109 | 813 | 1630342 | 1593 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 4779 | 39.0043 | -122.762 | BEYONDFUCO571LASTSPANTOEOL | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005930 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245708 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006116&numberofmonths=24&showchangehistorylog=1 | 17-0006116 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1101 | 42601101 | SWITCH | 5779 | 20170109 | 959 | 1630771 | 1831 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 9155 | 39.0516 | -123.4356 | GALLETTITIMTREETHROUGHLINE2O500TUMBLINGMCDRDSAPID102198149 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006116 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245839 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006219&numberofmonths=24&showchangehistorylog=1 | 17-0006219 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1101 | 42601101 | FUSE | 1413 | 20170109 | 1556 | 1631690 | 2837 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 28370 | 38.9037 | -123.3146 | 16PLDSOF1413 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006219 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245923 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006166&numberofmonths=24&showchangehistorylog=1 | 17-0006166 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1102 | 42601102 | FUSE | 893 | 20170109 | 1209 | 1631170 | 1481 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 5924 | 39.0578 | -123.4518 | 2SLDSIDEOFFUSE | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006166 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245875 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006506&numberofmonths=24&showchangehistorylog=1 | 17-0006506 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | RIO DELL-1102 | 192251102 | FUSE | 6115 | 20170109 | 1926 | 1632134 | 2422 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2422 | 40.4152 | -123.9362 | METER1009436486 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006506 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246172 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007513&numberofmonths=24&showchangehistorylog=1 | 17-0007513 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ANNAPOLIS-1101 | 42861101 | RECLOSER | 76842 | 20170110 | 1730 | 1634723 | 1120 | Distribution Circuit | Vegetation | Tree - fell into line | 171 | 191436 | 38.6803 | -123.3125 | WOF4587 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007513 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247058 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006521&numberofmonths=24&showchangehistorylog=1 | 17-0006521 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 8481 | 20170110 | 805 | 1632657 | 2185 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 34960 | 39.3616 | -123.7904 | 1PSSOF8481 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0006521 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1246180 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006581&numberofmonths=24&showchangehistorylog=1 | 17-0006581 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 1579 | 20170110 | 449 | 1632488 | 845 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 14365 | 39.3056 | -123.792 | 5PLD16DOWN | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006581 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246230 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007252&numberofmonths=24&showchangehistorylog=1 | 17-0007252 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BRIDGEVILLE-1101 | 192461101 | FUSE | 4115 | 20170110 | 2310 | 1635202 | 879 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 3516 | 40.4867 | -123.7406 | 1SPANLDSIDEOFFU4115 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007252 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1246832 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006956&numberofmonths=24&showchangehistorylog=1 | 17-0006956 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | RECLOSER | 1260 | 20170110 | 1839 | 1635588 | 1511 | Distribution Circuit | Vegetation | Tree - branch fell on line | 95 | 111625 | 39.1293 | -123.7112 | 2SLSOF8631 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006956 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246538 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006810&numberofmonths=24&showchangehistorylog=1 | 17-0006810 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 8561 | 20170110 | 1515 | 1633970 | 1251 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 18765 | 39.5109 | -123.7622 | MTR1010035182 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0006810 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1246396 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006994&numberofmonths=24&showchangehistorylog=1 | 17-0006994 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 3173 | 20170110 | 1512 | 1633956 | 1784 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3568 | 39.6337 | -123.7825 | SIGHTSJUSTIN3SPANSLOADSIDEOFFUSES3173 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006994 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246576 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007231&numberofmonths=24&showchangehistorylog=1 | 17-0007231 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 7085 | 20170110 | 1725 | 1634687 | 1733 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2714 | 39.4757 | -123.7311 | LASTSPANLDSIDE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007231 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246810 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006493&numberofmonths=24&showchangehistorylog=1 | 17-0006493 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | JUMPER | OPENJUMPERSNORTHOF2071LINEBUCK | 20170110 | 948 | 1632845 | 1874 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 7496 | 39.3946 | -123.7986 | FelicichDavid4spansloadsideCO2071 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006493 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246165 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006836&numberofmonths=24&showchangehistorylog=1 | 17-0006836 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 1801 | 20170110 | 1702 | 1634566 | 85 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 850 | 39.4154 | -123.7825 | FelicichDavid10JAN171805CREWWORKINGONSECTIONOFLINE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006836 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246419 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007238&numberofmonths=24&showchangehistorylog=1 | 17-0007238 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | JUMPER | OJSFEEDINGMTR1006277257 | 20170110 | 2114 | 1637989 | 1266 | Distribution Circuit | Vegetation | Tree - fell into line | 128 | 5173 | 39.4071 | -123.7449 | MTR1006277257 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0007238 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246817 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006726&numberofmonths=24&showchangehistorylog=1 | 17-0006726 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 1757 | 20170110 | 1051 | 1633702 | 1786 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 28576 | 39.4416 | -123.7285 | MTR1010029291 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006726 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246332 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006555&numberofmonths=24&showchangehistorylog=1 | 17-0006555 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 4599 | 20170110 | 1136 | 1633088 | 1868 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 13076 | 40.2376 | -123.8333 | 4SPANSLDSIDEOF4599 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006555 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246201 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006904&numberofmonths=24&showchangehistorylog=1 | 17-0006904 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 8437 | 20170110 | 1611 | 1635231 | 229 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 7328 | 41.2105 | -123.7574 | 4SPANSLDSIDEOF8439 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006904 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246485 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006612&numberofmonths=24&showchangehistorylog=1 | 17-0006612 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LUCERNE-1106 | 43351106 | RECLOSER | 38632 | 20170110 | 1224 | 1633199 | 666 | Distribution Circuit | Vegetation | Tree - fell into line | 259 | 17964 | 38.9913 | -122.7481 | 3SPAST1145 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006612 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246253 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006516&numberofmonths=24&showchangehistorylog=1 | 17-0006516 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1101 | 42601101 | FUSE | 1311 | 20170110 | 800 | 1632630 | 582 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 7566 | 39.007 | -123.4158 | 1SPANLDSIDEOF1311 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006516 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246175 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006682&numberofmonths=24&showchangehistorylog=1 | 17-0006682 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER | 37506 | 20170110 | 1348 | 1633520 | 1900 | Distribution Circuit | Vegetation | Tree - fell into line | 89 | 122926 | 39.4831 | -123.3611 | 30000NHIWAY1012NDSPANLDSIDEOFLR37506WIREDOWNandbrokencrossarm | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0006682 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246303 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007780&numberofmonths=24&showchangehistorylog=1 | 17-0007780 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE | 4599 | 20170111 | 1520 | 1640218 | 28 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 112 | 38.7481 | -123.3506 | UNKNOWN | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007780 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1247248 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007483&numberofmonths=24&showchangehistorylog=1 | 17-0007483 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 5233 | 20170111 | 29 | 1638185 | 1111 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 45551 | 39.2282 | -123.7663 | 8SPANSLDSIDEOF5233 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007483 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247040 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007543&numberofmonths=24&showchangehistorylog=1 | 17-0007543 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 1457 | 20170111 | 805 | 1638984 | 624 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 5616 | 39.2197 | -123.7293 | 6SLDSOF1457 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007543 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247080 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007840&numberofmonths=24&showchangehistorylog=1 | 17-0007840 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 8259 | 20170111 | 1701 | 1640399 | 89 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 178 | 39.4725 | -123.7983 | WIREDOWNENTIRECONDUCTORTOEOL | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007840 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1247300 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0008241&numberofmonths=24&showchangehistorylog=1 | 17-0008241 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | SWITCH | 5989 | 20170111 | 2319 | 1640874 | 789 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 39450 | 39.4077 | -123.7333 | 27300HWY20 | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0008241 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Force Out | 1247684 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007609&numberofmonths=24&showchangehistorylog=1 | 17-0007609 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 4365 | 20170111 | 1120 | 1639677 | 340 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1360 | 39.9608 | -123.7701 | RapichRobertK1987T199517spansloasside4365 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007609 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247124 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007652&numberofmonths=24&showchangehistorylog=1 | 17-0007652 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 1707 | 20170111 | 1005 | 1639395 | 1551 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 9306 | 39.9261 | -123.7576 | 3SPANSFROMEOLLDSIDEOF1707 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007652 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247159 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007725&numberofmonths=24&showchangehistorylog=1 | 17-0007725 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 1879 | 20170111 | 1319 | 1639605 | 1608 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 10800 | 39.8178 | -123.7635 | 5SPANSLDSIDEOFTHEENDOFTHE3PHASETWDEOL | Overcast-Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0007725 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247208 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007778&numberofmonths=24&showchangehistorylog=1 | 17-0007778 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE | 5395 | 20170111 | 849 | 1639110 | 1658 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1658 | 39.8249 | -123.6745 | 1POLEFROM1731TWD1729 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007778 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1247246 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0008438&numberofmonths=24&showchangehistorylog=1 | 17-0008438 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE | 1729 | 20170111 | 1233 | 1639774 | 1668 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 11676 | 39.8271 | -123.6771 | 1POLEFROM1731TWD1729 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0008438 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247821 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007389&numberofmonths=24&showchangehistorylog=1 | 17-0007389 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LUCERNE-1106 | 43351106 | FUSE | 4123 | 20170111 | 105 | 1638293 | 1090 | Distribution Circuit | Vegetation | Tree - fell into line | 107 | 57882 | 39 | -122.7528 | MTR1008031778 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007389 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1246976 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007819&numberofmonths=24&showchangehistorylog=1 | 17-0007819 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1101 | 42601101 | RECLOSER | 3700 | 20170111 | 1520 | 1640169 | 1515 | Distribution Circuit | Vegetation | Tree - branch fell on line | 243 | 18939 | 38.9969 | -123.357 | ESPINOLACHRISTOPHERatcopole1605 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 17-0007819 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247280 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0009722&numberofmonths=24&showchangehistorylog=1 | 17-0009722 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ARCATA-1122 | 192021122 | SWITCH | 4571 | 20170118 | 415 | 1645681 | 986 | Distribution Circuit | Vegetation | Tree - fell into line | 131 | 69074 | 40.7927 | -124.0232 | 6SPANSLDSIDEFU6783 | Overcast-Drizzle-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0009722 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1248910 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0010058&numberofmonths=24&showchangehistorylog=1 | 17-0010058 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | BRIDGEVILLE-1102 | 192461102 | FUSE | 3717 | 20170118 | 1140 | 1646052 | 265 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 530 | 40.425 | -123.7639 | 6LDSIDEFU3717 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010058 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1249091 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0010541&numberofmonths=24&showchangehistorylog=1 | 17-0010541 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | EEL RIVER-1102 | 192381102 | FUSE | 1909 | 20170118 | 1908 | 1648406 | 901 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 21624 | 40.5115 | -124.1597 | 5SPANSLDSIDEOF1909 | Partly Cloudy-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010541 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1249558 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0010227&numberofmonths=24&showchangehistorylog=1 | 17-0010227 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 5823 | 20170118 | 1501 | 1646586 | 1256 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 6280 | 39.2267 | -123.7335 | 31760ALBIONRIDGERD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010227 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Multi-Fault | 1249232 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0010088&numberofmonths=24&showchangehistorylog=1 | 17-0010088 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | JUMPER | WIREDOWN3POLESSOUTHOF87707 | 20170118 | 1425 | s1249472 | 388 | Distribution Circuit | Vegetation | Tree - fell into line | 177 | 68466 | 39.6326 | -123.7822 | 3PSOF87707 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010088 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1249472 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0010049&numberofmonths=24&showchangehistorylog=1 | 17-0010049 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | RECLOSER | 6054 | 20170118 | 1458 | 1646619 | 1532 | Distribution Circuit | Vegetation | Tree - branch fell on line | 565 | 62542 | 40.2854 | -123.8367 | 3SPANSLDSIDEOF80565ONTHEMAINLINEONJAYSMIITHRD | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010049 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Multi-Fault | 1249083 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0010015&numberofmonths=24&showchangehistorylog=1 | 17-0010015 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 6084 | 20170118 | 1428 | 1646451 | 1851 | Distribution Circuit | Vegetation | Tree - fell into line | 117 | 132061 | 40.0621 | -123.9619 | 16565BricelandThornRDmeter1008027538 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010015 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Multi-Fault | 1249061 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0010411&numberofmonths=24&showchangehistorylog=1 | 17-0010411 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 4651 | 20170118 | 1419 | 1648814 | 1646 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 8230 | 40.0322 | -123.953 | BryanJoeK3426T2067EOLonco4651meter1008974096 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010411 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1249428 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0010184&numberofmonths=24&showchangehistorylog=1 | 17-0010184 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | JUMPER | OJFLYINGBELL1PNOF8519 | 20170118 | 1643 | 1647122 | 1570 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 7805 | 38.6522 | -123.3988 | 8519 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010184 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1249192 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0009905&numberofmonths=24&showchangehistorylog=1 | 17-0009905 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1112 | 42841112 | FUSE | 7291 | 20170118 | 1154 | 1646083 | 326 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 652 | 38.8171 | -123.5992 | TAPTOWESTOF7291 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0009905 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1248997 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0010236&numberofmonths=24&showchangehistorylog=1 | 17-0010236 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1101 | 42601101 | FUSE | 1311 | 20170118 | 1541 | 1646802 | 1170 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 15210 | 39.007 | -123.4158 | 2SPANSSSOFMTRA22023 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010236 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1249240 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0009930&numberofmonths=24&showchangehistorylog=1 | 17-0009930 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE | 7527 | 20170118 | 1047 | 1646050 | 1473 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 2946 | 38.9093 | -123.6346 | 1SPANLDSIDEOFFUCO7527 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0009930 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Multi-Fault | 1249010 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0010007&numberofmonths=24&showchangehistorylog=1 | 17-0010007 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | RECLOSER | 83354 | 20170118 | 1254 | 1646194 | 568 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 24864 | 38.8808 | -123.6621 | 1PNOF96625COS96625 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010007 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1249055 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0009995&numberofmonths=24&showchangehistorylog=1 | 17-0009995 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1103 | 42661103 | FUSE | 3651 | 20170118 | 1217 | 1646119 | 1755 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 27209 | 39.3784 | -123.2935 | MTR1006274091 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0009995 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Three Phase Fault | 1249048 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0010660&numberofmonths=24&showchangehistorylog=1 | 17-0010660 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 551 | 20170119 | 253 | 1649783 | 682 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 11594 | 39.3266 | -123.7929 | 44451SURFWOODDR | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010660 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1249678 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0010867&numberofmonths=24&showchangehistorylog=1 | 17-0010867 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | JUMPER | WIREDOWNNO4471 | 20170119 | 956 | 1650538 | 404 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 13453 | 38.8708 | -123.6535 | 1NO4471 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010867 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1249821 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011511&numberofmonths=24&showchangehistorylog=1 | 17-0011511 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT SEWARD-1121 | 192321121 | FUSE | 1803 | 20170120 | 808 | 1653293 | 597 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 24477 | 40.2013 | -123.4814 | RapichRobertK1987T199528spansloadside1803 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011511 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1250385 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011329&numberofmonths=24&showchangehistorylog=1 | 17-0011329 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 3789 | 20170120 | 749 | 1652023 | 362 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 724 | 40.2829 | -123.8339 | BryanJoeK3426T2067tsarnasrd4spldsdco3789 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011329 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1250226 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011322&numberofmonths=24&showchangehistorylog=1 | 17-0011322 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | FUSE | 2823 | 20170120 | 724 | 1653014 | 312 | Distribution Circuit | Vegetation | Tree - fell into line | 251 | 78312 | 39.3949 | -123.3133 | GALLETTITIMTREETRHOUGHLINENOEASTHILLRDBRIDGENOFCO7665 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011322 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1250221 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012563&numberofmonths=24&showchangehistorylog=1 | 17-0012563 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | RECLOSER | 31304 | 20170121 | 2320 | 1657760 | 2170 | Distribution Circuit | Vegetation | Tree - fell into line | 134 | 121680 | 39.4151 | -123.7704 | 4SPANSLDSIDEOFREGS40111SPANLDSIDEOF4011ONHARDTAP | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012563 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1251385 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012042&numberofmonths=24&showchangehistorylog=1 | 17-0012042 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT SEWARD-1121 | 192321121 | FUSE | 7333 | 20170121 | 1200 | 1656548 | 1776 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1776 | 40.1771 | -123.4626 | 4SPANSLDSIDEOF7333 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012042 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1250856 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011880&numberofmonths=24&showchangehistorylog=1 | 17-0011880 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 3769 | 20170121 | 54 | 1655381 | 603 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 9045 | 40.2642 | -123.8276 | 3SPANSLDSIDEOFMTR1010157961 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011880 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1250707 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012530&numberofmonths=24&showchangehistorylog=1 | 17-0012530 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | RECLOSER | 445166 | 20170121 | 2151 | 1657406 | 1192 | Distribution Circuit | Vegetation | Tree - branch fell on line | 317 | 286999 | 38.6937 | -123.4237 | JONESMICHAELCOs1511 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0012530 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1251349 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012978&numberofmonths=24&showchangehistorylog=1 | 17-0012978 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1112 | 42841112 | FUSE | 9289 | 20170121 | 2316 | 1657750 | 947 | Distribution Circuit | Vegetation | Tree - branch fell on line | 54 | 36615 | 38.8134 | -123.5785 | LASTSPANATEOLAT1STHARDTAPLDSIDEOF9289 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012978 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1251800 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011878&numberofmonths=24&showchangehistorylog=1 | 17-0011878 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LOW GAP-1101 | 192411101 | RECLOSER | 4086 | 20170121 | 333 | 1655460 | 827 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 41570 | 40.3025 | -123.3539 | 8SPANSLDSIDEOFFU4081 | Overcast-Fog-Snow-32-90 F | Pole-Wood | Broken, wire on ground | 17-0011878 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1250705 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012000&numberofmonths=24&showchangehistorylog=1 | 17-0012000 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LOW GAP-1101 | 192411101 | FUSE | 4137 | 20170121 | 928 | 1656470 | 246 | Distribution Circuit | Environmental/External | Ice or snow | 72 | 17712 | 40.4495 | -123.5271 | MTR1008279950 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012000 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1250817 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012120&numberofmonths=24&showchangehistorylog=1 | 17-0012120 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LOW GAP-1101 | 192411101 | FUSE | 4185 | 20170121 | 730 | 1655765 | 645 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 14 | 9030 | 40.2414 | -123.3121 | 1SPANLDSOFUCO4185 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012120 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1250934 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012951&numberofmonths=24&showchangehistorylog=1 | 17-0012951 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 90655 | 20170122 | 712 | 1659444 | 421 | Distribution Circuit | Vegetation | Tree - fell into line | 145 | 21229 | 39.3884 | -123.7762 | 16654MITCHELLCREEK | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012951 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1251771 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013022&numberofmonths=24&showchangehistorylog=1 | 17-0013022 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | JUMPER | HOTWIREDOWN | 20170122 | 914 | 1660366 | 568 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2272 | 39.3861 | -123.7999 | BET2ND3RDPOLELDSIDEOF5579 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013022 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Force Out | 1251843 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012937&numberofmonths=24&showchangehistorylog=1 | 17-0012937 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 1815 | 20170122 | 133 | 1658053 | 1967 | Distribution Circuit | Vegetation | Tree - branch fell on line | 29 | 57043 | 39.868 | -123.7169 | LDSIDEOFFU1815 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012937 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1251758 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013117&numberofmonths=24&showchangehistorylog=1 | 17-0013117 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 8223 | 20170122 | 736 | 1659534 | 654 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2616 | 38.7 | -123.425 | SINGLEPHASEHARDTAPLDSIDEOF8223 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013117 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1251936 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013134&numberofmonths=24&showchangehistorylog=1 | 17-0013134 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1112 | 42841112 | FUSE | 7287 | 20170122 | 744 | 1659576 | 374 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 6358 | 38.8139 | -123.5856 | ENDOFTAP | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013134 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Force Out | 1251950 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013256&numberofmonths=24&showchangehistorylog=1 | 17-0013256 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | HARRIS-1109 | 192431109 | FUSE | 6259 | 20170122 | 1343 | 1661587 | 168 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 2856 | 40.7709 | -124.0722 | LDSIDEOF6259 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013256 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1252071 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012851&numberofmonths=24&showchangehistorylog=1 | 17-0012851 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LOW GAP-1101 | 192411101 | RECLOSER | 4086 | 20170122 | 646 | 1659328 | 2133 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 123714 | 40.3025 | -123.3539 | 18LDSIDEOF5159FLOATERLDSIDEOF4081 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012851 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1251674 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013525&numberofmonths=24&showchangehistorylog=1 | 17-0013525 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | NEWBURG-1133 | 192151133 | FUSE | 4401 | 20170122 | 2223 | 1662544 | 692 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 3460 | 40.6018 | -124.1427 | EOLON3PHASE | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013525 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1252343 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012794&numberofmonths=24&showchangehistorylog=1 | 17-0012794 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | RECLOSER | 474 | 20170122 | 205 | 1658149 | 546 | Distribution Circuit | Equipment Failure/Involved | Overhead | 217 | 118482 | 38.9128 | -123.6795 | 1STSPANLDSIDEOF6415ONMAINLINE | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0012794 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Multi-Fault | 1251616 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013057&numberofmonths=24&showchangehistorylog=1 | 17-0013057 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE | 2653 | 20170122 | 1041 | 1660436 | 1540 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 12320 | 38.932 | -123.6916 | 43601HARRISRANCHRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013057 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1251877 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013189&numberofmonths=24&showchangehistorylog=1 | 17-0013189 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE | 8989 | 20170122 | 1154 | 1660722 | 1492 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 8952 | 38.8852 | -123.6375 | 1ST2SPANSBEYOND8989 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0013189 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1252000 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013081&numberofmonths=24&showchangehistorylog=1 | 17-0013081 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | RIO DELL-1101 | 192251101 | FUSE | 1907 | 20170122 | 1144 | 1660670 | 340 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 5440 | 40.4872 | -124.2599 | 23SPANSLDSIDEOF1907 | Partly Cloudy-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013081 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1251900 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013094&numberofmonths=24&showchangehistorylog=1 | 17-0013094 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | UPPER LAKE-1101 | 42871101 | FUSE | 4773 | 20170122 | 1204 | 1660776 | 196 | Distribution Circuit | Vegetation | Tree - branch fell on line | 10 | 1960 | 39.1714 | -122.8813 | MTR1008153315 | Overcast-Below 32 F | Conductor, Overhead | Broken, wire on object | 17-0013094 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Force Out | 1251913 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012601&numberofmonths=24&showchangehistorylog=1 | 17-0012601 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1104 | 42661104 | FUSE | 5365 | 20170122 | 151 | 1658097 | 705 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 3525 | 39.4472 | -123.4264 | 5SPANSLDSIDEOF5365 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012601 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1251423 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013845&numberofmonths=24&showchangehistorylog=1 | 17-0013845 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | BRIDGEVILLE-1102 | 192461102 | FUSE | 3711 | 20170123 | 1204 | 1663955 | 649 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 649 | 40.4217 | -123.8072 | 2SPANSSSOFMTR1008025117 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0013845 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1252615 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013631&numberofmonths=24&showchangehistorylog=1 | 17-0013631 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 56048 | 20170123 | 750 | 1663109 | 507 | Distribution Circuit | Vegetation | Tree - branch fell on line | 117 | 64904 | 40.1477 | -124.0196 | 200FTLOADSIDEOF370544SPANSLOADSIDEOF37054 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013631 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1252452 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013701&numberofmonths=24&showchangehistorylog=1 | 17-0013701 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1103 | 42661103 | FUSE | 2853 | 20170123 | 845 | 1663288 | 423 | Distribution Circuit | Vegetation | Tree - branch fell on line | 93 | 32239 | 39.4683 | -123.3974 | MTR1007091923 | Clear-32-90 F | Insulator | Broken, wire on ground | 17-0013701 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1252503 | INS | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013827&numberofmonths=24&showchangehistorylog=1 | 17-0013827 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1103 | 42661103 | JUMPER | OJS2SPANSSMTR1008761141 | 20170123 | 845 | 1664091 | 555 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 555 | 39.4799 | -123.4115 | RegeRobert110228970SHERWOODRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013827 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Multi-Fault | 1252602 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018160&numberofmonths=24&showchangehistorylog=1 | 17-0018160 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | RECLOSER | 1260 | 20170207 | 401 | 1677894 | 488 | Distribution Circuit | Vegetation | Tree - branch fell on line | 95 | 37336 | 39.1293 | -123.7112 | LDSIDEOFFU5931ONMAINLINEmm571 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018160 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1256023 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018345&numberofmonths=24&showchangehistorylog=1 | 17-0018345 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 801579 | 20170207 | 410 | 1677713 | 874 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 3496 | 39.5229 | -123.7585 | 1SPANOF6CDOWNJUSTLDSIDEOFCUTOUTS | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018345 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1256183 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018464&numberofmonths=24&showchangehistorylog=1 | 17-0018464 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 6069 | 20170207 | 316 | 1679710 | 2024 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 41580 | 39.6578 | -123.7827 | 2SPANSLDSOSBCO91173 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018464 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Three Phase Fault | 1256275 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018588&numberofmonths=24&showchangehistorylog=1 | 17-0018588 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 3173 | 20170207 | 1025 | 1679718 | 1565 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3130 | 39.6337 | -123.7825 | BET2ND3RDPOLELDSIDEOF3173 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018588 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1256359 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018313&numberofmonths=24&showchangehistorylog=1 | 17-0018313 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 551 | 20170207 | 35 | 1677632 | 925 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 15725 | 39.3266 | -123.7929 | 44901SURFWOODDRMENDOCINO | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018313 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1256150 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018615&numberofmonths=24&showchangehistorylog=1 | 17-0018615 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3071 | 20170207 | 1152 | 1680018 | 163 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 163 | 39.4051 | -123.7234 | 1STSPANLDSOFUCO3071 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018615 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1256386 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018704&numberofmonths=24&showchangehistorylog=1 | 17-0018704 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3321 | 20170207 | 717 | 1679122 | 707 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2828 | 39.4049 | -123.7415 | 1SPANLDSOFUCO3321 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018704 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1256457 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018052&numberofmonths=24&showchangehistorylog=1 | 17-0018052 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT SEWARD-1121 | 192321121 | RECLOSER | 1690 | 20170207 | 231 | 1677429 | 606 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 53694 | 40.1677 | -123.6109 | 2SPANSLSSIDEOF4983ONMAINLINE | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018052 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1255906 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018744&numberofmonths=24&showchangehistorylog=1 | 17-0018744 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | RECLOSER | 2026 | 20170207 | 2130 | 1679549 | 806 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 7254 | 39.8515 | -123.7181 | LDSIDE18792SPANSSSOFEOL | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018744 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Force Out | 1256491 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018949&numberofmonths=24&showchangehistorylog=1 | 17-0018949 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 1879 | 20170207 | 943 | 1681736 | 1900 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 30400 | 39.8178 | -123.7635 | 2SPANSFROMEOL | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018949 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1256652 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018352&numberofmonths=24&showchangehistorylog=1 | 17-0018352 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE | 2747 | 20170207 | 326 | 1677594 | 879 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 18459 | 39.678 | -123.495 | 1350LAKESIDEDR | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018352 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Three Phase Fault | 1256189 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018452&numberofmonths=24&showchangehistorylog=1 | 17-0018452 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE | 7093 | 20170207 | 843 | 1678957 | 346 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 8996 | 39.6446 | -123.4783 | 42501TWINPINESCIRCLE | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018452 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1256266 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018425&numberofmonths=24&showchangehistorylog=1 | 17-0018425 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | MIDDLETOWN-1101 | 43141101 | FUSE | 78083 | 20170207 | 825 | 1678936 | 330 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 1490 | 38.7168 | -122.6195 | 2POLESNOF1493 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018425 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1256249 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018119&numberofmonths=24&showchangehistorylog=1 | 17-0018119 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1102 | 42601102 | RECLOSER | 1308 | 20170207 | 226 | 1677401 | 872 | Distribution Circuit | Vegetation | Tree - fell into line | 292 | 206364 | 39.1863 | -123.5804 | 7400FLYNNCREEK | Overcast-Fog-Heavy Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0018119 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1255981 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018179&numberofmonths=24&showchangehistorylog=1 | 17-0018179 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1104 | 42661104 | RECLOSER | 34008 | 20170207 | 359 | 1677687 | 542 | Distribution Circuit | Vegetation | Tree - fell into line | 298 | 68528 | 39.4366 | -123.3893 | 2SPANSLDSIDE6261TWD3769 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018179 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1256042 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018490&numberofmonths=24&showchangehistorylog=1 | 17-0018490 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1104 | 42661104 | FUSE | 5415 | 20170207 | 546 | 1677989 | 888 | Distribution Circuit | Vegetation | Tree - branch fell on line | 22 | 19536 | 39.3713 | -123.3607 | 4501MUIRMILLRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018490 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1256300 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018311&numberofmonths=24&showchangehistorylog=1 | 17-0018311 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | RECLOSER | 2936 | 20170207 | 431 | 1678835 | 1698 | Distribution Circuit | Vegetation | Tree - fell into line | 290 | 475244 | 40.8665 | -123.5144 | 13SPANSLDSIDEOFFUCO2963 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018311 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Multi-Fault | 1256149 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0019388&numberofmonths=24&showchangehistorylog=1 | 17-0019388 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE | 5689 | 20170209 | 818 | 1682859 | 407 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 2035 | 38.7222 | -123.3954 | 2POLESLDSIDEOF5689 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019388 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1256933 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0019580&numberofmonths=24&showchangehistorylog=1 | 17-0019580 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE | 6073 | 20170209 | 1159 | 1683246 | 1745 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 12215 | 38.658 | -123.2886 | 8SPANSLDSIDEOF6073 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019580 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Three Phase Fault | 1257056 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0019302&numberofmonths=24&showchangehistorylog=1 | 17-0019302 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | EEL RIVER-1103 | 192381103 | FUSE | 6527 | 20170209 | 744 | 1682821 | 279 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 1674 | 40.5487 | -124.3536 | 6SPANSFROMEOL | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019302 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1256894 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0019380&numberofmonths=24&showchangehistorylog=1 | 17-0019380 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 94127 | 20170209 | 915 | 1682966 | 405 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2025 | 39.2277 | -123.7423 | 1STSPANLDSIDEOFFUCO94127 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019380 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1256930 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0019338&numberofmonths=24&showchangehistorylog=1 | 17-0019338 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 3163 | 20170209 | 909 | 1683016 | 321 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 12519 | 39.6521 | -123.7826 | 23451WAGESCREEKRD | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019338 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1256910 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0019577&numberofmonths=24&showchangehistorylog=1 | 17-0019577 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 1931 | 20170209 | 1428 | 1683640 | 465 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 4185 | 39.7372 | -123.811 | 8SLSOF1931 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019577 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1257054 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0019589&numberofmonths=24&showchangehistorylog=1 | 17-0019589 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3961 | 20170209 | 1608 | 1683856 | 2817 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 43631 | 39.3599 | -123.647 | MILEMARKER1125HI20 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019589 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1257063 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0019336&numberofmonths=24&showchangehistorylog=1 | 17-0019336 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | RECLOSER | 6054 | 20170209 | 1009 | 1683053 | 234 | Distribution Circuit | Vegetation | Tree - branch fell on line | 551 | 40158 | 40.2854 | -123.8367 | MelloAdamK4736T1963lr92324 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019336 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1256908 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0019322&numberofmonths=24&showchangehistorylog=1 | 17-0019322 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1103 | 192221103 | FUSE | 2505 | 20170209 | 439 | 1682851 | 2216 | Distribution Circuit | Equipment Failure/Involved | Overhead | 35 | 77560 | 40.3068 | -124.2964 | 13SPANSLDSIDEOF2505 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019322 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1256902 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0019450&numberofmonths=24&showchangehistorylog=1 | 17-0019450 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1103 | 192221103 | RECLOSER | 11032 | 20170209 | 1303 | 1683446 | 1859 | Distribution Circuit | Vegetation | Tree - fell into line | 2653 | 1247182 | 40.1033 | -123.7926 | 4SPANSSSOFLR1510 | Overcast-Heavy Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0019450 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Multi-Fault | 1256974 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0019494&numberofmonths=24&showchangehistorylog=1 | 17-0019494 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | RECLOSER | 445166 | 20170209 | 1223 | 1683371 | 507 | Distribution Circuit | Vegetation | Tree - fell into line | 315 | 65541 | 38.6937 | -123.4237 | 1SPANSSOF483 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019494 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Multi-Fault | 1257002 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0019229&numberofmonths=24&showchangehistorylog=1 | 17-0019229 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | RECLOSER | 37202 | 20170209 | 35 | 1682655 | 883 | Distribution Circuit | Environmental/External | Flood/Erosion | 64 | 56512 | 41.1894 | -123.7104 | MURDOUGHJEREMY500ftnorthoftullycreekrd | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019229 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1256849 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0019960&numberofmonths=24&showchangehistorylog=1 | 17-0019960 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1101 | 42681101 | RECLOSER | 2026 | 20170209 | 2346 | 1684385 | 2504 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 62600 | 39.8515 | -123.7181 | 2SPANSSSOFFUCO1879 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019960 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1257352 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0019209&numberofmonths=24&showchangehistorylog=1 | 17-0019209 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1101 | 42601101 | FUSE | 821 | 20170209 | 31 | 1682652 | 747 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 24051 | 39.0089 | -123.3837 | MTR1009790402 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019209 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1256822 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0019288&numberofmonths=24&showchangehistorylog=1 | 17-0019288 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | FUSE | 1659 | 20170209 | 728 | 1682804 | 431 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 20257 | 39.3879 | -123.3241 | MTR1006279994 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019288 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1256884 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0019395&numberofmonths=24&showchangehistorylog=1 | 17-0019395 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1104 | 42661104 | FUSE | 8831 | 20170209 | 1018 | 1683066 | 438 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 13578 | 39.4626 | -123.4332 | 4691BLUELAKERD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019395 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1256940 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0022268&numberofmonths=24&showchangehistorylog=1 | 17-0022268 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 5651 | 20170217 | 1202 | 1695273 | 474 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2448 | 39.2768 | -123.7905 | LASTSPANATEOL | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022268 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1259339 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0022153&numberofmonths=24&showchangehistorylog=1 | 17-0022153 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1112 | 42841112 | FUSE | 4427 | 20170217 | 1101 | 1694634 | 319 | Distribution Circuit | Vegetation | Tree - fell into line | 82 | 26158 | 38.8168 | -123.5843 | MTR1008029327 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022153 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1259232 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0022229&numberofmonths=24&showchangehistorylog=1 | 17-0022229 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1112 | 42841112 | RECLOSER | 1294 | 20170217 | 1157 | 1695296 | 773 | Distribution Circuit | Vegetation | Tree - fell into line | 544 | 118435 | 38.8037 | -123.5835 | 4475FUSES | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0022229 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Three Phase Fault | 1259304 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0022109&numberofmonths=24&showchangehistorylog=1 | 17-0022109 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | MAPLE CREEK-1101 | 192101101 | FUSE | 6529 | 20170217 | 1127 | 1694961 | 178 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 534 | 40.7486 | -123.8673 | 14SPANSLOADSIDEOF6529 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022109 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1259193 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0022876&numberofmonths=24&showchangehistorylog=1 | 17-0022876 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | CARLOTTA-1121 | 192291121 | OTHER | WIREDOWN4SLDOF5841 | 20170218 | 351 | 1698869 | 414 | Distribution Circuit | Vegetation | Tree - fell into line | 230 | 27697 | 40.5194 | -124.0237 | 4SLDOF5841 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022876 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1259888 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0022905&numberofmonths=24&showchangehistorylog=1 | 17-0022905 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 7415 | 20170218 | 424 | 1699084 | 570 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2850 | 39.2271 | -123.7448 | 1SPANLOADSIDEOF7415 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022905 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1259919 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0022935&numberofmonths=24&showchangehistorylog=1 | 17-0022935 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 1687 | 20170218 | 649 | 1699000 | 641 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 3846 | 39.3965 | -123.7815 | 3SLSOF1687 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022935 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1259951 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0022959&numberofmonths=24&showchangehistorylog=1 | 17-0022959 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 6793 | 20170218 | 408 | 1698868 | 442 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 3536 | 39.3848 | -123.7865 | 31360TURNER | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022959 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1259974 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0022953&numberofmonths=24&showchangehistorylog=1 | 17-0022953 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE | 2345 | 20170218 | 805 | 1699127 | 585 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1755 | 38.8336 | -123.5647 | 3SPANSLOADSIDEOF2345 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022953 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1259968 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023003&numberofmonths=24&showchangehistorylog=1 | 17-0023003 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER | 37506 | 20170218 | 1019 | 1699420 | 822 | Distribution Circuit | Vegetation | Tree - branch fell on line | 89 | 35363 | 39.4831 | -123.3611 | 3SPANSSSOF65561TAPWIREDOWN3SSOURCESIDEMTR888N52 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023003 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1260019 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024976&numberofmonths=24&showchangehistorylog=1 | 17-0024976 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE | 5113 | 20170220 | 2050 | 1708048 | 1079 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 4814 | 38.7189 | -123.38 | CGC216064038835 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024976 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1261936 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023957&numberofmonths=24&showchangehistorylog=1 | 17-0023957 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 5651 | 20170220 | 1641 | 1704236 | 1254 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 40192 | 39.2768 | -123.7905 | FelicichDavidat8175nhwy1mtr1009745022 | Clear-32-90 F | Conductor, Overhead | On Ground | 17-0023957 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1260929 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024078&numberofmonths=24&showchangehistorylog=1 | 17-0024078 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | SWITCH | 1599 | 20170220 | 1953 | 1705782 | 1028 | Distribution Circuit | Vegetation | Tree - fell into line | 122 | 35879 | 40.2197 | -123.8089 | RapichRobertK1987T1995nearmtr1006750720 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024078 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1261043 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023655&numberofmonths=24&showchangehistorylog=1 | 17-0023655 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | RECLOSER | 445166 | 20170220 | 322 | 1702367 | 841 | Distribution Circuit | Equipment Failure/Involved | Overhead | 314 | 264074 | 38.6937 | -123.4237 | JUSTSOF1367 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023655 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Multi-Fault | 1260658 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023732&numberofmonths=24&showchangehistorylog=1 | 17-0023732 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1112 | 42841112 | OTHER | 6591 | 20170220 | 940 | 1702931 | 320 | Distribution Circuit | Environmental/External | Flood/Erosion | 1 | 320 | 38.7623 | -123.5139 | FIRSTOVERHEADSECTIONBEYONDFUCO6591 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023732 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1260723 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023979&numberofmonths=24&showchangehistorylog=1 | 17-0023979 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | RECLOSER | 3174 | 20170220 | 1741 | 1705017 | 1467 | Distribution Circuit | Vegetation | Tree - branch fell on line | 133 | 156970 | 41.2232 | -123.6551 | MM2026WIREDOWN10SPANSLDSIDE3174 | Partly Cloudy-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023979 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1260950 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025064&numberofmonths=24&showchangehistorylog=1 | 17-0025064 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | SWITCH | 3155 | 20170220 | 1741 | 1708350 | 1745 | Distribution Circuit | Vegetation | Tree - fell into line | 465 | 811425 | 41.281 | -123.5864 | 13SPANSLDSIDEOF3155 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025064 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1262002 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024064&numberofmonths=24&showchangehistorylog=1 | 17-0024064 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | KONOCTI-1102 | 43311102 | RECLOSER | 532 | 20170220 | 1856 | 1705418 | 90 | Distribution Circuit | Vegetation | Tree - fell into line | 282 | 25380 | 38.8576 | -122.7221 | 1SPANLDSIDEOF532 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024064 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1261030 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024320&numberofmonths=24&showchangehistorylog=1 | 17-0024320 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | MIDDLETOWN-1101 | 43141101 | TRIP-SAVER | 1079 | 20170220 | 2034 | 1705947 | 1508 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 48324 | 38.8145 | -122.7088 | OAKSTMULTIPLELOCATIONS | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0024320 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1261284 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024838&numberofmonths=24&showchangehistorylog=1 | 17-0024838 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | MIDDLETOWN-1101 | 43141101 | FUSE | 1073 | 20170220 | 2348 | 1706765 | 2384 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 50064 | 38.708 | -122.6097 | 4SPANSLDSIDEOF1073 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0024838 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1261807 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024905&numberofmonths=24&showchangehistorylog=1 | 17-0024905 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | MIDDLETOWN-1101 | 43141101 | FUSE | 78083 | 20170220 | 2119 | 1706142 | 1459 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 8754 | 38.7168 | -122.6195 | 23390SHADYGROVE | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0024905 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Three Phase Fault | 1261879 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024560&numberofmonths=24&showchangehistorylog=1 | 17-0024560 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1101 | 42601101 | RECLOSER | 37222 | 20170220 | 2125 | 1706809 | 863 | Distribution Circuit | Vegetation | Tree - fell into line | 149 | 44345 | 38.9147 | -123.272 | MTR5000119682 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024560 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1261722 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023733&numberofmonths=24&showchangehistorylog=1 | 17-0023733 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | UKIAH-1115 | 42771115 | FUSE | 3405 | 20170220 | 829 | 1702742 | 716 | Distribution Circuit | Vegetation | Tree - fell into line | 129 | 27302 | 39.1429 | -123.1727 | 1990RIDGEROAD | Partly Cloudy-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023733 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1260724 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023880&numberofmonths=24&showchangehistorylog=1 | 17-0023880 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1104 | 42661104 | RECLOSER | 504 | 20170220 | 1440 | 1703577 | 1390 | Distribution Circuit | Vegetation | Tree - fell into line | 938 | 271604 | 39.4048 | -123.3854 | ESPINOLACHRISTOPHER1spanssof3769onmainline | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023880 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1260858 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024132&numberofmonths=24&showchangehistorylog=1 | 17-0024132 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1104 | 42661104 | FUSE | 9215 | 20170220 | 1439 | 1706083 | 1645 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 13160 | 39.4348 | -123.3784 | 2POLESNORTHOF9215 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024132 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Force Out | 1261096 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025205&numberofmonths=24&showchangehistorylog=1 | 17-0025205 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | HUMBOLDT BAY-1102 | 192341102 | FUSE | 5301 | 20170221 | 1231 | 1708531 | 266 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1064 | 40.7008 | -124.138 | 3SPANSLDSIDEOF5301 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025205 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1262106 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024934&numberofmonths=24&showchangehistorylog=1 | 17-0024934 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | MIDDLETOWN-1101 | 43141101 | FUSE | 4539 | 20170221 | 534 | 1707450 | 481 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1924 | 38.7379 | -122.6424 | 1SPANLOADSIDEOF4539 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024934 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1261908 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025699&numberofmonths=24&showchangehistorylog=1 | 17-0025699 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | KONOCTI-1108 | 43311108 | FUSE | 513427 | 20170222 | 1501 | 1710847 | 238 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 5957 | 38.9605 | -122.7095 | WOODARDKYLE10772BorenBega | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025699 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1262502 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025703&numberofmonths=24&showchangehistorylog=1 | 17-0025703 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | POTTER VALLEY P H-1105 | 42281105 | RECLOSER | 1904 | 20170222 | 1450 | 1710908 | 590 | Distribution Circuit | Vegetation | Tree - fell into line | 357 | 62400 | 39.3193 | -123.0944 | MTR1009670719 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025703 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Multi-Fault | 1262506 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0036900&numberofmonths=24&showchangehistorylog=1 | 17-0036900 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ARCATA-1122 | 192021122 | RECLOSER | 4218 | 20170406 | 147 | 1745114 | 586 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 8806 | 40.7595 | -123.9934 | 2SPANSFROM7093TWD6049ONMAINLINE | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0036900 | OH | Sus | 0 | yes | 2017 | APR | Yes | Multi-Fault | 1271254 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037311&numberofmonths=24&showchangehistorylog=1 | 17-0037311 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | OTHER | 23WIRESDOWNMTR1008391365 | 20170406 | 1934 | 1747547 | 1197 | Distribution Circuit | Vegetation | Tree - fell into line | 111 | 129435 | 39.2886 | -123.76 | 42601COMPTCHERD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037311 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1271527 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037320&numberofmonths=24&showchangehistorylog=1 | 17-0037320 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 8127 | 20170406 | 1847 | 1746093 | 1437 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 30177 | 39.3138 | -123.7466 | 41911POWERS | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037320 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1271535 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037983&numberofmonths=24&showchangehistorylog=1 | 17-0037983 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 5087 | 20170406 | 1931 | 1751113 | 1364 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 13640 | 39.2859 | -123.7511 | 2SPANSNO5087 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037983 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1272074 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037112&numberofmonths=24&showchangehistorylog=1 | 17-0037112 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | EEL RIVER-1102 | 192381102 | FUSE | 1929 | 20170406 | 540 | 1745261 | 1760 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 12320 | 40.4616 | -124.3678 | 13SPANSSSOF93155TWD1929 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037112 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1271378 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037472&numberofmonths=24&showchangehistorylog=1 | 17-0037472 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 1719 | 20170406 | 1833 | 1745940 | 2472 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 12360 | 39.2296 | -123.6823 | ESPINOLACHRISTOPHER3loadsideof1719 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037472 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1271687 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037475&numberofmonths=24&showchangehistorylog=1 | 17-0037475 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 6645 | 20170406 | 1910 | 1746107 | 1310 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 15720 | 39.2428 | -123.7707 | 4SPANSLDSIDEOF6645 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037475 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1271691 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037495&numberofmonths=24&showchangehistorylog=1 | 17-0037495 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 3041 | 20170406 | 2029 | 1746809 | 1055 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 31650 | 39.1862 | -123.7002 | 28620NAVARRORIDGERD | Partly Cloudy-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037495 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1271711 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037728&numberofmonths=24&showchangehistorylog=1 | 17-0037728 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 8639 | 20170406 | 1924 | 1746221 | 2544 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 15264 | 39.1218 | -123.5971 | ATMTR101005430528340GREEBWOODROAD | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037728 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Line | 1271923 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0036882&numberofmonths=24&showchangehistorylog=1 | 17-0036882 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 8595 | 20170406 | 25 | 1745025 | 278 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 556 | 39.6272 | -123.7818 | BUCKFEEDINGMTR1009746765 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0036882 | OH | Sus | 42984508 | yes | 2017 | APR | Yes | Line to Ground | 1271234 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037309&numberofmonths=24&showchangehistorylog=1 | 17-0037309 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 6069 | 20170406 | 1902 | 1746177 | 2734 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 78664 | 39.6578 | -123.7827 | ESPINOLACHRISTOPHER3spansss1611 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037309 | OH | Sus | 0 | yes | 2017 | APR | Yes | Three Phase Fault | 1271525 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037511&numberofmonths=24&showchangehistorylog=1 | 17-0037511 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 3015 | 20170406 | 2306 | 1748639 | 2524 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 25240 | 39.5925 | -123.7785 | MTR9H6031 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037511 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1271728 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037500&numberofmonths=24&showchangehistorylog=1 | 17-0037500 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | JUMPER | OJSAT42765CASPARLITTLELAKERD | 20170406 | 1914 | 1749127 | 1476 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1476 | 39.3424 | -123.7757 | 42765CASPARLITTLELAKERD | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037500 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1271718 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0036890&numberofmonths=24&showchangehistorylog=1 | 17-0036890 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1141 | 192311141 | RECLOSER | 95324 | 20170406 | 137 | 1745074 | 516 | Distribution Circuit | Vegetation | Tree - fell into line | 223 | 114508 | 40.284 | -123.8723 | MelloAdamK4736T19631spanload5583 | Partly Cloudy-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0036890 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1271243 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037421&numberofmonths=24&showchangehistorylog=1 | 17-0037421 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | OTHER | 1OF3HOTWIRESDOWN | 20170406 | 2013 | 1748482 | 1090 | Distribution Circuit | Vegetation | Tree - fell into line | 1039 | 975240 | 38.7179 | -123.4564 | ONMAINLINEATCOUTS4351 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037421 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1271634 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037246&numberofmonths=24&showchangehistorylog=1 | 17-0037246 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1112 | 42841112 | RECLOSER | 1294 | 20170406 | 1725 | 1745838 | 2964 | Distribution Circuit | Vegetation | Tree - fell into line | 624 | 166036 | 38.8037 | -123.5835 | ONMAINLINE5819 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037246 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Line | 1271465 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037463&numberofmonths=24&showchangehistorylog=1 | 17-0037463 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1112 | 42841112 | FUSE | 5621 | 20170406 | 2043 | 1747039 | 2393 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 38288 | 38.7797 | -123.5437 | MTR108391872 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037463 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1271677 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0036920&numberofmonths=24&showchangehistorylog=1 | 17-0036920 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | HARRIS-1109 | 192431109 | FUSE | 6671 | 20170406 | 231 | 1745200 | 514 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 7710 | 40.7652 | -124.1072 | 2SPANSLDSIDEOF6671 | Strong Winds-Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0036920 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1271269 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037151&numberofmonths=24&showchangehistorylog=1 | 17-0037151 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 3073 | 20170406 | 1334 | 1745565 | 356 | Distribution Circuit | Vegetation | Tree - fell into line | 170 | 60520 | 41.062 | -123.6942 | 4SPANSLDSIDEOFFUCO3073 | Strong Winds-Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037151 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1271391 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037481&numberofmonths=24&showchangehistorylog=1 | 17-0037481 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | KONOCTI-1102 | 43311102 | FUSE | 2307 | 20170406 | 2204 | 1748190 | 1006 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 39234 | 38.9025 | -122.7558 | 9053HWY175 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037481 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1271697 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0036905&numberofmonths=24&showchangehistorylog=1 | 17-0036905 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LOW GAP-1101 | 192411101 | RECLOSER | 2094 | 20170406 | 256 | 1745167 | 2511 | Distribution Circuit | Vegetation | Tree - fell into line | 304 | 104424 | 40.436 | -123.4882 | 6SPANSEASTOF4107 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0036905 | OH | Sus | 0 | yes | 2017 | APR | Yes | Three Phase Fault | 1271259 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037077&numberofmonths=24&showchangehistorylog=1 | 17-0037077 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | MAPLE CREEK-1101 | 192101101 | FUSE | 5917 | 20170406 | 924 | 1745327 | 656 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 656 | 40.7493 | -123.8674 | 7SPANSLDSIDEOF5917 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037077 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1271357 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037181&numberofmonths=24&showchangehistorylog=1 | 17-0037181 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | MIDDLETOWN-1101 | 43141101 | FUSE | 4165 | 20170406 | 1244 | 1745500 | 257 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 771 | 38.8429 | -122.7499 | 2SPANSLDSIDEOF4165 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037181 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1271405 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037415&numberofmonths=24&showchangehistorylog=1 | 17-0037415 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | MIDDLETOWN-1101 | 43141101 | TRIP-SAVER | 1325 | 20170406 | 2101 | 1747398 | 851 | Distribution Circuit | Vegetation | Tree - fell into line | 97 | 82547 | 38.876 | -122.7753 | MTR1008654528 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037415 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1271628 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037203&numberofmonths=24&showchangehistorylog=1 | 17-0037203 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | FUSE | 3807 | 20170406 | 1543 | 1745780 | 555 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 32745 | 39.4556 | -123.2434 | 6POLESLDSIDEOFSINGLEPHASETAPFEEDINGMTR1006730008ONTHEMAINLINE | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0037203 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Line | 1271424 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037342&numberofmonths=24&showchangehistorylog=1 | 17-0037342 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER | 91948 | 20170406 | 2056 | 1747345 | 1333 | Distribution Circuit | Vegetation | Tree - fell into line | 119 | 57121 | 39.4275 | -123.3154 | 4SOFMTR1006279111 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037342 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1271554 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037441&numberofmonths=24&showchangehistorylog=1 | 17-0037441 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1103 | 42661103 | FUSE | 3651 | 20170406 | 2109 | 1747443 | 1131 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 19227 | 39.3784 | -123.2935 | 7SPANSSSOFT1420 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037441 | OH | Sus | 0 | yes | 2017 | APR | Yes | Three Phase Fault | 1271655 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037531&numberofmonths=24&showchangehistorylog=1 | 17-0037531 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1103 | 42661103 | FUSE | 8049 | 20170406 | 2132 | 1747803 | 1279 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2543 | 39.5043 | -123.4563 | 25SPANSSEOF8049 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037531 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1271749 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037272&numberofmonths=24&showchangehistorylog=1 | 17-0037272 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1104 | 42661104 | FUSE | 8831 | 20170406 | 1829 | 1745935 | 1444 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 8287 | 39.4626 | -123.4332 | 4SPANSLDSIDEOF7797 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037272 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Line | 1271492 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037941&numberofmonths=24&showchangehistorylog=1 | 17-0037941 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 7343 | 20170407 | 1407 | 1750166 | 208 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 2704 | 39.3111 | -123.7758 | 2SPANSLOADSIDEOF7343 | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0037941 | OH | Sus | 0 | yes | 2017 | APR | Yes | Force Out | 1272050 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037706&numberofmonths=24&showchangehistorylog=1 | 17-0037706 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | EEL RIVER-1102 | 192381102 | FUSE | 1909 | 20170407 | 17 | 1748995 | 938 | Distribution Circuit | Vegetation | Tree - branch fell on line | 24 | 22512 | 40.5115 | -124.1597 | 5SPANSLDSIDEOF1909 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037706 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Line | 1271908 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0038023&numberofmonths=24&showchangehistorylog=1 | 17-0038023 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT SEWARD-1121 | 192321121 | FUSE | 1659 | 20170407 | 743 | 1749889 | 1832 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 7328 | 40.1631 | -123.616 | 9SPANLDSIDEOFFUCO1659 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0038023 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1272096 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037967&numberofmonths=24&showchangehistorylog=1 | 17-0037967 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | OTHER | WIREDOWNCAPBK884 | 20170407 | 1423 | 1751068 | 2802 | Distribution Circuit | Vegetation | Tree - fell into line | 2452 | 132368 | 38.6844 | -123.4254 | MoonrakerandHwy1CAPBK884 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037967 | OH | Sus | 0 | yes | 2017 | APR | Yes | Open Circuit | 1272065 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037815&numberofmonths=24&showchangehistorylog=1 | 17-0037815 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 654897 | 20170407 | 717 | 1749779 | 1847 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 4145 | 41.1882 | -123.7056 | 3SPANSSSOFMTR1008859392 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037815 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Line | 1271982 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0038106&numberofmonths=24&showchangehistorylog=1 | 17-0038106 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | UPPER LAKE-1101 | 42871101 | RECLOSER | 1276 | 20170407 | 1903 | 1751575 | 888 | Distribution Circuit | Vegetation | Tree - fell into line | 291 | 127434 | 39.1586 | -122.989 | 5680BLUELAKERD | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0038106 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1272164 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0042022&numberofmonths=24&showchangehistorylog=1 | 17-0042022 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 1949 | 20170421 | 1424 | 1764233 | 759 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 3795 | 40.2283 | -123.7818 | 2SPANSLDSIDEOF1949 | Clear-32-90 F | Conductor, Overhead | On Ground | 17-0042022 | OH | Sus | 42999178 | No | 2017 | APR | Yes | Line to Ground | 1275159 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0056092&numberofmonths=24&showchangehistorylog=1 | 17-0056092 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT SEWARD-1121 | 192321121 | FUSE | 1837 | 20170618 | 1056 | 1807649 | 198 | Distribution Circuit | 3rd Party | Vehicle | 6 | 1188 | 40.2029 | -123.4817 | RUTHZENIARD | Clear-Heat Wave-32-90 F | Pole-Wood | Broken, wire on ground | 17-0056092 | OH | Sus | 0 | yes | 2017 | JUN | Yes | Multi-Fault | 1285577 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0085214&numberofmonths=24&showchangehistorylog=1 | 17-0085214 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | HIGHLANDS-1103 | 43361103 | FUSE | 7117 | 20171008 | 2018 | 1893966 | 1293 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 67236 | 38.8682 | -122.623 | PEARSONPAUL2spansloadsifucos711713171hwy29 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085214 | OH | Sus | 31355575 | yes | 2017 | OCT | Yes | Line to Line | 1306660 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0085739&numberofmonths=24&showchangehistorylog=1 | 17-0085739 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | MIDDLETOWN-1101 | 43141101 | FUSE | 3587 | 20171008 | 2254 | 1894140 | 2451 | Distribution Circuit | Vegetation | Tree - fell into line | 97 | 186751 | 38.877 | -122.7667 | THORNTONELLIS7725HARRINGTONFLATRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085739 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1307064 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0085418&numberofmonths=24&showchangehistorylog=1 | 17-0085418 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | CALPELLA-1101 | 43411101 | FUSE | 3513 | 20171009 | 620 | 1895763 | 10105 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 111 | 1048890 | 39.2716 | -123.2463 | MULTIPLELOCATIONS | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0085418 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Force Out | 1306869 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0085344&numberofmonths=24&showchangehistorylog=1 | 17-0085344 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | KONOCTI-1102 | 43311102 | OTHER | WIREDOWN1PSSIDEOF9789 | 20171009 | 142 | 1894986 | 2690 | Distribution Circuit | Vegetation | Tree - branch fell on line | 336 | 218099 | 38.8458 | -122.724 | 3PSSOF2167 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085344 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Open Circuit | 1306794 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0085361&numberofmonths=24&showchangehistorylog=1 | 17-0085361 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LUCERNE-1106 | 43351106 | OCB | 11062 | 20171009 | 51 | 1894798 | 2036 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2972 | 1633084 | 39.1104 | -122.8128 | 47198 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085361 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Three Phase Fault | 1306814 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0085395&numberofmonths=24&showchangehistorylog=1 | 17-0085395 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | MENDOCINO-1101 | 42951101 | FUSE | 80695 | 20171009 | 52 | 1898710 | 8143 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 7 | 57001 | 39.3132 | -123.2198 | MULTIPLEBEYONDFUSES | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085395 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1307520 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0085335&numberofmonths=24&showchangehistorylog=1 | 17-0085335 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | REDBUD-1101 | 43191101 | JUMPER | 4PLD90439 | 20171009 | 29 | 1894896 | 630 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 13314 | 39.0728 | -122.5866 | 4PLD90439 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085335 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1306785 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0102101&numberofmonths=24&showchangehistorylog=1 | 17-0102101 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | MIDDLETOWN-1101 | 43141101 | JUMPER | WIREDOWN | 20171216 | 1151 | 1945058 | 353 | Distribution Circuit | Vegetation | Tree - fell into line | 76 | 26120 | 38.8171 | -122.703 | 1LDSIDEOFMTR1008034156 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0102101 | OH | Sus | 0 | yes | 2017 | DEC | Yes | Three Phase Fault | 1320011 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0023246&numberofmonths=24&showchangehistorylog=1 | 18-0023246 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | CALPELLA-1101 | 43411101 | FUSE | 6369 | 20180316 | 453 | 45212 | 447 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 447 | 39.319 | -123.3146 | 16SLDSIDEOF6369 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023246 | OH | Sus | 43302651 | yes | 2018 | MAR | Yes | Line to Ground | 1336152 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0098214&numberofmonths=24&showchangehistorylog=1 | 18-0098214 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | MIDDLETOWN-1101 | 43141101 | FUSE | 7927 | 20181108 | 945 | 211460 | 423 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2538 | 38.6748 | -122.6567 | STONEJARED6spansbeyonssd | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0098214 | OH | Sus | 43533911 | yes | 2018 | NOV | Yes | Line to Line | 1391424 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0101683&numberofmonths=24&showchangehistorylog=1 | 18-0101683 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | EEL RIVER-1102 | 192381102 | FUSE | 1929 | 20181121 | 216 | 219464 | 579 | Distribution Circuit | 3rd Party | Gun Shot | 78 | 4834 | 40.4616 | -124.3678 | 15SPANSSSOF93155 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0101683 | OH | Sus | 43584639 | yes | 2018 | NOV | Yes | Open Circuit | 1393952 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0104657&numberofmonths=24&showchangehistorylog=1 | 18-0104657 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | RECLOSER | 1770 | 20181129 | 36 | 227355 | 748 | Distribution Circuit | Vegetation | Tree - fell into line | 350 | 79638 | 39.9153 | -123.7634 | TREETHROUGHLINECGC115160620316 | Clear-32-90 F | Conductor, Overhead | On Ground | 18-0104657 | OH | Sus | 31417162 | yes | 2018 | NOV | Yes | Multi-Fault | 1395971 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005081&numberofmonths=24&showchangehistorylog=1 | 19-0005081 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | EEL RIVER-1102 | 192381102 | FUSE | 1915 | 20190106 | 1140 | 255289 | 235 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 235 | 40.4651 | -124.2546 | 8SPANSLDSIDEOF1915 | Overcast-Fog-Rain-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0005081 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1403553 | CSO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005695&numberofmonths=24&showchangehistorylog=1 | 19-0005695 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 4451 | 20190106 | 2326 | 258392 | 826 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 5782 | 38.7903 | -123.5105 | 6POLESLDSIDEOF4451 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005695 | OH | Sus | 31421138 | yes | 2019 | JAN | Yes | Line to Line | 1404107 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0009691&numberofmonths=24&showchangehistorylog=1 | 19-0009691 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE | 4557 | 20190116 | 1206 | 266852 | 1541 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 46230 | 38.6377 | -123.3159 | MTR1009664491 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009691 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1406642 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0009773&numberofmonths=24&showchangehistorylog=1 | 19-0009773 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE | 5113 | 20190116 | 1400 | 267082 | 1613 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 9678 | 38.7189 | -123.38 | INSPANLDSIDEOFFUCO5113 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009773 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1406678 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010041&numberofmonths=24&showchangehistorylog=1 | 19-0010041 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 3611 | 20190116 | 1706 | 268214 | 2548 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 10192 | 39.2913 | -123.7678 | 2LDSIDEOFFUCO3611 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010041 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1406905 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010128&numberofmonths=24&showchangehistorylog=1 | 19-0010128 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 5173 | 20190116 | 1719 | 268442 | 2448 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 31824 | 39.2859 | -123.7801 | 6SPANSLOADSIDE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010128 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1406997 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010291&numberofmonths=24&showchangehistorylog=1 | 19-0010291 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 79817 | 20190116 | 1745 | 268768 | 2655 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 124785 | 39.2085 | -123.7266 | FelicichDavid31300MIDDLERIDGERD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010291 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1407156 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010308&numberofmonths=24&showchangehistorylog=1 | 19-0010308 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 4197 | 20190116 | 1951 | 269761 | 2434 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 36510 | 39.312 | -123.7673 | 43016LITTLELAKERD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010308 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407174 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010336&numberofmonths=24&showchangehistorylog=1 | 19-0010336 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 8189 | 20190116 | 1703 | 268196 | 2429 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 12145 | 39.3077 | -123.7928 | 1SPANLDSIDEOFFUCO818944740PINEST | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010336 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407201 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010091&numberofmonths=24&showchangehistorylog=1 | 19-0010091 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | EEL RIVER-1102 | 192381102 | FUSE | 1909 | 20190116 | 1727 | 268538 | 1463 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 7371 | 40.5115 | -124.1597 | MTR1008868437 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010091 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1406958 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0009782&numberofmonths=24&showchangehistorylog=1 | 19-0009782 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | RECLOSER | 1298 | 20190116 | 1353 | 267068 | 1727 | Distribution Circuit | Vegetation | Tree - fell into line | 908 | 154568 | 39.1426 | -123.7284 | 2SPANSSOURCESIDEOFR8315 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009782 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1406684 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0009901&numberofmonths=24&showchangehistorylog=1 | 19-0009901 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | RECLOSER | 1260 | 20190116 | 1431 | 267175 | 3958 | Distribution Circuit | Vegetation | Tree - fell into line | 88 | 141214 | 39.1293 | -123.7112 | 38SPANSLDSIDEOFFUCO8633 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009901 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1406776 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010079&numberofmonths=24&showchangehistorylog=1 | 19-0010079 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | OTHER | WIREDOWN1SOURCESIDEOF3921 | 20190116 | 1825 | 269163 | 2425 | Distribution Circuit | Vegetation | Tree - fell into line | 151 | 363151 | 39.2065 | -123.7084 | 1SPANSOURCESIDEOFFUCO3921 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010079 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1406944 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011962&numberofmonths=24&showchangehistorylog=1 | 19-0011962 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 8639 | 20190116 | 1431 | 276225 | 4207 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 25242 | 39.1218 | -123.5971 | 2LDSIDEOF8639 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011962 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Open Circuit | 1408299 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010545&numberofmonths=24&showchangehistorylog=1 | 19-0010545 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | TRIP-SAVER | 3113 | 20190116 | 1811 | 268999 | 1600 | Distribution Circuit | Vegetation | Tree - fell into line | 102 | 82069 | 39.5073 | -123.7645 | 5SPANSLOADSIDEOF3227 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010545 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407407 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010022&numberofmonths=24&showchangehistorylog=1 | 19-0010022 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3311 | 20190116 | 1727 | 268518 | 1688 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 35448 | 39.4153 | -123.7727 | 2SPANSLDSIDEOF3311 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010022 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1406887 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010170&numberofmonths=24&showchangehistorylog=1 | 19-0010170 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 3109 | 20190116 | 1724 | 268821 | 1291 | Distribution Circuit | Vegetation | Tree - branch fell on line | 83 | 107153 | 39.4629 | -123.7936 | GarciaDanT1260K346731901airportrd | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010170 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407038 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010172&numberofmonths=24&showchangehistorylog=1 | 19-0010172 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 1487 | 20190116 | 1724 | 270366 | 1700 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 6582 | 39.4661 | -123.7835 | FelicichDavid31594AirportRdonespanloadsideco1487 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010172 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407040 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010078&numberofmonths=24&showchangehistorylog=1 | 19-0010078 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1141 | 192311141 | RECLOSER | 8860 | 20190116 | 1841 | 269539 | 2552 | Distribution Circuit | Vegetation | Tree - fell into line | 159 | 405768 | 40.2829 | -123.8726 | 11SPANSLDSIDEOF8860 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010078 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1406943 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011499&numberofmonths=24&showchangehistorylog=1 | 19-0011499 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1141 | 192311141 | FUSE | 8301 | 20190116 | 1802 | 273261 | 2539 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2539 | 40.3236 | -123.9234 | LDSIDEFUCO8301 | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011499 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1408041 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0009952&numberofmonths=24&showchangehistorylog=1 | 19-0009952 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 56048 | 20190116 | 1711 | 268396 | 2868 | Distribution Circuit | Vegetation | Tree - fell into line | 850 | 1157121 | 40.1477 | -124.0196 | 5PNOFTRANSF1141024331601SOURCESIDEOFFUCO44891 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009952 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1406822 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011360&numberofmonths=24&showchangehistorylog=1 | 19-0011360 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 1971 | 20190116 | 1855 | 269534 | 2645 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 21160 | 40.1113 | -123.8905 | 1STSPANLDSIDEOF1971 | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011360 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407906 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0009660&numberofmonths=24&showchangehistorylog=1 | 19-0009660 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 2011 | 20190116 | 1211 | 267002 | 502 | Distribution Circuit | Vegetation | Tree - fell into line | 65 | 32630 | 38.7062 | -123.4298 | 1SPANSOURCESIDEOF46441 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009660 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1406638 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0009931&numberofmonths=24&showchangehistorylog=1 | 19-0009931 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 4437 | 20190116 | 1234 | 266894 | 1601 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 40025 | 38.8248 | -123.5765 | MTR1010450544 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009931 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1406802 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010287&numberofmonths=24&showchangehistorylog=1 | 19-0010287 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | HIGHLANDS-1103 | 43361103 | FUSE | 49361 | 20190116 | 1859 | 269559 | 2461 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 36915 | 38.9366 | -122.6084 | EOL | Strong Winds-Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0010287 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407152 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010238&numberofmonths=24&showchangehistorylog=1 | 19-0010238 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | HUMBOLDT BAY-1102 | 192341102 | FUSE | 7617 | 20190116 | 1858 | 269555 | 1073 | Distribution Circuit | Vegetation | Tree - branch fell on line | 39 | 3315 | 40.7037 | -124.1524 | 1SPANLOADSIDE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010238 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1407103 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010056&numberofmonths=24&showchangehistorylog=1 | 19-0010056 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | KONOCTI-1102 | 43311102 | RECLOSER | 532 | 20190116 | 1836 | 269390 | 1181 | Distribution Circuit | Vegetation | Tree - fell into line | 336 | 394688 | 38.8576 | -122.7221 | MAINLINE2SO2169 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0010056 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Three Phase Fault | 1406923 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011295&numberofmonths=24&showchangehistorylog=1 | 19-0011295 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | KONOCTI-1102 | 43311102 | FUSE | 2343 | 20190116 | 1906 | 269618 | 2632 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 42112 | 38.8617 | -122.719 | 2SPANSLOADSIDE | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011295 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407859 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010012&numberofmonths=24&showchangehistorylog=1 | 19-0010012 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1102 | 42681102 | RECLOSER | 68436 | 20190116 | 1805 | 268942 | 2922 | Distribution Circuit | Vegetation | Tree - fell into line | 127 | 278574 | 39.5523 | -123.4252 | 2NEOF25431WOF98079 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010012 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1406877 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010069&numberofmonths=24&showchangehistorylog=1 | 19-0010069 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LUCERNE-1106 | 43351106 | RECLOSER | 38632 | 20190116 | 1849 | 269490 | 1703 | Distribution Circuit | Vegetation | Tree - fell into line | 260 | 100636 | 38.9913 | -122.7481 | MTR1007973652 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0010069 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1406935 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011132&numberofmonths=24&showchangehistorylog=1 | 19-0011132 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | MENDOCINO-1101 | 42951101 | FUSE | 2771 | 20190116 | 2044 | 270797 | 2691 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 39115 | 39.3737 | -123.2525 | 3SPANSSOFMTR1005576715 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011132 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407750 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0009593&numberofmonths=24&showchangehistorylog=1 | 19-0009593 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE | 7871 | 20190116 | 1139 | 266819 | 1472 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 5888 | 38.922 | -123.6227 | 3SPANSLOADSIDE7871 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009593 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1406601 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010021&numberofmonths=24&showchangehistorylog=1 | 19-0010021 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER | 37506 | 20190116 | 1802 | 268983 | 4161 | Distribution Circuit | Vegetation | Tree - fell into line | 88 | 145920 | 39.4831 | -123.3611 | BARRINGTONSORRELT1102K3455northwestofcutouts64083eastof31050hwy101 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010021 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1406886 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010431&numberofmonths=24&showchangehistorylog=1 | 19-0010431 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | FUSE | 7653 | 20190116 | 2302 | 272101 | 3734 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 29872 | 39.4746 | -123.3641 | EOLSEOF7653 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010431 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407296 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010932&numberofmonths=24&showchangehistorylog=1 | 19-0010932 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER | 538 | 20190116 | 1816 | 269159 | 4077 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 82839 | 39.4236 | -123.3017 | 5401CANYONRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010932 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407618 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011203&numberofmonths=24&showchangehistorylog=1 | 19-0011203 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1103 | 42661103 | FUSE | 6423 | 20190116 | 1808 | 268951 | 2963 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 57914 | 39.4878 | -123.4249 | 29SPANSLOADSIDEOF6423 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011203 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407795 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010175&numberofmonths=24&showchangehistorylog=1 | 19-0010175 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1104 | 42661104 | FUSE | 3769 | 20190116 | 1803 | 268915 | 2807 | Distribution Circuit | Vegetation | Tree - fell into line | 111 | 129612 | 39.4348 | -123.3795 | 25026COBBDR | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010175 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1407043 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011320&numberofmonths=24&showchangehistorylog=1 | 19-0011320 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 8771 | 20190117 | 1726 | 274715 | 1378 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2756 | 39.2469 | -123.7634 | 33166FROGPONDRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011320 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407875 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010918&numberofmonths=24&showchangehistorylog=1 | 19-0010918 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 6069 | 20190117 | 508 | 273608 | 1927 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 98277 | 39.6578 | -123.7827 | MTR1010302937 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010918 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407606 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010961&numberofmonths=24&showchangehistorylog=1 | 19-0010961 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1141 | 192311141 | FUSE | 3931 | 20190117 | 159 | 272304 | 984 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 15678 | 40.338 | -123.9124 | 3SPANSLDSIDEOF7453NGINSULATOR9SPANSLDSIDEOF7453FOUNDTREETHROUGHLINE2SPANSOFWIREDOWN | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010961 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407633 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011223&numberofmonths=24&showchangehistorylog=1 | 19-0011223 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 54634 | 20190117 | 1226 | 273945 | 1672 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3344 | 40.1272 | -123.8463 | EOL | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0011223 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407806 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011149&numberofmonths=24&showchangehistorylog=1 | 19-0011149 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | MIDDLETOWN-1101 | 43141101 | TRIP-SAVER | 1079 | 20190117 | 125 | 272256 | 2369 | Distribution Circuit | Vegetation | Tree - fell into line | 91 | 50222 | 38.8145 | -122.7088 | SMITHCODY11085OAKST | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 19-0011149 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407761 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011198&numberofmonths=24&showchangehistorylog=1 | 19-0011198 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | MIDDLETOWN-1101 | 43141101 | FUSE | 547 | 20190117 | 647 | 273871 | 1922 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 34596 | 38.847 | -122.7548 | 547TWDMTR1009746188 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011198 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407793 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011465&numberofmonths=24&showchangehistorylog=1 | 19-0011465 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1102 | 42601102 | RECLOSER | 1308 | 20190117 | 1952 | 274924 | 2899 | Distribution Circuit | Vegetation | Tree - branch fell on line | 455 | 233033 | 39.1863 | -123.5804 | ESPINOLACHRISpolesap102171742 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0011465 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1408005 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0016978&numberofmonths=24&showchangehistorylog=1 | 19-0016978 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 262813 | 20190202 | 240 | 286092 | 662 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 7282 | 38.8137 | -123.5708 | CGC215534041935 | Partly Cloudy-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0016978 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1411437 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0017015&numberofmonths=24&showchangehistorylog=1 | 19-0017015 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE | 8205 | 20190202 | 724 | 286748 | 312 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 312 | 38.903 | -123.6262 | 1SPANLDSIDEOF8205 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017015 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1411469 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018024&numberofmonths=24&showchangehistorylog=1 | 19-0018024 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ARCATA-1121 | 192021121 | OTHER | 1269 | 20190204 | 1210 | 290365 | 385 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 5390 | 40.8148 | -123.9935 | 6SPANSLDSIDEOF1269 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0018024 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1412305 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018155&numberofmonths=24&showchangehistorylog=1 | 19-0018155 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 8519 | 20190204 | 1834 | 291084 | 1166 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 5830 | 41.214 | -123.7601 | JUSTLDSIDEOF8519 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0018155 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1412396 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018075&numberofmonths=24&showchangehistorylog=1 | 19-0018075 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLOW CREEK-1101 | 192171101 | FUSE | 5233 | 20190204 | 1431 | 290570 | 1448 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 26064 | 40.9521 | -123.6775 | MTR1007717473 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0018075 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1412328 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020356&numberofmonths=24&showchangehistorylog=1 | 19-0020356 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE | 3621 | 20190209 | 1304 | 297028 | 386 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 758 | 38.7174 | -123.3612 | 3LDSIDEOFFU3621ONTAPTOWEST | Overcast-Rain-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0020356 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1414037 | CSO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020326&numberofmonths=24&showchangehistorylog=1 | 19-0020326 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ARCATA-1121 | 192021121 | FUSE | 1269 | 20190209 | 925 | 296874 | 382 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 5348 | 40.8148 | -123.9935 | 12SPANSLDSIDEOFFUCO1255ONMAINLINE | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020326 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1414018 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020385&numberofmonths=24&showchangehistorylog=1 | 19-0020385 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BRIDGEVILLE-1101 | 192461101 | RECLOSER | 37484 | 20190209 | 1724 | 297227 | 5824 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 124272 | 40.4523 | -123.6539 | BIONDINIJUSTINK1914T2370Sbcos8809 | Overcast-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020385 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1414059 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020485&numberofmonths=24&showchangehistorylog=1 | 19-0020485 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | RECLOSER | 3304 | 20190209 | 2350 | 297595 | 8364 | Distribution Circuit | Vegetation | Tree - fell into line | 510 | 2240269 | 41.1053 | -123.6888 | 15MILENORTHOF3304 | Overcast-Fog-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0020485 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Multi-Fault | 1414162 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020836&numberofmonths=24&showchangehistorylog=1 | 19-0020836 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 8435 | 20190209 | 2350 | 299370 | 8364 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 184008 | 41.2085 | -123.7558 | 2930AND31SPANSLDSIDEOF8435 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020836 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Three Phase Fault | 1414538 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021513&numberofmonths=24&showchangehistorylog=1 | 19-0021513 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 3261 | 20190209 | 2350 | 300809 | 8282 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 82820 | 41.1904 | -123.6907 | LDSIDEOFFUSES | Clear-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0021513 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Multi-Fault | 1414979 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020330&numberofmonths=24&showchangehistorylog=1 | 19-0020330 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLOW CREEK-1101 | 192171101 | OTHER | WIREDOWN3NWOF3161 | 20190209 | 1323 | 297041 | 8994 | Distribution Circuit | Vegetation | Tree - fell into line | 84 | 570842 | 40.924 | -123.8368 | 3SPANSNWOF31611LDSIDEOF55437 | Overcast-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0020330 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1414021 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020999&numberofmonths=24&showchangehistorylog=1 | 19-0020999 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLOW CREEK-1101 | 192171101 | FUSE | 55437 | 20190209 | 1326 | 299771 | 8969 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 8969 | 40.917 | -123.8302 | 3SPANSLDSIDEOF55347 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020999 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1414682 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020808&numberofmonths=24&showchangehistorylog=1 | 19-0020808 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ARCATA-1122 | 192021122 | FUSE | 6267 | 20190210 | 17 | 299274 | 3938 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 15752 | 40.765 | -123.998 | 3SPANSLOADSIDE | Clear-Strong Winds-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020808 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1414508 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021548&numberofmonths=24&showchangehistorylog=1 | 19-0021548 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ARCATA-1122 | 192021122 | JUMPER | OJTOCGC114440453436 | 20190210 | 17 | 300885 | 4018 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 8036 | 40.7823 | -124.0095 | CONFIRMEDDAMAGEBEYONDCGC114440453436 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0021548 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1414993 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021549&numberofmonths=24&showchangehistorylog=1 | 19-0021549 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ARCATA-1122 | 192021122 | FUSE | 4591 | 20190210 | 16 | 300888 | 3969 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 15876 | 40.763 | -123.9971 | LOADSIDE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021549 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1414994 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021550&numberofmonths=24&showchangehistorylog=1 | 19-0021550 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ARCATA-1122 | 192021122 | FUSE | 5457 | 20190210 | 17 | 300892 | 3960 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 23760 | 40.8 | -124.0383 | DAMAGEBEYOND5457 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021550 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1414995 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020528&numberofmonths=24&showchangehistorylog=1 | 19-0020528 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BRIDGEVILLE-1101 | 192461101 | RECLOSER | 11012 | 20190210 | 316 | 297827 | 5268 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 320960 | 40.4798 | -123.7803 | 1SPANNOF4101 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020528 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Three Phase Fault | 1414203 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021196&numberofmonths=24&showchangehistorylog=1 | 19-0021196 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BRIDGEVILLE-1101 | 192461101 | FUSE | 4119 | 20190210 | 316 | 300203 | 6632 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 53056 | 40.4837 | -123.7276 | 1STSPANLDSIDEOF4119 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021196 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1414790 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020741&numberofmonths=24&showchangehistorylog=1 | 19-0020741 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BRIDGEVILLE-1102 | 192461102 | FUSE | 3473 | 20190210 | 1009 | 298639 | 1656 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 39744 | 40.4651 | -123.8566 | 5SPANSLOADSIDEOF3473 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020741 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1414444 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020837&numberofmonths=24&showchangehistorylog=1 | 19-0020837 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BRIDGEVILLE-1102 | 192461102 | FUSE | 3463 | 20190210 | 629 | 298087 | 1791 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 19701 | 40.4786 | -123.8889 | 3SPANSLOADSIDE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020837 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1414539 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020567&numberofmonths=24&showchangehistorylog=1 | 19-0020567 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | CARLOTTA-1121 | 192291121 | RECLOSER | 44150 | 20190210 | 554 | 298064 | 3629 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 49966 | 40.4761 | -123.9427 | 3SPANSSSOF4071 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020567 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1414248 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021156&numberofmonths=24&showchangehistorylog=1 | 19-0021156 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT SEWARD-1121 | 192321121 | FUSE | 1637 | 20190210 | 1121 | 298832 | 2873 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 54587 | 40.1473 | -123.6358 | 1SPANSSOF4367 | Partly Cloudy-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021156 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1414765 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020569&numberofmonths=24&showchangehistorylog=1 | 19-0020569 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1141 | 192311141 | RECLOSER | 95324 | 20190210 | 654 | 298132 | 2118 | Distribution Circuit | Vegetation | Tree - branch fell on line | 224 | 393741 | 40.284 | -123.8723 | GALLETTITIMTREEBRANCHTHROUGHLINE12POLESLSOFLR95324 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020569 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1414251 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020635&numberofmonths=24&showchangehistorylog=1 | 19-0020635 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1141 | 192311141 | OCB | 11412 | 20190210 | 928 | 298309 | 1963 | Distribution Circuit | Vegetation | Tree - fell into line | 170 | 330690 | 40.2866 | -123.8369 | 5POLESSSOF6807 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020635 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1414330 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020811&numberofmonths=24&showchangehistorylog=1 | 19-0020811 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 6865 | 20190210 | 827 | 298480 | 1943 | Distribution Circuit | Vegetation | Tree - fell into line | 95 | 184585 | 40.2936 | -123.8176 | 4PSSOF8055 | Clear-Strong Winds-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020811 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1414511 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020571&numberofmonths=24&showchangehistorylog=1 | 19-0020571 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | RECLOSER | 35706 | 20190210 | 447 | 298139 | 2050 | Distribution Circuit | Vegetation | Tree - fell into line | 323 | 517807 | 39.8714 | -123.7119 | MAINLINEATFUCO96717 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020571 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1414253 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020576&numberofmonths=24&showchangehistorylog=1 | 19-0020576 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | OCB | 11012 | 20190210 | 710 | 298102 | 6230 | Distribution Circuit | Vegetation | Tree - fell into line | 985 | 1158702 | 40.1033 | -123.7926 | BETWEENSW4345SW7203 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020576 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Three Phase Fault | 1414259 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021112&numberofmonths=24&showchangehistorylog=1 | 19-0021112 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 4521 | 20190210 | 638 | 299983 | 2136 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 12816 | 39.9452 | -123.7777 | 20SPANSLDSIDEOF4521 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021112 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1414749 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020546&numberofmonths=24&showchangehistorylog=1 | 19-0020546 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 2500 | 20190210 | 502 | 297966 | 2134 | Distribution Circuit | Vegetation | Tree - fell into line | 446 | 747992 | 40.1079 | -123.9289 | 2LDSIDEOFFUCO2535ONMAINLINE | Overcast-Fog-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0020546 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1414224 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020550&numberofmonths=24&showchangehistorylog=1 | 19-0020550 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 11022 | 20190210 | 510 | 297988 | 5074 | Distribution Circuit | Vegetation | Tree - fell into line | 1360 | 1786477 | 40.1033 | -123.7926 | CURNOWRAYK1616T1270rewaydr2SPANSSOURCESIDEOF53073SPANSLDSIDEOF53075SPANSSOURCESIDEOF2529 | Overcast-Fog-Snow-32-90 F | Pole-Wood | Broken, wire on ground | 19-0020550 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Multi-Fault | 1414228 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020857&numberofmonths=24&showchangehistorylog=1 | 19-0020857 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | JUMPER | OJS1SSOFMTR1008282876 | 20190210 | 121 | 299421 | 3829 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 38290 | 41.0946 | -123.6923 | 1008282876 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020857 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1414559 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021186&numberofmonths=24&showchangehistorylog=1 | 19-0021186 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 3247 | 20190210 | 121 | 300150 | 5049 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 5049 | 41.1041 | -123.6898 | VARIOUSLOADSIDE | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0021186 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1414779 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020682&numberofmonths=24&showchangehistorylog=1 | 19-0020682 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE | 2577 | 20190210 | 1056 | 298795 | 309 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 14523 | 39.6878 | -123.4951 | 2SPANSSSOF2743 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020682 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1414383 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020691&numberofmonths=24&showchangehistorylog=1 | 19-0020691 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE | 91239 | 20190210 | 1142 | 298823 | 368 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1104 | 39.6478 | -123.5295 | 1POLELDSIDEOFFUCO91239 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020691 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1414395 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020621&numberofmonths=24&showchangehistorylog=1 | 19-0020621 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LOW GAP-1101 | 192411101 | RECLOSER | 2094 | 20190210 | 904 | 298476 | 5951 | Distribution Circuit | Vegetation | Tree - fell into line | 302 | 563459 | 40.436 | -123.4882 | MAINLINEFUCO86765 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020621 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1414311 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020494&numberofmonths=24&showchangehistorylog=1 | 19-0020494 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | MAPLE CREEK-1101 | 192101101 | OCB | 11012 | 20190210 | 59 | 297704 | 5176 | Distribution Circuit | Vegetation | Tree - fell into line | 130 | 371859 | 40.7683 | -123.874 | 1WOF85851SSOFFU68559 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020494 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1414168 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020815&numberofmonths=24&showchangehistorylog=1 | 19-0020815 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | MAPLE CREEK-1101 | 192101101 | FUSE | 6235 | 20190210 | 59 | 299287 | 5311 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 74354 | 40.7678 | -123.8718 | 2LDSIDEOFSBCO3105 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020815 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1414516 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020596&numberofmonths=24&showchangehistorylog=1 | 19-0020596 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | NEWBURG-1131 | 192151131 | FUSE | 7049 | 20190210 | 231 | 297796 | 2288 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 19346 | 40.5681 | -124.1227 | 9SPANSLDSIDEOFFUCO7049 | Overcast-Fog-32-90 F | Pole-Wood | Broken, wire on ground | 19-0020596 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1414285 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020718&numberofmonths=24&showchangehistorylog=1 | 19-0020718 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | RIO DELL-1102 | 192251102 | RECLOSER | 4230 | 20190210 | 1337 | 298987 | 1890 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 49140 | 40.4173 | -124.0895 | 11SPANSSSOF750641 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020718 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1414422 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020639&numberofmonths=24&showchangehistorylog=1 | 19-0020639 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER | 37506 | 20190210 | 938 | 298539 | 521 | Distribution Circuit | Equipment Failure/Involved | Overhead | 88 | 12521 | 39.4831 | -123.3611 | 14SPANSSSOF7097 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0020639 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1414334 | CSO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020798&numberofmonths=24&showchangehistorylog=1 | 19-0020798 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER | 826 | 20190210 | 1621 | 299174 | 232 | Distribution Circuit | Vegetation | Tree - branch fell on line | 868 | 96096 | 39.4204 | -123.3598 | FUCO9219ONMAINLINE | Clear-32-90 F | Conductor, Overhead | On Ground | 19-0020798 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1414498 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020714&numberofmonths=24&showchangehistorylog=1 | 19-0020714 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1104 | 42661104 | RECLOSER | 34008 | 20190210 | 1306 | 298957 | 1358 | Distribution Circuit | Vegetation | Tree - fell into line | 571 | 70142 | 39.4366 | -123.3893 | 5SPANSFROMSW6095TWDSBCO7053 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020714 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1414419 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020693&numberofmonths=24&showchangehistorylog=1 | 19-0020693 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLOW CREEK-1101 | 192171101 | OTHER | 2WIRESDOWNFEEDINGLR4904 | 20190210 | 109 | 298903 | 6299 | Distribution Circuit | Equipment Failure/Involved | Overhead | 81 | 317669 | 40.9468 | -123.642 | LR4904 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020693 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1414397 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020724&numberofmonths=24&showchangehistorylog=1 | 19-0020724 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1101 | 192171101 | SWITCH | 394285 | 20190210 | 109 | 298999 | 3925 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 15700 | 40.9448 | -123.6188 | 3SPANSLDSIDE | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020724 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1414428 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020920&numberofmonths=24&showchangehistorylog=1 | 19-0020920 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLOW CREEK-1101 | 192171101 | FUSE | 5233 | 20190210 | 109 | 299589 | 5121 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 92178 | 40.9521 | -123.6775 | 15SPANSLDSIDEOF5233 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020920 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1414614 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020772&numberofmonths=24&showchangehistorylog=1 | 19-0020772 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1102 | 192171102 | JUMPER | OJSONHARDTAPFEEDINGMTR1006304361 | 20190210 | 109 | 299101 | 2283 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 15981 | 40.9248 | -123.6259 | MTR1006304361 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020772 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1414473 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020924&numberofmonths=24&showchangehistorylog=1 | 19-0020924 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1102 | 192171102 | FUSE | 68539 | 20190210 | 109 | 299601 | 4136 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 49632 | 40.8746 | -123.5246 | 1SPANLDSIDEOF68539 | Overcast-Fog-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0020924 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1414616 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021476&numberofmonths=24&showchangehistorylog=1 | 19-0021476 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1102 | 192171102 | FUSE | 5521 | 20190210 | 109 | 300749 | 6706 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 114002 | 40.8906 | -123.5608 | MULTIPLELOCATIONSLDSIDEOFFUSES | Clear-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0021476 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Multi-Fault | 1414968 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021540&numberofmonths=24&showchangehistorylog=1 | 19-0021540 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | RECLOSER | 3090 | 20190210 | 109 | 300865 | 8423 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 404304 | 40.8889 | -123.5927 | VARIOUSLOADSIDE | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0021540 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1414988 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022555&numberofmonths=24&showchangehistorylog=1 | 19-0022555 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE | 7507 | 20190210 | 109 | 305581 | 10949 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 10949 | 40.8416 | -123.4867 | 1LDSIDEFU7507 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0022555 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1415792 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022557&numberofmonths=24&showchangehistorylog=1 | 19-0022557 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE | 48809 | 20190210 | 109 | 305605 | 12027 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 216486 | 40.8191 | -123.5091 | 3SPANSLDSIDEOFFU48809 | Clear-Below 32 F | Crossarm, Wood | Broken, wire on ground | 19-0022557 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1415794 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022872&numberofmonths=24&showchangehistorylog=1 | 19-0022872 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | JUMPER | OJ1SSMTR1008024281 | 20190210 | 109 | 307307 | 10944 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 32832 | 40.8651 | -123.5024 | MTR1008024281 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0022872 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416110 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023086&numberofmonths=24&showchangehistorylog=1 | 19-0023086 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE | 2971 | 20190210 | 109 | 308264 | 11297 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 214643 | 40.8075 | -123.4784 | MTR1008022100 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0023086 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1416285 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021585&numberofmonths=24&showchangehistorylog=1 | 19-0021585 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 3151 | 20190212 | 1906 | 301003 | 4154 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 58156 | 39.3416 | -123.811 | 45401OVERTONRD | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021585 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1415029 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021652&numberofmonths=24&showchangehistorylog=1 | 19-0021652 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 3725 | 20190212 | 2131 | 301312 | 2712 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 8136 | 39.2657 | -123.7493 | 1SPANLDSIDEOF3725 | Clear-32-90 F | Conductor, Overhead | On Ground | 19-0021652 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1415099 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021694&numberofmonths=24&showchangehistorylog=1 | 19-0021694 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | OTHER | WIREDOWNBETWEENFUCO7713ANDFUCO667805 | 20190212 | 2218 | 301347 | 2582 | Distribution Circuit | Vegetation | Tree - branch fell on line | 66 | 168090 | 39.2698 | -123.6992 | WIREDOWNBETWEENFUCO7713ANDFUCO667805 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021694 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1415141 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022095&numberofmonths=24&showchangehistorylog=1 | 19-0022095 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 5187 | 20190212 | 2156 | 301237 | 2744 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 24696 | 39.2861 | -123.7796 | 3LDSIDEOFFU5187 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022095 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1415471 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022224&numberofmonths=24&showchangehistorylog=1 | 19-0022224 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 1917 | 20190212 | 2152 | 301209 | 953 | Distribution Circuit | Vegetation | Tree - branch fell on line | 20 | 19060 | 39.292 | -123.7704 | 8SPANSLDSIDEOFFU1917 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022224 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1415556 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024119&numberofmonths=24&showchangehistorylog=1 | 19-0024119 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 3163 | 20190212 | 1852 | 312377 | 5228 | Distribution Circuit | Vegetation | Tree - grew into line | 39 | 185620 | 39.6521 | -123.7826 | SSMTR1010320956 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024119 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1417207 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021642&numberofmonths=24&showchangehistorylog=1 | 19-0021642 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | RECLOSER | 816 | 20190212 | 2213 | 301152 | 1221 | Distribution Circuit | Vegetation | Tree - branch fell on line | 389 | 441731 | 39.4119 | -123.7985 | GarciaDanT1260K34671spaneoreg17889eoellisononsimpsonln | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021642 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1415088 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021777&numberofmonths=24&showchangehistorylog=1 | 19-0021777 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3969 | 20190212 | 2111 | 302651 | 2582 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 152338 | 39.3811 | -123.7737 | 13SPANSLDSIDEOF3969 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | On Ground | 19-0021777 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1415228 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021882&numberofmonths=24&showchangehistorylog=1 | 19-0021882 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 7253 | 20190212 | 2209 | 301307 | 2666 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 45322 | 39.4188 | -123.778 | 1SPANLDSIDEOF7253 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0021882 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1415327 | PW | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022482&numberofmonths=24&showchangehistorylog=1 | 19-0022482 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 1607 | 20190212 | 1935 | 305318 | 2819 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 11276 | 39.4419 | -123.773 | 1SPANLDSIDEOF160731012MARSBENLN | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022482 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1415733 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021502&numberofmonths=24&showchangehistorylog=1 | 19-0021502 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 4483 | 20190212 | 1311 | 300706 | 234 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 468 | 40.0491 | -123.7918 | 4SPANSLOADSIDE | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021502 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1414974 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021644&numberofmonths=24&showchangehistorylog=1 | 19-0021644 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | RECLOSER | 1294 | 20190212 | 2128 | 301150 | 1031 | Distribution Circuit | Vegetation | Tree - fell into line | 611 | 68487 | 38.8037 | -123.5835 | ThorpeTim20941spanLSOSw4405 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021644 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1415091 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022211&numberofmonths=24&showchangehistorylog=1 | 19-0022211 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 7287 | 20190212 | 2128 | 304443 | 2200 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 37400 | 38.8139 | -123.5856 | 2SPANSLDSIDEOF7287 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022211 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1415548 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021645&numberofmonths=24&showchangehistorylog=1 | 19-0021645 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LOW GAP-1101 | 192411101 | RECLOSER | 4160 | 20190212 | 2234 | 301375 | 3935 | Distribution Circuit | Equipment Failure/Involved | Overhead | 417 | 1303157 | 40.4272 | -123.481 | 1SPANNO5193ONMAINLINE | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021645 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1415092 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021565&numberofmonths=24&showchangehistorylog=1 | 19-0021565 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | MENDOCINO-1101 | 42951101 | FUSE | 2771 | 20190212 | 1714 | 300901 | 4355 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 23593 | 39.3737 | -123.2525 | MTR1008394297 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 19-0021565 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1415005 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021577&numberofmonths=24&showchangehistorylog=1 | 19-0021577 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1102 | 42601102 | RECLOSER | 2600 | 20190212 | 2010 | 301078 | 4348 | Distribution Circuit | Vegetation | Tree - fell into line | 97 | 120301 | 39.0853 | -123.485 | 1SPANWOF895 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021577 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1415020 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021648&numberofmonths=24&showchangehistorylog=1 | 19-0021648 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | FUSE | 2831 | 20190212 | 1651 | 301404 | 3926 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 340423 | 39.3834 | -123.3013 | 3900RIDGEWOODRD | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021648 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1415095 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021651&numberofmonths=24&showchangehistorylog=1 | 19-0021651 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | FUSE | 2823 | 20190212 | 1914 | 301069 | 3724 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 160132 | 39.3949 | -123.3133 | ESPINOLACHRIS3900RidgewoodRd | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021651 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Three Phase Fault | 1415098 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021712&numberofmonths=24&showchangehistorylog=1 | 19-0021712 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1103 | 42661103 | FUSE | 4961 | 20190212 | 1651 | 301765 | 4311 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 99153 | 39.3814 | -123.2818 | SSTO5143 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021712 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1415160 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021717&numberofmonths=24&showchangehistorylog=1 | 19-0021717 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1103 | 42661103 | FUSE | 1661 | 20190212 | 1651 | 301790 | 4311 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 303710 | 39.3744 | -123.2758 | JUSTLDOF4961 | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 19-0021717 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1415165 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021761&numberofmonths=24&showchangehistorylog=1 | 19-0021761 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1103 | 42661103 | FUSE | 1843 | 20190212 | 2156 | 302591 | 3667 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 88008 | 39.3732 | -123.2753 | 13PLDSIDEOF1843 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021761 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1415213 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023527&numberofmonths=24&showchangehistorylog=1 | 19-0023527 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1103 | 42661103 | JUMPER | OJS2SOF3651 | 20190212 | 1914 | 310247 | 4225 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 8450 | 39.3772 | -123.2932 | ESPINOLACHRIS3323ridgewoodrd | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023527 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1416672 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021579&numberofmonths=24&showchangehistorylog=1 | 19-0021579 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1104 | 42661104 | FUSE | 8019 | 20190212 | 1829 | 300962 | 1633 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 74161 | 39.3625 | -123.3202 | 1SPANLOADSIDEOFMTR1009537685 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0021579 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1415023 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021580&numberofmonths=24&showchangehistorylog=1 | 19-0021580 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1104 | 42661104 | FUSE | 2785 | 20190212 | 1843 | 300977 | 1527 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 38175 | 39.4043 | -123.3869 | 6SPANSLOADSIDE | Strong Winds-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0021580 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1415024 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022122&numberofmonths=24&showchangehistorylog=1 | 19-0022122 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 722265 | 20190213 | 1054 | 303948 | 4614 | Distribution Circuit | Vegetation | Tree - branch fell on line | 66 | 240124 | 39.0992 | -123.568 | GALLETTITIMTREELIMBTHROUGHLINE25SPANSEOFCO722265GREENWOODRD | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022122 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1415487 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022322&numberofmonths=24&showchangehistorylog=1 | 19-0022322 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 3015 | 20190213 | 407 | 304736 | 2058 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 20580 | 39.5925 | -123.7785 | 31800BRUHELPOINTRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022322 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1415623 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022325&numberofmonths=24&showchangehistorylog=1 | 19-0022325 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 8541 | 20190213 | 228 | 304741 | 2223 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 17784 | 39.4936 | -123.7856 | 24925PARKDR | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022325 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Three Phase Fault | 1415624 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022550&numberofmonths=24&showchangehistorylog=1 | 19-0022550 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 3173 | 20190213 | 228 | 305557 | 3742 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 7484 | 39.6337 | -123.7825 | MULTIPLELOCATIONSLDSIDEOF3173 | Overcast-Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0022550 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1415788 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023535&numberofmonths=24&showchangehistorylog=1 | 19-0023535 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 8567 | 20190213 | 2222 | 305807 | 1113 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 10017 | 39.5113 | -123.7561 | SAME | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023535 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416681 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021790&numberofmonths=24&showchangehistorylog=1 | 19-0021790 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 6081 | 20190213 | 457 | 302680 | 1030 | Distribution Circuit | Vegetation | Tree - fell into line | 140 | 123432 | 39.3922 | -123.7995 | 2SPANSLOADSIDEOF6453 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021790 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1415241 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022128&numberofmonths=24&showchangehistorylog=1 | 19-0022128 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 7361 | 20190213 | 1023 | 303686 | 1877 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 5631 | 39.4163 | -123.7925 | 7361 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022128 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1415492 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022379&numberofmonths=24&showchangehistorylog=1 | 19-0022379 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | JUMPER | OJSSOMTR1008944984 | 20190213 | 620 | 302883 | 3260 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 3260 | 39.381 | -123.7954 | MTR100894498416303PEARSONLN | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022379 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1415659 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022736&numberofmonths=24&showchangehistorylog=1 | 19-0022736 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3069 | 20190213 | 2315 | 305877 | 1160 | Distribution Circuit | Vegetation | Tree - fell into line | 160 | 101050 | 39.4158 | -123.7779 | 5SPANSNOF3069 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022736 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Three Phase Fault | 1415974 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023044&numberofmonths=24&showchangehistorylog=1 | 19-0023044 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 2857 | 20190213 | 1834 | 305522 | 1238 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 37140 | 39.3912 | -123.7745 | 6LDSIDE2857 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023044 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416258 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021812&numberofmonths=24&showchangehistorylog=1 | 19-0021812 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 8247 | 20190213 | 407 | 302618 | 3437 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 6874 | 39.4524 | -123.7698 | LDSIDEOF8247MULTIPLEPOLESBROKEN | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0021812 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Multi-Fault | 1415264 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022525&numberofmonths=24&showchangehistorylog=1 | 19-0022525 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 262813 | 20190213 | 1259 | 304548 | 2793 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 30723 | 38.8137 | -123.5708 | 46450GRETCHELGULCHRD | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022525 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1415765 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022577&numberofmonths=24&showchangehistorylog=1 | 19-0022577 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | KONOCTI-1102 | 43311102 | FUSE | 2297 | 20190213 | 1903 | 305550 | 1032 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 51239 | 38.9359 | -122.6574 | 5733SUNRISEDR | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022577 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1415810 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022315&numberofmonths=24&showchangehistorylog=1 | 19-0022315 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE | 5097 | 20190213 | 1008 | 303457 | 1889 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 26446 | 38.9019 | -123.6034 | 9SPANSLDSIDEOF5097 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022315 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1415617 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021840&numberofmonths=24&showchangehistorylog=1 | 19-0021840 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | UKIAH-1114 | 42771114 | FUSE | 781 | 20190213 | 138 | 301798 | 5337 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 112077 | 39.0392 | -123.2673 | 11SPANSLDSIDEOF781 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021840 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Three Phase Fault | 1415289 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021803&numberofmonths=24&showchangehistorylog=1 | 19-0021803 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1101 | 192171101 | SWITCH | 394285 | 20190213 | 326 | 302813 | 484 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1936 | 40.9448 | -123.6188 | 2SPANSLDSIDEOF394285 | Clear-Strong Winds-Below 32 F | Conductor, Overhead | On Ground | 19-0021803 | OH | Sus | 0 | yes | 2019 | FEB | Yes | None | 1415254 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023579&numberofmonths=24&showchangehistorylog=1 | 19-0023579 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 7745 | 20190214 | 1414 | 309608 | 1479 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 7395 | 39.3171 | -123.7281 | 1SPANLOADSIDE | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023579 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416726 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022956&numberofmonths=24&showchangehistorylog=1 | 19-0022956 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | EEL RIVER-1102 | 192381102 | FUSE | 1899 | 20190214 | 513 | 307177 | 392 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 4312 | 40.5106 | -124.1608 | 4SPANSLDSIDEOFFUCO1899HOWECREEKRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022956 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1416184 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023262&numberofmonths=24&showchangehistorylog=1 | 19-0023262 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | SWITCH | 3901 | 20190214 | 645 | 309266 | 1725 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 36225 | 39.2262 | -123.7483 | 3721ALBIONRIDGERD | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023262 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1416452 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023437&numberofmonths=24&showchangehistorylog=1 | 19-0023437 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 8639 | 20190214 | 805 | 307595 | 3286 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 19716 | 39.1218 | -123.5971 | 28400GREENWOOD | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023437 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416589 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023621&numberofmonths=24&showchangehistorylog=1 | 19-0023621 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | RECLOSER | 1260 | 20190214 | 1843 | 310646 | 1290 | Distribution Circuit | Vegetation | Tree - fell into line | 110 | 64164 | 39.1293 | -123.7112 | 27300PhiloGreenwoodRD1ST2SPANSEOFSBCO2605 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023621 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1416769 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022944&numberofmonths=24&showchangehistorylog=1 | 19-0022944 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 2023 | 20190214 | 730 | 307400 | 1605 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 57780 | 39.5493 | -123.7595 | FUCO9409 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022944 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1416173 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022972&numberofmonths=24&showchangehistorylog=1 | 19-0022972 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 2595 | 20190214 | 846 | 307912 | 494 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 494 | 40.0754 | -123.9572 | EOL | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0022972 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416198 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023207&numberofmonths=24&showchangehistorylog=1 | 19-0023207 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 8223 | 20190214 | 726 | 307384 | 3144 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 12576 | 38.7 | -123.425 | LDSIDEOFFUCO8223 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023207 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1416396 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024370&numberofmonths=24&showchangehistorylog=1 | 19-0024370 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 3151 | 20190215 | 1911 | 312909 | 1150 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 16100 | 39.3416 | -123.811 | 45401OVERTONDR | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024370 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1417455 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024369&numberofmonths=24&showchangehistorylog=1 | 19-0024369 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BRIDGEVILLE-1101 | 192461101 | FUSE | 6697 | 20190215 | 2225 | 313201 | 848 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 848 | 40.4744 | -123.6553 | 1SPANLDSIDEOF6697 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024369 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1417454 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024050&numberofmonths=24&showchangehistorylog=1 | 19-0024050 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LOW GAP-1101 | 192411101 | FUSE | 67185 | 20190215 | 1024 | 311845 | 1651 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 4953 | 40.4604 | -123.5127 | 1SSMTR101048135 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024050 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1417153 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024262&numberofmonths=24&showchangehistorylog=1 | 19-0024262 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LOW GAP-1101 | 192411101 | RECLOSER | 37498 | 20190215 | 1917 | 312684 | 1234 | Distribution Circuit | Vegetation | Tree - fell into line | 144 | 177696 | 40.2998 | -123.3426 | 1STSPANSSOFFU7015ONTHEMAINLINE | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024262 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1417340 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024651&numberofmonths=24&showchangehistorylog=1 | 19-0024651 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | JUMPER | OJS9SPANSLSOFLR3090 | 20190215 | 2133 | 314703 | 1214 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 4856 | 40.8806 | -123.5883 | 9SPANSSOFLR3090 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024651 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1417722 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024674&numberofmonths=24&showchangehistorylog=1 | 19-0024674 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE | 5247 | 20190215 | 2133 | 314800 | 2221 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 33315 | 40.8533 | -123.5731 | 5954SOUTHFORKRD | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024674 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1417748 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024517&numberofmonths=24&showchangehistorylog=1 | 19-0024517 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BRIDGEVILLE-1101 | 192461101 | RECLOSER | 11012 | 20190216 | 1124 | 314020 | 1761 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 66199 | 40.4798 | -123.7803 | EASTOF47929 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024517 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1417600 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024570&numberofmonths=24&showchangehistorylog=1 | 19-0024570 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | RECLOSER | 445166 | 20190216 | 1154 | 314111 | 347 | Distribution Circuit | Vegetation | Tree - fell into line | 316 | 100494 | 38.6937 | -123.4237 | BET44954497 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024570 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1417646 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025194&numberofmonths=24&showchangehistorylog=1 | 19-0025194 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BRIDGEVILLE-1102 | 192461102 | FUSE | 3463 | 20190217 | 1152 | 315780 | 238 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 2618 | 40.4786 | -123.8889 | 4SPANSLOADSIDE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025194 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1418272 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025107&numberofmonths=24&showchangehistorylog=1 | 19-0025107 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT SEWARD-1121 | 192321121 | RECLOSER | 1602 | 20190217 | 1116 | 315683 | 1594 | Distribution Circuit | Vegetation | Tree - fell into line | 86 | 47908 | 40.1834 | -123.5765 | 14SPANSLOADSIDEOF1837 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025107 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1418184 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025268&numberofmonths=24&showchangehistorylog=1 | 19-0025268 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LOW GAP-1101 | 192411101 | FUSE | 4157 | 20190217 | 801 | 315353 | 2024 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 12144 | 40.4084 | -123.4716 | 9SPANSLOADSIDE | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025268 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Multi-Fault | 1418327 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025278&numberofmonths=24&showchangehistorylog=1 | 19-0025278 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1102 | 192171102 | FUSE | 3113 | 20190217 | 1531 | 316405 | 1415 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 39620 | 40.7789 | -123.3308 | LDSIDEOF3113 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025278 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1418334 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025294&numberofmonths=24&showchangehistorylog=1 | 19-0025294 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE | 3079 | 20190217 | 1745 | 316582 | 1281 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 10248 | 40.7984 | -123.4043 | LDSIDEOF3079 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025294 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1418346 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028121&numberofmonths=24&showchangehistorylog=1 | 19-0028121 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | JUMPER | 5503 | 20190226 | 709 | 324052 | 435 | Distribution Circuit | Vegetation | Tree - fell into line | 225 | 97875 | 39.267 | -123.7531 | 2SPANSLDSIDEOF44269ONMAINLINE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028121 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Multi-Fault | 1420213 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028957&numberofmonths=24&showchangehistorylog=1 | 19-0028957 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 8127 | 20190226 | 2333 | 326174 | 1167 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 24507 | 39.3138 | -123.7466 | 4SPANSLDSIDE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028957 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Multi-Fault | 1420797 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0029110&numberofmonths=24&showchangehistorylog=1 | 19-0029110 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 5651 | 20190226 | 2213 | 325435 | 1159 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 8906 | 39.2768 | -123.7905 | 1SPANEOCGC214938059140 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0029110 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1420873 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028688&numberofmonths=24&showchangehistorylog=1 | 19-0028688 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | JUMPER | WIREDOWNATSB134281 | 20190226 | 2255 | 325726 | 937 | Distribution Circuit | Vegetation | Tree - branch fell on line | 95 | 50542 | 39.123 | -123.6038 | BARRINGTONSORRELT1102K3455atcos134281 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028688 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1420598 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028724&numberofmonths=24&showchangehistorylog=1 | 19-0028724 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 87163 | 20190226 | 2316 | 325565 | 969 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 21107 | 39.2261 | -123.7481 | 2SPANSLDSIDEOFSBCO3901 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028724 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1420635 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0029001&numberofmonths=24&showchangehistorylog=1 | 19-0029001 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 1905 | 20190226 | 2332 | 325724 | 1157 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 26611 | 39.228 | -123.7414 | LDSIDE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0029001 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Multi-Fault | 1420817 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028935&numberofmonths=24&showchangehistorylog=1 | 19-0028935 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 6069 | 20190226 | 2229 | 325488 | 2181 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 111231 | 39.6578 | -123.7827 | ATSBCO91173 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028935 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Multi-Fault | 1420786 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0029288&numberofmonths=24&showchangehistorylog=1 | 19-0029288 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 8947 | 20190226 | 2227 | 325313 | 7982 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 17474 | 39.6456 | -123.7506 | MTR1008390939 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0029288 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Multi-Fault | 1421014 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028507&numberofmonths=24&showchangehistorylog=1 | 19-0028507 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | RECLOSER | 35592 | 20190226 | 1739 | 324987 | 329 | Distribution Circuit | Vegetation | Tree - fell into line | 537 | 82593 | 39.3941 | -123.7793 | FelicichDavidsourcesideSB738867PERALDRANDNMITCHELLCREEKRD | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028507 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Three Phase Fault | 1420414 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028509&numberofmonths=24&showchangehistorylog=1 | 19-0028509 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 8573 | 20190226 | 1723 | 324950 | 955 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 11460 | 39.4205 | -123.7776 | 1SPANLDSIDEOF8573 | Clear-32-90 F | Conductor, Overhead | On Ground | 19-0028509 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1420418 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028461&numberofmonths=24&showchangehistorylog=1 | 19-0028461 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 3109 | 20190226 | 1423 | 324816 | 217 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 18879 | 39.4629 | -123.7936 | 32001AIRPORTRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028461 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1420384 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028598&numberofmonths=24&showchangehistorylog=1 | 19-0028598 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 1757 | 20190226 | 2114 | 325303 | 2428 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 38848 | 39.4416 | -123.7285 | 1SPANSSOF580787 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0028598 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1420504 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028503&numberofmonths=24&showchangehistorylog=1 | 19-0028503 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 2529 | 20190226 | 1447 | 324701 | 1528 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 7640 | 40.0889 | -123.9445 | 9SLDSIDEOF2529 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028503 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1420411 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028126&numberofmonths=24&showchangehistorylog=1 | 19-0028126 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 7461 | 20190226 | 745 | 324064 | 5825 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 34950 | 38.7685 | -123.5155 | LDSIDE | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028126 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Multi-Fault | 1420215 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028161&numberofmonths=24&showchangehistorylog=1 | 19-0028161 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | KONOCTI-1102 | 43311102 | FUSE | 92677 | 20190226 | 817 | 324061 | 605 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2420 | 38.947 | -122.6866 | LDSIDE | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028161 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Multi-Fault | 1420241 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028170&numberofmonths=24&showchangehistorylog=1 | 19-0028170 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1101 | 42601101 | FUSE | 4687 | 20190226 | 731 | 323924 | 295 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 7375 | 39.0335 | -123.3894 | 11611GOODACRELANE | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028170 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Multi-Fault | 1420248 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028100&numberofmonths=24&showchangehistorylog=1 | 19-0028100 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | UPPER LAKE-1101 | 42871101 | FUSE | 773 | 20190226 | 627 | 323875 | 414 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 1342 | 39.1713 | -122.8898 | 4SPANSLDSIDEOFFUSES | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028100 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1420199 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028252&numberofmonths=24&showchangehistorylog=1 | 19-0028252 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLOW CREEK-1101 | 192171101 | FUSE | 8247 | 20190226 | 1121 | 324322 | 149 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 298 | 40.8976 | -123.7714 | LDSIDEOF8247 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0028252 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Multi-Fault | 1420288 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028550&numberofmonths=24&showchangehistorylog=1 | 19-0028550 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1102 | 192171102 | RECLOSER | 3090 | 20190226 | 1931 | 325167 | 1424 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 68352 | 40.8889 | -123.5927 | AmbroseMark6spansldsideof3090 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028550 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1420455 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0029138&numberofmonths=24&showchangehistorylog=1 | 19-0029138 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE | 6073 | 20190227 | 1037 | 326844 | 1590 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 25471 | 38.658 | -123.2886 | JUSTNORTHOFCGC216421736361 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0029138 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1420891 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0029014&numberofmonths=24&showchangehistorylog=1 | 19-0029014 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 7341 | 20190227 | 224 | 326677 | 1074 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 4296 | 39.3199 | -123.8 | LDSIDE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0029014 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Multi-Fault | 1420823 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028962&numberofmonths=24&showchangehistorylog=1 | 19-0028962 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 5233 | 20190227 | 4 | 325930 | 2135 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 32399 | 39.2282 | -123.7663 | MTR1008874343 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028962 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Multi-Fault | 1420801 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0029004&numberofmonths=24&showchangehistorylog=1 | 19-0029004 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 4451 | 20190227 | 321 | 326234 | 2327 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 16289 | 38.7903 | -123.5105 | 2SPANSLDSIDEOF4451 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0029004 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1420818 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028726&numberofmonths=24&showchangehistorylog=1 | 19-0028726 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 7155 | 20190227 | 226 | 326167 | 701 | Distribution Circuit | Vegetation | Tree - fell into line | 98 | 22238 | 41.0509 | -123.6676 | MTR1008028496 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028726 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1420637 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028929&numberofmonths=24&showchangehistorylog=1 | 19-0028929 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1102 | 42601102 | FUSE | 9059 | 20190227 | 906 | 326674 | 452 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 4068 | 39.104 | -123.4974 | 4SPANSLDSIDEOF9059 | Overcast-Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0028929 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Multi-Fault | 1420783 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0065314&numberofmonths=24&showchangehistorylog=1 | 19-0065314 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 79817 | 20190610 | 1120 | 403592 | 200 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 9400 | 39.2085 | -123.7266 | 1STSPANLDSIDEOF79817 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0065314 | OH | Sus | 43837205 | yes | 2019 | JUN | Yes | Line to Line | 1447567 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0102283&numberofmonths=24&showchangehistorylog=1 | 19-0102283 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 1473 | 20190923 | 513 | 604148 | 389 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 3890 | 39.4173 | -123.7954 | 3SPANSLDSIDEOF1473 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0102283 | OH | Sus | 0 | yes | 2019 | SEP | Yes | Line to Ground | 1471938 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0126622&numberofmonths=24&showchangehistorylog=1 | 19-0126622 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | EEL RIVER-1102 | 192381102 | FUSE | 1907 | 20191120 | 130 | 710642 | 536 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 8576 | 40.4872 | -124.2599 | 4SPANSSSOFSBCO77379 | Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0126622 | OH | Sus | 0 | yes | 2019 | NOV | Yes | Line to Ground | 1492651 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0129754&numberofmonths=24&showchangehistorylog=1 | 19-0129754 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 2431 | 20191126 | 1601 | 716168 | 1565 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 27358 | 39.3456 | -123.7802 | 14310HUCKELBERRYPATH | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0129754 | OH | Sus | 0 | yes | 2019 | NOV | Yes | Line to Ground | 1494728 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0129264&numberofmonths=24&showchangehistorylog=1 | 19-0129264 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1104 | 42761104 | OTHER | WIREDOWN1SPLDSIDEOF3223 | 20191126 | 1536 | 716066 | 290 | Distribution Circuit | Vegetation | Tree - branch fell on line | 495 | 82500 | 39.4415 | -123.7783 | 1SPANLDSIDEOF3223 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0129264 | OH | Sus | 0 | yes | 2019 | NOV | Yes | Line to Ground | 1494287 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0009594&numberofmonths=24&showchangehistorylog=1 | 20-0009594 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ARCATA-1121 | 192021121 | FUSE | 1359 | 20200116 | 202 | 761903 | 2101 | Distribution Circuit | Vegetation | Tree - branch fell on line | 39 | 81939 | 40.8248 | -124.0015 | 2SPSSOFFUCO1269 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0009594 | OH | Sus | 0 | yes | 2020 | JAN | Yes | Line to Line | 1506718 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0009498&numberofmonths=24&showchangehistorylog=1 | 20-0009498 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ARCATA-1122 | 192021122 | FUSE | 5709 | 20200116 | 146 | 761891 | 689 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 11024 | 40.777 | -124.0035 | MTR1009022937MTR1010551746 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 20-0009498 | OH | Sus | 0 | yes | 2020 | JAN | Yes | Line to Ground | 1506668 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0009497&numberofmonths=24&showchangehistorylog=1 | 20-0009497 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BRIDGEVILLE-1101 | 192461101 | RECLOSER | 11012 | 20200116 | 432 | 761980 | 597 | Distribution Circuit | Vegetation | Tree - fell into line | 94 | 55514 | 40.4798 | -123.7803 | 3SPANSLDSIDEOF4101 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0009497 | OH | Sus | 0 | yes | 2020 | JAN | Yes | Line to Line | 1506667 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0010994&numberofmonths=24&showchangehistorylog=1 | 20-0010994 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT SEWARD-1121 | 192321121 | FUSE | 1659 | 20200116 | 614 | 765253 | 4630 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 18520 | 40.1631 | -123.616 | 12SPANSLDSIDE1659 | Overcast-Fog-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 20-0010994 | OH | Sus | 0 | yes | 2020 | JAN | Yes | Line to Line | 1507458 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0011174&numberofmonths=24&showchangehistorylog=1 | 20-0011174 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT SEWARD-1121 | 192321121 | FUSE | 4367 | 20200116 | 614 | 766118 | 4897 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 73455 | 40.1473 | -123.6358 | 950RANCHOSEQUOIARD | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0011174 | OH | Sus | 0 | yes | 2020 | JAN | Yes | Line to Ground | 1507704 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0009525&numberofmonths=24&showchangehistorylog=1 | 20-0009525 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1141 | 192311141 | RECLOSER | 8860 | 20200116 | 610 | 762125 | 601 | Distribution Circuit | Vegetation | Tree - fell into line | 161 | 96761 | 40.2829 | -123.8726 | 4SPANSLDSIDEOF8860 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0009525 | OH | Sus | 0 | yes | 2020 | JAN | Yes | Line to Line | 1506689 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0011186&numberofmonths=24&showchangehistorylog=1 | 20-0011186 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 1679 | 20200116 | 726 | 766142 | 4968 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 228528 | 40.2781 | -123.7929 | 2SPSSOF8055 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0011186 | OH | Sus | 0 | yes | 2020 | JAN | Yes | Line to Ground | 1507715 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0009495&numberofmonths=24&showchangehistorylog=1 | 20-0009495 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 1510 | 20200116 | 413 | 761956 | 2265 | Distribution Circuit | Vegetation | Tree - fell into line | 356 | 792687 | 40.1221 | -123.8352 | ATFUCO2583 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0009495 | OH | Sus | 0 | yes | 2020 | JAN | Yes | Multi-Fault | 1506665 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0010326&numberofmonths=24&showchangehistorylog=1 | 20-0010326 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 1793 | 20200116 | 413 | 763648 | 2265 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 18120 | 40.0258 | -123.9471 | 1SPANLDSIDE1793 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0010326 | OH | Sus | 0 | yes | 2020 | JAN | Yes | Open Circuit | 1507043 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0010920&numberofmonths=24&showchangehistorylog=1 | 20-0010920 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 1787 | 20200116 | 413 | 765118 | 3457 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 48398 | 40.0106 | -123.9297 | 5817POLESLDSIDE1787 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0010920 | OH | Sus | 0 | yes | 2020 | JAN | Yes | Open Circuit | 1507417 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0009489&numberofmonths=24&showchangehistorylog=1 | 20-0009489 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | RECLOSER | 1294 | 20200116 | 318 | 761942 | 347 | Distribution Circuit | Vegetation | Tree - fell into line | 630 | 62299 | 38.8037 | -123.5835 | ThorpeTim2094SSO4455Fucos | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0009489 | OH | Sus | 0 | yes | 2020 | JAN | Yes | Force Out | 1506659 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0010303&numberofmonths=24&showchangehistorylog=1 | 20-0010303 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 8435 | 20200116 | 259 | 763568 | 6605 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 145310 | 41.2085 | -123.7558 | 11SPANSLDSIDEOFFU8435 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0010303 | OH | Sus | 0 | yes | 2020 | JAN | Yes | Open Circuit | 1507018 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0011049&numberofmonths=24&showchangehistorylog=1 | 20-0011049 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 7535 | 20200116 | 259 | 765494 | 5001 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 25005 | 41.1272 | -123.7254 | 24SPANSLDSIDEOFFUSES | Overcast-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 20-0011049 | OH | Sus | 0 | yes | 2020 | JAN | Yes | Multi-Fault | 1507544 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0011341&numberofmonths=24&showchangehistorylog=1 | 20-0011341 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 6633 | 20200116 | 259 | 766566 | 10666 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 42664 | 41.2495 | -123.6496 | DAMAGEEVERYWHERE | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 20-0011341 | OH | Sus | 0 | yes | 2020 | JAN | Yes | Open Circuit | 1507859 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0010377&numberofmonths=24&showchangehistorylog=1 | 20-0010377 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1101 | 42681101 | RECLOSER | 518 | 20200116 | 627 | 762105 | 4832 | Distribution Circuit | Vegetation | Tree - fell into line | 525 | 1796587 | 39.7981 | -123.5405 | 7SSLR176020LDSDLR1760 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0010377 | OH | Sus | 0 | yes | 2020 | JAN | Yes | Line to Ground | 1507097 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0009710&numberofmonths=24&showchangehistorylog=1 | 20-0009710 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE | 2503 | 20200116 | 545 | 762026 | 4945 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 39560 | 39.7479 | -123.5342 | 4SPANSLDSIDEOF2503 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0009710 | OH | Sus | 0 | yes | 2020 | JAN | Yes | Line to Line | 1506800 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0009939&numberofmonths=24&showchangehistorylog=1 | 20-0009939 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE | 4639 | 20200116 | 606 | 762073 | 3579 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 60843 | 39.7139 | -123.4909 | 9SPLDSIDEOF463910SPLDSIDEOF4639 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0009939 | OH | Sus | 0 | yes | 2020 | JAN | Yes | Line to Ground | 1506868 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0009955&numberofmonths=24&showchangehistorylog=1 | 20-0009955 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE | 2457 | 20200116 | 613 | 762038 | 3195 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 146765 | 39.741 | -123.5169 | VALLEYDRIVE3POLESLDSIDEOFLBTWD7177 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0009955 | OH | Sus | 0 | yes | 2020 | JAN | Yes | Line to Ground | 1506873 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0010932&numberofmonths=24&showchangehistorylog=1 | 20-0010932 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE | 2577 | 20200116 | 649 | 765124 | 2290 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 107630 | 39.6878 | -123.4951 | LDSIDE2577851BAUERRD | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0010932 | OH | Sus | 0 | yes | 2020 | JAN | Yes | Multi-Fault | 1507418 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0009576&numberofmonths=24&showchangehistorylog=1 | 20-0009576 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE | 5259 | 20200116 | 620 | 762221 | 822 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 15618 | 39.6513 | -123.4846 | 1PLDSIDEOFCGC215822572677 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0009576 | OH | Sus | 0 | yes | 2020 | JAN | Yes | Line to Line | 1506714 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0009587&numberofmonths=24&showchangehistorylog=1 | 20-0009587 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1102 | 42681102 | OCB | 11022 | 20200116 | 748 | 762227 | 1973 | Distribution Circuit | Vegetation | Tree - fell into line | 601 | 270017 | 39.6848 | -123.477 | GALLETTITIMTREEINTOLINE175MULLIGANLN | Overcast-Fog-Rain-32-90 F | Crossarm, Wood | Broken, wire on object | 20-0009587 | OH | Sus | 0 | yes | 2020 | JAN | Yes | Line to Ground | 1506717 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0010301&numberofmonths=24&showchangehistorylog=1 | 20-0010301 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1102 | 42681102 | JUMPER | OJ20SPANSLDSIDEOF3893 | 20200116 | 519 | 763565 | 1744 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 22672 | 39.6993 | -123.653 | 21SPANSLDSIDE3893 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0010301 | OH | Sus | 0 | yes | 2020 | JAN | Yes | Open Circuit | 1507017 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0010309&numberofmonths=24&showchangehistorylog=1 | 20-0010309 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE | 80039 | 20200116 | 658 | 763582 | 2023 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 135541 | 39.6734 | -123.5005 | SBCO5741 | Overcast-Fog-Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 20-0010309 | OH | Sus | 0 | yes | 2020 | JAN | Yes | Open Circuit | 1507025 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0010315&numberofmonths=24&showchangehistorylog=1 | 20-0010315 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE | 2359 | 20200116 | 1153 | 763354 | 3187 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 54179 | 39.6189 | -123.4633 | GALLETTITIMTREESTHROUGHLINE39700BOARRD | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0010315 | OH | Sus | 0 | yes | 2020 | JAN | Yes | Line to Ground | 1507031 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0009490&numberofmonths=24&showchangehistorylog=1 | 20-0009490 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LOW GAP-1101 | 192411101 | RECLOSER | 2094 | 20200116 | 317 | 761945 | 2412 | Distribution Circuit | Vegetation | Tree - fell into line | 303 | 275436 | 40.436 | -123.4882 | 3SPANSSSOFFUCO43723 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0009490 | OH | Sus | 0 | yes | 2020 | JAN | Yes | Multi-Fault | 1506660 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0009480&numberofmonths=24&showchangehistorylog=1 | 20-0009480 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | MAPLE CREEK-1101 | 192101101 | OCB | 11012 | 20200116 | 125 | 761886 | 976 | Distribution Circuit | Vegetation | Tree - fell into line | 146 | 34096 | 40.7683 | -123.874 | MTR1007960424 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0009480 | OH | Sus | 0 | yes | 2020 | JAN | Yes | Line to Line | 1506650 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0009483&numberofmonths=24&showchangehistorylog=1 | 20-0009483 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | RIO DELL-1102 | 192251102 | RECLOSER | 4230 | 20200116 | 217 | 761896 | 11 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 286 | 40.4173 | -124.0895 | MULTIPLELOCBETWEEN200175286 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0009483 | OH | Sus | 0 | yes | 2020 | JAN | Yes | Multi-Fault | 1506653 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0009481&numberofmonths=24&showchangehistorylog=1 | 20-0009481 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLOW CREEK-1101 | 192171101 | RECLOSER | 29362 | 20200116 | 134 | 761887 | 9185 | Distribution Circuit | Vegetation | Tree - fell into line | 95 | 871469 | 40.8941 | -123.7726 | HIGHTOWERWALT6polesloadsideof30501polessof3023 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0009481 | OH | Sus | 0 | yes | 2020 | JAN | Yes | Line to Ground | 1506651 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0009554&numberofmonths=24&showchangehistorylog=1 | 20-0009554 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLOW CREEK-1101 | 192171101 | SWITCH | 3139 | 20200116 | 259 | 762158 | 6436 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 51488 | 40.9147 | -123.7024 | 2SPANSSSAND6SPANSLOADSIDEOF3043 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 20-0009554 | OH | Sus | 0 | yes | 2020 | JAN | Yes | Line to Ground | 1506700 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0010592&numberofmonths=24&showchangehistorylog=1 | 20-0010592 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLOW CREEK-1101 | 192171101 | FUSE | 3053 | 20200116 | 300 | 764770 | 3522 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 91572 | 40.9506 | -123.6537 | 5WOF3173 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0010592 | OH | Sus | 0 | yes | 2020 | JAN | Yes | Open Circuit | 1507309 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0010959&numberofmonths=24&showchangehistorylog=1 | 20-0010959 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLOW CREEK-1101 | 192171101 | FUSE | 7283 | 20200116 | 259 | 765175 | 6649 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 6649 | 40.9112 | -123.7055 | 2SPANSLDSIDEFU7283 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 20-0010959 | OH | Sus | 0 | yes | 2020 | JAN | Yes | Open Circuit | 1507433 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0010307&numberofmonths=24&showchangehistorylog=1 | 20-0010307 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE | 5521 | 20200116 | 300 | 763576 | 3425 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 58225 | 40.8906 | -123.5608 | 151ODENFLATRD | Clear-Below 32 F | Connector or Splice (OH) | Broken, wire on ground | 20-0010307 | OH | Sus | 0 | yes | 2020 | JAN | Yes | Line to Ground | 1507022 | CSO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0010579&numberofmonths=24&showchangehistorylog=1 | 20-0010579 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE | 2899 | 20200116 | 1942 | 764754 | 2576 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 54096 | 40.871 | -123.5778 | 7SPANSLDSIDEOFFU2899 | Overcast-Fog-Below 32 F | Pole-Wood | Broken, wire on ground | 20-0010579 | OH | Sus | 0 | yes | 2020 | JAN | Yes | Multi-Fault | 1507301 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0010636&numberofmonths=24&showchangehistorylog=1 | 20-0010636 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | JUMPER | WIREDOWN3SPANSLDSIDEOF2989 | 20200116 | 1921 | 764829 | 2601 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 6841 | 40.8366 | -123.4913 | 3SPANSLDSIDEOFFU2989 | Partly Cloudy-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0010636 | OH | Sus | 0 | yes | 2020 | JAN | Yes | Open Circuit | 1507334 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0019275&numberofmonths=24&showchangehistorylog=1 | 20-0019275 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LOW GAP-1101 | 192411101 | FUSE | 4199 | 20200209 | 1230 | 784209 | 592 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1776 | 40.418 | -123.4574 | 2POLESLDSIDEOFFUCO4199 | Clear | Pole-Wood | Broken, wire on ground | 20-0019275 | OH | Sus | 0 | yes | 2020 | FEB | Yes | Open Circuit | 1513304 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0032183&numberofmonths=24&showchangehistorylog=1 | 20-0032183 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | OCB | 11012 | 20200315 | 406 | 851771 | 800 | Distribution Circuit | Environmental/External | Ice or snow | 1270 | 158601 | 40.1033 | -123.7926 | 5671ONMAINLINE | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0032183 | OH | Sus | 0 | yes | 2020 | MAR | Yes | Multi-Fault | 1521516 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0032241&numberofmonths=24&showchangehistorylog=1 | 20-0032241 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1101 | 42681101 | OTHER | WIREDOWN46800NHIGHWAY101 | 20200315 | 623 | 851911 | 323 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 2263 | 39.7125 | -123.4977 | 46800NHIGHWAY101 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 20-0032241 | OH | Sus | 0 | yes | 2020 | MAR | Yes | Line to Ground | 1521574 | CSO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0032250&numberofmonths=24&showchangehistorylog=1 | 20-0032250 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE | 2499 | 20200315 | 634 | 851917 | 794 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 12704 | 39.668 | -123.5141 | 10SPANSLDSIDEOF2499BEFORE3483 | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0032250 | OH | Sus | 0 | yes | 2020 | MAR | Yes | Line to Line | 1521580 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0032249&numberofmonths=24&showchangehistorylog=1 | 20-0032249 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1104 | 42661104 | FUSE | 4943 | 20200315 | 836 | 852070 | 249 | Distribution Circuit | Vegetation | Tree - fell into line | 113 | 10545 | 39.4387 | -123.3913 | 1SPANLDSIDEOFMTR5000119705 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0032249 | OH | Sus | 0 | yes | 2020 | MAR | Yes | Line to Ground | 1521579 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0085153&numberofmonths=24&showchangehistorylog=1 | 20-0085153 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOPLAND-1101 | 42251101 | FUSE | 5865 | 20200816 | 1503 | 1013103 | 434 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 19530 | 39.0413 | -123.1868 | 11SPLS5865 | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 20-0085153 | OH | Sus | 0 | yes | 2020 | AUG | Yes | Line to Ground | 1555583 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0084718&numberofmonths=24&showchangehistorylog=1 | 20-0084718 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LUCERNE-1106 | 43351106 | RECLOSER | 38632 | 20200816 | 552 | 1010933 | 560 | Distribution Circuit | Vegetation | Tree - fell into line | 259 | 145040 | 38.9913 | -122.7481 | THORNTONELLIST2348K3415rivierawestandmountaincrest | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0084718 | OH | Sus | 0 | yes | 2020 | AUG | Yes | Line to Line | 1555191 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0113188&numberofmonths=24&showchangehistorylog=1 | 20-0113188 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | POTTER VALLEY P H-1105 | 42281105 | RECLOSER | 64118 | 20201025 | 2041 | 1127408 | 956 | Distribution Circuit | Vegetation | Tree - branch fell on line | 634 | 604799 | 39.362 | -123.1283 | GALLETTITIMTREEBRANCHNOFCGC216855060457 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0113188 | OH | Sus | 0 | No | 2020 | OCT | Yes | Line to Ground | 1574323 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0009573&numberofmonths=24&showchangehistorylog=1 | 21-0009573 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE | 1817 | 20210118 | 248 | 1212078 | 600 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 3600 | 39.8644 | -123.7247 | 3SPANSLDSIDEOF1817 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0009573 | OH | Sus | 0 | No | 2021 | JAN | Yes | Multi-Fault | 1593620 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0010034&numberofmonths=24&showchangehistorylog=1 | 21-0010034 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | KONOCTI-1102 | 43311102 | RECLOSER | 64664 | 20210119 | 142 | 1214075 | 818 | Distribution Circuit | Vegetation | Tree - fell into line | 305 | 100272 | 38.9433 | -122.8017 | SW5345 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0010034 | OH | Sus | 0 | No | 2021 | JAN | Yes | Multi-Fault | 1593996 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0010215&numberofmonths=24&showchangehistorylog=1 | 21-0010215 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LOW GAP-1101 | 192411101 | RECLOSER | 37484 | 20210119 | 546 | 1214919 | 1057 | Distribution Circuit | Vegetation | Tree - fell into line | 319 | 80153 | 40.436 | -123.4882 | MTR100868534022SPANSSSOF4107HADALIMBONLINE | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0010215 | OH | Sus | 0 | No | 2021 | JAN | Yes | Three Phase Fault | 1594183 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0014749&numberofmonths=24&showchangehistorylog=1 | 21-0014749 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 6865 | 20210126 | 1541 | 1226346 | 289 | Distribution Circuit | Vegetation | Tree - branch fell on line | 95 | 27455 | 40.2936 | -123.8176 | 12SPLDSIDEOF6865 | Clear-32-90 F | Conductor, Overhead | On Ground | 21-0014749 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1597286 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0014752&numberofmonths=24&showchangehistorylog=1 | 21-0014752 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 2540 | 20210126 | 1708 | 1226433 | 8712 | Distribution Circuit | Vegetation | Tree - fell into line | 347 | 215664 | 40.2432 | -124.1269 | MULTIPLELOCATIONS | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0014752 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Line | 1597289 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0014550&numberofmonths=24&showchangehistorylog=1 | 21-0014550 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | RIO DELL-1102 | 192251102 | RECLOSER | 75970 | 20210126 | 1255 | 1226028 | 235 | Distribution Circuit | Equipment Failure/Involved | Overhead | 210 | 7772 | 40.471 | -124.1364 | 23SPANSLDSIDEOFLR75970 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 21-0014550 | OH | Sus | 0 | No | 2021 | JAN | Yes | Force Out | 1597190 | CSO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0017859&numberofmonths=24&showchangehistorylog=1 | 21-0017859 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | RECLOSER | 63170 | 20210128 | 1745 | 1240385 | 222 | Distribution Circuit | Vegetation | Tree - fell into line | 146 | 32412 | 40.222 | -123.82 | 3SPWESTOF1599 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0017859 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1599900 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0099421&numberofmonths=24&showchangehistorylog=1 | 21-0099421 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | MAPLE CREEK-1101 | 192101101 | OCB | 11012 | 20210804 | 55 | 1433291 | 102 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 150 | 6191 | 40.7683 | -123.874 | BETWEENSW6047LR6906 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0099421 | OH | Sus | 0 | No | 2021 | AUG | Yes | Three Phase Fault | 1654383 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0132067&numberofmonths=24&showchangehistorylog=1 | 21-0132067 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 5681 | 20211017 | 1502 | 1499622 | 533 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 5330 | 39.4801 | -123.7869 | 2LDSIDEOFFU5681 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0132067 | OH | Sus | 31554914 | No | 2021 | OCT | Yes | Line to Ground | 1674914 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0135570&numberofmonths=24&showchangehistorylog=1 | 21-0135570 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ARCATA-1122 | 192021122 | OTHER | 4571 | 20211024 | 213 | 1507503 | 634 | Distribution Circuit | Vegetation | Tree - fell into line | 130 | 82420 | 40.7929 | -124.0234 | 1SSFU8679 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0135570 | OH | Sus | 0 | No | 2021 | OCT | Yes | Open Circuit | 1677086 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0135839&numberofmonths=24&showchangehistorylog=1 | 21-0135839 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3909 | 20211024 | 750 | 1508616 | 209 | Distribution Circuit | Vegetation | Tree - branch fell on line | 141 | 5920 | 39.3996 | -123.7155 | TRANSPOLE366 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0135839 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Ground | 1677315 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0135917&numberofmonths=24&showchangehistorylog=1 | 21-0135917 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 7253 | 20211024 | 710 | 1508214 | 301 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 5117 | 39.4188 | -123.778 | 4SPANSEOF7253 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0135917 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Ground | 1677387 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0136152&numberofmonths=24&showchangehistorylog=1 | 21-0136152 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 1757 | 20211024 | 736 | 1508483 | 544 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 8704 | 39.4414 | -123.7283 | 1SPANSOFCGC215186565050 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0136152 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Line | 1677627 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0136049&numberofmonths=24&showchangehistorylog=1 | 21-0136049 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 1879 | 20211024 | 1149 | 1509238 | 391 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 3796 | 39.8178 | -123.7647 | 2NDTOLASTSPAN | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0136049 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Ground | 1677517 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0135812&numberofmonths=24&showchangehistorylog=1 | 21-0135812 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1102 | 42601102 | FUSE | 2603 | 20211024 | 605 | 1507762 | 658 | Distribution Circuit | Vegetation | Tree - branch fell on line | 42 | 27636 | 39.0767 | -123.519 | CGC215691151652 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0135812 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Ground | 1677290 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0137448&numberofmonths=24&showchangehistorylog=1 | 21-0137448 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 502837 | 20211025 | 1310 | 1519411 | 325 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 325 | 41.286 | -123.8276 | 2SPANSLDSIDEOFFUCO502837 | Clear-32-90 F | Conductor, Overhead | On Ground | 21-0137448 | OH | Sus | 0 | No | 2021 | OCT | Yes | Force Out | 1678792 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0156920&numberofmonths=24&showchangehistorylog=1 | 21-0156920 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | OTHER | WIREDOWN2SSOF8035 | 20211213 | 319 | 1565670 | 478 | Distribution Circuit | Vegetation | Tree - fell into line | 375 | 163972 | 40.1861 | -124.0914 | 2SPANSSOURCESIDEOF8035 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0156920 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1693810 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0158512&numberofmonths=24&showchangehistorylog=1 | 21-0158512 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 1607 | 20211215 | 1517 | 1572900 | 363 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 1815 | 39.4422 | -123.7723 | 2SPANSLDSIDEOFFUCO1607 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0158512 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1695505 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0158440&numberofmonths=24&showchangehistorylog=1 | 21-0158440 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | HARRIS-1109 | 192431109 | FUSE | 893 | 20211215 | 1127 | 1572477 | 344 | Distribution Circuit | Vegetation | Tree - branch fell on line | 28 | 9632 | 40.7585 | -124.0501 | 12SPANSLDSIDEOF0893 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0158440 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1695415 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0158436&numberofmonths=24&showchangehistorylog=1 | 21-0158436 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | HUMBOLDT BAY-1102 | 192341102 | FUSE | 4301 | 20211215 | 1135 | 1572633 | 425 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 16575 | 40.703 | -124.1535 | 1LSSIDEOFFU7617 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0158436 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1695409 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0158432&numberofmonths=24&showchangehistorylog=1 | 21-0158432 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1103 | 42661103 | FUSE | 2853 | 20211215 | 1046 | 1572419 | 347 | Distribution Circuit | Vegetation | Tree - fell into line | 125 | 15946 | 39.4684 | -123.3974 | ONTAPFEEDINGCGC216002766431 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0158432 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1695403 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0160523&numberofmonths=24&showchangehistorylog=1 | 21-0160523 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 461681 | 20211225 | 158 | 1581130 | 714 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 19278 | 40.2217 | -123.7969 | 2SSOF3773HODGESRD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0160523 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1697995 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0160664&numberofmonths=24&showchangehistorylog=1 | 21-0160664 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1102 | 42601102 | RECLOSER | 2600 | 20211225 | 2353 | 1581956 | 540 | Distribution Circuit | Vegetation | Tree - branch fell on line | 95 | 22232 | 39.0853 | -123.4851 | WelshTyler7078069777LR2600 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0160664 | OH | Sus | 0 | No | 2021 | DEC | Yes | Force Out | 1698147 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0160770&numberofmonths=24&showchangehistorylog=1 | 21-0160770 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1103 | 42661103 | FUSE | 8049 | 20211226 | 1213 | 1582444 | 467 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1868 | 39.4991 | -123.4507 | 2PSSCGC215902167125 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0160770 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Line | 1698270 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0160782&numberofmonths=24&showchangehistorylog=1 | 21-0160782 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1103 | 42661103 | FUSE | 6423 | 20211226 | 1324 | 1582635 | 293 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 8204 | 39.4878 | -123.4249 | 29401TIMBERLINERD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0160782 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Line | 1698284 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0160942&numberofmonths=24&showchangehistorylog=1 | 21-0160942 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BRIDGEVILLE-1101 | 192461101 | FUSE | 43757 | 20211227 | 246 | 1585593 | 2427 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 4854 | 40.4857 | -123.7583 | 1SPANLDSIDEOFFU43757 | Clear-32-90F | Conductor, Overhead | On Ground | 21-0160942 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1698635 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0160947&numberofmonths=24&showchangehistorylog=1 | 21-0160947 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1102 | 42661102 | FUSE | 1765 | 20211227 | 149 | 1583825 | 501 | Distribution Circuit | Vegetation | Tree - fell into line | 120 | 60120 | 39.4126 | -123.3575 | 1SPANLDSIDEOF1765 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0160947 | OH | Sus | 0 | No | 2021 | DEC | Yes | Three Phase Fault | 1698472 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0161157&numberofmonths=24&showchangehistorylog=1 | 21-0161157 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | OTHER | 6779 | 20211227 | 1228 | 1585745 | 329 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1316 | 39.4344 | -123.2451 | 2POLESLDSIDEOFCGC216499164515 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0161157 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1698736 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0161012&numberofmonths=24&showchangehistorylog=1 | 21-0161012 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1104 | 42661104 | FUSE | 2007 | 20211227 | 709 | 1584730 | 306 | Distribution Circuit | Vegetation | Tree - branch fell on line | 40 | 12240 | 39.4227 | -123.4035 | 23660RIDGERD | Clear-32-90F | Conductor, Overhead | On Ground | 21-0161012 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Line | 1698551 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0107533&numberofmonths=24&showchangehistorylog=1 | 22-0107533 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 2500 | 20220907 | 1502 | 1804705 | 413 | Distribution Circuit | Vegetation | Tree - fell into line | 452 | 165918 | 40.1083 | -123.9286 | 2SPANSSOF8035SBCO | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0107533 | OH | Sus | 31615353 | No | 2022 | SEP | Yes | Line to Line | 1766832 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0138047&numberofmonths=24&showchangehistorylog=1 | 22-0138047 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | RECLOSER | 79628 | 20221210 | 409 | 1880294 | 517 | Distribution Circuit | Vegetation | Tree - fell into line | 371 | 152117 | 39.312 | -123.786 | PARDINIJAKE43901littlelakerd | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0138047 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1788872 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0138072&numberofmonths=24&showchangehistorylog=1 | 22-0138072 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 8721 | 20221210 | 542 | 1880333 | 278 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 6672 | 39.3656 | -123.7983 | 7SPANSLDSIDE8721 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0138072 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1788897 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0138069&numberofmonths=24&showchangehistorylog=1 | 22-0138069 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 6645 | 20221210 | 426 | 1880375 | 650 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 7800 | 39.2439 | -123.7705 | W2VJ5SZ3spanssourceside6645cutouts | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0138069 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1788894 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0138077&numberofmonths=24&showchangehistorylog=1 | 22-0138077 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | OTHER | WIREDOWN1LDSIDE215049057372 | 20221210 | 611 | 1880349 | 526 | Distribution Circuit | Vegetation | Tree - branch fell on line | 23 | 10729 | 39.228 | -123.7505 | 1SPANLDSIDECGC215049057372 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0138077 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1788903 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0138343&numberofmonths=24&showchangehistorylog=1 | 22-0138343 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 2519 | 20221210 | 248 | 1880253 | 841 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 10682 | 40.2781 | -124.2429 | EOL | Clear-32-90F | Crossarm, Wood | Broken, wire on ground | 22-0138343 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1789172 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0138032&numberofmonths=24&showchangehistorylog=1 | 22-0138032 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | RECLOSER | 7514 | 20221210 | 118 | 1880153 | 815 | Distribution Circuit | Vegetation | Tree - fell into line | 1274 | 699327 | 40.9333 | -123.6249 | HIGHTOWERWALTFUCO5685 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0138032 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Line | 1788856 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0142634&numberofmonths=24&showchangehistorylog=1 | 22-0142634 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER | 37506 | 20221231 | 1519 | 1904736 | 411 | Distribution Circuit | Equipment Failure/Involved | Overhead | 84 | 20742 | 39.4823 | -123.3615 | WIREDOWNLDSIDEOFCGC216132966996 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0142634 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1794434 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0005533&numberofmonths=24&showchangehistorylog=1 | 23-0005533 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | CALPELLA-1101 | 43411101 | RECLOSER | 542 | 20230104 | 631 | 1912349 | 5182 | Distribution Circuit | Vegetation | Tree - fell into line | 390 | 173125 | 39.2357 | -123.1786 | TREEBRANCHDEADENDPOLECGC216740057665TREECGC21671935788 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 23-0005533 | OH | Sus | 0 | No | 2023 | JAN | Yes | Multi-Fault | 1796003 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0005593&numberofmonths=24&showchangehistorylog=1 | 23-0005593 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 3139 | 20230104 | 635 | 1912357 | 398 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 21492 | 39.5106 | -123.7644 | W2VJ5SZCustmisassignedshouldbessd3139fusecutouts | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0005593 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Line | 1796047 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0005723&numberofmonths=24&showchangehistorylog=1 | 23-0005723 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 8229 | 20230104 | 754 | 1913135 | 586 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 586 | 39.4543 | -123.7942 | JASONSUTTONLoadsideof8229toeol | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0005723 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1796131 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0005797&numberofmonths=24&showchangehistorylog=1 | 23-0005797 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 364133 | 20230104 | 823 | 1913458 | 469 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 7504 | 39.4437 | -123.7787 | 5EOF913495 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0005797 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Line | 1796197 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0005861&numberofmonths=24&showchangehistorylog=1 | 23-0005861 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | MENDOCINO-1101 | 42951101 | RECLOSER | 48750 | 20230104 | 1140 | 1913604 | 4713 | Distribution Circuit | Vegetation | Tree - fell into line | 152 | 27967 | 39.3316 | -123.2248 | 2SPNOFCGC216517561765 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0005861 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1796243 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0008775&numberofmonths=24&showchangehistorylog=1 | 23-0008775 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | JUMPER | OJS2SSOFMTR1008917383 | 20230107 | 1037 | 1926384 | 441 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 882 | 40.1108 | -123.8926 | MTR1008917383 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0008775 | OH | Sus | 0 | No | 2023 | JAN | Yes | Open Circuit | 1798647 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0010804&numberofmonths=24&showchangehistorylog=1 | 23-0010804 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 3063 | 20230109 | 359 | 1935576 | 505 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 23230 | 39.2846 | -123.7929 | 7LOADSIDE | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0010804 | OH | Sus | 0 | No | 2023 | JAN | Yes | Three Phase Fault | 1800664 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0010931&numberofmonths=24&showchangehistorylog=1 | 23-0010931 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1102 | 42681102 | JUMPER | OJS1SPANSSOFFUCO7593 | 20230109 | 815 | 1937153 | 540 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1080 | 39.4719 | -123.3634 | SS7593 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0010931 | OH | Sus | 0 | No | 2023 | JAN | Yes | Force Out | 1800771 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0011200&numberofmonths=24&showchangehistorylog=1 | 23-0011200 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | LAYTONVILLE-1102 | 42681102 | FUSE | 2583 | 20230109 | 1238 | 1937492 | 261 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 1566 | 39.5109 | -123.4402 | 2SPLDSIDEFUCO2543 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0011200 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1800999 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0012134&numberofmonths=24&showchangehistorylog=1 | 23-0012134 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 3291 | 20230110 | 748 | 1943475 | 606 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 10908 | 39.3095 | -123.7497 | 42271LITTLELAKERD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0012134 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1801904 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0012389&numberofmonths=24&showchangehistorylog=1 | 23-0012389 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LUCERNE-1106 | 43351106 | FUSE | 4131 | 20230110 | 1110 | 1944767 | 282 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 1128 | 39.0087 | -122.7528 | FOUND1WIREDOWN1SPANTREELIMBBETWEENFUSESCGC217865848958 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0012389 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1802114 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0012160&numberofmonths=24&showchangehistorylog=1 | 23-0012160 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1101 | 42601101 | FUSE | 821 | 20230110 | 533 | 1943137 | 790 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 31366 | 39.0093 | -123.3842 | 1SPANLDSIDEOFLINEBUCKTWDSCGC215996049165 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0012160 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Line | 1801928 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0012104&numberofmonths=24&showchangehistorylog=1 | 23-0012104 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1103 | 42661103 | FUSE | 1855 | 20230110 | 56 | 1939843 | 1000 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 32000 | 39.3785 | -123.275 | 5SPANSLDSIDEOF1855 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0012104 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1801878 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0015919&numberofmonths=24&showchangehistorylog=1 | 23-0015919 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 3287 | 20230114 | 650 | 1952957 | 357 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 22134 | 39.3136 | -123.7466 | 4SPANSSOURCESIDEOFFUCO7745 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0015919 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Line | 1804753 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0016021&numberofmonths=24&showchangehistorylog=1 | 23-0016021 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | RECLOSER | 69032 | 20230114 | 949 | 1953753 | 584 | Distribution Circuit | Vegetation | Tree - fell into line | 126 | 73584 | 39.2996 | -123.7895 | GarciaDanT1260K346744071comptcherd | Clear-32-90F | Pole-Wood | Broken, wire on ground | 23-0016021 | OH | Sus | 0 | No | 2023 | JAN | Yes | Three Phase Fault | 1804838 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0015866&numberofmonths=24&showchangehistorylog=1 | 23-0015866 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BRIDGEVILLE-1102 | 192461102 | RECLOSER | 55612 | 20230114 | 701 | 1952925 | 330 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 9240 | 40.4664 | -123.8013 | 5LDSIDEOFFUCO4361 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0015866 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1804705 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0015849&numberofmonths=24&showchangehistorylog=1 | 23-0015849 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | RECLOSER | 1260 | 20230114 | 637 | 1952832 | 447 | Distribution Circuit | Vegetation | Tree - branch fell on line | 96 | 20272 | 39.1294 | -123.7111 | ThorpeTim20941lso997095 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0015849 | OH | Sus | 0 | No | 2023 | JAN | Yes | Three Phase Fault | 1804691 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0016075&numberofmonths=24&showchangehistorylog=1 | 23-0016075 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 600433 | 20230114 | 810 | 1953177 | 662 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 6620 | 39.5161 | -123.7319 | 3SPANSFROMEOLFROMCGC215078068280 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0016075 | OH | Sus | 0 | No | 2023 | JAN | Yes | Three Phase Fault | 1804878 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0016123&numberofmonths=24&showchangehistorylog=1 | 23-0016123 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT SEWARD-1122 | 192321122 | OTHER | WIREDOWN3SPANSLDSIDE | 20230114 | 727 | 1954161 | 767 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1311 | 40.2395 | -123.6251 | 16953SPANSLDSIDEWIREDOWN | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0016123 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1804913 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0015853&numberofmonths=24&showchangehistorylog=1 | 23-0015853 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | OTHER | WIREDOWN16LDSIDE202293 | 20230114 | 633 | 1952847 | 557 | Distribution Circuit | Vegetation | Tree - fell into line | 1146 | 336874 | 40.2834 | -123.8668 | 16LDSIDE202293ATHWY254HIDDENSPRINGSCAMPROUND | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0015853 | OH | Sus | 0 | No | 2023 | JAN | Yes | Open Circuit | 1804696 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0015863&numberofmonths=24&showchangehistorylog=1 | 23-0015863 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | JUMPER | WIREDOWN10SPANSSEOF8331 | 20230114 | 655 | 1952901 | 197 | Distribution Circuit | Vegetation | Tree - fell into line | 1109 | 89069 | 40.1272 | -123.822 | 10SPANSSEOF83315253 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0015863 | OH | Sus | 0 | No | 2023 | JAN | Yes | Open Circuit | 1804702 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0015859&numberofmonths=24&showchangehistorylog=1 | 23-0015859 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | MENDOCINO-1101 | 42951101 | RECLOSER | 48750 | 20230114 | 659 | 1952917 | 352 | Distribution Circuit | Vegetation | Tree - fell into line | 152 | 14204 | 39.3316 | -123.2248 | WelshTyler7078069777CGCNumber216540960995 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0015859 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1804699 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0015950&numberofmonths=24&showchangehistorylog=1 | 23-0015950 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1102 | 42601102 | RECLOSER | 2600 | 20230114 | 842 | 1953415 | 11 | Distribution Circuit | Vegetation | Tree - fell into line | 76 | 836 | 39.0853 | -123.4851 | CGC215552552182 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0015950 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1804780 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0015973&numberofmonths=24&showchangehistorylog=1 | 23-0015973 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1102 | 42601102 | FUSE | 2625 | 20230114 | 903 | 1953566 | 288 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2299 | 39.0991 | -123.5707 | SSOFCGC215552552182 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0015973 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1804798 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0015868&numberofmonths=24&showchangehistorylog=1 | 23-0015868 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | POTTER VALLEY P H-1105 | 42281105 | RECLOSER | 64118 | 20230114 | 709 | 1952931 | 529 | Distribution Circuit | Equipment Failure/Involved | Overhead | 652 | 191492 | 39.362 | -123.1283 | 1SPWIREDOWN905253 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0015868 | OH | Sus | 0 | No | 2023 | JAN | Yes | Multi-Fault | 1804707 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0015998&numberofmonths=24&showchangehistorylog=1 | 23-0015998 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1104 | 42661104 | JUMPER | WIREDOWNLDSIDEMETER1009745169 | 20230114 | 654 | 1953656 | 680 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1770 | 39.349 | -123.3303 | NA | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0015998 | OH | Sus | 0 | No | 2023 | JAN | Yes | Open Circuit | 1804817 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0017014&numberofmonths=24&showchangehistorylog=1 | 23-0017014 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ANNAPOLIS-1101 | 42861101 | RECLOSER | 528344 | 20230116 | 805 | 1957295 | 406 | Distribution Circuit | Vegetation | Tree - fell into line | 152 | 61712 | 38.7112 | -123.3388 | ThorpeTim2094Bothsides4573andlso4155onmainline | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0017014 | OH | Sus | 0 | No | 2023 | JAN | Yes | Multi-Fault | 1805718 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0017317&numberofmonths=24&showchangehistorylog=1 | 23-0017317 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1112 | 42841112 | FUSE | 7287 | 20230116 | 1526 | 1958442 | 217 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 3689 | 38.8139 | -123.5856 | 34900TOCKLN | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0017317 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1805994 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0031017&numberofmonths=24&showchangehistorylog=1 | 23-0031017 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 3279 | 20230221 | 1055 | 1990124 | 513 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 7290 | 39.3113 | -123.7877 | FelicichDavidAtendofBlairrdCGC214940260274 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0031017 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Ground | 1814762 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0031177&numberofmonths=24&showchangehistorylog=1 | 23-0031177 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 1319 | 20230221 | 1057 | 1990128 | 440 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1320 | 39.2159 | -123.68 | 1SPANLDSIDE | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0031177 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Ground | 1814869 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0031467&numberofmonths=24&showchangehistorylog=1 | 23-0031467 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 4399 | 20230221 | 1328 | 1991346 | 373 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 2611 | 40.0838 | -123.8183 | 1SWOF4399 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0031467 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Line | 1815102 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0032941&numberofmonths=24&showchangehistorylog=1 | 23-0032941 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | BRIDGEVILLE-1102 | 192461102 | RECLOSER | 11022 | 20230223 | 851 | 1999038 | 624 | Distribution Circuit | Vegetation | Tree - fell into line | 248 | 70532 | 40.4797 | -123.7803 | 10SPANSLDSIDEOF3869 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 23-0032941 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Ground | 1816209 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0033088&numberofmonths=24&showchangehistorylog=1 | 23-0033088 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | EEL RIVER-1102 | 192381102 | FUSE | 1899 | 20230223 | 520 | 1998840 | 678 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 7458 | 40.5113 | -124.1605 | 8SPANDLDSIDEAND7PLDSIDE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0033088 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Ground | 1816279 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0034009&numberofmonths=24&showchangehistorylog=1 | 23-0034009 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 6625 | 20230224 | 1036 | 2005092 | 375 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 750 | 39.2101 | -123.6838 | 3SPANSLDSIDE6625 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0034009 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Ground | 1816979 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0034056&numberofmonths=24&showchangehistorylog=1 | 23-0034056 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 1767 | 20230224 | 1008 | 2004907 | 524 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 4192 | 39.6704 | -123.7789 | 3SPANSLDSIDE1767 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0034056 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Line | 1817010 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0033529&numberofmonths=24&showchangehistorylog=1 | 23-0033529 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1104 | 42661104 | RECLOSER | 34008 | 20230224 | 31 | 2001317 | 1168 | Distribution Circuit | Vegetation | Tree - fell into line | 571 | 430706 | 39.4366 | -123.3892 | 8031ONMAINLINE25280POPPYDR | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0033529 | OH | Sus | 0 | No | 2023 | FEB | Yes | Multi-Fault | 1816561 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0036652&numberofmonths=24&showchangehistorylog=1 | 23-0036652 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | KONOCTI-1102 | 43311102 | OTHER | WIREDOWNSSOFCGC217743946937 | 20230227 | 1543 | 2012905 | 2843 | Distribution Circuit | Environmental/External | Ice or snow | 1183 | 109614 | 38.9519 | -122.7933 | SSOFCGC217743946937 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0036652 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Ground | 1819223 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0036118&numberofmonths=24&showchangehistorylog=1 | 23-0036118 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | POTTER VALLEY P H-1105 | 42281105 | RECLOSER | 640888 | 20230227 | 812 | 2011373 | 465 | Distribution Circuit | Vegetation | Tree - fell into line | 97 | 45105 | 39.3887 | -123.1173 | BARRINGTONSORRELT1102K34556spanspast1941ML | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0036118 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Ground | 1818889 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0036509&numberofmonths=24&showchangehistorylog=1 | 23-0036509 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | FUSE | 1999 | 20230227 | 1009 | 2011737 | 405 | Distribution Circuit | Vegetation | Tree - fell into line | 71 | 28755 | 39.4313 | -123.3729 | DicksonJosh7072936004CGCNumber216119964525 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0036509 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Line | 1819109 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0037087&numberofmonths=24&showchangehistorylog=1 | 23-0037087 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ANNAPOLIS-1101 | 42861101 | OTHER | WIREDOWN13SPLDSIDEOF4557 | 20230228 | 551 | 2014155 | 396 | Distribution Circuit | Vegetation | Tree - fell into line | 229 | 13944 | 38.6534 | -123.3371 | 13SPANSLDSIDEOF4557 | Overcast-Fog-Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 23-0037087 | OH | Sus | 0 | No | 2023 | FEB | Yes | None | 1819600 | CAW | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0038783&numberofmonths=24&showchangehistorylog=1 | 23-0038783 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 3769 | 20230228 | 702 | 2019853 | 3467 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 52005 | 40.2643 | -123.828 | 4LDSIDEOF3769 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0038783 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Ground | 1820858 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0037272&numberofmonths=24&showchangehistorylog=1 | 23-0037272 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | POTTER VALLEY P H-1105 | 42281105 | RECLOSER | 76498 | 20230228 | 1115 | 2014256 | 220 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 5060 | 39.3623 | -123.1279 | 2SPANLOADSIDE6757ONRADIAL | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0037272 | OH | Sus | 0 | No | 2023 | FEB | Yes | Multi-Fault | 1819706 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0037049&numberofmonths=24&showchangehistorylog=1 | 23-0037049 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER | 91810 | 20230228 | 442 | 2014119 | 808 | Distribution Circuit | Equipment Failure/Involved | Overhead | 811 | 393278 | 39.4457 | -123.3807 | GALLETTITIMWiredown4polesLSofLR826 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0037049 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Ground | 1819586 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0042317&numberofmonths=24&showchangehistorylog=1 | 23-0042317 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1112 | 42841112 | FUSE | 7801 | 20230309 | 1609 | 2027935 | 115 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 805 | 38.7817 | -123.5409 | ThorpeTim20941lso560079 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0042317 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Line | 1823177 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0042311&numberofmonths=24&showchangehistorylog=1 | 23-0042311 | HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1103 | 42661103 | FUSE | 1855 | 20230309 | 1434 | 2027784 | 203 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 6496 | 39.3785 | -123.275 | 3SPANSLDSIDEOF1855 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0042311 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Line | 1823175 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0044999&numberofmonths=24&showchangehistorylog=1 | 23-0044999 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | RECLOSER | 1298 | 20230314 | 1224 | 2038408 | 455 | Distribution Circuit | Vegetation | Tree - fell into line | 914 | 387465 | 39.1422 | -123.7286 | FelicichDavidAt3401southhwy1 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0044999 | OH | Sus | 0 | No | 2023 | MAR | Yes | Multi-Fault | 1825078 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0044611&numberofmonths=24&showchangehistorylog=1 | 23-0044611 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 1931 | 20230314 | 900 | 2035483 | 520 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 4680 | 39.737 | -123.8119 | FUSES188275 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0044611 | OH | Sus | 0 | No | 2023 | MAR | Yes | Multi-Fault | 1824789 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0044947&numberofmonths=24&showchangehistorylog=1 | 23-0044947 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 8652 | 20230314 | 1203 | 2038135 | 180 | Distribution Circuit | Vegetation | Tree - fell into line | 254 | 45016 | 40.1069 | -123.9276 | 5SSOFR506 |  | Conductor, Overhead | Broken, wire on ground | 23-0044947 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1825033 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0045651&numberofmonths=24&showchangehistorylog=1 | 23-0045651 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 7461 | 20230314 | 1010 | 2043726 | 475 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2850 | 38.7685 | -123.5157 | LDSIDEOF7461 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0045651 | OH | Sus | 0 | No | 2023 | MAR | Yes | Three Phase Fault | 1825593 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0044559&numberofmonths=24&showchangehistorylog=1 | 23-0044559 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1112 | 42841112 | FUSE | 4475 | 20230314 | 713 | 2035294 | 362 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 4706 | 38.8216 | -123.6032 | JUSTLDSIDEOF4475 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0044559 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Line | 1824763 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0044660&numberofmonths=24&showchangehistorylog=1 | 23-0044660 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1112 | 42841112 | FUSE | 4053 | 20230314 | 910 | 2035433 | 372 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 22320 | 38.8554 | -123.588 | SAPID102179917 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0044660 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Line | 1824814 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0045438&numberofmonths=24&showchangehistorylog=1 | 23-0045438 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE | 5085 | 20230314 | 1311 | 2040093 | 425 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 2585 | 39.7071 | -123.501 | CGC215772574718 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0045438 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Line | 1825415 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0044894&numberofmonths=24&showchangehistorylog=1 | 23-0044894 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE | 1363 | 20230314 | 1058 | 2036339 | 330 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 18810 | 38.9152 | -123.6395 | FUCO908999ONMAINLINE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0044894 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Line | 1824995 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0049334&numberofmonths=24&showchangehistorylog=1 | 23-0049334 | HUMBOLDT | FIELD OPS NORTH | Tier 2 | LOW GAP-1101 | 192411101 | FUSE | 7167 | 20230321 | 1128 | 2054126 | 302 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 906 | 40.2958 | -123.3394 | 1SPANLDSIDEOFFUSES | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0049334 | OH | Sus | 31640137 | No | 2023 | MAR | Yes | Line to Ground | 1828132 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076008&numberofmonths=24&showchangehistorylog=1 | 14-0076008 | KERN | FIELD OPS SOUTH | Tier 2 | POSO MOUNTAIN-2101 | 253642101 | RECLOSER | 3990 | 20141211 | 2342 | 1136682 | 2368 | Distribution Circuit | Equipment Failure/Involved | Other | 27 | 63936 | 35.558 | -118.9771 | BEYOJNDLR | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 14-0076008 | OH | Sus | 0 | yes | 2014 | DEC | Yes |  | 99193079 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0022826&numberofmonths=24&showchangehistorylog=1 | 13-0022826 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | PERRY-1101 | 183071101 | OCB | W14 | 20130408 | 2246 | 771246 | 874 | Distribution Circuit | 3rd Party | Vehicle | 3591 | 204109 | 35.5716 | -121.056 | V94NEARHWY1HWY46 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0022826 | OH | Sus | 30988253 | yes | 2013 | APR | Yes | Line to Ground | 99291760 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075760&numberofmonths=24&showchangehistorylog=1 | 14-0075760 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | CAMBRIA-1102 | 182771102 | FUSE | 3865 | 20141211 | 1732 | 1135157 | 1822 | Distribution Circuit | Equipment Failure/Involved | Other | 80 | 120108 | 35.5742 | -121.1038 | LOADSIDEOF3865 | Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 14-0075760 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194286 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075837&numberofmonths=24&showchangehistorylog=1 | 14-0075837 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | CAMBRIA-1102 | 182771102 | RECLOSER | W50 | 20141211 | 1919 | 1135720 | 769 | Distribution Circuit | Vegetation | Tree - fell into line | 611 | 79832 | 35.567 | -121.1052 | MOLNARNICKfuses15151 | Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 14-0075837 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194257 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076586&numberofmonths=24&showchangehistorylog=1 | 14-0076586 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | FOOTHILL-1101 | 182951101 | FUSE | 10549 | 20141211 | 1928 | 1139274 | 2084 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 18756 | 35.3153 | -120.8098 | 1sploadsideofMtr5000054324 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076586 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99193441 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075784&numberofmonths=24&showchangehistorylog=1 | 14-0075784 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | PERRY-1101 | 183071101 | RECLOSER | V74 | 20141211 | 1901 | 1135524 | 547 | Distribution Circuit | Vegetation | Tree - fell into line | 522 | 160563 | 35.5459 | -121.0679 | MOLNARNICKloadsideofV41 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075784 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Multi-Fault | 99194277 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075587&numberofmonths=24&showchangehistorylog=1 | 14-0075587 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | PURISIMA-1101 | 182971101 | OTHER |  | 20141211 | 1139 | 1133323 | 518 | Distribution Circuit | Equipment Failure/Involved | Other | 14 | 7186 | 34.7272 | -120.4366 | 4SPANSSSOF20139 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075587 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194760 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076103&numberofmonths=24&showchangehistorylog=1 | 14-0076103 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | SAN LUIS OBISPO-1107 | 182631107 | FUSE | 4391 | 20141211 | 2157 | 1136947 | 1484 | Distribution Circuit | Vegetation | Tree - branch fell on line | 77 | 135674 | 35.2355 | -120.6491 | SSOF941615ONMAINLINE | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076103 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99193515 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075934&numberofmonths=24&showchangehistorylog=1 | 14-0075934 | LOS PADRES | FIELD OPS SOUTH | Tier 3 | SANTA MARIA-1108 | 182671108 | RECLOSER | M80 | 20141211 | 2110 | 1136342 | 2755 | Distribution Circuit | 3rd Party | Vehicle | 319 | 561161 | 35.0145 | -120.3599 | STOWELLDOUGHUASANARDMTR5000015692 | Drizzle-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0075934 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99193537 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076665&numberofmonths=24&showchangehistorylog=1 | 14-0076665 | LOS PADRES | FIELD OPS SOUTH | Tier 3 | SANTA MARIA-1108 | 182671108 | FUSE | 2175 | 20141211 | 1920 | 1139430 | 3600 | Distribution Circuit | Equipment Failure/Involved | Other | 58 | 208800 | 35.1532 | -120.4222 | 3POLELOADSIDE21753990JATARD | Rain-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0076665 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99193205 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076098&numberofmonths=24&showchangehistorylog=1 | 14-0076098 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | SANTA YNEZ-1104 | 182721104 | FUSE | 6205 | 20141211 | 2047 | 1136032 | 3398 | Distribution Circuit | Vegetation | Tree - branch fell on line | 56 | 190288 | 34.6439 | -120.1375 | MTR1009256485 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 14-0076098 | OH | Sus | 0 | yes | 2014 | DEC | Yes |  | 99193207 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075708&numberofmonths=24&showchangehistorylog=1 | 14-0075708 | LOS PADRES | FIELD OPS SOUTH | Tier 3 | TEMPLETON-2110 | 183052110 | FUSE | 7147 | 20141211 | 1558 | 1134769 | 592 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 20802 | 35.5353 | -120.8061 | 3720CLOUDYMEDOWLN | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075708 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99194675 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076201&numberofmonths=24&showchangehistorylog=1 | 14-0076201 | LOS PADRES | FIELD OPS SOUTH | Tier 3 | TEMPLETON-2113 | 183052113 | FUSE | 6343 | 20141211 | 1838 | 1135375 | 1688 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 28696 | 35.3953 | -120.5203 | LSOFMTR1009176882WIRESDOWN | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 14-0076201 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194102 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076296&numberofmonths=24&showchangehistorylog=1 | 14-0076296 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | BUELLTON-1101 | 183041101 | FUSE | 20149 | 20141212 | 634 | 1137198 | 1781 | Distribution Circuit | Equipment Failure/Involved | Other | 33 | 65822 | 34.5318 | -120.2918 | 6000HWY1 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076296 | OH | Sus | 0 | yes | 2014 | DEC | Yes |  | 99193491 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076453&numberofmonths=24&showchangehistorylog=1 | 14-0076453 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | SANTA YNEZ-1102 | 182721102 | FUSE | 20195 | 20141212 | 621 | 1138040 | 2410 | Distribution Circuit | Equipment Failure/Involved | Other | 21 | 50610 | 34.5827 | -120.1457 | VARIOUS | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076453 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99193462 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010615&numberofmonths=24&showchangehistorylog=1 | 15-0010615 | LOS PADRES | FIELD OPS SOUTH | Tier 3 | TEMPLETON-2113 | 183052113 | RECLOSER | A10 | 20150206 | 1932 | 1177984 | 773 | Distribution Circuit | Vegetation | Tree - fell into line | 406 | 54085 | 35.4108 | -120.5657 | LAYUGANJIM6210PARKHILLRD | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0010615 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99183939 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011274&numberofmonths=24&showchangehistorylog=1 | 15-0011274 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | SAN LUIS OBISPO-1107 | 182631107 | FUSE | 10895 | 20150207 | 1429 | 1181338 | 281 | Distribution Circuit | Vegetation | Tree - fell into line | 179 | 11149 | 35.1943 | -120.7142 | MOLNARNICK3165meadowbrook | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011274 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99184296 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0048930&numberofmonths=24&showchangehistorylog=1 | 15-0048930 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | OCEANO-1108 | 182601108 | FUSE | 9589 | 20150719 | 1354 | 1272537 | 946 | Distribution Circuit | Environmental/External | Lightning | 32 | 30272 | 35.0851 | -120.5557 | 1SOF9589 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0048930 | OH | Sus | 0 | yes | 2015 | JUL | Yes | Line to Ground | 1146431 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0048751&numberofmonths=24&showchangehistorylog=1 | 15-0048751 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | PERRY-1101 | 183071101 | OTHER | WIREDOWNSS14843 | 20150719 | 735 | 1272189 | 1535 | Distribution Circuit | Environmental/External | Lightning | 96 | 97605 | 35.5455 | -121.0844 | WILKINSARMANDO15899135057ATCOPOLE14843 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0048751 | OH | Sus | 0 | yes | 2015 | JUL | Yes | Open Circuit | 1146244 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0071600&numberofmonths=24&showchangehistorylog=1 | 15-0071600 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | OCEANO-1104 | 182601104 | RECLOSER | Q06 | 20151018 | 2159 | 1325661 | 291 | Distribution Circuit | Equipment Failure/Involved | Overhead | 819 | 155970 | 35.1341 | -120.5703 | STOWELLDOUGPRINZERDTORREYRD | Overcast-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 15-0071600 | OH | Sus | 42521324 | yes | 2015 | OCT | Yes | Line to Ground | 1163287 | CSO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0013484&numberofmonths=24&showchangehistorylog=1 | 16-0013484 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | GOLDTREE-1107 | 182581107 | OCB | 11072 | 20160217 | 2242 | 1407584 | 364 | Distribution Circuit | Equipment Failure/Involved | Overhead | 47 | 9169 | 35.3203 | -120.6931 | MOLNARNICKfuses9181 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013484 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Line to Ground | 1186572 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0018118&numberofmonths=24&showchangehistorylog=1 | 16-0018118 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | CAYUCOS-1101 | 182551101 | FUSE | 9217 | 20160305 | 2337 | 1420675 | 425 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 10200 | 35.5484 | -121.0893 | MTR69A687 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | On Ground | 16-0018118 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1189988 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0018035&numberofmonths=24&showchangehistorylog=1 | 16-0018035 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | TEMPLETON-2111 | 183052111 | RECLOSER | A66 | 20160305 | 2310 | 1420581 | 800 | Distribution Circuit | Vegetation | Tree - fell into line | 959 | 131092 | 35.5213 | -120.7126 | 1SPNW6029ONTAPLINE | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018035 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1189906 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005110&numberofmonths=24&showchangehistorylog=1 | 17-0005110 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | ATASCADERO-1103 | 182541103 | FUSE | 4617 | 20170108 | 1004 | 1624576 | 369 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 2302 | 35.4488 | -120.6491 | MTR1006176385 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005110 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1244908 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005667&numberofmonths=24&showchangehistorylog=1 | 17-0005667 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | TEMPLETON-2111 | 183052111 | FUSE | 7581 | 20170108 | 1859 | 1628888 | 206 | Distribution Circuit | Vegetation | Tree - fell into line | 124 | 13999 | 35.4991 | -120.7023 | 2SPANSSSOF31335 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005667 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Force Out | 1245448 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005865&numberofmonths=24&showchangehistorylog=1 | 17-0005865 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | TEMPLETON-2110 | 183052110 | FUSE | 30185 | 20170109 | 210 | 1629943 | 610 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 4310 | 35.5983 | -120.8321 | 8SPANSLDSIDEOF30185 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005865 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1245648 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007344&numberofmonths=24&showchangehistorylog=1 | 17-0007344 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | ATASCADERO-1101 | 182541101 | FUSE | 30459 | 20170111 | 14 | 1638172 | 306 | Distribution Circuit | Vegetation | Tree - branch fell on line | 62 | 14072 | 35.4755 | -120.6805 | IFOMTR1008187301 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007344 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1246928 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007581&numberofmonths=24&showchangehistorylog=1 | 17-0007581 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | PERRY-1101 | 183071101 | OTHER | 14851 | 20170111 | 957 | 1639368 | 790 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2370 | 35.5435 | -121.083 | 2SPANSLOADSIDEFUSE14851 | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 17-0007581 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247105 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0010071&numberofmonths=24&showchangehistorylog=1 | 17-0010071 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | FOOTHILL-1101 | 182951101 | FUSE | 3561 | 20170118 | 1453 | 1646560 | 186 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 2046 | 35.2924 | -120.7159 | BRIGGSCHARLESfuses10799 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010071 | OH | Sus | 42929062 | yes | 2017 | JAN | Yes | Line to Ground | 1249098 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0009934&numberofmonths=24&showchangehistorylog=1 | 17-0009934 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | SANTA MARIA-1108 | 182671108 | OTHER | WIREDOWN2LDSDSW7345 | 20170118 | 1248 | 1646173 | 950 | Distribution Circuit | Equipment Failure/Involved | Overhead | 439 | 105340 | 34.9994 | -120.3628 | 2LDSDSW7345 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0009934 | OH | Sus | 42929077 | yes | 2017 | JAN | Yes | Open Circuit | 1249013 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011234&numberofmonths=24&showchangehistorylog=1 | 17-0011234 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | PERRY-1101 | 183071101 | FUSE | 9179 | 20170120 | 540 | 1652521 | 443 | Distribution Circuit | Vegetation | Tree - fell into line | 303 | 48013 | 35.5437 | -121.0717 | 1SPAN | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011234 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1250147 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011615&numberofmonths=24&showchangehistorylog=1 | 17-0011615 | LOS PADRES | FIELD OPS SOUTH | Tier 3 | TEMPLETON-2110 | 183052110 | FUSE | 5581 | 20170120 | 728 | 1653008 | 663 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 26520 | 35.5552 | -120.8377 | CATESDOUG2spansloadsidemtr1008498058 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011615 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1250471 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012685&numberofmonths=24&showchangehistorylog=1 | 17-0012685 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | ATASCADERO-1101 | 182541101 | RECLOSER | A02 | 20170122 | 339 | 1658478 | 770 | Distribution Circuit | Vegetation | Tree - fell into line | 487 | 40648 | 35.4838 | -120.6842 | METER1009295454 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012685 | OH | Sus | 42929174 | yes | 2017 | JAN | Yes | Line to Ground | 1251507 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012925&numberofmonths=24&showchangehistorylog=1 | 17-0012925 | LOS PADRES | FIELD OPS SOUTH | Tier 3 | ATASCADERO-1101 | 182541101 | SWITCH | 2793 | 20170122 | 831 | 1659777 | 300 | Distribution Circuit | Vegetation | Tree - fell into line | 175 | 37389 | 35.4848 | -120.725 | 3SPANSLSOF2793 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012925 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1251745 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013079&numberofmonths=24&showchangehistorylog=1 | 17-0013079 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | ATASCADERO-1103 | 182541103 | FUSE | 4617 | 20170122 | 435 | 1658770 | 1047 | Distribution Circuit | Equipment Failure/Involved | Overhead | 36 | 26938 | 35.4488 | -120.6491 | 4POLEWESTOF4617 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0013079 | OH | Sus | 31297289 | yes | 2017 | JAN | Yes | Line to Ground | 1251898 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013034&numberofmonths=24&showchangehistorylog=1 | 17-0013034 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | FOOTHILL-1101 | 182951101 | FUSE | 2815 | 20170122 | 626 | 1659255 | 896 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 9856 | 35.3082 | -120.8198 | ENDOFTAPLINE | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013034 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1251854 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013259&numberofmonths=24&showchangehistorylog=1 | 17-0013259 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | FOOTHILL-1101 | 182951101 | JUMPER | OJS1SPANSOF1008717736 | 20170122 | 831 | 1659776 | 3109 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 6218 | 35.2878 | -120.8029 | 1SPANLSOFMETER1008717736 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013259 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1252074 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013341&numberofmonths=24&showchangehistorylog=1 | 17-0013341 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | MESA-1101 | 182821101 | FUSE | 6119 | 20170122 | 820 | 1660464 | 2124 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 36108 | 35.0356 | -120.466 | IFOMTR5000031262 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0013341 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1252156 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013038&numberofmonths=24&showchangehistorylog=1 | 17-0013038 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | OCEANO-1104 | 182601104 | FUSE | 9347 | 20170122 | 734 | 1659529 | 346 | Distribution Circuit | Vegetation | Tree - branch fell on line | 32 | 11072 | 35.1542 | -120.5987 | 1SPANEO9347 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013038 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1251857 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013045&numberofmonths=24&showchangehistorylog=1 | 17-0013045 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | OCEANO-1104 | 182601104 | JUMPER | WIREDOWN3NEOF9407 | 20170122 | 703 | 1660466 | 3312 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1449 | 260666 | 35.1353 | -120.5403 | KELLEYRANDY8054418781BranchMillRdandHuasnaRd | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013045 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1251865 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012852&numberofmonths=24&showchangehistorylog=1 | 17-0012852 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | PERRY-1101 | 183071101 | FUSE | 9547 | 20170122 | 647 | 1659311 | 267 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2136 | 35.5433 | -121.0726 | FUSE9547 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012852 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1251675 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012934&numberofmonths=24&showchangehistorylog=1 | 17-0012934 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | PERRY-1101 | 183071101 | FUSE | 9179 | 20170122 | 748 | 1659595 | 466 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 8388 | 35.5437 | -121.0717 | MOLNARNICKbradfordcircle | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012934 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1251754 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012998&numberofmonths=24&showchangehistorylog=1 | 17-0012998 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | PERRY-1101 | 183071101 | FUSE | 4747 | 20170122 | 638 | 1659420 | 552 | Distribution Circuit | Vegetation | Tree - fell into line | 81 | 44712 | 35.5503 | -121.0856 | 5POLESLDSIDEOF4747 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012998 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1251819 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013523&numberofmonths=24&showchangehistorylog=1 | 17-0013523 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | SANTA YNEZ-1101 | 182721101 | RECLOSER | Y52 | 20170122 | 2045 | 1662536 | 1585 | Distribution Circuit | Equipment Failure/Involved | Overhead | 190 | 259226 | 34.5981 | -120.0296 | 2NEOFSW1645 | Partly Cloudy-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013523 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1252341 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013257&numberofmonths=24&showchangehistorylog=1 | 17-0013257 | LOS PADRES | FIELD OPS SOUTH | Tier 3 | TEMPLETON-2113 | 183052113 | SWITCH | 858255 | 20170122 | 1456 | 1661588 | 2377 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 52294 | 35.4282 | -120.5061 | METER1007997552 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0013257 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1252072 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013854&numberofmonths=24&showchangehistorylog=1 | 17-0013854 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | CABRILLO-1104 | 183101104 | FUSE | 6085 | 20170123 | 813 | 1663170 | 1799 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1799 | 34.574 | -120.5173 | 4SPLDSIDEFUSE6085 | Overcast-Drizzle-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0013854 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1252626 | CSO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013804&numberofmonths=24&showchangehistorylog=1 | 17-0013804 | LOS PADRES | FIELD OPS SOUTH | Tier 3 | TEMPLETON-2110 | 183052110 | FUSE | 6095 | 20170123 | 649 | 1662990 | 1801 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 30547 | 35.5382 | -120.8413 | COXBOB8420StStevensxstHwy46W | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013804 | OH | Sus | 31297289 | yes | 2017 | JAN | Yes | Line to Ground | 1252581 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013600&numberofmonths=24&showchangehistorylog=1 | 17-0013600 | LOS PADRES | FIELD OPS SOUTH | Tier 3 | TEMPLETON-2113 | 183052113 | FUSE | 6343 | 20170123 | 123 | 1662645 | 822 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 13974 | 35.395 | -120.5203 | MTR1008185960 | Rain-Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013600 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1252423 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018731&numberofmonths=24&showchangehistorylog=1 | 17-0018731 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | CAMBRIA-1101 | 182771101 | OTHER | WIREDOWN19019HWY1 | 20170207 | 1651 | 1680705 | 1344 | Distribution Circuit | Vegetation | Tree - fell into line | 71 | 37965 | 35.7816 | -121.3286 | 19019HWY1 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018731 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Open Circuit | 1256480 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0022620&numberofmonths=24&showchangehistorylog=1 | 17-0022620 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | ATASCADERO-1103 | 182541103 | RECLOSER | A18 | 20170217 | 1806 | 1697994 | 1478 | Distribution Circuit | Vegetation | Tree - fell into line | 1613 | 415250 | 35.4489 | -120.6491 | SpinolaRichard17250CHESTNUTAVE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022620 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1259643 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0022640&numberofmonths=24&showchangehistorylog=1 | 17-0022640 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | OCEANO-1104 | 182601104 | FUSE | 10485 | 20170217 | 925 | 1698372 | 6020 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 355180 | 35.1491 | -120.576 | DERYKKEVIN62153038651112loc1hwy227doris21spnosb10487 | Partly Cloudy-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0022640 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1259663 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023378&numberofmonths=24&showchangehistorylog=1 | 17-0023378 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | OCEANO-1104 | 182601104 | FUSE | 11007 | 20170217 | 930 | 1701241 | 3896 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 27272 | 35.1557 | -120.5868 | WHITNEYDWIGHT572LasLomas | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023378 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1260363 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023411&numberofmonths=24&showchangehistorylog=1 | 17-0023411 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | OCEANO-1104 | 182601104 | FUSE | 11005 | 20170217 | 930 | 1701361 | 4380 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 13140 | 35.1579 | -120.5866 | L14REK81424NoyesRd | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023411 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1260396 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0022024&numberofmonths=24&showchangehistorylog=1 | 17-0022024 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | OCEANO-1105 | 182601105 | OCB | V02 | 20170217 | 959 | 1693522 | 3576 | Distribution Circuit | Vegetation | Tree - fell into line | 9178 | 3700800 | 35.101 | -120.581 | MULTIPLEONSELMST | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022024 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1259120 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0022227&numberofmonths=24&showchangehistorylog=1 | 17-0022227 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | OCEANO-1108 | 182601108 | FUSE | 58417 | 20170217 | 957 | 1694172 | 4458 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 4458 | 35.0912 | -120.5611 | 2SPANSLDSIDEOF58417 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022227 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1259302 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0022333&numberofmonths=24&showchangehistorylog=1 | 17-0022333 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | OCEANO-1108 | 182601108 | FUSE | 77699 | 20170217 | 1029 | 1696511 | 3010 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 6020 | 35.0636 | -120.562 | 2SPANSLDSIDE77699 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022333 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1259389 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0022557&numberofmonths=24&showchangehistorylog=1 | 17-0022557 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | OCEANO-1108 | 182601108 | SWITCH | 8511 | 20170217 | 1750 | 1696038 | 10 | Distribution Circuit | Vegetation | Tree - fell into line | 890 | 8900 | 35.076 | -120.5826 | MesaMiddleSch | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0022557 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1259580 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0022828&numberofmonths=24&showchangehistorylog=1 | 17-0022828 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | OCEANO-1108 | 182601108 | FUSE | 15239 | 20170217 | 1015 | 1694221 | 2918 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 145900 | 35.0973 | -120.5676 | WIREDWNHAWKVIEWFALCONCREST | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022828 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1259845 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023187&numberofmonths=24&showchangehistorylog=1 | 17-0023187 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | TEMPLETON-2113 | 183052113 | FUSE | 6323 | 20170217 | 1101 | 1694781 | 2092 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 18828 | 35.5091 | -120.6561 | LOADSIDEFUSES | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023187 | OH | Sus | 42949651 | yes | 2017 | FEB | Yes | Multi-Fault | 1260190 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023007&numberofmonths=24&showchangehistorylog=1 | 17-0023007 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | CABRILLO-1103 | 183101103 | FUSE | 11221 | 20170218 | 744 | 1699093 | 289 | Distribution Circuit | Equipment Failure/Involved | Overhead | 163 | 7093 | 34.6169 | -120.3859 | FUSE11221 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023007 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1260023 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023308&numberofmonths=24&showchangehistorylog=1 | 17-0023308 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | OCEANO-1104 | 182601104 | FUSE | 9313 | 20170218 | 2344 | 1700964 | 1225 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 18375 | 35.1318 | -120.5558 | AVALOJORGE953crewtomakerepairstowiredownco9313openandtagged | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023308 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1260311 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0022979&numberofmonths=24&showchangehistorylog=1 | 17-0022979 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | PERRY-1101 | 183071101 | FUSE | 9211 | 20170218 | 953 | 1699402 | 1834 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 18340 | 35.5466 | -121.076 | MOLNARNICKfuses9211 | Overcast-Strong Winds-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022979 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1259994 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023111&numberofmonths=24&showchangehistorylog=1 | 17-0023111 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | PERRY-1101 | 183071101 | FUSE | 15567 | 20170218 | 1321 | 1699925 | 3013 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 123533 | 35.5574 | -121.0828 | LDSIDE15567 | Strong Winds-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0023111 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1260119 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023115&numberofmonths=24&showchangehistorylog=1 | 17-0023115 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | PERRY-1101 | 183071101 | FUSE | 9547 | 20170218 | 1345 | 1699960 | 1214 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 9712 | 35.5433 | -121.0726 | ATFUCO9547 | Strong Winds-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023115 | OH | Sus | 42949651 | yes | 2017 | FEB | Yes | Line to Line | 1260122 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023038&numberofmonths=24&showchangehistorylog=1 | 17-0023038 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | TEMPLETON-2113 | 183052113 | FUSE | 30877 | 20170218 | 1118 | 1699608 | 1447 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1447 | 35.517 | -120.6403 | 2470HONESTEAD | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023038 | OH | Sus | 31306099 | yes | 2017 | FEB | Yes | Line to Ground | 1260049 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023909&numberofmonths=24&showchangehistorylog=1 | 17-0023909 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | PERRY-1101 | 183071101 | FUSE | 5429 | 20170220 | 1553 | 1703819 | 512 | Distribution Circuit | Equipment Failure/Involved | Overhead | 107 | 54784 | 35.5497 | -121.0879 | WIREDOWN1POLELOADSIDEOF5429 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023909 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1260885 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023646&numberofmonths=24&showchangehistorylog=1 | 17-0023646 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | SAN LUIS OBISPO-1104 | 182631104 | RECLOSER | Q08 | 20170220 | 534 | 1702489 | 450 | Distribution Circuit | Vegetation | Tree - fell into line | 183 | 46692 | 35.1481 | -120.5893 | L14REK8assistGCcrew | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0023646 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1260648 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023599&numberofmonths=24&showchangehistorylog=1 | 17-0023599 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | SAN LUIS OBISPO-1107 | 182631107 | FUSE | 10895 | 20170220 | 1120 | 1703107 | 766 | Distribution Circuit | Vegetation | Tree - fell into line | 1179 | 166918 | 35.1945 | -120.7141 | MITCHELLDAN2711SEECANYONRD | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023599 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1260758 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024923&numberofmonths=24&showchangehistorylog=1 | 17-0024923 | LOS PADRES | FIELD OPS SOUTH | Tier 3 | ATASCADERO-1103 | 182541103 | RECLOSER | A12 | 20170221 | 746 | 1707754 | 1054 | Distribution Circuit | Equipment Failure/Involved | Overhead | 131 | 21824 | 35.3806 | -120.4432 | CATESDOUG1225parkhillrd | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024923 | OH | Sus | 31306099 | yes | 2017 | FEB | Yes | Line to Ground | 1261898 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025179&numberofmonths=24&showchangehistorylog=1 | 17-0025179 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | PERRY-1101 | 183071101 | FUSE | 15567 | 20170221 | 1134 | 1708392 | 412 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 8906 | 35.5574 | -121.0828 | MTR1008472844 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025179 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1262086 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025134&numberofmonths=24&showchangehistorylog=1 | 17-0025134 | LOS PADRES | FIELD OPS SOUTH | Tier 3 | TEMPLETON-2110 | 183052110 | FUSE | 4479 | 20170221 | 833 | 1708645 | 412 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2060 | 35.5352 | -120.778 | LOADSIDEOF4479 | Heavy Rain-Strong Winds-Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025134 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1262053 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0038104&numberofmonths=24&showchangehistorylog=1 | 17-0038104 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | TEMPLETON-2111 | 183052111 | FUSE | 2521 | 20170407 | 1729 | 1751417 | 1229 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 13519 | 35.5262 | -120.7173 | 2WO2521 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0038104 | OH | Sus | 31318406 | yes | 2017 | APR | Yes | Line to Ground | 1272162 | CSO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0089249&numberofmonths=24&showchangehistorylog=1 | 17-0089249 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | CABRILLO-1103 | 183101103 | FUSE | 6085 | 20171020 | 1610 | 1906380 | 173 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 173 | 34.574 | -120.5173 | 17polesloadside6085 | Partly Cloudy-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0089249 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1309738 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0099678&numberofmonths=24&showchangehistorylog=1 | 17-0099678 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | SANTA MARIA-1108 | 182671108 | FUSE | 6461 | 20171204 | 930 | 1934673 | 813 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 2439 | 34.9955 | -120.3435 | MITCHELLDANCREWTOREPAIRWIREDOWN3RD4TH5THPOLELOADSIDEOFFUCO6461 | Strong Winds-Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0099678 | OH | Sus | 43227091 | yes | 2017 | DEC | Yes | Line to Ground | 1317444 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0023230&numberofmonths=24&showchangehistorylog=1 | 18-0023230 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | MESA-1103 | 182821103 | SWITCH | 12047 | 20180316 | 1653 | 46189 | 11 | Distribution Circuit | Company Initiated | Return Circuit Normal | 1 | 11 | 35.0614 | -120.5265 | MTR1008893500 | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 18-0023230 | OH | Sus | 31384355 | yes | 2018 | MAR | Yes | None | 1336365 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0104799&numberofmonths=24&showchangehistorylog=1 | 18-0104799 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | OCEANO-1104 | 182601104 | FUSE | 9313 | 20181129 | 222 | 227529 | 855 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 12825 | 35.1318 | -120.5558 | PEREZMARIO1491BRANCHMILL | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0104799 | OH | Sus | 43587912 | yes | 2018 | NOV | Yes | Line to Ground | 1396105 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010176&numberofmonths=24&showchangehistorylog=1 | 19-0010176 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | TEMPLETON-2113 | 183052113 | RECLOSER | A08 | 20190116 | 2011 | 270405 | 1008 | Distribution Circuit | Equipment Failure/Involved | Overhead | 924 | 414175 | 35.4621 | -120.6221 | LAYUGANJIM16815NELCAMINOREAL | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0010176 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407044 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011313&numberofmonths=24&showchangehistorylog=1 | 19-0011313 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | SAN LUIS OBISPO-1107 | 182631107 | RECLOSER | V02 | 20190117 | 1713 | 274695 | 429 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2706 | 679889 | 35.2383 | -120.6792 | 9071 | Partly Cloudy-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0011313 | OH | Sus | 31422124 | yes | 2019 | JAN | Yes | Line to Ground | 1407873 | CSO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0016901&numberofmonths=24&showchangehistorylog=1 | 19-0016901 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | ATASCADERO-1101 | 182541101 | FUSE | 81595 | 20190202 | 331 | 286221 | 704 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 3803 | 35.4824 | -120.692 | CGC511993173310 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0016901 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1411361 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0017307&numberofmonths=24&showchangehistorylog=1 | 19-0017307 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | ATASCADERO-1101 | 182541101 | JUMPER | LINEBUCKAT10500SANMARCOSRD | 20190202 | 1230 | 287402 | 1511 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1511 | 35.4688 | -120.6963 | LINEBUCKAT10500SANMARCOSRD | Strong Winds-Heavy Rain-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0017307 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1411723 | CSO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0017067&numberofmonths=24&showchangehistorylog=1 | 19-0017067 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | BUELLTON-1102 | 183041102 | FUSE | 20391 | 20190202 | 428 | 287123 | 2218 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 17744 | 34.615 | -120.1651 | 2SPLD20391 | Overcast-Fog-Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0017067 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1411515 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0017199&numberofmonths=24&showchangehistorylog=1 | 19-0017199 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | CABRILLO-1104 | 183101104 | FUSE | 8695 | 20190202 | 830 | 286967 | 2061 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 20610 | 34.6345 | -120.5287 | 2SPLDSIDE8695 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017199 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1411627 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0017515&numberofmonths=24&showchangehistorylog=1 | 19-0017515 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | FOOTHILL-1101 | 182951101 | FUSE | 3229 | 20190202 | 559 | 286585 | 3592 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 8978 | 35.2719 | -120.7627 | 1SPSSMTR1003915194 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017515 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1411928 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0016863&numberofmonths=24&showchangehistorylog=1 | 19-0016863 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | PALMER-1101 | 183031101 | RECLOSER | M82 | 20190202 | 236 | 286085 | 622 | Distribution Circuit | Vegetation | Tree - branch fell on line | 787 | 74114 | 34.7369 | -120.2589 | TIRADOJOSE80545982564300hwy135 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0016863 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1411322 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0016882&numberofmonths=24&showchangehistorylog=1 | 19-0016882 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | PERRY-1101 | 183071101 | FUSE | 14851 | 20190202 | 151 | 286027 | 1164 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 3492 | 35.5435 | -121.083 | 2SPANSLDSIDE | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0016882 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1411343 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0017348&numberofmonths=24&showchangehistorylog=1 | 19-0017348 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | PERRY-1101 | 183071101 | RECLOSER | V74 | 20190202 | 2039 | 288120 | 1208 | Distribution Circuit | Vegetation | Tree - fell into line | 382 | 212654 | 35.5457 | -121.0679 | BETWEEN10973LINEBUCKATBRADFORDPINERIDGE | Overcast-Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0017348 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1411760 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0017374&numberofmonths=24&showchangehistorylog=1 | 19-0017374 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | SANTA YNEZ-1104 | 182721104 | FUSE | 7973 | 20190202 | 1413 | 288255 | 2828 | Distribution Circuit | Equipment Failure/Involved | Overhead | 43 | 121604 | 34.6579 | -120.0911 | FOUND2POLESDOWNONHILL8SPANSLOADSIDE7973 | Strong Winds-Rain-Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 19-0017374 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Multi-Fault | 1411786 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0017271&numberofmonths=24&showchangehistorylog=1 | 19-0017271 | LOS PADRES | FIELD OPS SOUTH | Tier 3 | TEMPLETON-2110 | 183052110 | FUSE | 6289 | 20190202 | 901 | 287046 | 1664 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 13312 | 35.5459 | -120.8219 | LAYUGANJIM8054598257NOBLELN | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017271 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1411691 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0017042&numberofmonths=24&showchangehistorylog=1 | 19-0017042 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | TEMPLETON-2111 | 183052111 | FUSE | 6023 | 20190202 | 533 | 286526 | 975 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 13650 | 35.5205 | -120.7116 | 3SPLDSIDE6023 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017042 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1411496 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0016944&numberofmonths=24&showchangehistorylog=1 | 19-0016944 | LOS PADRES | FIELD OPS SOUTH | Tier 3 | TEMPLETON-2113 | 183052113 | RECLOSER | A12 | 20190202 | 611 | 286610 | 1670 | Distribution Circuit | Vegetation | Tree - fell into line | 130 | 106171 | 35.3806 | -120.4432 | CGC512982567161 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0016944 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1411404 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0016880&numberofmonths=24&showchangehistorylog=1 | 19-0016880 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | ZACA-1102 | 182681102 | OCB | 11022 | 20190202 | 327 | 286215 | 1176 | Distribution Circuit | Vegetation | Tree - fell into line | 1427 | 751030 | 34.6968 | -120.1519 | ONMAINLINEAT11301 | Overcast-Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0016880 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1411341 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0017961&numberofmonths=24&showchangehistorylog=1 | 19-0017961 | LOS PADRES | FIELD OPS SOUTH | Tier 3 | BUELLTON-1102 | 183041102 | FUSE | 6075 | 20190204 | 1326 | 290380 | 1433 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 7165 | 34.5111 | -120.2236 | 6075ACROSS101 | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 19-0017961 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1412265 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022150&numberofmonths=24&showchangehistorylog=1 | 19-0022150 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | CAMBRIA-1101 | 182771101 | FUSE | 789803 | 20190213 | 1044 | 303783 | 836 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 7539 | 35.6958 | -121.2914 | CGC510148484397 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022150 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1415506 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021876&numberofmonths=24&showchangehistorylog=1 | 19-0021876 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | MORRO BAY-1102 | 183011102 | FUSE | 10573 | 20190213 | 709 | 302969 | 436 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 3052 | 35.306 | -120.8122 | MTR1008474135 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021876 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1415320 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0029173&numberofmonths=24&showchangehistorylog=1 | 19-0029173 | LOS PADRES | FIELD OPS SOUTH | Tier 3 | TEMPLETON-2110 | 183052110 | FUSE | 5581 | 20190227 | 1606 | 327387 | 1373 | Distribution Circuit | Equipment Failure/Involved | Overhead | 40 | 11864 | 35.5552 | -120.8377 | MTR1008492305 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 19-0029173 | OH | Sus | 31426870 | yes | 2019 | FEB | Yes | Line to Line | 1420915 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0032262&numberofmonths=24&showchangehistorylog=1 | 20-0032262 | LOS PADRES | FIELD OPS SOUTH | Tier 3 | TEMPLETON-2110 | 183052110 | FUSE | 30099 | 20200315 | 851 | 852090 | 507 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 4563 | 35.5401 | -120.8366 | CGC511561175493 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0032262 | OH | Sus | 44258655 | yes | 2020 | MAR | Yes | Multi-Fault | 1521596 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0010922&numberofmonths=24&showchangehistorylog=1 | 21-0010922 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | BUELLTON-1101 | 183041101 | FUSE | 8673 | 20210119 | 1223 | 1217455 | 382 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 2674 | 34.5354 | -120.1808 | 2PEOF8673 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0010922 | OH | Sus | 0 | No | 2021 | JAN | Yes | Multi-Fault | 1594739 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0010709&numberofmonths=24&showchangehistorylog=1 | 21-0010709 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | PERRY-1101 | 183071101 | RECLOSER | W12 | 20210119 | 1142 | 1216804 | 589 | Distribution Circuit | Vegetation | Tree - fell into line | 783 | 64893 | 35.5488 | -121.0891 | 2PWOF9219 | Clear-32-90F | Crossarm, Wood | Broken, wire on ground | 21-0010709 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Line | 1594598 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0015564&numberofmonths=24&showchangehistorylog=1 | 21-0015564 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | PERRY-1101 | 183071101 | RECLOSER | V72 | 20210127 | 251 | 1232418 | 436 | Distribution Circuit | Vegetation | Tree - fell into line | 1579 | 233641 | 35.5505 | -121.0724 | LAWSONPLRICHARDAVE | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0015564 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Line | 1598115 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0103873&numberofmonths=24&showchangehistorylog=1 | 21-0103873 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | CAMBRIA-1102 | 182771102 | FUSE | 3865 | 20210812 | 1618 | 1441321 | 356 | Distribution Circuit | Equipment Failure/Involved | Overhead | 83 | 29548 | 35.5742 | -121.1038 | NOFCGC510774376979 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 21-0103873 | OH | Sus | 44945723 | No | 2021 | AUG | Yes | Line to Ground | 1657064 | CSO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0136963&numberofmonths=24&showchangehistorylog=1 | 21-0136963 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | PASO ROBLES-1104 | 182611104 | OTHER | WIREDOWNTWDCGC511598579063 | 20211025 | 14 | 1516133 | 1016 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2032 | 35.6396 | -120.8283 | CGC511598579063 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0136963 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Ground | 1678435 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0136878&numberofmonths=24&showchangehistorylog=1 | 21-0136878 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | SAN LUIS OBISPO-1107 | 182631107 | RECLOSER | V18 | 20211025 | 455 | 1516952 | 853 | Distribution Circuit | Vegetation | Tree - fell into line | 1042 | 316084 | 35.1831 | -120.7038 | CGC511927762252 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0136878 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Ground | 1678377 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0138378&numberofmonths=24&showchangehistorylog=1 | 22-0138378 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | PERRY-1101 | 183071101 | RECLOSER | V74 | 20221210 | 1222 | 1882329 | 387 | Distribution Circuit | Vegetation | Tree - fell into line | 382 | 64752 | 35.5459 | -121.0678 | 9547PINERIDGEATELLIS | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0138378 | OH | Sus | 31630223 | No | 2022 | DEC | Yes | Line to Line | 1789207 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0007093&numberofmonths=24&showchangehistorylog=1 | 23-0007093 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | OCEANO-1104 | 182601104 | FUSE | 15185 | 20230105 | 421 | 1920579 | 548 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 15892 | 35.1492 | -120.5716 | JNO15183 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0007093 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Line | 1797387 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0010233&numberofmonths=24&showchangehistorylog=1 | 23-0010233 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | CABRILLO-1104 | 183101104 | FUSE | 6345 | 20230108 | 1258 | 1933594 | 519 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 6607 | 34.6409 | -120.5021 | 3LDSIDEOF658059 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0010233 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1800083 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0016277&numberofmonths=24&showchangehistorylog=1 | 23-0016277 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | OCEANO-1102 | 182601102 | FUSE | 8631 | 20230114 | 1421 | 1954545 | 254 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 5588 | 35.0679 | -120.5939 | 2SPANSLDSIDEOF8631 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0016277 | OH | Sus | 0 | No | 2023 | JAN | Yes | Three Phase Fault | 1805036 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0033704&numberofmonths=24&showchangehistorylog=1 | 23-0033704 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | PURISIMA-1101 | 182971101 | FUSE | 20139 | 20230224 | 511 | 2003221 | 424 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 4240 | 34.73 | -120.4364 | 2PLOADSIDEOF20139 | Overcast-Drizzle-Strong Winds-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 23-0033704 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Ground | 1816741 | CSO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0044832&numberofmonths=24&showchangehistorylog=1 | 23-0044832 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | PERRY-1101 | 183071101 | FUSE | 9211 | 20230314 | 1028 | 2035944 | 464 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 4640 | 35.5467 | -121.0762 | LDSIDEOF9211 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0044832 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Line | 1824943 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0044881&numberofmonths=24&showchangehistorylog=1 | 23-0044881 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | PERRY-1101 | 183071101 | RECLOSER | V74 | 20230314 | 1140 | 2037502 | 392 | Distribution Circuit | Vegetation | Tree - fell into line | 372 | 66360 | 35.5459 | -121.0678 | WIREDOWNLDANDSOURCEOF14837 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0044881 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1824987 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0004232&numberofmonths=24&showchangehistorylog=1 | 23-0004232 | LOS PADRES | FIELD OPS SOUTH | Tier 2 | CABRILLO-1104 | 183101104 | FUSE | 6345 | 20221231 | 2353 | 1907547 | 1069 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 13028 | 34.6409 | -120.5021 | 3LDSIDEOF658059 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0004232 | OH | Sus | 0 | No | 2022 | DEC | Yes | Three Phase Fault | 1794824 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079088&numberofmonths=24&showchangehistorylog=1 | 14-0079088 | MISSION | FIELD OPS CENTRAL | Tier 3 | CASTRO VALLEY-1108 | 14091108 | RECLOSER | MR243 | 20141230 | 1330 | 1152313 | 435 | Distribution Circuit | Vegetation | Tree - fell into line | 394 | 71393 | 37.7023 | -122.0453 | ARAQUISTAIN3110TREEFELLONPRIMARYOFFCROWCANYONRD | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 14-0079088 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99190599 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079393&numberofmonths=24&showchangehistorylog=1 | 14-0079393 | MISSION | FIELD OPS CENTRAL | Tier 2 | CAYETANO-2111 | 14422111 | FUSE | 71835 | 20141230 | 1820 | 1154724 | 365 | Distribution Circuit | Vegetation | Tree - branch fell on line | 23 | 8255 | 37.7112 | -121.8057 | 1PNOF5800COLLIERCANYONRD | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079393 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Multi-Fault | 99190379 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079180&numberofmonths=24&showchangehistorylog=1 | 14-0079180 | MISSION | FIELD OPS CENTRAL | Tier 2 | VINEYARD-2107 | 14502107 | FUSE | 72640 | 20141230 | 1419 | 1152687 | 1259 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 42125 | 37.6365 | -121.8803 | SOUTHOF8128 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079180 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99190192 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005889&numberofmonths=24&showchangehistorylog=1 | 17-0005889 | MISSION | FIELD OPS CENTRAL | Tier 3 | SAN RAMON-2108 | 14232108 | FUSE | 8928 | 20170109 | 417 | 1630063 | 612 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 3060 | 37.7586 | -122.0286 | 5PWOFUCOS8928 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005889 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245673 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006767&numberofmonths=24&showchangehistorylog=1 | 17-0006767 | MISSION | FIELD OPS CENTRAL | Tier 3 | CASTRO VALLEY-1108 | 14091108 | FUSE | 12851 | 20170110 | 1412 | 1633645 | 721 | Distribution Circuit | Vegetation | Tree - fell into line | 121 | 87241 | 37.6755 | -122.0126 | 31111PALOMARESRD | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006767 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246360 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006380&numberofmonths=24&showchangehistorylog=1 | 17-0006380 | MISSION | FIELD OPS CENTRAL | Tier 3 | SAN RAMON-2108 | 14232108 | FUSE | 13115 | 20170110 | 31 | 1632426 | 1049 | Distribution Circuit | Vegetation | Tree - branch fell on line | 99 | 34726 | 37.7702 | -122.0036 | MAINLINEANDTAPLINEATCUTOUTS10694 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006380 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246086 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011676&numberofmonths=24&showchangehistorylog=1 | 17-0011676 | MISSION | FIELD OPS CENTRAL | Tier 3 | CASTRO VALLEY-1108 | 14091108 | RECLOSER | MR243 | 20170120 | 1523 | 1654572 | 1198 | Distribution Circuit | Vegetation | Tree - fell into line | 385 | 84293 | 37.7022 | -122.0452 | 5588CROWCANYONRD | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011676 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1250525 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012145&numberofmonths=24&showchangehistorylog=1 | 17-0012145 | MISSION | FIELD OPS CENTRAL | Tier 3 | SUNOL-1101 | 14241101 | OTHER | WIREDOWN2373KILKARE | 20170121 | 1715 | 1657026 | 941 | Distribution Circuit | Vegetation | Tree - fell into line | 205 | 99799 | 37.6265 | -121.9118 | BERRIOS51762373kilkare | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012145 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1250961 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0022796&numberofmonths=24&showchangehistorylog=1 | 17-0022796 | MISSION | FIELD OPS CENTRAL | Tier 2 | CAYETANO-2109 | 14422109 | FUSE | 12334 | 20170217 | 1946 | 1698321 | 449 | Distribution Circuit | Equipment Failure/Involved | Overhead | 47 | 21103 | 37.7585 | -121.7925 | HIGHLANDMANNING | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022796 | OH | Sus | 0 | yes | 2017 | FEB | Yes | None | 1259812 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0090336&numberofmonths=24&showchangehistorylog=1 | 18-0090336 | MISSION | FIELD OPS CENTRAL | Tier 3 | SAN RAMON-2108 | 14232108 | RECLOSER | 53732 | 20181014 | 2305 | 195161 | 686 | Distribution Circuit | Vegetation | Tree - branch fell on line | 90 | 54411 | 37.7758 | -121.9974 | 3POLESSO15631 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0090336 | OH | Sus | 43506702 | yes | 2018 | OCT | Yes | Line to Line | 1385579 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0105428&numberofmonths=24&showchangehistorylog=1 | 18-0105428 | MISSION | FIELD OPS CENTRAL | Tier 3 | CASTRO VALLEY-1108 | 14091108 | TRIP-SAVER | 10315 | 20181129 | 2218 | 229734 | 1062 | Distribution Circuit | 3rd Party | Vehicle | 67 | 57285 | 37.6517 | -121.9818 | 34400PALOMARESRD | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 18-0105428 | OH | Sus | 0 | yes | 2018 | NOV | Yes | Line to Ground | 1396466 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0085343&numberofmonths=24&showchangehistorylog=1 | 20-0085343 | MISSION | FIELD OPS CENTRAL | Tier 3 | SUNOL-1101 | 14241101 | FUSE | 12787 | 20200816 | 2054 | 1014171 | 1235 | Distribution Circuit | Vegetation | Tree - fell into line | 114 | 132929 | 37.6138 | -121.8989 | MTR1006631579 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0085343 | OH | Sus | 0 | yes | 2020 | AUG | Yes | Line to Ground | 1555774 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0161713&numberofmonths=24&showchangehistorylog=1 | 21-0161713 | MISSION | FIELD OPS CENTRAL | Tier 3 | TASSAJARA-2113 | 14662113 | FUSE | 62482 | 20211229 | 2239 | 1589247 | 692 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 692 | 37.7463 | -122.0236 | WIREDOWN7PNOSBCO62481 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0161713 | OH | Sus | 31588487 | No | 2021 | DEC | Yes | Line to Ground | 1699546 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0011302&numberofmonths=24&showchangehistorylog=1 | 23-0011302 | MISSION | FIELD OPS CENTRAL | Tier 3 | CASTRO VALLEY-1110 | 14091110 | FUSE | 779893 | 20230109 | 1301 | 1938202 | 484 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 484 | 37.6214 | -121.9437 | 8SPANSSOF779893 | Heavy Rain-Strong Winds-Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0011302 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1801080 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0034027&numberofmonths=24&showchangehistorylog=1 | 23-0034027 | MISSION | FIELD OPS CENTRAL | Tier 3 | SAN RAMON-2108 | 14232108 | FUSE | 6878 | 20230224 | 632 | 2003468 | 613 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 11034 | 37.8133 | -122.0446 | 1POLESOURCESIDEOFCGC315490848305 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 23-0034027 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Ground | 1816988 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0022604&numberofmonths=24&showchangehistorylog=1 | 13-0022604 | NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1124 | 42031124 | FUSE | 623 | 20130408 | 750 | 769920 | 690 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 31274 | 37.9136 | -122.5523 | CORTEMADERAAVEKINGMILLVALLEY | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0022604 | OH | Sus | 30988242 | yes | 2013 | APR | Yes | Line to Ground | 99292013 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078697&numberofmonths=24&showchangehistorylog=1 | 13-0078697 | NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 8321 | 20131122 | 721 | 911109 | 984 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 3936 | 38.6034 | -122.6443 | 2SPANSONTHELOADSIDEOFLCO8321 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078697 | OH | Sus | 0 | yes | 2013 | NOV | Yes |  | 99251489 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078272&numberofmonths=24&showchangehistorylog=1 | 13-0078272 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 2663 | 20131122 | 210 | 910505 | 795 | Distribution Circuit | Equipment Failure/Involved | Other | 1 | 795 | 38.6093 | -122.4591 | 1400INKGRADERD | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0078272 | OH | Sus | 0 | yes | 2013 | NOV | Yes |  | 99251714 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078276&numberofmonths=24&showchangehistorylog=1 | 13-0078276 | NORTH BAY | FIELD OPS NORTH | Tier 2 | SILVERADO-2104 | 43432104 | SECTIONALIZER | 7917 | 20131122 | 29 | 910249 | 946 | Distribution Circuit | Vegetation | Tree - fell into line | 225 | 198570 | 38.6632 | -122.4482 | 18SPANSLDSIDEOF3245 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 13-0078276 | OH | Sus | 0 | yes | 2013 | NOV | Yes | Line to Ground | 99251711 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078295&numberofmonths=24&showchangehistorylog=1 | 13-0078295 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 3345 | 20131122 | 218 | 910590 | 1043 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 46101 | 38.5506 | -122.4846 | 2SPANSLDSIDEOFSW483TWD6825 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078295 | OH | Sus | 0 | yes | 2013 | NOV | Yes | Line to Ground | 99251698 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0052765&numberofmonths=24&showchangehistorylog=1 | 14-0052765 | NORTH BAY | FIELD OPS NORTH | Tier 2 | PUEBLO-2103 | 43292103 | FUSE | 5479 | 20140824 | 329 | 1071789 | 1156 | Distribution Circuit | Environmental/External | Earthquake | 9 | 10404 | 38.3283 | -122.3533 | LDSIDEOF5479 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0052765 | OH | Sus | 0 | No | 2014 | AUG | Yes | Line to Ground | 99210825 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0073572&numberofmonths=24&showchangehistorylog=1 | 14-0073572 | NORTH BAY | FIELD OPS NORTH | Tier 2 | PUEBLO-1104 | 43291104 | FUSE | 1091 | 20141203 | 1448 | 1123622 | 677 | Distribution Circuit | Vegetation | Tree - bark fell into line | 16 | 10832 | 38.4406 | -122.246 | 9SPLDSIDEOFRISE3889 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073572 | OH | Sus | 0 | yes | 2014 | DEC | Yes |  | 99196698 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0073189&numberofmonths=24&showchangehistorylog=1 | 14-0073189 | NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2103 | 43292103 | FUSE | 5561 | 20141203 | 243 | 1121645 | 542 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 3252 | 38.3357 | -122.3863 | MTR1009655401 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073189 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99196971 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0073264&numberofmonths=24&showchangehistorylog=1 | 14-0073264 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1108 | 42011108 | FUSE | 463 | 20141203 | 842 | 1122049 | 423 | Distribution Circuit | Vegetation | Tree - branch fell on line | 124 | 14652 | 37.9812 | -122.5923 | MTR116671 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073264 | OH | Sus | 0 | yes | 2014 | DEC | Yes |  | 99196909 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075690&numberofmonths=24&showchangehistorylog=1 | 14-0075690 | NORTH BAY | FIELD OPS NORTH | Tier 2 | ALTO-1125 | 42031125 | FUSE | 5173 | 20141211 | 727 | 1130628 | 1498 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 55426 | 37.8783 | -122.5393 | 23SPANSFROM5173 | Heavy rain-32 - 90 F | Conductor, Overhead | On Ground | 14-0075690 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99194302 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075862&numberofmonths=24&showchangehistorylog=1 | 14-0075862 | NORTH BAY | FIELD OPS NORTH | Tier 2 | ALTO-1125 | 42031125 | FUSE | 1207 | 20141211 | 601 | 1129696 | 1986 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 25053 | 37.8853 | -122.5486 | 12SPANSLDSIDEOF1207 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 14-0075862 | OH | Sus | 0 | yes | 2014 | DEC | Yes | None | 99194250 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0074792&numberofmonths=24&showchangehistorylog=1 | 14-0074792 | NORTH BAY | FIELD OPS NORTH | Tier 2 | BOLINAS-1101 | 42261101 | RECLOSER | 504 | 20141211 | 51 | 1128816 | 2253 | Distribution Circuit | Vegetation | Tree - fell into line | 820 | 179748 | 37.934 | -122.6966 | SW3251 | Heavy rain-32 - 90 F | Conductor, Overhead | On Ground | 14-0074792 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Multi-Fault | 99193591 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075789&numberofmonths=24&showchangehistorylog=1 | 14-0075789 | NORTH BAY | FIELD OPS NORTH | Tier 2 | BOLINAS-1101 | 42261101 | RECLOSER | 1232 | 20141211 | 1734 | 1135428 | 773 | Distribution Circuit | Equipment Failure/Involved | Other | 415 | 320761 | 37.9361 | -122.7033 | Hlebakos431perDObetweenLR461426287 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075789 | OH | Sus | 0 | yes | 2014 | DEC | Yes |  | 99194275 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075425&numberofmonths=24&showchangehistorylog=1 | 14-0075425 | NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 8321 | 20141211 | 946 | 1132435 | 344 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1376 | 38.6032 | -122.6443 | 4SPANSLDSIDEOF8321 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075425 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99194882 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076269&numberofmonths=24&showchangehistorylog=1 | 14-0076269 | NORTH BAY | FIELD OPS NORTH | Tier 3 | GREENBRAE-1102 | 43091102 | FUSE | 2379 | 20141211 | 1005 | 1132651 | 1773 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 69147 | 37.9535 | -122.5352 | 185VISTAGRANDE | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076269 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194048 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075216&numberofmonths=24&showchangehistorylog=1 | 14-0075216 | NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 3585 | 20141211 | 433 | 1129103 | 772 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 14668 | 38.1033 | -122.8633 | 2SPANSLDSIDEOFFUCO3585 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075216 | OH | Sus | 0 | yes | 2014 | DEC | Yes |  | 99195053 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075224&numberofmonths=24&showchangehistorylog=1 | 14-0075224 | NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 7467 | 20141211 | 433 | 1132169 | 772 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 5404 | 38.0997 | -122.8766 | 4SPANSLDSIDEOFFUCO7467 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075224 | OH | Sus | 0 | yes | 2014 | DEC | Yes |  | 99195048 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075312&numberofmonths=24&showchangehistorylog=1 | 14-0075312 | NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 1973 | 20141211 | 800 | 1131786 | 545 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 21800 | 38.1092 | -122.8653 | 29KEHOEWAY | Strong winds-Below 32 F | Conductor, Overhead | On Ground | 14-0075312 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99194973 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075400&numberofmonths=24&showchangehistorylog=1 | 14-0075400 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1107 | 42011107 | FUSE | 4965 | 20141211 | 727 | 1130627 | 423 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 10152 | 37.9461 | -122.5564 | 3SPLDSIDEOFFUSE4965 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075400 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194898 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0074913&numberofmonths=24&showchangehistorylog=1 | 14-0074913 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1108 | 42011108 | RECLOSER | 1250 | 20141211 | 527 | 1129451 | 1133 | Distribution Circuit | Equipment Failure/Involved | Other | 19 | 19709 | 37.9607 | -122.5709 | 2SPANSLDSIDEOFLR1250SSOFSW55939 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074913 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194396 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075242&numberofmonths=24&showchangehistorylog=1 | 14-0075242 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 4505 | 20141211 | 847 | 1131567 | 232 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 3712 | 38.5823 | -122.4595 | 925BELLCANYONRD | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075242 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99195030 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075853&numberofmonths=24&showchangehistorylog=1 | 14-0075853 | NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1101 | 43021101 | FUSE | 4585 | 20141211 | 1736 | 1135264 | 1475 | Distribution Circuit | Vegetation | Tree - branch fell on line | 70 | 103250 | 38.0142 | -122.6894 | BET129AND140RESACAAVEFORESTKNOLLS | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 14-0075853 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194252 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076370&numberofmonths=24&showchangehistorylog=1 | 14-0076370 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 6841 | 20141212 | 1053 | 1138059 | 382 | Distribution Circuit | Equipment Failure/Involved | Other | 32 | 12224 | 38.5793 | -122.4501 | 400CIRCLEDR | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076370 | OH | Sus | 0 | yes | 2014 | DEC | Yes |  | 99193971 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079431&numberofmonths=24&showchangehistorylog=1 | 14-0079431 | NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1124 | 42031124 | FUSE | 2147 | 20141230 | 1432 | 1152819 | 501 | Distribution Circuit | Equipment Failure/Involved | Other | 63 | 31563 | 37.9059 | -122.5522 | WIREDOWN | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 14-0079431 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99190357 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079308&numberofmonths=24&showchangehistorylog=1 | 14-0079308 | NORTH BAY | FIELD OPS NORTH | Tier 2 | CALISTOGA-1101 | 42711101 | FUSE | 9541 | 20141230 | 1534 | 1153473 | 807 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 8877 | 38.622 | -122.6792 | COROFRANZVALLEYRDSPENCERRD | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 14-0079308 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99190437 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079480&numberofmonths=24&showchangehistorylog=1 | 14-0079480 | NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2103 | 43292103 | OTHER |  | 20141230 | 1651 | 1154541 | 1274 | Distribution Circuit | Equipment Failure/Involved | Other | 1 | 1274 | 38.3725 | -122.4319 | UNKNOWN | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 14-0079480 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99190128 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079407&numberofmonths=24&showchangehistorylog=1 | 14-0079407 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2105 | 43432105 | FUSE | 3363 | 20141230 | 1654 | 1154549 | 1271 | Distribution Circuit | Equipment Failure/Involved | Other | 36 | 26696 | 38.4944 | -122.4874 | TRANSMISSIONTOWER1421SPANLDSIDEOF3363 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 14-0079407 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99190143 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011343&numberofmonths=24&showchangehistorylog=1 | 15-0011343 | NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1124 | 42031124 | FUSE | 5869 | 20150206 | 2201 | 1178926 | 1716 | Distribution Circuit | Equipment Failure/Involved | Other | 90 | 154440 | 37.9057 | -122.5667 | SSTOFUCOS915ONMUIRAVE | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 15-0011343 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99184259 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010514&numberofmonths=24&showchangehistorylog=1 | 15-0010514 | NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1125 | 42031125 | FUSE | 3523 | 20150206 | 1315 | 1175327 | 1440 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 113760 | 37.8669 | -122.5774 | 1SPANLDSIDEOFFUCO6863 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010514 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99184600 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010738&numberofmonths=24&showchangehistorylog=1 | 15-0010738 | NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1125 | 42031125 | FUSE | 54471 | 20150206 | 2210 | 1179101 | 2104 | Distribution Circuit | Equipment Failure/Involved | Other | 9 | 18936 | 37.8997 | -122.5419 | 379MOLINOAVEINMILLVALLEY | Strong winds-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 15-0010738 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99183929 | CSO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0009790&numberofmonths=24&showchangehistorylog=1 | 15-0009790 | NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | RECLOSER | 602 | 20150206 | 417 | 1173145 | 801 | Distribution Circuit | Vegetation | Tree - fell into line | 155 | 124155 | 38.1093 | -122.87 | 2PBEYONDLR602 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0009790 | OH | Sus | 31133058 | yes | 2015 | FEB | Yes | Line to Line | 99185343 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010393&numberofmonths=24&showchangehistorylog=1 | 15-0010393 | NORTH BAY | FIELD OPS NORTH | Tier 2 | PUEBLO-2103 | 43292103 | FUSE | 1391 | 20150206 | 1514 | 1176092 | 644 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 3098 | 38.3115 | -122.3621 | 1481PARTRICKRDNAPA | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010393 | OH | Sus | 0 | yes | 2015 | FEB | Yes | None | 99184995 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011247&numberofmonths=24&showchangehistorylog=1 | 15-0011247 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1107 | 42011107 | FUSE | 3323 | 20150206 | 1924 | 1177915 | 1839 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 33102 | 37.9575 | -122.5415 | LOADSIDEOF3323 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 15-0011247 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99184313 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010265&numberofmonths=24&showchangehistorylog=1 | 15-0010265 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1108 | 42011108 | FUSE | 6745 | 20150206 | 1332 | 1175419 | 298 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 5662 | 37.9845 | -122.581 | 129LANDSDALEAVE | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010265 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99185073 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010897&numberofmonths=24&showchangehistorylog=1 | 15-0010897 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1108 | 42011108 | FUSE | 2743 | 20150206 | 1919 | 1177855 | 1306 | Distribution Circuit | Vegetation | Tree - branch fell on line | 85 | 65650 | 37.9676 | -122.5689 | SCHERERJRMARK150OAKAVE | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010897 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99184508 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0009841&numberofmonths=24&showchangehistorylog=1 | 15-0009841 | NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1101 | 43021101 | OTHER |  | 20150206 | 527 | 1173403 | 613 | Distribution Circuit | Vegetation | Tree - branch fell on line | 233 | 125603 | 38.0138 | -122.6977 | IFO7159SIRFRANCISDRAKELAGUNITAS | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on object | 15-0009841 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99185317 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010282&numberofmonths=24&showchangehistorylog=1 | 15-0010282 | NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1101 | 43021101 | FUSE | 953 | 20150206 | 1358 | 1175657 | 779 | Distribution Circuit | Vegetation | Tree - fell into line | 132 | 39128 | 38.0139 | -122.6884 | FUCOS5841 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010282 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Three Phase Fault | 99185062 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011262&numberofmonths=24&showchangehistorylog=1 | 15-0011262 | NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1101 | 43021101 | FUSE | 2629 | 20150206 | 1737 | 1176969 | 1318 | Distribution Circuit | Vegetation | Tree - branch fell on line | 64 | 84352 | 38.0103 | -122.7019 | 5SPANSLDSIDEOF2629 | Strong winds-32 - 90 F | Cutout, Fused, Distribution | Broken, wire on ground | 15-0011262 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99184302 | COF | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011368&numberofmonths=24&showchangehistorylog=1 | 15-0011368 | NORTH BAY | FIELD OPS NORTH | Tier 2 | ALTO-1125 | 42031125 | FUSE | 2243 | 20150207 | 1839 | 1181788 | 201 | Distribution Circuit | Equipment Failure/Involved | Other | 357 | 67711 | 37.8804 | -122.5384 | IFO550NORTHERNAVEMILLVALLEY | Strong winds-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 15-0011368 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99184246 | CSO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010826&numberofmonths=24&showchangehistorylog=1 | 15-0010826 | NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 1703 | 20150207 | 5 | 1179608 | 2376 | Distribution Circuit | Vegetation | Tree - branch fell on line | 28 | 3429 | 38.0746 | -122.8434 | JENSENWILLIAMendofelizabethave | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on object | 15-0010826 | OH | Sus | 0 | yes | 2015 | FEB | Yes | None | 99183918 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011361&numberofmonths=24&showchangehistorylog=1 | 15-0011361 | NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 1677 | 20150207 | 1519 | 1180503 | 2862 | Distribution Circuit | Vegetation | Tree - branch fell on line | 21 | 44011 | 38.1321 | -122.9067 | DUCKCOVERDFUCOS1677 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011361 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183360 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011001&numberofmonths=24&showchangehistorylog=1 | 15-0011001 | NORTH BAY | FIELD OPS NORTH | Tier 2 | SAN RAFAEL-1109 | 42011109 | FUSE | 2213 | 20150207 | 54 | 1179707 | 1396 | Distribution Circuit | Vegetation | Tree - branch fell on line | 26 | 36296 | 38.009 | -122.5193 | 7CRESTVIEWDRIVESANRAFAEL | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011001 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99184462 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011143&numberofmonths=24&showchangehistorylog=1 | 15-0011143 | NORTH BAY | FIELD OPS NORTH | Tier 2 | SAN RAFAEL-1109 | 42011109 | OTHER |  | 20150207 | 855 | 1180841 | 400 | Distribution Circuit | Vegetation | Tree - branch fell on line | 33 | 1925 | 38.0078 | -122.5091 | MTR1009802917 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011143 | OH | Sus | 0 | yes | 2015 | FEB | Yes | None | 99183889 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010991&numberofmonths=24&showchangehistorylog=1 | 15-0010991 | NORTH BAY | FIELD OPS NORTH | Tier 2 | SILVERADO-2104 | 43432104 | FUSE | 489 | 20150207 | 338 | 1179963 | 942 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 8478 | 38.6523 | -122.4814 | 2SPANSPAST1570AETNASPRINGSRD | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010991 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99184468 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011936&numberofmonths=24&showchangehistorylog=1 | 15-0011936 | NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 863 | 20150208 | 2359 | 1185454 | 2623 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 10492 | 38.5693 | -122.6277 | Boydston24865800petrifiedforrestrdTREEDOWN | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 15-0011936 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Three Phase Fault | 99182797 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011721&numberofmonths=24&showchangehistorylog=1 | 15-0011721 | NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1102 | 43021102 | FUSE | 2387 | 20150208 | 1803 | 1183583 | 364 | Distribution Circuit | Vegetation | Tree - fell into line | 205 | 74620 | 37.9874 | -122.594 | Donahue439 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011721 | OH | Sus | 0 | yes | 2015 | FEB | Yes | None | 99183613 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0039553&numberofmonths=24&showchangehistorylog=1 | 15-0039553 | NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 1891 | 20150608 | 2050 | 1246905 | 990 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 5347 | 38.1004 | -122.8622 | 550ABERDEEN | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0039553 | OH | Sus | 0 | yes | 2015 | JUN | Yes | Line to Ground | 99164770 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0039246&numberofmonths=24&showchangehistorylog=1 | 15-0039246 | NORTH BAY | FIELD OPS NORTH | Tier 2 | PUEBLO-1105 | 43291105 | FUSE | 7553 | 20150608 | 1000 | 1245524 | 229 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 794 | 38.372 | -122.2682 | 4SPANSLDSIDEOF7553 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0039246 | OH | Sus | 42401796 | yes | 2015 | JUN | Yes | Line to Ground | 99164966 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0084782&numberofmonths=24&showchangehistorylog=1 | 15-0084782 | NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1125 | 42031125 | FUSE | 2227 | 20151213 | 849 | 1360540 | 471 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 5652 | 37.8959 | -122.6009 | 10SPANSNOFFUCO2227 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | On Ground | 15-0084782 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1174449 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0084945&numberofmonths=24&showchangehistorylog=1 | 15-0084945 | NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1125 | 42031125 | FUSE | 3979 | 20151213 | 1505 | 1362526 | 66 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 132 | 37.8906 | -122.565 | 4SPANSLDSIDEOFFUCO3979 | Overcast-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084945 | OH | Sus | 0 | yes | 2015 | DEC | Yes | None | 1174619 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0084593&numberofmonths=24&showchangehistorylog=1 | 15-0084593 | NORTH BAY | FIELD OPS NORTH | Tier 2 | BOLINAS-1101 | 42261101 | RECLOSER | 504 | 20151213 | 843 | 1360524 | 853 | Distribution Circuit | Vegetation | Tree - fell into line | 820 | 208420 | 37.9343 | -122.6968 | RITCHIETIMOTHYro7220PanoramicHwymtr1009956330 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 15-0084593 | OH | Sus | 42589004 | yes | 2015 | DEC | Yes | Line to Ground | 1174256 | CSO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0084758&numberofmonths=24&showchangehistorylog=1 | 15-0084758 | NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1102 | 42711102 | OTHER | WIREDOWNAT1011TWD9139 | 20151213 | 928 | s1174426 | 367 | Distribution Circuit | Vegetation | Tree - fell into line | 64 | 20027 | 38.5712 | -122.5173 | AT1011TWD9139 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084758 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1174426 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0084650&numberofmonths=24&showchangehistorylog=1 | 15-0084650 | NORTH BAY | FIELD OPS NORTH | Tier 2 | MONTICELLO-1101 | 43051101 | RECLOSER | 4360 | 20151213 | 829 | 1360465 | 866 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 22516 | 38.4042 | -122.2043 | Boydston2486COPOLE7467 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 15-0084650 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Line | 1174316 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017642&numberofmonths=24&showchangehistorylog=1 | 16-0017642 | NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1125 | 42031125 | JUMPER | WIREDOWNPANORAMICANDSTJUDE | 20160305 | 1736 | 1417941 | 635 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1297 | 195739 | 37.9012 | -122.5682 | WIREDOWNPANORAMICSTJUDE | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 16-0017642 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Open Circuit | 1189496 | CSO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0018041&numberofmonths=24&showchangehistorylog=1 | 16-0018041 | NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1125 | 42031125 | FUSE | 2249 | 20160305 | 2008 | 1418779 | 1387 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 66576 | 37.8897 | -122.5435 | IFO1209LATTIELNMV | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on object | 16-0018041 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Three Phase Fault | 1189912 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017457&numberofmonths=24&showchangehistorylog=1 | 16-0017457 | NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 3585 | 20160305 | 1045 | 1416501 | 648 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 16601 | 38.1033 | -122.8632 | 300VISIONRD | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017457 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1189340 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0018142&numberofmonths=24&showchangehistorylog=1 | 16-0018142 | NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | OTHER | WIREDOWN8PINEHILLRD | 20160305 | 2304 | 1420950 | 1793 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 16418 | 38.1087 | -122.8674 | WIREDOWN8PINEHILLRD | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018142 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190013 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017566&numberofmonths=24&showchangehistorylog=1 | 16-0017566 | NORTH BAY | FIELD OPS NORTH | Tier 2 | PUEBLO-1105 | 43291105 | FUSE | 1767 | 20160305 | 1453 | 1417281 | 322 | Distribution Circuit | Vegetation | Tree - fell into line | 161 | 46642 | 38.3825 | -122.2919 | 1SPANNOMTR1009365167 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017566 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1189423 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017530&numberofmonths=24&showchangehistorylog=1 | 16-0017530 | NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2103 | 43292103 | FUSE | 311 | 20160305 | 1449 | 1416818 | 821 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 9031 | 38.3492 | -122.3789 | 14SPANSLDSIDE311 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 16-0017530 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1189391 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017956&numberofmonths=24&showchangehistorylog=1 | 16-0017956 | NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2103 | 43292103 | FUSE | 1145 | 20160305 | 1729 | 1417663 | 481 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2886 | 38.3344 | -122.373 | 1338MTVEEDER | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017956 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1189818 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0018138&numberofmonths=24&showchangehistorylog=1 | 16-0018138 | NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2103 | 43292103 | FUSE | 3583 | 20160305 | 2205 | 1420745 | 1136 | Distribution Circuit | Vegetation | Tree - fell into line | 191 | 112494 | 38.3745 | -122.4204 | 8SPANSPASTSW3119TWD3123 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018138 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190009 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017902&numberofmonths=24&showchangehistorylog=1 | 16-0017902 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1107 | 42011107 | FUSE | 2499 | 20160305 | 2012 | 1418810 | 935 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 15895 | 37.9583 | -122.5345 | 46WOLFECANYON | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017902 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1189762 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0018152&numberofmonths=24&showchangehistorylog=1 | 16-0018152 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 797 | 20160305 | 1831 | 1418159 | 1441 | Distribution Circuit | Vegetation | Tree - fell into line | 124 | 138380 | 38.5901 | -122.4425 | 2000SUMMITLAKEDR2SPANSLDSIDEOF1107 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | On Ground | 16-0018152 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Three Phase Fault | 1190023 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0018237&numberofmonths=24&showchangehistorylog=1 | 16-0018237 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | OTHER | WIREDOWN1700HOWELLMTNRD | 20160305 | 2125 | 1421101 | 1039 | Distribution Circuit | Equipment Failure/Involved | Overhead | 528 | 471460 | 38.6068 | -122.4329 | 1700HOWELLMTNRD | Overcast-Fog-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018237 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190104 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017833&numberofmonths=24&showchangehistorylog=1 | 16-0017833 | NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1101 | 43021101 | OCB | 11012 | 20160305 | 2051 | 1419222 | 489 | Distribution Circuit | Vegetation | Tree - fell into line | 1211 | 71100 | 38.0125 | -122.654 | 485SANGARONIMOVLYRD | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017833 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Multi-Fault | 1189687 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0018236&numberofmonths=24&showchangehistorylog=1 | 16-0018236 | NORTH BAY | FIELD OPS NORTH | Tier 2 | WOODACRE-1102 | 43021102 | JUMPER | OJLINESIDEOF40DEBURGHDR | 20160305 | 2038 | 1419315 | 1217 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 17038 | 38.0062 | -122.5833 | IFO40DEBURGHDR | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | On Ground | 16-0018236 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190103 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0072389&numberofmonths=24&showchangehistorylog=1 | 16-0072389 | NORTH BAY | FIELD OPS NORTH | Tier 2 | CALISTOGA-1102 | 42711102 | OCB | 11022 | 20161014 | 2357 | 1560534 | 297 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2112 | 151605 | 38.5924 | -122.5785 | 4024BRANNANST | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0072389 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Ground | 1229452 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0072063&numberofmonths=24&showchangehistorylog=1 | 16-0072063 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1107 | 42011107 | FUSE | 4497 | 20161014 | 1102 | 1559009 | 299 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 7375 | 37.9654 | -122.5514 | 114WINDINGWAY | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0072063 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Ground | 1229222 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0072113&numberofmonths=24&showchangehistorylog=1 | 16-0072113 | NORTH BAY | FIELD OPS NORTH | Tier 2 | SILVERADO-2102 | 43432102 | SWITCH | 5101 | 20161014 | 1024 | 1559279 | 775 | Distribution Circuit | Equipment Failure/Involved | Overhead | 354 | 258709 | 38.5075 | -122.4065 | SW6581CONNVLYRD8MIEOROSSISTHELENA | Overcast-Rain-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 16-0072113 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Ground | 1229259 | CSO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0003388&numberofmonths=24&showchangehistorylog=1 | 17-0003388 | NORTH BAY | FIELD OPS NORTH | Tier 2 | ALTO-1122 | 42031122 | FUSE | 1075 | 20170103 | 2301 | 1617421 | 625 | Distribution Circuit | Equipment Failure/Involved | Overhead | 45 | 18323 | 37.9165 | -122.5155 | LDSIDEOFOF12KVJUMPERSON1100MEADOWSWEETDR | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003388 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1243570 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0003201&numberofmonths=24&showchangehistorylog=1 | 17-0003201 | NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1125 | 42031125 | RECLOSER | 902 | 20170103 | 1852 | 1616469 | 2148 | Distribution Circuit | Equipment Failure/Involved | Overhead | 202 | 396358 | 37.8892 | -122.5553 | SW5031LDsideofFUCO3881 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0003201 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1243370 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0003346&numberofmonths=24&showchangehistorylog=1 | 17-0003346 | NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1125 | 42031125 | FUSE | 54471 | 20170103 | 1917 | 1616573 | 827 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 8270 | 37.8997 | -122.542 | 1SPANLDSIDEOF5447135Woodsidelane | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003346 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1243519 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0003331&numberofmonths=24&showchangehistorylog=1 | 17-0003331 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1108 | 42011108 | FUSE | 5377 | 20170103 | 1746 | 1616324 | 638 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 12760 | 37.9762 | -122.577 | 286REDWOODRD | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003331 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1243504 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0003348&numberofmonths=24&showchangehistorylog=1 | 17-0003348 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1108 | 42011108 | OTHER | WIREDOWN31FERNHILL | 20170103 | 2215 | 1617093 | 559 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 10360 | 37.9669 | -122.5643 | 2SPANSLDSIDE269531Fernhill | Overcast-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0003348 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1243521 | PW | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0003221&numberofmonths=24&showchangehistorylog=1 | 17-0003221 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 797 | 20170103 | 1901 | 1616550 | 449 | Distribution Circuit | Vegetation | Tree - fell into line | 124 | 48680 | 38.5901 | -122.4425 | BOCKMIKE707695899714841145SummittLakeDr | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003221 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1243390 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005176&numberofmonths=24&showchangehistorylog=1 | 17-0005176 | NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1122 | 42031122 | FUSE | 6385 | 20170108 | 725 | 1623105 | 1631 | Distribution Circuit | Vegetation | Tree - branch fell on line | 28 | 45668 | 37.9195 | -122.5269 | BradlyGearldine2567470MONTECITO | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005176 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1244970 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005514&numberofmonths=24&showchangehistorylog=1 | 17-0005514 | NORTH BAY | FIELD OPS NORTH | Tier 2 | ALTO-1122 | 42031122 | FUSE | 1073 | 20170108 | 915 | 1623260 | 757 | Distribution Circuit | Vegetation | Tree - fell into line | 135 | 102195 | 37.9183 | -122.5141 | 966MEADOWSWEETDRCORTEMADERA | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005514 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245297 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005562&numberofmonths=24&showchangehistorylog=1 | 17-0005562 | NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1125 | 42031125 | FUSE | 6333 | 20170108 | 1251 | 1626580 | 1965 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 180780 | 37.9024 | -122.557 | CARTERDAVID41613855868330laverne | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005562 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1245344 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005267&numberofmonths=24&showchangehistorylog=1 | 17-0005267 | NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 731 | 20170108 | 1200 | 1625954 | 770 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 34650 | 38.5774 | -122.587 | GREENEJOSEPH4440KortumCanyonrd | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0005267 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Three Phase Fault | 1245057 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005607&numberofmonths=24&showchangehistorylog=1 | 17-0005607 | NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 9415 | 20170108 | 1845 | 1628653 | 1860 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1860 | 38.614 | -122.6922 | 4SofFUCO9415 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005607 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1245385 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005870&numberofmonths=24&showchangehistorylog=1 | 17-0005870 | NORTH BAY | FIELD OPS NORTH | Tier 3 | MIDDLETOWN-1101 | 43141101 | FUSE | 473 | 20170108 | 1139 | 1630079 | 2276 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 31864 | 38.6737 | -122.5872 | BOCKMIKE707695899714843rdpolefromcos | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005870 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1245653 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005059&numberofmonths=24&showchangehistorylog=1 | 17-0005059 | NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 757 | 20170108 | 840 | 1623734 | 957 | Distribution Circuit | Vegetation | Tree - branch fell on line | 35 | 33495 | 38.073 | -122.8278 | INFRONTOF61LAURELANDINVERNESS | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | On Ground | 17-0005059 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1244858 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005063&numberofmonths=24&showchangehistorylog=1 | 17-0005063 | NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 4479 | 20170108 | 909 | 1624182 | 1866 | Distribution Circuit | Vegetation | Tree - fell into line | 109 | 40413 | 38.1096 | -122.8691 | DOYLETRAVIS225caminodelmar | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0005063 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1244862 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005182&numberofmonths=24&showchangehistorylog=1 | 17-0005182 | NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 3261 | 20170108 | 834 | 1623684 | 846 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2428 | 38.0735 | -122.8282 | DOYLETRAVIS65kyleswoodpl | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005182 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1244976 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005782&numberofmonths=24&showchangehistorylog=1 | 17-0005782 | NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 311 | 20170108 | 1056 | 1629785 | 5800 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 61300 | 38.0439 | -122.7468 | 2SPANSSSDOF1733 | Strong Winds-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005782 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245569 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005873&numberofmonths=24&showchangehistorylog=1 | 17-0005873 | NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 1945 | 20170108 | 1632 | 1628054 | 2930 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 43950 | 38.1395 | -122.9001 | DOYLETRAVISendofpiercepointrdoffofmarshallbeachrd | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005873 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245656 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005183&numberofmonths=24&showchangehistorylog=1 | 17-0005183 | NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2103 | 43292103 | FUSE | 1143 | 20170108 | 726 | 1623182 | 2694 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 33654 | 38.3462 | -122.4002 | RUPPDONOVANrearof4870REDWOODRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005183 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1244977 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005512&numberofmonths=24&showchangehistorylog=1 | 17-0005512 | NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2103 | 43292103 | FUSE | 3343 | 20170108 | 1526 | 1627922 | 1307 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 32028 | 38.3614 | -122.3713 | 4897DRYCREEKRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005512 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245295 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005589&numberofmonths=24&showchangehistorylog=1 | 17-0005589 | NORTH BAY | FIELD OPS NORTH | Tier 2 | PUEBLO-2103 | 43292103 | FUSE | 9275 | 20170108 | 1116 | 1628573 | 899 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2697 | 38.3271 | -122.3524 | REDWOODRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005589 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245369 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005592&numberofmonths=24&showchangehistorylog=1 | 17-0005592 | NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2103 | 43292103 | FUSE | 3583 | 20170108 | 1222 | 1626146 | 3133 | Distribution Circuit | Equipment Failure/Involved | Overhead | 93 | 164801 | 38.3745 | -122.4204 | WIREDOWNSSof31254037MtVeederRd | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005592 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245371 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0004893&numberofmonths=24&showchangehistorylog=1 | 17-0004893 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1107 | 42011107 | OTHER | WIREDOWN | 20170108 | 107 | 1622436 | 412 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1648 | 37.944 | -122.5564 | 215SOUTHBRDIGEWOODRD | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004893 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1244693 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005004&numberofmonths=24&showchangehistorylog=1 | 17-0005004 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1108 | 42011108 | FUSE | 3913 | 20170108 | 713 | 1622984 | 1127 | Distribution Circuit | Vegetation | Tree - fell into line | 408 | 60186 | 37.9819 | -122.5768 | 100HUMBOLTCTSANANSELMO | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005004 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1244804 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005119&numberofmonths=24&showchangehistorylog=1 | 17-0005119 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1108 | 42011108 | RECLOSER | 322 | 20170108 | 1015 | 1624812 | 1337 | Distribution Circuit | Vegetation | Tree - fell into line | 3074 | 752850 | 37.9774 | -122.5654 | NOF5123 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | On Ground | 17-0005119 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1244917 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005447&numberofmonths=24&showchangehistorylog=1 | 17-0005447 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2105 | 43432105 | FUSE | 835 | 20170108 | 1107 | 1625288 | 1679 | Distribution Circuit | Vegetation | Tree - branch fell on line | 143 | 293696 | 38.5073 | -122.4915 | GREERJEFFWOC04753 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005447 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245231 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005360&numberofmonths=24&showchangehistorylog=1 | 17-0005360 | NORTH BAY | FIELD OPS NORTH | Tier 2 | STAFFORD-1101 | 43201101 | RECLOSER | 1298 | 20170108 | 1331 | 1626941 | 1004 | Distribution Circuit | Vegetation | Tree - fell into line | 2023 | 332436 | 38.1199 | -122.5858 | 3RDSTNOVATO | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005360 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245147 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0004985&numberofmonths=24&showchangehistorylog=1 | 17-0004985 | NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1102 | 43021102 | FUSE | 2387 | 20170108 | 703 | 1623118 | 2241 | Distribution Circuit | Vegetation | Tree - fell into line | 203 | 454923 | 37.9874 | -122.5939 | 446SCENIC | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004985 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Three Phase Fault | 1244786 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005332&numberofmonths=24&showchangehistorylog=1 | 17-0005332 | NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1102 | 43021102 | OCB | 11022 | 20170108 | 1219 | 1623506 | 798 | Distribution Circuit | Vegetation | Tree - fell into line | 2689 | 563462 | 38.0125 | -122.654 | SCENICANDSPRUCE | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005332 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245122 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005937&numberofmonths=24&showchangehistorylog=1 | 17-0005937 | NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1125 | 42031125 | OTHER | WIREDOWNMADERAANDLONETREE | 20170109 | 435 | 1630371 | 975 | Distribution Circuit | Vegetation | Tree - fell into line | 76 | 37810 | 37.9013 | -122.5637 | MADERAANDLONETREE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005937 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245713 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006273&numberofmonths=24&showchangehistorylog=1 | 17-0006273 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1108 | 42011108 | FUSE | 5411 | 20170109 | 1702 | 1631874 | 486 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 6804 | 37.9783 | -122.5785 | SCENICCANYON | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006273 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245970 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006287&numberofmonths=24&showchangehistorylog=1 | 17-0006287 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2102 | 43432102 | FUSE | 2093 | 20170109 | 723 | 1631788 | 3382 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 37202 | 38.4904 | -122.3482 | 2SPANSLDSIDE | Overcast-Fog-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006287 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1245985 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007204&numberofmonths=24&showchangehistorylog=1 | 17-0007204 | NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1125 | 42031125 | FUSE | 3115 | 20170110 | 1913 | 1636046 | 699 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 8388 | 37.9076 | -122.559 | EUGENESTCASCADEDRMILLVALLEY | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007204 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1246784 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007563&numberofmonths=24&showchangehistorylog=1 | 17-0007563 | NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 683 | 20170110 | 1451 | 1635050 | 2190 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 37136 | 38.5925 | -122.6118 | YaughnKip1335firviewdr | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0007563 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247092 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007648&numberofmonths=24&showchangehistorylog=1 | 17-0007648 | NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1102 | 42711102 | FUSE | 9195 | 20170110 | 2255 | 1638828 | 2640 | Distribution Circuit | Equipment Failure/Involved | Overhead | 68 | 179520 | 38.5638 | -122.5594 | 3SPANSLD9195 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007648 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247156 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0008265&numberofmonths=24&showchangehistorylog=1 | 17-0008265 | NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1102 | 42711102 | FUSE | 6143 | 20170110 | 1455 | 1634935 | 2762 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 16572 | 38.5489 | -122.531 | BootheStatePark | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0008265 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247704 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007214&numberofmonths=24&showchangehistorylog=1 | 17-0007214 | NORTH BAY | FIELD OPS NORTH | Tier 3 | LAS GALLINAS A-1105 | 42991105 | FUSE | 3221 | 20170110 | 1824 | 1635375 | 1566 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 7830 | 38.0406 | -122.6056 | 2500LUCASVLYRD60KVCROSSING | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007214 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246793 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006360&numberofmonths=24&showchangehistorylog=1 | 17-0006360 | NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | RECLOSER | 602 | 20170110 | 8 | 1632412 | 1034 | Distribution Circuit | Vegetation | Tree - fell into line | 134 | 138556 | 38.1094 | -122.8698 | 5PSOURCESIDEOFFUCO5467 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006360 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1246068 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006843&numberofmonths=24&showchangehistorylog=1 | 17-0006843 | NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 5469 | 20170110 | 1537 | 1634107 | 585 | Distribution Circuit | Equipment Failure/Involved | Overhead | 68 | 39780 | 38.0646 | -122.8251 | 4SPLDSIDEOFFUCO5469 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006843 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246424 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006947&numberofmonths=24&showchangehistorylog=1 | 17-0006947 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1108 | 42011108 | OTHER | WIREDOWN43ALLYNNRD | 20170110 | 1835 | 1635382 | 393 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 13473 | 37.9751 | -122.5773 | 43ALLYNAAVE | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006947 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246529 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007429&numberofmonths=24&showchangehistorylog=1 | 17-0007429 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1108 | 42011108 | RECLOSER | 1250 | 20170110 | 1921 | 1638850 | 2312 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 43928 | 37.961 | -122.571 | MTR736T29 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007429 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247012 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006405&numberofmonths=24&showchangehistorylog=1 | 17-0006405 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 7341 | 20170110 | 622 | 1632520 | 686 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 10290 | 38.5819 | -122.4422 | 460HOWELLRD | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006405 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246107 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006748&numberofmonths=24&showchangehistorylog=1 | 17-0006748 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | SWITCH | 4397 | 20170110 | 1439 | 1633752 | 1756 | Distribution Circuit | Vegetation | Tree - fell into line | 182 | 93355 | 38.5955 | -122.4368 | BOCKMIKE707695899714841430Howellmntrd | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006748 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246346 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007284&numberofmonths=24&showchangehistorylog=1 | 17-0007284 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | OTHER | OJSSOF1449 | 20170110 | 1822 | 1636689 | 1041 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1457 | 283939 | 38.538 | -122.4765 | ROSELANEEMATHIERDANGWIN | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007284 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246864 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007412&numberofmonths=24&showchangehistorylog=1 | 17-0007412 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 4419 | 20170110 | 1812 | 1638666 | 1372 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 18964 | 38.6111 | -122.4596 | BOCKMIKE707695899714841500InkGrade | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007412 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246999 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0008244&numberofmonths=24&showchangehistorylog=1 | 17-0008244 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 5369 | 20170110 | 1805 | 1635219 | 2117 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 86797 | 38.52 | -122.4692 | Madroneknoll300WofSilveradoTrail | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0008244 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247686 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006551&numberofmonths=24&showchangehistorylog=1 | 17-0006551 | NORTH BAY | FIELD OPS NORTH | Tier 2 | STAFFORD-1102 | 43201102 | OTHER | WIREDOWNWOMTR100837551 | 20170110 | 1034 | 1632937 | 476 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 1936 | 38.0879 | -122.5847 | HOLCOMBAVEWILLIAMAVE | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006551 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246199 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006778&numberofmonths=24&showchangehistorylog=1 | 17-0006778 | NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1101 | 43021101 | FUSE | 5827 | 20170110 | 1535 | 1634078 | 1825 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 33458 | 38.0224 | -122.7012 | FUCO5231 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006778 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1246371 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0008222&numberofmonths=24&showchangehistorylog=1 | 17-0008222 | NORTH BAY | FIELD OPS NORTH | Tier 2 | ALTO-1125 | 42031125 | FUSE | 5189 | 20170111 | 2245 | 1640827 | 380 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 6460 | 37.8783 | -122.5367 | Hlebakos12774spansfromCO5189 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0008222 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247665 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007601&numberofmonths=24&showchangehistorylog=1 | 17-0007601 | NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 2641 | 20170111 | 633 | 1638794 | 803 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 4015 | 38.5966 | -122.6172 | YaughnKip3377hwy128 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007601 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247116 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007902&numberofmonths=24&showchangehistorylog=1 | 17-0007902 | NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 5803 | 20170111 | 722 | 1639211 | 1110 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 22200 | 38.5737 | -122.5897 | 440KORTUMCANYONRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007902 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247357 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007915&numberofmonths=24&showchangehistorylog=1 | 17-0007915 | NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 5461 | 20170111 | 800 | 1639386 | 2090 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 12540 | 38.6075 | -122.6501 | 18775FOSSHILLRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007915 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247367 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0008208&numberofmonths=24&showchangehistorylog=1 | 17-0008208 | NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 3805 | 20170111 | 1728 | 1640464 | 27019 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 79402 | 38.5485 | -122.578 | 2SPANSSOUTHWESTOF2091DIAMONDMOUNTAINRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0008208 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1247651 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0008211&numberofmonths=24&showchangehistorylog=1 | 17-0008211 | NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 9229 | 20170111 | 1748 | 1640498 | 2727 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 18887 | 38.5816 | -122.657 | PVTDRIVWAYAT9445FRANZEVALLEYRD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0008211 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1247654 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0008261&numberofmonths=24&showchangehistorylog=1 | 17-0008261 | NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 3391 | 20170111 | 1802 | 1640528 | 3148 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 18888 | 38.5592 | -122.6291 | Atunfusedlinebuck | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0008261 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247698 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0008240&numberofmonths=24&showchangehistorylog=1 | 17-0008240 | NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1102 | 42711102 | FUSE | 585 | 20170111 | 1351 | 1640898 | 1724 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 6896 | 38.563 | -122.5456 | 4199 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0008240 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1247683 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007473&numberofmonths=24&showchangehistorylog=1 | 17-0007473 | NORTH BAY | FIELD OPS NORTH | Tier 2 | MONTICELLO-1101 | 43051101 | FUSE | 1589 | 20170111 | 532 | 1638656 | 1211 | Distribution Circuit | Vegetation | Tree - fell into line | 175 | 70469 | 38.4069 | -122.2056 | TERRILLRICH41517073152058cocolumbineandcountryclubln | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007473 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247035 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007427&numberofmonths=24&showchangehistorylog=1 | 17-0007427 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1107 | 42011107 | FUSE | 4475 | 20170111 | 622 | 1638730 | 438 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 22776 | 37.9607 | -122.5415 | KNIFFINANDREW25HILLDR | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007427 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247010 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0010296&numberofmonths=24&showchangehistorylog=1 | 17-0010296 | NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | RECLOSER | 75686 | 20170118 | 1820 | 1648052 | 1216 | Distribution Circuit | Vegetation | Tree - fell into line | 129 | 229787 | 38.0487 | -122.7435 | WIREDOWN3SPANSSEOFFUCO6573 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010296 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Multi-Fault | 1249300 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0010389&numberofmonths=24&showchangehistorylog=1 | 17-0010389 | NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1101 | 43021101 | FUSE | 2627 | 20170118 | 1834 | 1648173 | 550 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 44000 | 38.0122 | -122.702 | ONFUCO5853 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010389 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1249405 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011176&numberofmonths=24&showchangehistorylog=1 | 17-0011176 | NORTH BAY | FIELD OPS NORTH | Tier 3 | BOLINAS-1101 | 42261101 | RECLOSER | 806 | 20170120 | 217 | 1652054 | 171 | Distribution Circuit | Environmental/External | Flood/Erosion | 345 | 58995 | 37.9559 | -122.6176 | NofRockyRidgeFirerd2spansEofLR806 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011176 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Multi-Fault | 1250089 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011252&numberofmonths=24&showchangehistorylog=1 | 17-0011252 | NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 5469 | 20170120 | 431 | 1652308 | 566 | Distribution Circuit | Vegetation | Tree - fell into line | 68 | 38488 | 38.0646 | -122.8251 | 4POLESLDSIDEOF5469 | Overcast-Heavy Rain-Lightning-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011252 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1250160 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011762&numberofmonths=24&showchangehistorylog=1 | 17-0011762 | NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1101 | 43021101 | FUSE | 1455 | 20170120 | 1828 | 1655055 | 2800 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 5600 | 38.0033 | -122.7081 | 3SPANSLDSIDE | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011762 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1250593 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012750&numberofmonths=24&showchangehistorylog=1 | 17-0012750 | NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 3585 | 20170122 | 310 | 1658395 | 545 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 14170 | 38.1033 | -122.8632 | SterlingWayVision | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012750 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1251572 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012834&numberofmonths=24&showchangehistorylog=1 | 17-0012834 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 1763 | 20170122 | 313 | 1658356 | 1068 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 8544 | 38.5931 | -122.4408 | HowellMtrdNofWhiteCottageRd | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0012834 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1251657 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018590&numberofmonths=24&showchangehistorylog=1 | 17-0018590 | NORTH BAY | FIELD OPS NORTH | Tier 2 | ALTO-1120 | 42031120 | FUSE | 941 | 20170207 | 1305 | 1680203 | 448 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1792 | 37.8696 | -122.5277 | 3SLOADSIDEOF941 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018590 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1256361 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018116&numberofmonths=24&showchangehistorylog=1 | 17-0018116 | NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1125 | 42031125 | FUSE | 2395 | 20170207 | 423 | 1677751 | 849 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 40814 | 37.8943 | -122.557 | SAMEPOLEASFUCO4879 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018116 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1255978 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018157&numberofmonths=24&showchangehistorylog=1 | 17-0018157 | NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1125 | 42031125 | FUSE | 3121 | 20170207 | 513 | 1677921 | 3687 | Distribution Circuit | Environmental/External | Flood/Erosion | 1840 | 294046 | 37.905 | -122.5579 | 150MONTEVISTAMILLVALLEY | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0018157 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1256020 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018453&numberofmonths=24&showchangehistorylog=1 | 17-0018453 | NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 3805 | 20170207 | 503 | 1677878 | 1232 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 23408 | 38.5485 | -122.578 | 5Eof1900DiamondMtnRd | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0018453 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1256267 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018290&numberofmonths=24&showchangehistorylog=1 | 17-0018290 | NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1102 | 42711102 | FUSE | 9195 | 20170207 | 501 | 1678224 | 4186 | Distribution Circuit | Vegetation | Tree - fell into line | 68 | 189914 | 38.5638 | -122.5594 | ZUNIGAJUAN1500DIAMONDMOUNTAINRDCALISTOGA | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018290 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Three Phase Fault | 1256130 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018180&numberofmonths=24&showchangehistorylog=1 | 17-0018180 | NORTH BAY | FIELD OPS NORTH | Tier 2 | SAN RAFAEL-1105 | 42011105 | FUSE | 5753 | 20170207 | 555 | 1678003 | 357 | Distribution Circuit | Vegetation | Tree - branch fell on line | 13 | 4641 | 37.98 | -122.4965 | 4SPANSLDSIDEOF5753 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018180 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1256043 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018209&numberofmonths=24&showchangehistorylog=1 | 17-0018209 | NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1101 | 43021101 | RECLOSER | 404 | 20170207 | 616 | 1678087 | 1189 | Distribution Circuit | Vegetation | Tree - fell into line | 831 | 300856 | 38.0131 | -122.6677 | LR123810spansSSofsamepoledown | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0018209 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Multi-Fault | 1256068 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018072&numberofmonths=24&showchangehistorylog=1 | 17-0018072 | NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1102 | 43021102 | FUSE | 1089 | 20170207 | 126 | 1677340 | 853 | Distribution Circuit | Vegetation | Tree - fell into line | 228 | 100460 | 38.0101 | -122.6401 | 14MAPLE | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018072 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1255927 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018092&numberofmonths=24&showchangehistorylog=1 | 17-0018092 | NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1102 | 43021102 | FUSE | 7103 | 20170207 | 322 | 1677630 | 803 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2409 | 38.0136 | -122.6425 | 4SPANSLDSIDEOFFUCO7103 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018092 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1255948 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0019421&numberofmonths=24&showchangehistorylog=1 | 17-0019421 | NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 1579 | 20170209 | 858 | 1682925 | 1169 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 14028 | 38.0924 | -122.8586 | 1SPANLDSIDEOF1579 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019421 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1256955 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0019470&numberofmonths=24&showchangehistorylog=1 | 17-0019470 | NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 3585 | 20170209 | 1337 | 1683477 | 1207 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 31382 | 38.1033 | -122.8632 | 3SPANSLDSIDEOF3585 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019470 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1256987 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0019512&numberofmonths=24&showchangehistorylog=1 | 17-0019512 | NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1101 | 43021101 | FUSE | 5827 | 20170209 | 1333 | 1683536 | 792 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 18216 | 38.0224 | -122.7012 | 7SPANSLDSIDEOFFUCO5827 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019512 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1257014 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0021922&numberofmonths=24&showchangehistorylog=1 | 17-0021922 | NORTH BAY | FIELD OPS NORTH | Tier 2 | ALTO-1120 | 42031120 | FUSE | 941 | 20170217 | 733 | 1691532 | 394 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1576 | 37.8696 | -122.5277 | 701TENNESSEEVALLEY | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0021922 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1259023 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0022009&numberofmonths=24&showchangehistorylog=1 | 17-0022009 | NORTH BAY | FIELD OPS NORTH | Tier 3 | MIDDLETOWN-1101 | 43141101 | FUSE | 473 | 20170217 | 908 | 1692915 | 2859 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 40026 | 38.6737 | -122.5872 | BOCKMIKE70769589971484loadsidef473 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022009 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1259108 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0022594&numberofmonths=24&showchangehistorylog=1 | 17-0022594 | NORTH BAY | FIELD OPS NORTH | Tier 2 | PUEBLO-1104 | 43291104 | RECLOSER | 1304 | 20170217 | 1114 | 1694844 | 3406 | Distribution Circuit | Equipment Failure/Involved | Overhead | 156 | 266906 | 38.3634 | -122.2651 | Griffith24832600Atlaspeakwiredown6sol | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022594 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1259617 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023166&numberofmonths=24&showchangehistorylog=1 | 17-0023166 | NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 3585 | 20170218 | 1351 | 1699976 | 673 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 17498 | 38.1033 | -122.8632 | 800VISIONRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023166 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1260170 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0022923&numberofmonths=24&showchangehistorylog=1 | 17-0022923 | NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1102 | 43021102 | FUSE | 7103 | 20170218 | 709 | 1699027 | 1354 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 4062 | 38.0136 | -122.6425 | 6NSof7103 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022923 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1259937 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024649&numberofmonths=24&showchangehistorylog=1 | 17-0024649 | NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1125 | 42031125 | FUSE | 6333 | 20170220 | 2200 | 1706294 | 1332 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 121656 | 37.9024 | -122.557 | 519TAMPALPAISDR | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024649 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1261615 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025059&numberofmonths=24&showchangehistorylog=1 | 17-0025059 | NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1102 | 42711102 | JUMPER | UNNUMBEREDFUCO | 20170220 | 2309 | 1707410 | 1086 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2172 | 38.5556 | -122.5754 | 1755DIAMONDMOUNTAINRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025059 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1261999 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023603&numberofmonths=24&showchangehistorylog=1 | 17-0023603 | NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | RECLOSER | 602 | 20170220 | 154 | 1702308 | 763 | Distribution Circuit | Vegetation | Tree - fell into line | 149 | 113687 | 38.1094 | -122.8698 | 7SPANSLDSIDEOFLR602 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023603 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1260598 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024023&numberofmonths=24&showchangehistorylog=1 | 17-0024023 | NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 5445 | 20170220 | 1610 | 1703959 | 1191 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 9528 | 38.0599 | -122.821 | 201SILVERHILLSRD | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024023 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1260992 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023993&numberofmonths=24&showchangehistorylog=1 | 17-0023993 | NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2103 | 43292103 | FUSE | 3583 | 20170220 | 1709 | 1704507 | 974 | Distribution Circuit | Vegetation | Tree - fell into line | 153 | 62117 | 38.3745 | -122.4204 | 2SPANSOFWIREDOWNBROKENPOLE2SPANSLDSIDEOFFUCO3583 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023993 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Multi-Fault | 1260962 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023987&numberofmonths=24&showchangehistorylog=1 | 17-0023987 | NORTH BAY | FIELD OPS NORTH | Tier 2 | SILVERADO-2102 | 43432102 | FUSE | 1601 | 20170220 | 1615 | 1704065 | 735 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 8550 | 38.5077 | -122.4067 | 2SPANSLDSIDEOFJUMPERSCORNEROFROSSIECONNVALLEYRD | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023987 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1260957 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024727&numberofmonths=24&showchangehistorylog=1 | 17-0024727 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 4019 | 20170220 | 2230 | 1706528 | 974 | Distribution Circuit | Equipment Failure/Involved | Overhead | 87 | 32258 | 38.5581 | -122.4566 | 285WHITECOTTAGERD | Overcast-Fog-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024727 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1261695 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024745&numberofmonths=24&showchangehistorylog=1 | 17-0024745 | NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1101 | 43021101 | FUSE | 4535 | 20170220 | 2115 | 1706127 | 850 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 6800 | 38.007 | -122.6989 | 4535 | Overcast-Fog-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024745 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1261713 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024264&numberofmonths=24&showchangehistorylog=1 | 17-0024264 | NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1102 | 43021102 | FUSE | 1089 | 20170220 | 2052 | 1706016 | 1052 | Distribution Circuit | Equipment Failure/Involved | Overhead | 228 | 77342 | 38.0101 | -122.6401 | 2SPANSLDSIDEOF2637 | Overcast-Fog-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024264 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1261229 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025139&numberofmonths=24&showchangehistorylog=1 | 17-0025139 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1107 | 42011107 | FUSE | 4475 | 20170221 | 732 | 1707705 | 448 | Distribution Circuit | Equipment Failure/Involved | Overhead | 49 | 21952 | 37.9607 | -122.5415 | 60UPPERTOYONDRSANRAFAEL | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025139 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1262058 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025168&numberofmonths=24&showchangehistorylog=1 | 17-0025168 | NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1101 | 43021101 | FUSE | 1455 | 20170221 | 1044 | 1708265 | 651 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1302 | 38.0033 | -122.7081 | 4SPANSLDSIDE | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025168 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1262079 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025873&numberofmonths=24&showchangehistorylog=1 | 17-0025873 | NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2103 | 43292103 | FUSE | 3583 | 20170222 | 2317 | 1711480 | 2468 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 128336 | 38.3745 | -122.4204 | 3132MTVEEDER | Clear-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025873 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1262670 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025669&numberofmonths=24&showchangehistorylog=1 | 17-0025669 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 3345 | 20170222 | 1406 | 1710827 | 572 | Distribution Circuit | Equipment Failure/Involved | Overhead | 50 | 18943 | 38.5515 | -122.4845 | 3SPANSLDSIDEOFSBCO7643 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025669 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1262482 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037454&numberofmonths=24&showchangehistorylog=1 | 17-0037454 | NORTH BAY | FIELD OPS NORTH | Tier 2 | BOLINAS-1101 | 42261101 | OTHER | WIREDOWN12SPANSLOADSIDEOF1232 | 20170406 | 1923 | 1746312 | 1682 | Distribution Circuit | Equipment Failure/Involved | Overhead | 477 | 799044 | 37.9241 | -122.7118 | 12SPANSLOADSIDEOF1232 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037454 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1271668 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037692&numberofmonths=24&showchangehistorylog=1 | 17-0037692 | NORTH BAY | FIELD OPS NORTH | Tier 2 | PUEBLO-1105 | 43291105 | OTHER | WIREONGRD1POLELDSIDEOF1767 | 20170406 | 1940 | 1750156 | 1345 | Distribution Circuit | Equipment Failure/Involved | Overhead | 211 | 219306 | 38.3832 | -122.2924 | 1POLELDSIDEOF1767 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037692 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1271896 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037052&numberofmonths=24&showchangehistorylog=1 | 17-0037052 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1108 | 42011108 | RECLOSER | 1210 | 20170406 | 1058 | 1745410 | 844 | Distribution Circuit | Vegetation | Tree - fell into line | 544 | 166949 | 37.9627 | -122.569 | 54SHADYLANE | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037052 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1271345 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037447&numberofmonths=24&showchangehistorylog=1 | 17-0037447 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 479 | 20170406 | 2229 | 1748349 | 1361 | Distribution Circuit | Equipment Failure/Involved | Overhead | 266 | 50506 | 38.576 | -122.4446 | 1POLELDSIDEOFFUCO5113 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037447 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1271661 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037995&numberofmonths=24&showchangehistorylog=1 | 17-0037995 | NORTH BAY | FIELD OPS NORTH | Tier 2 | MONTICELLO-1101 | 43051101 | OTHER | WIREDOWNSSOF9769 | 20170407 | 723 | 1751153 | 3107 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 8804 | 38.3575 | -122.1781 | 1700WOODENVALLEYRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037995 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1272080 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0038061&numberofmonths=24&showchangehistorylog=1 | 17-0038061 | NORTH BAY | FIELD OPS NORTH | Tier 2 | MONTICELLO-1101 | 43051101 | FUSE | 3453 | 20170407 | 1754 | 1751460 | 2762 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 24858 | 38.6529 | -122.2426 | EOL | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0038061 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1272129 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037800&numberofmonths=24&showchangehistorylog=1 | 17-0037800 | NORTH BAY | FIELD OPS NORTH | Tier 2 | SAN RAFAEL-1107 | 42011107 | FUSE | 5993 | 20170407 | 1036 | 1750502 | 665 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 26600 | 37.948 | -122.5493 | 2SPANSLOADSIDE | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0037800 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Line | 1271972 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037727&numberofmonths=24&showchangehistorylog=1 | 17-0037727 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 1385 | 20170407 | 207 | 1749185 | 1963 | Distribution Circuit | Vegetation | Tree - fell into line | 152 | 111644 | 38.5796 | -122.4489 | BAYMANZANITA | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037727 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1271922 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0038178&numberofmonths=24&showchangehistorylog=1 | 17-0038178 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 479 | 20170407 | 2334 | 1752201 | 1053 | Distribution Circuit | Equipment Failure/Involved | Overhead | 266 | 57355 | 38.576 | -122.4446 | 1SPANSLDSIDEOF479 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0038178 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Line | 1272237 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0077470&numberofmonths=24&showchangehistorylog=1 | 17-0077470 | NORTH BAY | FIELD OPS NORTH | Tier 2 | GREENBRAE-1103 | 43091103 | FUSE | 4997 | 20170911 | 420 | 1874799 | 548 | Distribution Circuit | Vegetation | Tree - branch fell on line | 80 | 13896 | 37.9342 | -122.538 | 16HAZELAVE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0077470 | OH | Sus | 31350105 | yes | 2017 | SEP | Yes | Line to Line | 1301367 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0085175&numberofmonths=24&showchangehistorylog=1 | 17-0085175 | NORTH BAY | FIELD OPS NORTH | Tier 2 | CALISTOGA-1101 | 42711101 | FUSE | 8339 | 20171008 | 1841 | 1893704 | 20024 | Distribution Circuit | Equipment Failure/Involved | Overhead | 62 | 1241488 | 38.6327 | -122.6744 | 15SPANSFROMFUCO8339 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085175 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1306622 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0085239&numberofmonths=24&showchangehistorylog=1 | 17-0085239 | NORTH BAY | FIELD OPS NORTH | Tier 2 | CALISTOGA-1101 | 42711101 | RECLOSER | 890 | 20171008 | 2202 | 1893951 | 19823 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 149 | 1855187 | 38.6158 | -122.6585 | Johnson1055MULTIPLE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085239 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1306685 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0086476&numberofmonths=24&showchangehistorylog=1 | 17-0086476 | NORTH BAY | FIELD OPS NORTH | Tier 2 | CALISTOGA-1101 | 42711101 | JUMPER | 1EOF773 | 20171008 | 2120 | 1898920 | 24194 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 3 | 66878 | 38.5995 | -122.6193 | 1EOF773 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0086476 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1307586 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0088360&numberofmonths=24&showchangehistorylog=1 | 17-0088360 | NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | SWITCH | 4879 | 20171008 | 2202 | 1903474 | 21238 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 2 | 42476 | 38.6411 | -122.647 | LOADSIDEOF4879 | Clear-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0088360 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1309067 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0088407&numberofmonths=24&showchangehistorylog=1 | 17-0088407 | NORTH BAY | FIELD OPS NORTH | Tier 2 | CALISTOGA-1101 | 42711101 | FUSE | 1843 | 20171008 | 2202 | 1903598 | 19950 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 39900 | 38.6295 | -122.6683 | 2SPANSLDSIDEOFMETER1010029011 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0088407 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1309083 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0089778&numberofmonths=24&showchangehistorylog=1 | 17-0089778 | NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 1463 | 20171008 | 2324 | 1908131 | 21147 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 3 | 63441 | 38.6061 | -122.6523 | 1463LOADSIDE | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0089778 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1310170 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0087501&numberofmonths=24&showchangehistorylog=1 | 17-0087501 | NORTH BAY | FIELD OPS NORTH | Tier 2 | PUEBLO-1104 | 43291104 | SWITCH | 9595 | 20171008 | 2259 | 1901273 | 19761 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 513786 | 38.4295 | -122.2479 | 4084ATLASPEAKRDNAPA | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0087501 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1308480 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0086893&numberofmonths=24&showchangehistorylog=1 | 17-0086893 | NORTH BAY | FIELD OPS NORTH | Tier 2 | PUEBLO-1105 | 43291105 | FUSE | 7565 | 20171008 | 2220 | 1899635 | 17025 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 34050 | 38.4071 | -122.2938 | 1sof7565 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0086893 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1307916 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0086273&numberofmonths=24&showchangehistorylog=1 | 17-0086273 | NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2103 | 43292103 | FUSE | 1143 | 20171008 | 2225 | 1894077 | 21285 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 617265 | 38.3454 | -122.3991 | 4715REDWOODDR | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0086273 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1307432 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0085216&numberofmonths=24&showchangehistorylog=1 | 17-0085216 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | RECLOSER | 722 | 20171008 | 2149 | 1893975 | 2774 | Distribution Circuit | Vegetation | Tree - branch fell on line | 526 | 1416648 | 38.5448 | -122.4757 | BOCKMIKE70769589971484325werstln | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085216 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1306662 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0085393&numberofmonths=24&showchangehistorylog=1 | 17-0085393 | NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1102 | 42711102 | FUSE | 589 | 20171009 | 11 | 1895660 | 5298 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 84768 | 38.5773 | -122.5194 | 1LDSIDEOF589 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085393 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Line | 1306846 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0087310&numberofmonths=24&showchangehistorylog=1 | 17-0087310 | NORTH BAY | FIELD OPS NORTH | Tier 2 | MONTICELLO-1101 | 43051101 | RECLOSER | 93384 | 20171009 | 138 | 1900638 | 10906 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 535 | 5266351 | 38.4789 | -122.1867 | NorthBayFires | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0087310 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Three Phase Fault | 1308303 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0087984&numberofmonths=24&showchangehistorylog=1 | 17-0087984 | NORTH BAY | FIELD OPS NORTH | Tier 2 | PUEBLO-1105 | 43291105 | FUSE | 567 | 20171009 | 154 | 1902561 | 16497 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 41 | 676377 | 38.3528 | -122.2241 | 2830MONTICELLORD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0087984 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1308840 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0087429&numberofmonths=24&showchangehistorylog=1 | 17-0087429 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2105 | 43432105 | JUMPER | OJ3SPANSWOF9319 | 20171014 | 2018 | 1901035 | 972 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 2916 | 38.5442 | -122.4927 | 3451SILVERADOTRAIL | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0087429 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1308416 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0099600&numberofmonths=24&showchangehistorylog=1 | 17-0099600 | NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 5073 | 20171204 | 921 | 1934647 | 620 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2480 | 38.6034 | -122.6389 | RUPPDONOVAN3835HWY128 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0099600 | OH | Sus | 0 | yes | 2017 | DEC | Yes | Three Phase Fault | 1317402 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0099617&numberofmonths=24&showchangehistorylog=1 | 17-0099617 | NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 731 | 20171204 | 911 | 1934633 | 454 | Distribution Circuit | Equipment Failure/Involved | Overhead | 46 | 20884 | 38.5774 | -122.587 | 440KORTUMCANYONRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0099617 | OH | Sus | 0 | yes | 2017 | DEC | Yes | Line to Line | 1317411 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0099624&numberofmonths=24&showchangehistorylog=1 | 17-0099624 | NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 767 | 20171204 | 1121 | 1934978 | 834 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 3336 | 38.6365 | -122.6816 | 2SPANSLDSIDEOF767 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0099624 | OH | Sus | 0 | yes | 2017 | DEC | Yes | Line to Ground | 1317415 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0099647&numberofmonths=24&showchangehistorylog=1 | 17-0099647 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 415 | 20171204 | 813 | 1934532 | 954 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 11448 | 38.5568 | -122.4932 | N1MFEC6JUSTBEFOREADDRESS282 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0099647 | OH | Sus | 0 | yes | 2017 | DEC | Yes | Line to Line | 1317425 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0099800&numberofmonths=24&showchangehistorylog=1 | 17-0099800 | NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1102 | 43021102 | FUSE | 7103 | 20171204 | 1736 | 1935873 | 319 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 957 | 38.0136 | -122.6425 | 7SPANSLDSIDE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0099800 | OH | Sus | 0 | yes | 2017 | DEC | Yes | Line to Ground | 1317543 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0101966&numberofmonths=24&showchangehistorylog=1 | 17-0101966 | NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1124 | 42031124 | FUSE | 915 | 20171216 | 908 | 1944195 | 394 | Distribution Circuit | Vegetation | Tree - branch fell on line | 55 | 21670 | 37.9041 | -122.5692 | 100AdamsAve | Partly Cloudy-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0101966 | OH | Sus | 0 | yes | 2017 | DEC | Yes | Line to Ground | 1319878 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0101995&numberofmonths=24&showchangehistorylog=1 | 17-0101995 | NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1124 | 42031124 | FUSE | 6953 | 20171216 | 939 | 1944273 | 477 | Distribution Circuit | Vegetation | Tree - fell into line | 1792 | 21402 | 37.91 | -122.5521 | mtr1009647342 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0101995 | OH | Sus | 0 | yes | 2017 | DEC | Yes | Line to Line | 1319905 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0101947&numberofmonths=24&showchangehistorylog=1 | 17-0101947 | NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2103 | 43292103 | FUSE | 6075 | 20171216 | 845 | 1944152 | 285 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 1425 | 38.3603 | -122.3695 | 4spansLDsideofFUCO6075 | Strong Winds-Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0101947 | OH | Sus | 0 | yes | 2017 | DEC | Yes | Line to Ground | 1319859 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0102074&numberofmonths=24&showchangehistorylog=1 | 17-0102074 | NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2103 | 43292103 | FUSE | 1143 | 20171216 | 924 | 1944474 | 1112 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 23408 | 38.3454 | -122.3991 | MTR1006744745 | Clear-32-90 F | Conductor, Overhead | On Ground | 17-0102074 | OH | Sus | 0 | yes | 2017 | DEC | Yes | Line to Ground | 1319985 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0102014&numberofmonths=24&showchangehistorylog=1 | 17-0102014 | NORTH BAY | FIELD OPS NORTH | Tier 2 | SAUSALITO-1102 | 42491102 | FUSE | 3033 | 20171216 | 1033 | 1944459 | 481 | Distribution Circuit | Vegetation | Tree - branch fell on line | 26 | 3896 | 37.8706 | -122.5139 | 55WALDOCT | Clear-Strong Winds-32-90 F | Conductor, Overhead | On Ground | 17-0102014 | OH | Sus | 0 | yes | 2017 | DEC | Yes | Line to Line | 1319924 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0023225&numberofmonths=24&showchangehistorylog=1 | 18-0023225 | NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1124 | 42031124 | FUSE | 2201 | 20180316 | 108 | 45156 | 620 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 19220 | 37.9163 | -122.5562 | 4spansLDsideofFUCO2201 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023225 | OH | Sus | 43301932 | yes | 2018 | MAR | Yes | Line to Line | 1336130 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0098264&numberofmonths=24&showchangehistorylog=1 | 18-0098264 | NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | JUMPER | OJS4SPANSNO3654 | 20181108 | 1220 | 211569 | 265 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 265 | 38.592 | -122.6221 | 2NOOFCGC3654 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0098264 | OH | Sus | 0 | yes | 2018 | NOV | Yes | None | 1391457 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0104940&numberofmonths=24&showchangehistorylog=1 | 18-0104940 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2103 | 43432103 | FUSE | 3721 | 20181129 | 945 | 228416 | 5925 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 22241 | 38.4639 | -122.4624 | BOCKMIKE70769589971484156 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0104940 | OH | Sus | 0 | yes | 2018 | NOV | Yes | Line to Ground | 1396213 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0104908&numberofmonths=24&showchangehistorylog=1 | 18-0104908 | NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1102 | 43021102 | FUSE | 7449 | 20181129 | 727 | 227916 | 554 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 23822 | 38.0076 | -122.6447 | 1Nof7449 | Overcast-Heavy Rain-Lightning-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0104908 | OH | Sus | 0 | yes | 2018 | NOV | Yes | Line to Line | 1396193 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005045&numberofmonths=24&showchangehistorylog=1 | 19-0005045 | NORTH BAY | FIELD OPS NORTH | Tier 2 | ALTO-1125 | 42031125 | FUSE | 5191 | 20190106 | 922 | 255021 | 280 | Distribution Circuit | Vegetation | Tree - fell into line | 120 | 33600 | 37.8827 | -122.5459 | 1SPANLDSIDEOF5191FUCO | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005045 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1403518 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005083&numberofmonths=24&showchangehistorylog=1 | 19-0005083 | NORTH BAY | FIELD OPS NORTH | Tier 2 | GREENBRAE-1103 | 43091103 | OTHER | WIREDOWN1EDENLANESTAIRS | 20190106 | 1227 | 255244 | 983 | Distribution Circuit | Vegetation | Tree - fell into line | 406 | 303746 | 37.9347 | -122.5391 | 1EDENLANESTAIRSATCORNEROFHAZEL | Overcast-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0005083 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1403555 | PW | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0009817&numberofmonths=24&showchangehistorylog=1 | 19-0009817 | NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1124 | 42031124 | FUSE | 3141 | 20190116 | 1445 | 267248 | 221 | Distribution Circuit | Vegetation | Tree - branch fell on line | 45 | 9945 | 37.916 | -122.5388 | ANDREWSKYLEIFO35GLENDR | Strong Winds-Heavy Rain-Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009817 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1406709 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0009996&numberofmonths=24&showchangehistorylog=1 | 19-0009996 | NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1125 | 42031125 | FUSE | 2167 | 20190116 | 1714 | 268460 | 1718 | Distribution Circuit | Equipment Failure/Involved | Overhead | 68 | 86010 | 37.9009 | -122.5499 | 86MOLINO | Strong Winds-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009996 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1406862 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010130&numberofmonths=24&showchangehistorylog=1 | 19-0010130 | NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1125 | 42031125 | FUSE | 2227 | 20190116 | 1617 | 267772 | 4060 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 48720 | 37.8959 | -122.6009 | ANDREWSKYLEMOUNTTAMSTATEPARK | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010130 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1406999 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0009830&numberofmonths=24&showchangehistorylog=1 | 19-0009830 | NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1102 | 42711102 | RECLOSER | 634 | 20190116 | 1542 | 267581 | 644 | Distribution Circuit | Vegetation | Tree - fell into line | 597 | 88673 | 38.5859 | -122.5715 | 480449 | Strong Winds-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009830 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1406719 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010784&numberofmonths=24&showchangehistorylog=1 | 19-0010784 | NORTH BAY | FIELD OPS NORTH | Tier 3 | GREENBRAE-1102 | 43091102 | FUSE | 5301 | 20190116 | 2031 | 270515 | 1272 | Distribution Circuit | Vegetation | Tree - branch fell on line | 104 | 132288 | 37.9503 | -122.5243 | ANDREWSKYLERO90CORTELOYOLA | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010784 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407537 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010528&numberofmonths=24&showchangehistorylog=1 | 19-0010528 | NORTH BAY | FIELD OPS NORTH | Tier 2 | MONTICELLO-1101 | 43051101 | RECLOSER | 630 | 20190116 | 1906 | 272351 | 2859 | Distribution Circuit | Equipment Failure/Involved | Overhead | 141 | 403119 | 38.5733 | -122.2442 | 1SPANWO7641 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010528 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1407390 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010417&numberofmonths=24&showchangehistorylog=1 | 19-0010417 | NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 1881 | 20190116 | 2144 | 271248 | 2315 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 25465 | 38.0971 | -122.8619 | 1SPANLDSIDE1881 | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010417 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407282 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010778&numberofmonths=24&showchangehistorylog=1 | 19-0010778 | NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2103 | 43292103 | FUSE | 1117 | 20190116 | 1954 | 270323 | 1351 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 26179 | 38.3727 | -122.417 | GRIFFITHFRANK24831198LAKOYATREEWIREDOWN | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010778 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407531 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010037&numberofmonths=24&showchangehistorylog=1 | 19-0010037 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1107 | 42011107 | FUSE | 2565 | 20190116 | 1633 | 267952 | 1918 | Distribution Circuit | Equipment Failure/Involved | Overhead | 158 | 228868 | 37.9594 | -122.5348 | 111HILLDR | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010037 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1406901 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010556&numberofmonths=24&showchangehistorylog=1 | 19-0010556 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1107 | 42011107 | FUSE | 2753 | 20190116 | 2020 | 272420 | 1442 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 37492 | 37.9536 | -122.5639 | 3SPANSLDSIDEOF2753 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010556 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407418 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0009999&numberofmonths=24&showchangehistorylog=1 | 19-0009999 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1108 | 42011108 | FUSE | 6647 | 20190116 | 1735 | 268629 | 249 | Distribution Circuit | Vegetation | Tree - branch fell on line | 124 | 30876 | 37.9792 | -122.5714 | PedersonRyley70749413969OliveAveSanAnselmo | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009999 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1406864 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010346&numberofmonths=24&showchangehistorylog=1 | 19-0010346 | NORTH BAY | FIELD OPS NORTH | Tier 2 | SAN RAFAEL-1109 | 42011109 | FUSE | 5397 | 20190116 | 2027 | 270621 | 959 | Distribution Circuit | Equipment Failure/Involved | Overhead | 28 | 26852 | 37.9781 | -122.5077 | 40BRODEAWAY | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010346 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407211 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010312&numberofmonths=24&showchangehistorylog=1 | 19-0010312 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 141 | 20190116 | 2017 | 270487 | 2533 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 15198 | 38.5785 | -122.4424 | BOCKMIKE70769589971484400howellmntssd141 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010312 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1407177 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010046&numberofmonths=24&showchangehistorylog=1 | 19-0010046 | NORTH BAY | FIELD OPS NORTH | Tier 2 | STAFFORD-1102 | 43201102 | FUSE | 949 | 20190116 | 1754 | 269292 | 1636 | Distribution Circuit | Vegetation | Tree - branch fell on line | 72 | 117792 | 38.102 | -122.6169 | 137WILDHORSEVALLEY | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010046 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Three Phase Fault | 1406910 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0009786&numberofmonths=24&showchangehistorylog=1 | 19-0009786 | NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1101 | 43021101 | FUSE | 5605 | 20190116 | 1418 | 267131 | 1824 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 9120 | 38.0494 | -122.6783 | 1SPANLDSIDEOF5605 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009786 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1406686 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0009821&numberofmonths=24&showchangehistorylog=1 | 19-0009821 | NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1102 | 43021102 | FUSE | 2657 | 20190116 | 1540 | 267467 | 440 | Distribution Circuit | Equipment Failure/Involved | Overhead | 33 | 3488 | 37.9918 | -122.5948 | IRONSPRINGSANDROCKRIDGERD | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009821 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1406714 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0009840&numberofmonths=24&showchangehistorylog=1 | 19-0009840 | NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1102 | 43021102 | FUSE | 3603 | 20190116 | 1525 | 267552 | 503 | Distribution Circuit | Vegetation | Tree - branch fell on line | 48 | 24144 | 38.0103 | -122.6399 | 3SPANSLDSIDEOF3603 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009840 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1406727 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0009925&numberofmonths=24&showchangehistorylog=1 | 19-0009925 | NORTH BAY | FIELD OPS NORTH | Tier 2 | WOODACRE-1102 | 43021102 | JUMPER | OJFEEDINGFUCO1421 | 20190116 | 1523 | 267446 | 550 | Distribution Circuit | Equipment Failure/Involved | Overhead | 511 | 54460 | 37.9981 | -122.594 | PedersonRyley7074941396SpanfeedingFUCO1421 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009925 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Force Out | 1406796 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010122&numberofmonths=24&showchangehistorylog=1 | 19-0010122 | NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1102 | 43021102 | RECLOSER | 137662 | 20190116 | 1930 | 269720 | 1098 | Distribution Circuit | Vegetation | Tree - fell into line | 1046 | 571468 | 37.9959 | -122.5972 | 1PWO5035 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010122 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1406992 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010751&numberofmonths=24&showchangehistorylog=1 | 19-0010751 | NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1102 | 43021102 | FUSE | 2635 | 20190116 | 2046 | 270625 | 1329 | Distribution Circuit | Vegetation | Tree - bark fell into line | 36 | 47844 | 38.0117 | -122.6441 | 55parkrd | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010751 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407521 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011067&numberofmonths=24&showchangehistorylog=1 | 19-0011067 | NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 3391 | 20190117 | 524 | 272547 | 3171 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 19026 | 38.5592 | -122.6291 | DYDOGREG41558904254500PETRIFIEDFORESTRDCROSSING | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011067 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407701 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010496&numberofmonths=24&showchangehistorylog=1 | 19-0010496 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1108 | 42011108 | OTHER | WIREDOWN17OAKKNOLLAVE | 20190117 | 135 | 272275 | 1645 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1222 | 60277 | 37.9838 | -122.5773 | 17OAKKNOLLAVE | Partly Cloudy-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010496 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407360 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011021&numberofmonths=24&showchangehistorylog=1 | 19-0011021 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1108 | 42011108 | JUMPER | WIREDOWN3NOFFUCO2197 | 20190117 | 422 | 273917 | 1868 | Distribution Circuit | Vegetation | Tree - branch fell on line | 546 | 40233 | 37.964 | -122.572 | 3SPANSNORTHOFFUCO2197 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011021 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Force Out | 1407683 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011488&numberofmonths=24&showchangehistorylog=1 | 19-0011488 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1108 | 42011108 | JUMPER | OJMEDWAYANDSANANSELMO | 20190117 | 2333 | 275084 | 329 | Distribution Circuit | Vegetation | Tree - branch fell on line | 27 | 8883 | 37.9842 | -122.5764 | ANDREWSKYLE25OAKKNOLLAVE | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011488 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1408030 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011023&numberofmonths=24&showchangehistorylog=1 | 19-0011023 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2102 | 43432102 | SWITCH | 42999 | 20190117 | 149 | 274009 | 973 | Distribution Circuit | Equipment Failure/Involved | Overhead | 41 | 39893 | 38.4786 | -122.3347 | 2Sof42999 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011023 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407685 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011167&numberofmonths=24&showchangehistorylog=1 | 19-0011167 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2103 | 43432103 | FUSE | 3721 | 20190117 | 651 | 272718 | 1329 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 18606 | 38.4639 | -122.4624 | 1975WHITEHALLLN | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011167 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1407772 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010906&numberofmonths=24&showchangehistorylog=1 | 19-0010906 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2105 | 43432105 | JUMPER | OJ3SWOF5937 | 20190117 | 1035 | 273624 | 2950 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 5900 | 38.5 | -122.4889 | 3SWOF5937 | Overcast-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010906 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407601 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022711&numberofmonths=24&showchangehistorylog=1 | 19-0022711 | NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1125 | 42031125 | FUSE | 2167 | 20190213 | 2116 | 305746 | 1244 | Distribution Circuit | Vegetation | Tree - fell into line | 68 | 18165 | 37.9009 | -122.5499 | 3SPANSLDSIDEUNNUMBEREDSBCONO6161 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022711 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1415945 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022172&numberofmonths=24&showchangehistorylog=1 | 19-0022172 | NORTH BAY | FIELD OPS NORTH | Tier 3 | BOLINAS-1101 | 42261101 | OTHER | WIREDOWN5SOF1803 | 20190213 | 1052 | 303957 | 3231 | Distribution Circuit | Vegetation | Tree - fell into line | 831 | 2532753 | 37.9013 | -122.6336 | KNIFFINANDREW70754845834SPANSLOADSIDEOFSW1803 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022172 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1415519 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022565&numberofmonths=24&showchangehistorylog=1 | 19-0022565 | NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 757 | 20190213 | 1924 | 305582 | 1032 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 36120 | 38.073 | -122.8278 | INFRONTOF127LAURELST | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022565 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1415802 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023559&numberofmonths=24&showchangehistorylog=1 | 19-0023559 | NORTH BAY | FIELD OPS NORTH | Tier 2 | ALTO-1120 | 42031120 | FUSE | 941 | 20190214 | 1719 | 310362 | 1544 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 6176 | 37.8696 | -122.5277 | HLEBAKOSFRANK41530662974spansfromCO941 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023559 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1416704 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023243&numberofmonths=24&showchangehistorylog=1 | 19-0023243 | NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1125 | 42031125 | FUSE | 701 | 20190214 | 322 | 307396 | 831 | Distribution Circuit | Vegetation | Tree - fell into line | 171 | 119045 | 37.8827 | -122.5769 | 4SPANSLDSIDEOF4789 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023243 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1416434 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022934&numberofmonths=24&showchangehistorylog=1 | 19-0022934 | NORTH BAY | FIELD OPS NORTH | Tier 2 | BOLINAS-1101 | 42261101 | OCB | 11012 | 20190214 | 822 | 307670 | 3227 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1160 | 122660 | 37.9407 | -122.7071 | 4SPANSSOURCESIDEOFLR12367SPANSLDSIDESW807 | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022934 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1416163 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023654&numberofmonths=24&showchangehistorylog=1 | 19-0023654 | NORTH BAY | FIELD OPS NORTH | Tier 3 | BOLINAS-1101 | 42261101 | OTHER | WIREDOWN78BOSQUEAVE | 20190214 | 948 | s1422019 | 4632 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 23160 | 37.9728 | -122.6145 | TURMELJOEL78Bosqueave | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0023654 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1422019 | PW | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023821&numberofmonths=24&showchangehistorylog=1 | 19-0023821 | NORTH BAY | FIELD OPS NORTH | Tier 3 | GREENBRAE-1102 | 43091102 | FUSE | 6371 | 20190214 | 1859 | 310675 | 2801 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 33612 | 37.9491 | -122.5241 | 1EofFUCO6371 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023821 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416965 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022798&numberofmonths=24&showchangehistorylog=1 | 19-0022798 | NORTH BAY | FIELD OPS NORTH | Tier 3 | LAS GALLINAS A-1105 | 42991105 | RECLOSER | 99904 | 20190214 | 401 | 306699 | 3782 | Distribution Circuit | Vegetation | Tree - fell into line | 78 | 224052 | 38.0443 | -122.6155 | GREENEJOSEPH50ElMiradorDr | Overcast-Fog-Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0022798 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416041 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022832&numberofmonths=24&showchangehistorylog=1 | 19-0022832 | NORTH BAY | FIELD OPS NORTH | Tier 2 | MONTICELLO-1101 | 43051101 | RECLOSER | 654 | 20190214 | 500 | 306973 | 3643 | Distribution Circuit | Vegetation | Tree - fell into line | 220 | 717520 | 38.5116 | -122.2134 | 1750knoxvilleberryessard8SPANSNOF654 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022832 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1416079 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023067&numberofmonths=24&showchangehistorylog=1 | 19-0023067 | NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 3513 | 20190214 | 250 | 308096 | 2386 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 57264 | 38.0752 | -122.8411 | 3SPANSLDSIDEOF3513 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023067 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416271 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023235&numberofmonths=24&showchangehistorylog=1 | 19-0023235 | NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 1579 | 20190214 | 804 | 307586 | 3266 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 39192 | 38.0924 | -122.8586 | 1SPANLDSIDEOF1579 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023235 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416428 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022842&numberofmonths=24&showchangehistorylog=1 | 19-0022842 | NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2103 | 43292103 | FUSE | 1117 | 20190214 | 358 | 306689 | 1012 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 21565 | 38.3727 | -122.417 | MTR1007363293 | Overcast-Fog-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022842 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416087 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023130&numberofmonths=24&showchangehistorylog=1 | 19-0023130 | NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2103 | 43292103 | FUSE | 5543 | 20190214 | 456 | 306898 | 2240 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 20160 | 38.3521 | -122.3613 | MTR1007039741 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023130 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416322 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023178&numberofmonths=24&showchangehistorylog=1 | 19-0023178 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1107 | 42011107 | FUSE | 4497 | 20190214 | 1205 | 308867 | 728 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 18928 | 37.9654 | -122.5514 | 12CANYONRD | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023178 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416369 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023276&numberofmonths=24&showchangehistorylog=1 | 19-0023276 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | RECLOSER | 632 | 20190214 | 1042 | 308405 | 1359 | Distribution Circuit | Vegetation | Tree - fell into line | 752 | 618261 | 38.574 | -122.4444 | BOCKMIKE70769589971484howellmntrd | Overcast-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023276 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1416466 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023143&numberofmonths=24&showchangehistorylog=1 | 19-0023143 | NORTH BAY | FIELD OPS NORTH | Tier 2 | WOODACRE-1102 | 43021102 | RECLOSER | 1280 | 20190214 | 156 | 306278 | 3606 | Distribution Circuit | Equipment Failure/Involved | Overhead | 729 | 525588 | 37.9962 | -122.5956 | 1500BUTTERFEILDRD | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023143 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1416336 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023501&numberofmonths=24&showchangehistorylog=1 | 19-0023501 | NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1102 | 43021102 | FUSE | 1089 | 20190214 | 233 | 306422 | 2444 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3064 | 402449 | 38.0101 | -122.6401 | TURMELJOELFuses2931 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023501 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416649 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024717&numberofmonths=24&showchangehistorylog=1 | 19-0024717 | NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1124 | 42031124 | TRIP-SAVER | 3121 | 20190216 | 1743 | 314867 | 1285 | Distribution Circuit | Vegetation | Tree - fell into line | 195 | 54393 | 37.905 | -122.5579 | ROSEAVEXStHAZELAVE | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024717 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1417792 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028584&numberofmonths=24&showchangehistorylog=1 | 19-0028584 | NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 3393 | 20190226 | 2041 | 325274 | 3310 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 49650 | 38.1297 | -122.899 | 490PIERCEPOINTRD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0028584 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1420489 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028590&numberofmonths=24&showchangehistorylog=1 | 19-0028590 | NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 53821 | 20190226 | 2107 | 325299 | 253 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 1771 | 38.0898 | -122.844 | 12740SFDRAKEBLVDNORTHDREAMFARM | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028590 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1420496 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028660&numberofmonths=24&showchangehistorylog=1 | 19-0028660 | NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 757 | 20190226 | 2338 | 325753 | 876 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 30660 | 38.073 | -122.8278 | IFO133LAURELST | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028660 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1420566 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028662&numberofmonths=24&showchangehistorylog=1 | 19-0028662 | NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 5683 | 20190226 | 2210 | 325428 | 1211 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 6055 | 38.0593 | -122.8163 | BEARVLYRD480NOFPXLANEOLEMA | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028662 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1420569 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028528&numberofmonths=24&showchangehistorylog=1 | 19-0028528 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1108 | 42011108 | FUSE | 5343 | 20190226 | 1607 | 324846 | 1542 | Distribution Circuit | Vegetation | Tree - branch fell on line | 37 | 21171 | 37.9759 | -122.5771 | 405REDWOOD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028528 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1420435 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028156&numberofmonths=24&showchangehistorylog=1 | 19-0028156 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | RECLOSER | 806 | 20190226 | 900 | 324120 | 370 | Distribution Circuit | Equipment Failure/Involved | Overhead | 415 | 65005 | 38.6169 | -122.4244 | WIREDOWNATMETER1007487652 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028156 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1420235 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028529&numberofmonths=24&showchangehistorylog=1 | 19-0028529 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | RECLOSER | 726 | 20190226 | 1914 | 325146 | 1225 | Distribution Circuit | Vegetation | Tree - fell into line | 351 | 417965 | 38.6151 | -122.4295 | 6613POPEVALLEY | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028529 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1420436 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028517&numberofmonths=24&showchangehistorylog=1 | 19-0028517 | NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1101 | 43021101 | FUSE | 2631 | 20190226 | 1746 | 324998 | 1424 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 7120 | 38.0057 | -122.7076 | 1spanLDsideofFUCO2631 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028517 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1420425 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028561&numberofmonths=24&showchangehistorylog=1 | 19-0028561 | NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1101 | 43021101 | FUSE | 2617 | 20190226 | 1931 | 325159 | 1344 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 6720 | 38.0302 | -122.6689 | 2SLDSIDEOF2617 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028561 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1420465 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028591&numberofmonths=24&showchangehistorylog=1 | 19-0028591 | NORTH BAY | FIELD OPS NORTH | Tier 2 | WOODACRE-1101 | 43021101 | RECLOSER | 96844 | 20190226 | 2203 | 325405 | 694 | Distribution Circuit | Equipment Failure/Involved | Overhead | 274 | 82726 | 38.0192 | -122.6631 | NA | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028591 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1420497 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028691&numberofmonths=24&showchangehistorylog=1 | 19-0028691 | NORTH BAY | FIELD OPS NORTH | Tier 2 | IGNACIO-1105 | 42481105 | FUSE | 6221 | 20190227 | 206 | 326120 | 956 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 42888 | 38.0927 | -122.5771 | IndianValleyrd2NofPachecoAve | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028691 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1420602 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0065525&numberofmonths=24&showchangehistorylog=1 | 19-0065525 | NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 5467 | 20190610 | 1912 | 404560 | 1503 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3006 | 38.1091 | -122.8956 | 3POLESLDSIDEOF5467 | Partly Cloudy-Heat Wave-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0065525 | OH | Sus | 0 | yes | 2019 | JUN | Yes | Line to Line | 1447681 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0102537&numberofmonths=24&showchangehistorylog=1 | 19-0102537 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 1189 | 20190923 | 1259 | 606674 | 257 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 771 | 38.5495 | -122.4721 | 1EOF1189FUCO | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0102537 | OH | Sus | 43964150 | yes | 2019 | SEP | Yes | None | 1472137 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0129529&numberofmonths=24&showchangehistorylog=1 | 19-0129529 | NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1125 | 42031125 | OTHER | WIREDOWN2SPANSLDSIDEOF947917 | 20191126 | 1802 | 716982 | 301 | Distribution Circuit | Equipment Failure/Involved | Overhead | 391 | 33779 | 37.9053 | -122.5712 | 2SPANSLDSIDEOF947917 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0129529 | OH | Sus | 0 | yes | 2019 | NOV | Yes | Line to Ground | 1494529 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0010955&numberofmonths=24&showchangehistorylog=1 | 20-0010955 | NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2103 | 43292103 | FUSE | 2117 | 20200117 | 1622 | 765121 | 405 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 405 | 38.3618 | -122.405 | LDSIDEOF2117 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0010955 | OH | Sus | 44159086 | yes | 2020 | JAN | Yes | Force Out | 1507431 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0019092&numberofmonths=24&showchangehistorylog=1 | 20-0019092 | NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1122 | 42031122 | FUSE | 3897 | 20200209 | 947 | 781825 | 382 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 34442 | 37.9246 | -122.5349 | MTR1007934117 | Clear-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 20-0019092 | OH | Sus | 0 | yes | 2020 | FEB | Yes | Line to Ground | 1513111 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0019668&numberofmonths=24&showchangehistorylog=1 | 20-0019668 | NORTH BAY | FIELD OPS NORTH | Tier 2 | SILVERADO-2105 | 43432105 | OTHER | WIREDOWN4SPANSLDSIDEOF3403 | 20200209 | 1440 | 786619 | 1413 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 6539 | 38.5354 | -122.5073 | 4SPANSLDSIDEOF3403 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0019668 | OH | Sus | 0 | yes | 2020 | FEB | Yes | Line to Ground | 1513694 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0085412&numberofmonths=24&showchangehistorylog=1 | 20-0085412 | NORTH BAY | FIELD OPS NORTH | Tier 2 | STAFFORD-1102 | 43201102 | RECLOSER | 1202 | 20200817 | 300 | 1014482 | 965 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 20290 | 38.1221 | -122.6224 | TURMELJOEL415299483210spansloadsideofcos3847 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0085412 | OH | Sus | 44437092 | yes | 2020 | AUG | Yes | Line to Line | 1555842 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0009559&numberofmonths=24&showchangehistorylog=1 | 21-0009559 | NORTH BAY | FIELD OPS NORTH | Tier 2 | CALISTOGA-1101 | 42711101 | RECLOSER | 890 | 20210118 | 530 | 1212104 | 466 | Distribution Circuit | Vegetation | Tree - fell into line | 161 | 75026 | 38.6155 | -122.6585 | 5SPANSLDSIDEOFLR890 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0009559 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1593610 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0009698&numberofmonths=24&showchangehistorylog=1 | 21-0009698 | NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 6549 | 20210118 | 854 | 1212242 | 470 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 4230 | 38.6116 | -122.6578 | 2SPANLDOF6549TWDSTREBELRD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0009698 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1593699 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0009557&numberofmonths=24&showchangehistorylog=1 | 21-0009557 | NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1102 | 42711102 | RECLOSER | 131531 | 20210118 | 435 | 1212094 | 495 | Distribution Circuit | Vegetation | Tree - branch fell on line | 70 | 7113 | 38.5637 | -122.5595 | 13115DIASMONDMTNRDCA | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0009557 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1593608 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0009586&numberofmonths=24&showchangehistorylog=1 | 21-0009586 | NORTH BAY | FIELD OPS NORTH | Tier 2 | PUEBLO-1105 | 43291105 | OTHER | WIREDOWNTAPWOF9259 | 20210118 | 537 | 1212105 | 428 | Distribution Circuit | Vegetation | Tree - fell into line | 148 | 34744 | 38.4404 | -122.2916 | ONHARDTAPWESTOFFU9259 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0009586 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1593626 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0010406&numberofmonths=24&showchangehistorylog=1 | 21-0010406 | NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 5469 | 20210119 | 421 | 1214621 | 845 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 56615 | 38.0646 | -122.8251 | 100BALBOAWAY | Clear-32-90F | Pole-Wood | Broken, wire on ground | 21-0010406 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Line | 1594369 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0010126&numberofmonths=24&showchangehistorylog=1 | 21-0010126 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | RECLOSER | 632 | 20210119 | 331 | 1214440 | 537 | Distribution Circuit | Vegetation | Tree - fell into line | 739 | 356565 | 38.574 | -122.4444 | 2SPANSSSOF7437 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 21-0010126 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1594093 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0010761&numberofmonths=24&showchangehistorylog=1 | 21-0010761 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2105 | 43432105 | FUSE | 5439 | 20210119 | 441 | 1214705 | 800 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 4000 | 38.5283 | -122.555 | 2SPANSFROMEOL2POTBK | Strong Winds-Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0010761 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Line | 1594634 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0010771&numberofmonths=24&showchangehistorylog=1 | 21-0010771 | NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1101 | 43021101 | JUMPER | WIREDOWN4SPANSSOF4307 | 20210119 | 216 | 1214175 | 949 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 2813 | 38.0044 | -122.7075 | 7495SIRFRANCISDRAKE | Strong Winds-Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0010771 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1594644 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0158500&numberofmonths=24&showchangehistorylog=1 | 21-0158500 | NORTH BAY | FIELD OPS NORTH | Tier 3 | OLEMA-1101 | 42291101 | FUSE | 311 | 20211215 | 1408 | 1572800 | 578 | Distribution Circuit | Vegetation | Tree - fell into line | 113 | 43607 | 38.0103 | -122.7019 | CGC313662555685 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0158500 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1695493 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0138070&numberofmonths=24&showchangehistorylog=1 | 22-0138070 | NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1125 | 42031125 | RECLOSER | 902 | 20221210 | 642 | 1880379 | 318 | Distribution Circuit | Vegetation | Tree - branch fell on line | 204 | 61243 | 37.8893 | -122.5549 | 12SPANSLDSIDEOF427 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0138070 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1788895 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0138159&numberofmonths=24&showchangehistorylog=1 | 22-0138159 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1107 | 42011107 | FUSE | 2565 | 20221210 | 726 | 1880453 | 796 | Distribution Circuit | Vegetation | Tree - fell into line | 156 | 75252 | 37.9595 | -122.5348 | 105CYPRESSAVE | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0138159 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1788993 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0140801&numberofmonths=24&showchangehistorylog=1 | 22-0140801 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1107 | 42011107 | FUSE | 2565 | 20221220 | 1539 | 1894528 | 328 | Distribution Circuit | Vegetation | Tree - fell into line | 156 | 24548 | 37.9595 | -122.5348 | 80VISTADRKENTFIELD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0140801 | OH | Sus | 31633601 | No | 2022 | DEC | Yes | Line to Ground | 1792213 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0008930&numberofmonths=24&showchangehistorylog=1 | 23-0008930 | NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1101 | 43021101 | FUSE | 2623 | 20230107 | 1656 | 1927206 | 147 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 1617 | 38.0138 | -122.6989 | 25LSVULETAVE | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0008930 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1798769 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0009825&numberofmonths=24&showchangehistorylog=1 | 23-0009825 | NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1125 | 42031125 | JUMPER | OJS1SPANLDSIDEOFCGC3141091171 | 20230108 | 5 | 1932237 | 1117 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 20809 | 37.8876 | -122.5424 | 2SPANSLDSIDEOFCGC314109251171 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0009825 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1799666 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0010921&numberofmonths=24&showchangehistorylog=1 | 23-0010921 | NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1108 | 42011108 | FUSE | 2681 | 20230109 | 739 | 1936505 | 511 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 3577 | 37.9768 | -122.5907 | 1SPANNOCGC313981554365 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0010921 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1800765 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0011743&numberofmonths=24&showchangehistorylog=1 | 23-0011743 | NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1125 | 42031125 | RECLOSER | 510 | 20230110 | 201 | 1939991 | 985 | Distribution Circuit | Equipment Failure/Involved | Overhead | 391 | 214567 | 37.8896 | -122.5551 | WIREDOWN1SPANSOURCESIDEOFSW947917 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0011743 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1801504 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0011919&numberofmonths=24&showchangehistorylog=1 | 23-0011919 | NORTH BAY | FIELD OPS NORTH | Tier 2 | SAN RAFAEL-1109 | 42011109 | RECLOSER | 418 | 20230110 | 527 | 1942704 | 505 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1779 | 422965 | 37.9912 | -122.5094 | 120MOUNTAINVIEWSANRAFAEL | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0011919 | OH | Sus | 0 | No | 2023 | JAN | Yes | Force Out | 1801689 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0015862&numberofmonths=24&showchangehistorylog=1 | 23-0015862 | NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1124 | 42031124 | RECLOSER | 430 | 20230114 | 704 | 1952924 | 626 | Distribution Circuit | Vegetation | Tree - fell into line | 980 | 118325 | 37.906 | -122.5505 | 132MARIONAVE1SPANWOCGC314064151835 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0015862 | OH | Sus | 35419665 | No | 2023 | JAN | Yes | Line to Ground | 1804701 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0031914&numberofmonths=24&showchangehistorylog=1 | 23-0031914 | NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1101 | 43021101 | RECLOSER | 11012 | 20230221 | 2134 | 1996076 | 191 | Distribution Circuit | Equipment Failure/Involved | Overhead | 810 | 153296 | 38.0131 | -122.6677 | 754CAPBK | Clear-Strong Winds-32-90 F | Connector or Splice (OH) | Broken, wire on object | 23-0031914 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Line | 1815512 | CSO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0042458&numberofmonths=24&showchangehistorylog=1 | 23-0042458 | NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1102 | 43021102 | FUSE | 2387 | 20230309 | 1814 | 2028496 | 419 | Distribution Circuit | Vegetation | Tree - bark fell into line | 202 | 83225 | 37.9874 | -122.5939 | 196TAMALPAISRDFAIRFAX | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0042458 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1823286 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0044682&numberofmonths=24&showchangehistorylog=1 | 23-0044682 | NORTH BAY | FIELD OPS NORTH | Tier 2 | WOODACRE-1102 | 43021102 | RECLOSER | 1280 | 20230314 | 1019 | 2035862 | 573 | Distribution Circuit | Equipment Failure/Involved | Overhead | 792 | 343178 | 37.9963 | -122.5956 | SO1319BUTTERFIELDRDNOIRVING | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0044682 | OH | Sus | 35431693 | No | 2023 | MAR | Yes | Line to Ground | 1824835 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0022592&numberofmonths=24&showchangehistorylog=1 | 13-0022592 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER | 1640 | 20130408 | 1034 | 769861 | 1693 | Distribution Circuit | Vegetation | Tree - fell into line | 168 | 283234 | 40.354 | -121.5767 | 3POLESSOF5275ANDSSLINETO5275AND1439 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0022592 | OH | Sus | 30988243 | yes | 2013 | APR | Yes | Line to Line | 99291782 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078087&numberofmonths=24&showchangehistorylog=1 | 13-0078087 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1101 | 103201101 | RECLOSER | 13026 | 20131121 | 1813 | 907875 | 1481 | Distribution Circuit | Vegetation | Tree - fell into line | 166 | 182166 | 39.6842 | -120.9831 | PAST5931AND5933 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078087 | OH | Sus | 0 | yes | 2013 | NOV | Yes | Line to Ground | 99251274 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0077677&numberofmonths=24&showchangehistorylog=1 | 13-0077677 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1104 | 103521104 | FUSE | 9595 | 20131121 | 845 | 906786 | 406 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 6902 | 40.6123 | -122.317 | LYTLE195911231OLDOREGONTRAILREDDING | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0077677 | OH | Sus | 31037684 | yes | 2013 | NOV | Yes |  | 99252224 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078134&numberofmonths=24&showchangehistorylog=1 | 13-0078134 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | ORO FINO-1102 | 103031102 | FUSE | 1937 | 20131121 | 2121 | 909633 | 3996 | Distribution Circuit | Vegetation | Tree - fell into line | 307 | 639553 | 40.0842 | -121.5327 | MULTIPLEANDVARIOUS | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078134 | OH | Sus | 0 | yes | 2013 | NOV | Yes |  | 99250927 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0077871&numberofmonths=24&showchangehistorylog=1 | 13-0077871 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ORO FINO-1102 | 103031102 | FUSE | 1139 | 20131121 | 1301 | 907169 | 421 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 2105 | 39.9022 | -121.5272 | 2SPANSLDSIDEOF1139 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 13-0077871 | OH | Sus | 41991455 | yes | 2013 | NOV | Yes |  | 99252105 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0077612&numberofmonths=24&showchangehistorylog=1 | 13-0077612 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | RED BLUFF-1104 | 103541104 | RECLOSER | 51238 | 20131121 | 634 | 906606 | 451 | Distribution Circuit | Vegetation | Tree - fell into line | 350 | 22255 | 40.2387 | -122.2593 | LDSIDEOFDDELOCATED1SPANSSMTR1008363687 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0077612 | OH | Sus | 31037645 | yes | 2013 | NOV | Yes | Line to Ground | 99252289 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0077991&numberofmonths=24&showchangehistorylog=1 | 13-0077991 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | FUSE | 1097 | 20131121 | 1546 | 907438 | 1224 | Distribution Circuit | Vegetation | Tree - bark fell into line | 4 | 4896 | 40.3489 | -121.6257 | ONMAINTAPSTARTINGLBFEEDINGMTR1009363643 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0077991 | OH | Sus | 0 | yes | 2013 | NOV | Yes | Line to Line | 99251792 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0077607&numberofmonths=24&showchangehistorylog=1 | 13-0077607 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | VOLTA-1102 | 102541102 | FUSE | 10505 | 20131121 | 356 | 906536 | 374 | Distribution Circuit | Vegetation | Tree - fell into line | 152 | 56848 | 40.5077 | -121.8198 | GERRARD17861SPANSOF7469 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0077607 | OH | Sus | 31037575 | yes | 2013 | NOV | Yes | Line to Line | 99252294 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0077798&numberofmonths=24&showchangehistorylog=1 | 13-0077798 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | VOLTA-1102 | 102541102 | FUSE | 4331 | 20131121 | 1056 | 907038 | 733 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 6142 | 40.5342 | -121.7406 | MTR5000024470 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0077798 | OH | Sus | 31038092 | yes | 2013 | NOV | Yes | Line to Line | 99252141 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078093&numberofmonths=24&showchangehistorylog=1 | 13-0078093 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | VOLTA-1102 | 102541102 | RECLOSER | 1502 | 20131121 | 1933 | 908743 | 507 | Distribution Circuit | Vegetation | Tree - fell into line | 1440 | 301083 | 40.4946 | -121.8729 | GERRARD1786UNKNOWNCREWFOUND | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078093 | OH | Sus | 0 | yes | 2013 | NOV | Yes | Line to Line | 99251772 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078626&numberofmonths=24&showchangehistorylog=1 | 13-0078626 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | BANGOR-1101 | 103191101 | RECLOSER | 85780 | 20131122 | 1333 | 912326 | 641 | Distribution Circuit | Equipment Failure/Involved | Other | 457 | 263412 | 39.4592 | -121.2909 | 2PEOFLR857801SPANEOFFUCO695 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078626 | OH | Sus | 0 | yes | 2013 | NOV | Yes | Multi-Fault | 99251527 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078619&numberofmonths=24&showchangehistorylog=1 | 13-0078619 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | BUCKS CREEK-1103 | 102211103 | FUSE | 9203 | 20131122 | 1307 | 912310 | 188 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 2444 | 39.8879 | -121.2048 | MTR1008046643 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 13-0078619 | OH | Sus | 0 | yes | 2013 | NOV | Yes | None | 99251529 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078839&numberofmonths=24&showchangehistorylog=1 | 13-0078839 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | BUCKS CREEK-1103 | 102211103 | RECLOSER | 1103 | 20131122 | 2146 | 913255 | 1497 | Distribution Circuit | Equipment Failure/Involved | Other | 321 | 477233 | 39.9118 | -121.3268 | SBCO9329 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0078839 | OH | Sus | 31037615 | yes | 2013 | NOV | Yes | Line to Ground | 99251179 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078298&numberofmonths=24&showchangehistorylog=1 | 13-0078298 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ORO FINO-1102 | 103031102 | FUSE | 17427 | 20131122 | 45 | 910277 | 2455 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 120295 | 39.9097 | -121.5308 | 11SPANEOFFUCO1742721SPANFROMMETER1007243669 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0078298 | OH | Sus | 0 | yes | 2013 | NOV | Yes | Line to Line | 99251247 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078347&numberofmonths=24&showchangehistorylog=1 | 13-0078347 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ORO FINO-1102 | 103031102 | FUSE | 27019 | 20131122 | 402 | 910689 | 437 | Distribution Circuit | Vegetation | Tree - fell into line | 167 | 87508 | 39.848 | -121.6173 | 2SPANSLDSIDEOF27019 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078347 | OH | Sus | 0 | yes | 2013 | NOV | Yes |  | 99251677 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078367&numberofmonths=24&showchangehistorylog=1 | 13-0078367 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ORO FINO-1102 | 103031102 | RECLOSER | 2096 | 20131122 | 543 | 910892 | 2127 | Distribution Circuit | Vegetation | Tree - branch fell on line | 267 | 175075 | 39.8795 | -121.611 | MULTIPLELOCATIONSTREESDOWNEVERYWHERE | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078367 | OH | Sus | 0 | yes | 2013 | NOV | Yes | Three Phase Fault | 99250779 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078612&numberofmonths=24&showchangehistorylog=1 | 13-0078612 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ORO FINO-1102 | 103031102 | FUSE | 1139 | 20131122 | 135 | 912292 | 2555 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 12775 | 39.9022 | -121.5272 | MTR1007239096 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 13-0078612 | OH | Sus | 0 | yes | 2013 | NOV | Yes | Line to Ground | 99251216 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078543&numberofmonths=24&showchangehistorylog=1 | 13-0078543 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | FUSE | 4925 | 20131122 | 1004 | 911871 | 221 | Distribution Circuit | Equipment Failure/Involved | Other | 46 | 6308 | 40.3446 | -121.6051 | MTR1008302679 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 13-0078543 | OH | Sus | 0 | yes | 2013 | NOV | Yes | Line to Ground | 99251570 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078597&numberofmonths=24&showchangehistorylog=1 | 13-0078597 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | FUSE | 5135 | 20131122 | 1010 | 911733 | 285 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 855 | 40.3092 | -121.7652 | 5SPANLDSIDEOF5135 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0078597 | OH | Sus | 0 | yes | 2013 | NOV | Yes | Line to Line | 99251536 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078514&numberofmonths=24&showchangehistorylog=1 | 13-0078514 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | VOLTA-1102 | 102541102 | FUSE | 7569 | 20131122 | 733 | 911134 | 222 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 1332 | 40.513 | -121.9334 | 3WOFMTR5000074125 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078514 | OH | Sus | 0 | yes | 2013 | NOV | Yes | Line to Ground | 99251581 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078271&numberofmonths=24&showchangehistorylog=1 | 13-0078271 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WHITMORE-1101 | 103601101 | RECLOSER | 1594 | 20131122 | 20 | 910238 | 991 | Distribution Circuit | Vegetation | Tree - fell into line | 542 | 253021 | 40.6312 | -121.9039 | HARDTAPFEEDINGMETR5000022140MAINLINEFUCO10117MTR5000076206MTR5000018271MTR5000079277 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078271 | OH | Sus | 0 | yes | 2013 | NOV | Yes |  | 99251715 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078378&numberofmonths=24&showchangehistorylog=1 | 13-0078378 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | WYANDOTTE-1105 | 102911105 | FUSE | 23667 | 20131122 | 557 | 910878 | 1920 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 5547 | 39.6914 | -121.3337 | TAPTO13340OROQCYHWY | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 13-0078378 | OH | Sus | 0 | yes | 2013 | NOV | Yes |  | 99251233 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0073477&numberofmonths=24&showchangehistorylog=1 | 14-0073477 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE | 23675 | 20141203 | 1301 | 1123165 | 323 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 969 | 39.5074 | -121.2569 | 2POLESPAST23675 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 14-0073477 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99196772 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075380&numberofmonths=24&showchangehistorylog=1 | 14-0075380 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BUCKS CREEK-1103 | 102211103 | FUSE | 1129 | 20141211 | 957 | 1132571 | 4646 | Distribution Circuit | Vegetation | Tree - fell into line | 313 | 1013602 | 39.8705 | -121.1738 | SECORD9742SOCO3085MTR1008682202TOTHENORTH | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0075380 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99193211 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075288&numberofmonths=24&showchangehistorylog=1 | 14-0075288 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | ELK CREEK-1101 | 102781101 | RECLOSER | 2004 | 20141211 | 819 | 1131506 | 299 | Distribution Circuit | Vegetation | Tree - fell into line | 170 | 45670 | 39.6102 | -122.5337 | NIELSEN1821NOFSW831 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075288 | OH | Sus | 0 | yes | 2014 | DEC | Yes |  | 99194993 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075121&numberofmonths=24&showchangehistorylog=1 | 14-0075121 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | GIRVAN-1101 | 103401101 | RECLOSER | 1330 | 20141211 | 654 | 1130432 | 436 | Distribution Circuit | Vegetation | Tree - fell into line | 416 | 59392 | 40.5176 | -122.5056 | MTR5000016394 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0075121 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99195133 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075354&numberofmonths=24&showchangehistorylog=1 | 14-0075354 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | JESSUP-1101 | 103441101 | RECLOSER | 41356 | 20141211 | 933 | 1132382 | 474 | Distribution Circuit | Equipment Failure/Involved | Other | 352 | 82248 | 40.4771 | -122.4547 | LYTLE195914699COBBLESTONEDRANDERSON | Strong winds-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 14-0075354 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194936 | CSO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075550&numberofmonths=24&showchangehistorylog=1 | 14-0075550 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KANAKA-1101 | 103221101 | FUSE | 301 | 20141211 | 1123 | 1133225 | 1685 | Distribution Circuit | Equipment Failure/Involved | Other | 8 | 13480 | 39.5857 | -121.2844 | 3PPASTLCO301 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 14-0075550 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Open Circuit | 99194329 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075451&numberofmonths=24&showchangehistorylog=1 | 14-0075451 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1103 | 103521103 | RECLOSER | 1448 | 20141211 | 954 | 1132765 | 585 | Distribution Circuit | Vegetation | Tree - fell into line | 233 | 54873 | 40.648 | -122.2218 | 1POLESOFLINEANDBUCKFEEDINGMTR79B940 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 14-0075451 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194863 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075081&numberofmonths=24&showchangehistorylog=1 | 14-0075081 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ORO FINO-1102 | 103031102 | FUSE | 16653 | 20141211 | 605 | 1129739 | 440 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 3080 | 39.9134 | -121.6536 | 16926HOMEPLACE | Heavy rain-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0075081 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99195161 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075147&numberofmonths=24&showchangehistorylog=1 | 14-0075147 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ORO FINO-1102 | 103031102 | RECLOSER | 2236 | 20141211 | 822 | 1131600 | 229 | Distribution Circuit | Equipment Failure/Involved | Other | 1070 | 125303 | 39.8719 | -121.6118 | POWERSDAVEMTR1009123037 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075147 | OH | Sus | 0 | yes | 2014 | DEC | Yes |  | 99195112 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075364&numberofmonths=24&showchangehistorylog=1 | 14-0075364 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1101 | 102831101 | FUSE | 4587 | 20141211 | 826 | 1131592 | 738 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 50922 | 39.7704 | -121.6193 | 1MTR10081459492MTR1008145751 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075364 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99194925 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075430&numberofmonths=24&showchangehistorylog=1 | 14-0075430 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | PIT NO 3-2101 | 103732101 | RECLOSER | 1482 | 20141211 | 1203 | 1133458 | 166 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 2625 | 40.9988 | -121.7478 | SBCO444511SPANSEOF1753 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 14-0075430 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99194878 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075028&numberofmonths=24&showchangehistorylog=1 | 14-0075028 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | RISING RIVER-1101 | 103551101 | RECLOSER | 1530 | 20141211 | 535 | 1129851 | 1421 | Distribution Circuit | Vegetation | Tree - fell into line | 534 | 718580 | 40.8719 | -121.5543 | BOONE196019710hwy893NOFMTR50000022441SOFBOOSTER10195 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075028 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194385 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075234&numberofmonths=24&showchangehistorylog=1 | 14-0075234 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | STILLWATER-1102 | 103561102 | RECLOSER | 75906 | 20141211 | 925 | 1132232 | 94 | Distribution Circuit | Vegetation | Tree - fell into line | 250 | 23500 | 40.6884 | -122.3174 | MTR1006189425 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0075234 | OH | Sus | 0 | yes | 2014 | DEC | Yes |  | 99195038 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075234&numberofmonths=24&showchangehistorylog=1 | 14-0075234 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | STILLWATER-1102 | 103561102 | OTHER |  | 20141211 | 925 | 1133115 | 575 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1725 | 40.6887 | -122.3172 | MTR1006189425 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0075234 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194930 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075186&numberofmonths=24&showchangehistorylog=1 | 14-0075186 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | SYCAMORE CREEK-1111 | 102971111 | FUSE | 949 | 20141211 | 755 | 1131175 | 500 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 10500 | 39.944 | -121.7246 | MTR1007766356 | Heavy rain-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0075186 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99195076 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075484&numberofmonths=24&showchangehistorylog=1 | 14-0075484 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | SYCAMORE CREEK-1111 | 102971111 | FUSE | 26487 | 20141211 | 816 | 1132500 | 634 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 17118 | 39.9403 | -121.7238 | 1SPANLDSIDEOF26487 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075484 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99194838 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075300&numberofmonths=24&showchangehistorylog=1 | 14-0075300 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | FUSE | 850245 | 20141211 | 436 | 1129110 | 1311 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 11358 | 40.4463 | -121.845 | MTR1008053294 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0075300 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194982 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075499&numberofmonths=24&showchangehistorylog=1 | 14-0075499 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | VOLTA-1102 | 102541102 | FUSE | 7245 | 20141211 | 508 | 1129265 | 1213 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 8563 | 40.4959 | -121.9101 | LDSIDEFUCO7245 | Heavy rain-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0075499 | OH | Sus | 0 | yes | 2014 | DEC | Yes |  | 99194826 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075672&numberofmonths=24&showchangehistorylog=1 | 14-0075672 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1102 | 102541102 | FUSE | 7611 | 20141211 | 1342 | 1134016 | 648 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 6462 | 40.4744 | -122.0005 | 2EOFMTR5000074116 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075672 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99194701 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075066&numberofmonths=24&showchangehistorylog=1 | 14-0075066 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WHITMORE-1101 | 103601101 | FUSE | 2211 | 20141211 | 538 | 1129600 | 1535 | Distribution Circuit | Vegetation | Tree - fell into line | 83 | 53023 | 40.6069 | -121.9557 | 7SPANSLDSIDESBCO6699 | Heavy rain-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0075066 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99194381 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075554&numberofmonths=24&showchangehistorylog=1 | 14-0075554 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | WYANDOTTE-1105 | 102911105 | FUSE | 2757 | 20141211 | 818 | 1131476 | 1166 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 37022 | 39.7698 | -121.5058 | CHRISTENSEN26982spansfrommeter1007459696 | Heavy rain-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0075554 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99194783 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076473&numberofmonths=24&showchangehistorylog=1 | 14-0076473 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | GANSNER-1101 | 103021101 | FUSE | 1795 | 20141212 | 701 | 1138660 | 934 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 4670 | 39.9833 | -120.9461 | 1SPANLDSIDEOFFUCO1795 | Fog-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 14-0076473 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99193899 | CSO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076376&numberofmonths=24&showchangehistorylog=1 | 14-0076376 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | GRAYS FLAT-0401 | 102530401 | FUSE | 3079 | 20141212 | 939 | 1137798 | 1923 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 72085 | 40.0214 | -121.0633 | MULTIPLELOCATIONS | Fog-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 14-0076376 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99193476 | CSO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076492&numberofmonths=24&showchangehistorylog=1 | 14-0076492 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | GRAYS FLAT-0401 | 102530401 | FUSE | 1787 | 20141212 | 1636 | 1138902 | 1054 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 12648 | 40.0163 | -121.0867 | WOODMANSEE1206pineairmotel | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076492 | OH | Sus | 0 | yes | 2014 | DEC | Yes |  | 99193456 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076425&numberofmonths=24&showchangehistorylog=1 | 14-0076425 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WYANDOTTE-1102 | 102911102 | OTHER |  | 20141212 | 1137 | 1138174 | 302 | Distribution Circuit | Equipment Failure/Involved | Other | 37 | 8306 | 39.5495 | -121.5414 | 1SPANWOFAND2SPANSSOFMTR1008257651 | Overcast-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 14-0076425 | OH | Sus | 0 | yes | 2014 | DEC | Yes | None | 99193467 | CSO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076251&numberofmonths=24&showchangehistorylog=1 | 14-0076251 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WYANDOTTE-1107 | 102911107 | FUSE | 13517 | 20141212 | 714 | 1137603 | 473 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 946 | 39.4238 | -121.4279 | 1PPAST13517 | Fog-32 - 90 F | Conductor, Overhead | On Ground | 14-0076251 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194061 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0078998&numberofmonths=24&showchangehistorylog=1 | 14-0078998 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE | 1811 | 20141230 | 1050 | 1151296 | 406 | Distribution Circuit | Equipment Failure/Involved | Other | 50 | 20300 | 39.4447 | -121.2767 | 5PSOFMTR1007460470 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 14-0078998 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99190674 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0078943&numberofmonths=24&showchangehistorylog=1 | 14-0078943 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KANAKA-1101 | 103221101 | OCB | OCB | 20141230 | 1021 | 1151159 | 909 | Distribution Circuit | Vegetation | Tree - fell into line | 726 | 157627 | 39.5752 | -121.3056 | SSSIDEREG13525 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 14-0078943 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99190724 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079100&numberofmonths=24&showchangehistorylog=1 | 14-0079100 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ORO FINO-1101 | 103031101 | FUSE | 2705 | 20141230 | 948 | 1150861 | 1200 | Distribution Circuit | Vegetation | Tree - fell into line | 204 | 244800 | 39.8432 | -121.5923 | POWERSDAVE3POLESLOADSIDECO2705ROSEWOODSGLENWOOD | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079100 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99190591 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079487&numberofmonths=24&showchangehistorylog=1 | 14-0079487 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ORO FINO-1101 | 103031101 | FUSE | 27231 | 20141230 | 928 | 1150821 | 1377 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 22032 | 39.8572 | -121.5987 | MTR1007694453 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079487 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99190127 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079339&numberofmonths=24&showchangehistorylog=1 | 14-0079339 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ORO FINO-1102 | 103031102 | FUSE | 17343 | 20141230 | 1205 | 1151741 | 790 | Distribution Circuit | Vegetation | Tree - branch fell on line | 89 | 70310 | 39.8292 | -121.6207 | ATMTR1008114634 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079339 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99190417 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0078941&numberofmonths=24&showchangehistorylog=1 | 14-0078941 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1101 | 102831101 | FUSE | 17613 | 20141230 | 929 | 1150781 | 2031 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 34527 | 39.7929 | -121.5894 | JESSENMIKE1443LOFTYLANE | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0078941 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99190225 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079237&numberofmonths=24&showchangehistorylog=1 | 14-0079237 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1101 | 102831101 | FUSE | 5181 | 20141230 | 1431 | 1152920 | 1012 | Distribution Circuit | Vegetation | Tree - fell into line | 88 | 27995 | 39.7774 | -121.5993 | JESSENMIKEROCKYLN250FTSOWAGSTAFFRD | Strong winds-32 - 90 F | Anchor or Guy | Broken, wire on object | 14-0079237 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99190179 | ANC | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0078902&numberofmonths=24&showchangehistorylog=1 | 14-0078902 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1104 | 102831104 | RECLOSER | 45674 | 20141230 | 849 | 1150608 | 587 | Distribution Circuit | Vegetation | Tree - fell into line | 1768 | 507031 | 39.7442 | -121.5724 | MTR1009395057 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0078902 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Multi-Fault | 99190763 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0078916&numberofmonths=24&showchangehistorylog=1 | 14-0078916 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1104 | 102831104 | FUSE | 1583 | 20141230 | 916 | 1150736 | 1772 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 31832 | 39.7487 | -121.5798 | 3SPANSSOFFUCO1583 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0078916 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99190229 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079284&numberofmonths=24&showchangehistorylog=1 | 14-0079284 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1104 | 102831104 | FUSE | 4523 | 20141230 | 1029 | 1151947 | 1186 | Distribution Circuit | Vegetation | Tree - fell into line | 124 | 87709 | 39.7345 | -121.6129 | 1SOFMTR1007548687 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0079284 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99190166 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079211&numberofmonths=24&showchangehistorylog=1 | 14-0079211 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1106 | 102831106 | FUSE | 2785 | 20141230 | 828 | 1150497 | 1380 | Distribution Circuit | Vegetation | Tree - fell into line | 291 | 156005 | 39.8207 | -121.6013 | POWERSDAVE14065TEMPLECIRCLEMAGALIA | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0079211 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99190185 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0078914&numberofmonths=24&showchangehistorylog=1 | 14-0078914 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | STILLWATER-1102 | 103561102 | FUSE | 4697 | 20141230 | 824 | 1150498 | 621 | Distribution Circuit | Vegetation | Tree - fell into line | 73 | 45333 | 40.6951 | -122.3173 | MTR1006235729 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0078914 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99190750 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0078922&numberofmonths=24&showchangehistorylog=1 | 14-0078922 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | FUSE | 1555 | 20141230 | 803 | 1150437 | 267 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 20559 | 40.4391 | -121.8492 | MTR1008260052 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0078922 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99190741 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0078898&numberofmonths=24&showchangehistorylog=1 | 14-0078898 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WHITMORE-1101 | 103601101 | RECLOSER | 1598 | 20141230 | 750 | 1150422 | 832 | Distribution Circuit | Vegetation | Tree - fell into line | 174 | 94299 | 40.6206 | -121.9335 | 1SPANLDSIDEOF2105 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0078898 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99190770 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0078885&numberofmonths=24&showchangehistorylog=1 | 14-0078885 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | WYANDOTTE-1103 | 102911103 | FUSE | 1477 | 20141230 | 705 | 1150386 | 288 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 5760 | 39.6364 | -121.3938 | LDSIDETRANSFTOMTR1008116238 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0078885 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99190788 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0078907&numberofmonths=24&showchangehistorylog=1 | 14-0078907 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | WYANDOTTE-1103 | 102911103 | FUSE | 1433 | 20141230 | 855 | 1150606 | 242 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 4840 | 39.6332 | -121.4172 | MAYSSEANtreefellthroughline | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0078907 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99190758 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079584&numberofmonths=24&showchangehistorylog=1 | 14-0079584 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WYANDOTTE-1105 | 102911105 | FUSE | 17135 | 20141230 | 800 | 1156019 | 1458 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 36702 | 39.7833 | -121.5179 | 3461HOFFMAN | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079584 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99190096 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0009807&numberofmonths=24&showchangehistorylog=1 | 15-0009807 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BIG MEADOWS-2101 | 102812101 | RECLOSER | 2510 | 20150206 | 531 | 1173218 | 6233 | Distribution Circuit | Equipment Failure/Involved | Other | 3 | 18699 | 40.2105 | -121.1643 | MULTIPLEBET7212510 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0009807 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182899 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0009789&numberofmonths=24&showchangehistorylog=1 | 15-0009789 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BURNEY-1101 | 103311101 | FUSE | 7831 | 20150206 | 209 | 1173106 | 3696 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 88704 | 40.9479 | -121.5716 | BEYOND7831 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0009789 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183966 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0009796&numberofmonths=24&showchangehistorylog=1 | 15-0009796 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BURNEY-1101 | 103311101 | FUSE | 10083 | 20150206 | 157 | 1173072 | 2383 | Distribution Circuit | Vegetation | Tree - fell into line | 120 | 285960 | 40.9165 | -121.6285 | 2POLELDSIDEOFFUCO10083 | Overcast-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0009796 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183434 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0009806&numberofmonths=24&showchangehistorylog=1 | 15-0009806 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BURNEY-1101 | 103311101 | RECLOSER | 9042 | 20150206 | 235 | 1173101 | 5557 | Distribution Circuit | Vegetation | Tree - fell into line | 398 | 191233 | 40.8785 | -121.6574 | GERRARD1786COTALLTIMBERANDTORONTOAVE | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0009806 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183433 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0009901&numberofmonths=24&showchangehistorylog=1 | 15-0009901 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BURNEY-1101 | 103311101 | FUSE | 76411 | 20150206 | 209 | 1173714 | 2260 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 58760 | 40.9203 | -121.6312 | 4PEOFMTR1006231401 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 15-0009901 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99184660 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010034&numberofmonths=24&showchangehistorylog=1 | 15-0010034 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BURNEY-1101 | 103311101 | FUSE | 10093 | 20150206 | 1029 | 1174173 | 2916 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 137052 | 40.9187 | -121.626 | MTR1006231388 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010034 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183959 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0009806&numberofmonths=24&showchangehistorylog=1 | 15-0009806 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BURNEY-1101 | 103311101 | RECLOSER | 9042 | 20150206 | 1006 | ODB-9918 | 532 | Distribution Circuit | Equipment Failure/Involved | Other | 257 | 77704 | 40.8785 | -121.6574 | 9042 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0009806 | OH | Sus | 0 | yes | 2015 | FEB | Yes |  | 99182886 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010479&numberofmonths=24&showchangehistorylog=1 | 15-0010479 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BURNEY-1101 | 103311101 | OTHER |  | 20150206 | 500 | 1173184 | 5220 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 32472 | 40.8824 | -121.673 | 1WOFMTR1008044184 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010479 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183414 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010385&numberofmonths=24&showchangehistorylog=1 | 15-0010385 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1101 | 103201101 | FUSE | 1967 | 20150206 | 1209 | 1174689 | 824 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 6592 | 39.5059 | -121.2049 | 2PPASTCOUTS | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010385 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99185001 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010127&numberofmonths=24&showchangehistorylog=1 | 15-0010127 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1102 | 103201102 | RECLOSER | 1064 | 20150206 | 1206 | 1174714 | 645 | Distribution Circuit | Vegetation | Tree - fell into line | 198 | 89506 | 39.4819 | -121.2419 | LCO1813 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010127 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183422 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010512&numberofmonths=24&showchangehistorylog=1 | 15-0010512 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE | 23413 | 20150206 | 1225 | 1174804 | 1491 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 5964 | 39.4814 | -121.2305 | 1PPASTCOUTS | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010512 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99184601 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010205&numberofmonths=24&showchangehistorylog=1 | 15-0010205 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | GANSNER-1101 | 103021101 | FUSE | 18545 | 20150206 | 920 | 1175443 | 1821 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 16389 | 39.9468 | -120.9572 | LDSIDEOFFUCO18545 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010205 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Open Circuit | 99184637 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0009866&numberofmonths=24&showchangehistorylog=1 | 15-0009866 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | GRAYS FLAT-0401 | 102530401 | FUSE | 3079 | 20150206 | 555 | 1173556 | 2246 | Distribution Circuit | Vegetation | Tree - branch fell on line | 39 | 87594 | 40.0214 | -121.0633 | TRANSMISSIONPOLE1821196199 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0009866 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99184661 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010742&numberofmonths=24&showchangehistorylog=1 | 15-0010742 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KANAKA-1101 | 103221101 | FUSE | 799 | 20150206 | 1210 | 1175980 | 1762 | Distribution Circuit | Equipment Failure/Involved | Other | 25 | 44050 | 39.5898 | -121.2772 | 12WAYBET799AND1405 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 15-0010742 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99184554 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010732&numberofmonths=24&showchangehistorylog=1 | 15-0010732 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1102 | 103521102 | RECLOSER | 1382 | 20150206 | 2157 | 1178915 | 2434 | Distribution Circuit | Vegetation | Tree - fell into line | 242 | 239578 | 40.6539 | -122.3335 | 2SOF1008767148 | Strong winds-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 15-0010732 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183403 | CSO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011122&numberofmonths=24&showchangehistorylog=1 | 15-0011122 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1104 | 103521104 | FUSE | 5673 | 20150206 | 2116 | 1178599 | 2534 | Distribution Circuit | Equipment Failure/Involved | Other | 64 | 122386 | 40.5523 | -122.2766 | MTR1005530419 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0011122 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183383 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0009795&numberofmonths=24&showchangehistorylog=1 | 15-0009795 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ORO FINO-1102 | 103031102 | RECLOSER | 2236 | 20150206 | 425 | 1173164 | 593 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 1077 | 365976 | 39.8719 | -121.6118 | 14MILELDSIDEOF14213 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0009795 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183965 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0009924&numberofmonths=24&showchangehistorylog=1 | 15-0009924 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | PIT NO 3-2101 | 103732101 | OCB | OCB | 20150206 | 744 | 1173484 | 6438 | Distribution Circuit | Vegetation | Tree - fell into line | 118 | 465599 | 40.9982 | -121.748 | SHERRODLARRYMETER100987262537985CLARKCREEKROAD | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0009924 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99182344 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011058&numberofmonths=24&showchangehistorylog=1 | 15-0011058 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | PIT NO 3-2101 | 103732101 | FUSE | 8543 | 20150206 | 744 | 1180610 | 6186 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 43302 | 41.0644 | -121.6461 | BEYOND8543 | Strong winds-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 15-0011058 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182525 | CAW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011060&numberofmonths=24&showchangehistorylog=1 | 15-0011060 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | PIT NO 3-2101 | 103732101 | FUSE | 7903 | 20150206 | 744 | 1180625 | 3343 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 90261 | 41 | -121.6311 | BEYONDFUCO7903 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0011060 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183387 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011241&numberofmonths=24&showchangehistorylog=1 | 15-0011241 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | PIT NO 3-2101 | 103732101 | OTHER |  | 20150206 | 744 | 1181299 | 4756 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 4756 | 41.0036 | -121.6301 | ATMET3H2631 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0011241 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183373 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0009784&numberofmonths=24&showchangehistorylog=1 | 15-0009784 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | RISING RIVER-1101 | 103551101 | RECLOSER | 1530 | 20150206 | 114 | 1173064 | 6814 | Distribution Circuit | Vegetation | Tree - fell into line | 192 | 1173616 | 40.8719 | -121.5543 | WIREDOWNJUSTLOADSIDEOFLR1530WIDESPREADDAMAGETOCIRCUITPOLESANDWIREDOWN | Overcast-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0009784 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182345 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0009784&numberofmonths=24&showchangehistorylog=1 | 15-0009784 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | RISING RIVER-1101 | 103551101 | OCB | OCB | 20150206 | 229 | ODB-9918 | 1052 | Distribution Circuit | Vegetation | Tree - fell into line | 201 | 91514 | 40.9289 | -121.5446 | WIREDOWNJUSTWESTOFSW7711WIDESPREADDAMAGEONCIRCUIT | Overcast-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0009784 | OH | Sus | 0 | yes | 2015 | FEB | Yes |  | 99182273 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0009791&numberofmonths=24&showchangehistorylog=1 | 15-0009791 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER | 80454 | 20150206 | 355 | 1173144 | 541 | Distribution Circuit | Vegetation | Tree - fell into line | 240 | 63900 | 40.4341 | -121.8715 | ONMAINLINESOURCESIDEOF1563 | Overcast-32 - 90 F | Conductor, Overhead | On Ground | 15-0009791 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99185342 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0009799&numberofmonths=24&showchangehistorylog=1 | 15-0009799 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER | 1640 | 20150206 | 455 | 1173195 | 3722 | Distribution Circuit | Vegetation | Tree - fell into line | 168 | 482901 | 40.354 | -121.5767 | BETWEEN10THAND20THPOLELDSIDEOF6087 | Overcast-32 - 90 F | Conductor, Overhead | On Ground | 15-0009799 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183964 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0009791&numberofmonths=24&showchangehistorylog=1 | 15-0009791 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | OTHER |  | 20150206 | 355 | 1175407 | 4780 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 4780 | 40.4419 | -121.7693 | ONTAP | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0009791 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183418 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0009778&numberofmonths=24&showchangehistorylog=1 | 15-0009778 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1102 | 102541102 | RECLOSER | 93418 | 20150206 | 201 | 1173093 | 2279 | Distribution Circuit | Vegetation | Tree - fell into line | 1441 | 1622357 | 40.5134 | -121.7867 | FUCO69685 | Overcast-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 15-0009778 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99184666 | CAW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011094&numberofmonths=24&showchangehistorylog=1 | 15-0011094 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | BUCKS CREEK-1102 | 102211102 | RECLOSER | 1102 | 20150207 | 257 | 1180224 | 5083 | Distribution Circuit | Vegetation | Tree - fell into line | 131 | 265640 | 39.9121 | -121.3269 | 1NEOFAND2NEOFSW565 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011094 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99182859 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011349&numberofmonths=24&showchangehistorylog=1 | 15-0011349 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | BUCKS CREEK-1103 | 102211103 | RECLOSER | 2414 | 20150207 | 132 | 1181709 | 2165 | Distribution Circuit | Vegetation | Tree - fell into line | 314 | 618504 | 39.8925 | -121.2054 | 1SSOF88165 | Strong winds-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 15-0011349 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99183840 | CAW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011398&numberofmonths=24&showchangehistorylog=1 | 15-0011398 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | BUCKS CREEK-1103 | 102211103 | FUSE | 18103 | 20150207 | 2115 | 1181923 | 3021 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 3021 | 39.8956 | -121.2793 | 3STRUCTURESBEYOND18103 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011398 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Three Phase Fault | 99182522 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011564&numberofmonths=24&showchangehistorylog=1 | 15-0011564 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1101 | 103201101 | RECLOSER | 13026 | 20150207 | 1330 | 1181235 | 1875 | Distribution Circuit | Equipment Failure/Involved | Other | 167 | 300525 | 39.6842 | -120.9831 | PASTSBCO5931 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011564 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183347 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010880&numberofmonths=24&showchangehistorylog=1 | 15-0010880 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1102 | 103201102 | OCB | OCB | 20150207 | 131 | 1179787 | 687 | Distribution Circuit | Equipment Failure/Involved | Other | 889 | 256542 | 39.4855 | -121.2204 | 3PWOFMTR50000024252 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010880 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Multi-Fault | 99183394 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011193&numberofmonths=24&showchangehistorylog=1 | 15-0011193 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | COTTONWOOD-1103 | 102931103 | RECLOSER | 9072 | 20150207 | 821 | 1180550 | 524 | Distribution Circuit | Vegetation | Tree - fell into line | 282 | 143733 | 40.3378 | -122.3718 | MASON1837TREETHROUGHLINE | Strong winds-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 15-0011193 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182856 | CSO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011020&numberofmonths=24&showchangehistorylog=1 | 15-0011020 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | DESCHUTES-1101 | 103351101 | FUSE | 9847 | 20150207 | 739 | 1179627 | 652 | Distribution Circuit | Equipment Failure/Involved | Other | 3 | 1956 | 40.591 | -122.1733 | 1STPOLELDSIDEOFMTR | Fog-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0011020 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Three Phase Fault | 99184450 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011355&numberofmonths=24&showchangehistorylog=1 | 15-0011355 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | GANSNER-1101 | 103021101 | SWITCH | 3491 | 20150207 | 1820 | 1181726 | 1719 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 39537 | 40.0156 | -120.966 | 1LDSIDEOF3491 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011355 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99183839 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0009920&numberofmonths=24&showchangehistorylog=1 | 15-0009920 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | GANSNER-1101 | 103021101 | FUSE | 79151 | 20150207 | 1548 | ODB-9918 | 2607 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 49533 | 40.0272 | -120.9641 | SEVERALLOCATIONSTHROUGHOUTTHE60KVAND21KVLINEASWELL | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0009920 | OH | Sus | 0 | yes | 2015 | FEB | Yes |  | 99181691 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011207&numberofmonths=24&showchangehistorylog=1 | 15-0011207 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | MC ARTHUR-1101 | 103491101 | FUSE | 4233 | 20150207 | 735 | 1180334 | 2112 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 35792 | 41.1068 | -121.3246 | TRNASFMTR1008049203 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011207 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99183874 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010964&numberofmonths=24&showchangehistorylog=1 | 15-0010964 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1101 | 102831101 | FUSE | 17629 | 20150207 | 445 | 1180042 | 644 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1932 | 39.7755 | -121.622 | 2SPANSLSOF17629 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0010964 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99184483 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010854&numberofmonths=24&showchangehistorylog=1 | 15-0010854 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER | 85234 | 20150207 | 39 | 1179687 | 949 | Distribution Circuit | Equipment Failure/Involved | Other | 391 | 296599 | 40.3484 | -121.6214 | VARIOUS | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0010854 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99184525 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010854&numberofmonths=24&showchangehistorylog=1 | 15-0010854 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | FUSE | 1175 | 20150207 | 39 | 1181929 | 2186 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 48092 | 40.3506 | -121.5861 | BEYOND1175 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010854 | OH | Sus | 0 | yes | 2015 | FEB | Yes | None | 99183826 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011126&numberofmonths=24&showchangehistorylog=1 | 15-0011126 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1102 | 102541102 | FUSE | 7607 | 20150207 | 342 | 1179968 | 2628 | Distribution Circuit | Equipment Failure/Involved | Other | 29 | 14052 | 40.4772 | -122.0009 | MTR5000020628 | Strong winds-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 15-0011126 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183382 | CSO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011091&numberofmonths=24&showchangehistorylog=1 | 15-0011091 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | WHITMORE-1101 | 103601101 | FUSE | 7653 | 20150207 | 935 | 1180768 | 1660 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 6704 | 40.708 | -121.9334 | INTERSECTIONOFOAKRUNFERNPHILLPSCOFFRD | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 15-0011091 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183893 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011496&numberofmonths=24&showchangehistorylog=1 | 15-0011496 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WHITMORE-1101 | 103601101 | OTHER |  | 20150207 | 200 | 1182385 | 2370 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2370 | 40.6483 | -121.9408 | EOL | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011496 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183771 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011326&numberofmonths=24&showchangehistorylog=1 | 15-0011326 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | WYANDOTTE-1105 | 102911105 | FUSE | 1735 | 20150207 | 26 | 1180221 | 2119 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 55094 | 39.6963 | -121.4809 | MTR1007768242 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011326 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99183848 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011538&numberofmonths=24&showchangehistorylog=1 | 15-0011538 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | PANORAMA-1102 | 103461102 | FUSE | 2017 | 20150208 | 1150 | 1182637 | 705 | Distribution Circuit | Equipment Failure/Involved | Other | 2 | 1410 | 40.3372 | -122.1218 | BELL1836TXPOLEFEEDINGMTR1008683489 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0011538 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183349 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011917&numberofmonths=24&showchangehistorylog=1 | 15-0011917 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1101 | 102831101 | TRANSFORMER |  | 20150208 | 2333 | 1185248 | 867 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 6290 | 39.7672 | -121.622 | JESSENMIKE6104MARLOWLN | Strong winds-32 - 90 F | Transformer | Broken, wire on ground | 15-0011917 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183273 | TX | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0048403&numberofmonths=24&showchangehistorylog=1 | 15-0048403 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 655 | 20150718 | 1643 | 1270179 | 485 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 6305 | 39.4256 | -121.3607 | MAIOCCOMARTYWIREDOWNACROSSCREEK | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 15-0048403 | OH | Sus | 31170289 | yes | 2015 | JUL | Yes | Line to Line | 1145881 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0084609&numberofmonths=24&showchangehistorylog=1 | 15-0084609 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ORO FINO-1101 | 103031101 | OCB | OCB | 20151213 | 856 | 1360571 | 175 | Distribution Circuit | Vegetation | Tree - fell into line | 2493 | 190854 | 39.8717 | -121.611 | KENNEDY3947madonnactMTR1007905424 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084609 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1174273 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0084753&numberofmonths=24&showchangehistorylog=1 | 15-0084753 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1104 | 102831104 | FUSE | 4513 | 20151213 | 858 | 1360574 | 249 | Distribution Circuit | Vegetation | Tree - fell into line | 165 | 41085 | 39.7412 | -121.5725 | KENNEDY3947cnrstearnscountryclub | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084753 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Line | 1174421 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0087229&numberofmonths=24&showchangehistorylog=1 | 15-0087229 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | CORNING-1102 | 103331102 | FUSE | 2027 | 20151224 | 2028 | 1371398 | 694 | Distribution Circuit | 3rd Party | Gun Shot | 61 | 39836 | 39.9753 | -122.5508 | SSOFMTR1008361835 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0087229 | OH | Sus | 31208880 | yes | 2015 | DEC | Yes | Line to Ground | 1177310 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0013446&numberofmonths=24&showchangehistorylog=1 | 16-0013446 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1101 | 103201101 | RECLOSER | 98174 | 20160217 | 2054 | 1407205 | 557 | Distribution Circuit | Vegetation | Tree - fell into line | 355 | 197735 | 39.6081 | -121.0754 | 12SPANSSSOF5927 | Snow-Overcast-Below 32 F | Conductor, Overhead | Broken, wire on ground | 16-0013446 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Line to Ground | 1186530 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017920&numberofmonths=24&showchangehistorylog=1 | 16-0017920 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | ANTLER-1101 | 103271101 | FUSE | 3317 | 20160305 | 1746 | 1417752 | 1319 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 14509 | 40.7852 | -122.318 | MTR5000021524 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017920 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1189783 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0018147&numberofmonths=24&showchangehistorylog=1 | 16-0018147 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | RECLOSER | 1804 | 20160305 | 2219 | 1420171 | 2464 | Distribution Circuit | Vegetation | Tree - fell into line | 426 | 131385 | 39.39 | -121.4043 | MaysSean2497treetookdown3spansofwireloadsideof545 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018147 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190018 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0018442&numberofmonths=24&showchangehistorylog=1 | 16-0018442 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | BUCKS CREEK-1101 | 102211101 | RECLOSER | 1101 | 20160305 | 2343 | 1420831 | 2625 | Distribution Circuit | Vegetation | Tree - branch fell on line | 28 | 60741 | 39.9128 | -121.3277 | 17183 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018442 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1190279 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017808&numberofmonths=24&showchangehistorylog=1 | 16-0017808 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1102 | 103201102 | RECLOSER | 1064 | 20160305 | 1923 | 1418475 | 354 | Distribution Circuit | Vegetation | Tree - fell into line | 198 | 54878 | 39.482 | -121.2419 | WoodmanseeMatt1751wiredownat17055newyorkhouserd | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017808 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1189661 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017773&numberofmonths=24&showchangehistorylog=1 | 16-0017773 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | FRENCH GULCH-1101 | 103381101 | FUSE | 2907 | 20160305 | 1755 | 1417821 | 545 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 13625 | 40.7588 | -122.615 | MTR5000074533 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017773 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1189626 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0018537&numberofmonths=24&showchangehistorylog=1 | 16-0018537 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KANAKA-1101 | 103221101 | JUMPER | WIREDOWN | 20160305 | 2211 | 1422568 | 1389 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 9723 | 39.5004 | -121.3449 | 1SPANLDSIDEOF469045 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018537 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Three Phase Fault | 1190375 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017656&numberofmonths=24&showchangehistorylog=1 | 16-0017656 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ORO FINO-1102 | 103031102 | FUSE | 1917 | 20160305 | 1727 | 1417653 | 1052 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 28846 | 39.8721 | -121.6791 | 6233 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 16-0017656 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1189512 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017617&numberofmonths=24&showchangehistorylog=1 | 16-0017617 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ORO FINO-1102 | 103031102 | RECLOSER | 2040 | 20160305 | 2132 | 1419627 | 138 | Distribution Circuit | Vegetation | Tree - fell into line | 316 | 43608 | 39.935 | -121.6468 | 1SPANLDSIDEOFREG16 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017617 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1189760 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017617&numberofmonths=24&showchangehistorylog=1 | 16-0017617 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ORO FINO-1102 | 103031102 | RECLOSER | 2236 | 20160305 | 1741 | 1417726 | 166 | Distribution Circuit | Vegetation | Tree - fell into line | 997 | 147826 | 39.8719 | -121.6119 | 1LDSIDEOFREG16 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017617 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1189471 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017771&numberofmonths=24&showchangehistorylog=1 | 16-0017771 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1104 | 102831104 | FUSE | 1593 | 20160305 | 1812 | 1417976 | 498 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 10458 | 39.751 | -121.5734 | 3LDSIDEOFFUCO1593 | Strong Winds-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017771 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1189624 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0018169&numberofmonths=24&showchangehistorylog=1 | 16-0018169 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1104 | 102831104 | FUSE | 17285 | 20160305 | 2156 | 1419848 | 579 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 6948 | 39.7414 | -121.5939 | 3WOFFUCO17285 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018169 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1190039 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0018010&numberofmonths=24&showchangehistorylog=1 | 16-0018010 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1105 | 102831105 | JUMPER | LINEBURNEDOPEN | 20160305 | 2146 | 1420623 | 324 | Distribution Circuit | Vegetation | Tree - fell into line | 1291 | 93786 | 39.7945 | -121.5797 | ONMAINLINEFUCO27153 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on object | 16-0018010 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Open Circuit | 1189881 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017720&numberofmonths=24&showchangehistorylog=1 | 16-0017720 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | RED BLUFF-1101 | 103541101 | FUSE | 4189 | 20160305 | 1820 | 1418086 | 196 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 12788 | 40.2239 | -122.3483 | 1PSAND1PEMTR1008224878 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017720 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1189575 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017941&numberofmonths=24&showchangehistorylog=1 | 16-0017941 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | RED BLUFF-1103 | 103541103 | RECLOSER | 1702 | 20160305 | 2101 | 1419432 | 191 | Distribution Circuit | Equipment Failure/Involved | Overhead | 221 | 42211 | 40.1649 | -122.2812 | 2093 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017941 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1189803 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017805&numberofmonths=24&showchangehistorylog=1 | 16-0017805 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | JUMPER | TSB2EOFMTR1008302681 | 20160305 | 1807 | 1417935 | 1926 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 15408 | 40.3465 | -121.6117 | MTR1008302681 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017805 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1189658 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017879&numberofmonths=24&showchangehistorylog=1 | 16-0017879 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER | 80454 | 20160305 | 2021 | 1418987 | 1401 | Distribution Circuit | Vegetation | Tree - fell into line | 240 | 84830 | 40.4341 | -121.8714 | 2SPANSEOF1571 | Overcast-Fog-Heavy Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 16-0017879 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1189737 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017865&numberofmonths=24&showchangehistorylog=1 | 16-0017865 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WYANDOTTE-1107 | 102911107 | FUSE | 13057 | 20160305 | 2037 | 1419076 | 285 | Distribution Circuit | Vegetation | Tree - branch fell on line | 33 | 9405 | 39.483 | -121.4822 | 196NARANJAAVEMTR10074562181SPAN1PHASEDOWNFEEDINGSOUTHTOLB | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017865 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1189719 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0018025&numberofmonths=24&showchangehistorylog=1 | 16-0018025 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WYANDOTTE-1109 | 102911109 | SWITCH | 68821 | 20160305 | 2119 | 1420604 | 376 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 32712 | 39.434 | -121.5174 | MAINLINEATFUCO23111 | Partly Cloudy-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018025 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1189896 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0071832&numberofmonths=24&showchangehistorylog=1 | 16-0071832 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | VOLTA-1102 | 102541102 | RECLOSER | 1646 | 20161014 | 132 | 1558011 | 826 | Distribution Circuit | Vegetation | Tree - fell into line | 540 | 213622 | 40.5007 | -121.9162 | FUCO9707ONMAINLINE | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 16-0071832 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Ground | 1229010 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0071897&numberofmonths=24&showchangehistorylog=1 | 16-0071897 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1102 | 102541102 | FUSE | 1531 | 20161014 | 432 | 1558437 | 779 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 38950 | 40.5228 | -121.6813 | 2MINEOF1531 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0071897 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Ground | 1229087 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0003454&numberofmonths=24&showchangehistorylog=1 | 17-0003454 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | CEDAR CREEK-1101 | 103321101 | FUSE | 1611 | 20170103 | 2111 | 1616945 | 753 | Distribution Circuit | Equipment Failure/Involved | Overhead | 46 | 24942 | 40.8232 | -121.9394 | MTR5000101338 | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003454 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1243631 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0003359&numberofmonths=24&showchangehistorylog=1 | 17-0003359 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ORO FINO-1102 | 103031102 | FUSE | 1147 | 20170103 | 2302 | 1617383 | 564 | Distribution Circuit | Vegetation | Tree - fell into line | 115 | 64860 | 39.8897 | -121.5781 | 17171TWD1147 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003359 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1243534 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0003238&numberofmonths=24&showchangehistorylog=1 | 17-0003238 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | PIT NO 3-2101 | 103732101 | OCB | 21012 | 20170103 | 2025 | 1616744 | 1497 | Distribution Circuit | Vegetation | Tree - branch fell on line | 154 | 157796 | 40.9981 | -121.7476 | 1SPANEOFTAPTOPIT4WIREDOWNLDSIDEAT354683TREEDAMAGESOURCEANDLOADSIDEATSBCO1733 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003238 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Multi-Fault | 1243407 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006104&numberofmonths=24&showchangehistorylog=1 | 17-0006104 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | BUCKS CREEK-1102 | 102211102 | OCB | 11022 | 20170108 | 1941 | 1630293 | 6944 | Distribution Circuit | Environmental/External | Flood/Erosion | 131 | 909664 | 39.9131 | -121.3271 | SW923 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0006104 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1245831 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005584&numberofmonths=24&showchangehistorylog=1 | 17-0005584 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE | 23423 | 20170108 | 1318 | 1626785 | 1917 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 29216 | 39.4654 | -121.281 | WoodmanseeMatt1751wiredownatchurch | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005584 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1245365 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005653&numberofmonths=24&showchangehistorylog=1 | 17-0005653 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | CLARK ROAD-1102 | 103091102 | FUSE | 815317 | 20170108 | 1516 | 1627654 | 1588 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 28584 | 39.672 | -121.5828 | 5PLD815317 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005653 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1245433 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006505&numberofmonths=24&showchangehistorylog=1 | 17-0006505 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KANAKA-1101 | 103221101 | FUSE | 1413 | 20170108 | 1808 | 1628523 | 2522 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 20176 | 39.5926 | -121.2679 | 5SPANSLDSIDEOF1413 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006505 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1246171 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005492&numberofmonths=24&showchangehistorylog=1 | 17-0005492 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | NOTRE DAME-1104 | 102041104 | TRIP-SAVER | 2537 | 20170108 | 1426 | 1626728 | 1946 | Distribution Circuit | Equipment Failure/Involved | Overhead | 44 | 85624 | 39.7912 | -121.7218 | 1poleeo2537 | Overcast-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0005492 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Three Phase Fault | 1245275 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006093&numberofmonths=24&showchangehistorylog=1 | 17-0006093 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1101 | 102831101 | TRANSFORMER | 221085576774 | 20170108 | 1123 | 1631133 | 3177 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 9531 | 39.7736 | -121.6154 | 6310RUBYLNPARADISE95969 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006093 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245823 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005345&numberofmonths=24&showchangehistorylog=1 | 17-0005345 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1103 | 102831103 | RECLOSER | 43008 | 20170108 | 1139 | 1625697 | 1370 | Distribution Circuit | Vegetation | Tree - fell into line | 564 | 584314 | 39.7371 | -121.6481 | BETSW7009AND17689INCLUDING17689 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0005345 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245135 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005084&numberofmonths=24&showchangehistorylog=1 | 17-0005084 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1104 | 102831104 | FUSE | 17327 | 20170108 | 814 | 1623578 | 515 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 3090 | 39.7297 | -121.5742 | MTR1007887564 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005084 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1244882 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005685&numberofmonths=24&showchangehistorylog=1 | 17-0005685 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1105 | 102831105 | FUSE | 1377 | 20170108 | 1336 | 1629184 | 2502 | Distribution Circuit | Vegetation | Tree - bark fell into line | 31 | 77562 | 39.7706 | -121.6031 | MTR1007921609 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0005685 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1245467 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005624&numberofmonths=24&showchangehistorylog=1 | 17-0005624 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER | 85234 | 20170108 | 1316 | 1626779 | 2917 | Distribution Circuit | Vegetation | Tree - fell into line | 548 | 1435667 | 40.3481 | -121.6206 | 11SPANSLDSIDEOF85234 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005624 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Multi-Fault | 1245405 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005410&numberofmonths=24&showchangehistorylog=1 | 17-0005410 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WYANDOTTE-1103 | 102911103 | FUSE | 791 | 20170108 | 1224 | 1626167 | 1786 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 25004 | 39.548 | -121.3482 | SparksMarty3864Meter1008114043 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005410 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1245193 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006051&numberofmonths=24&showchangehistorylog=1 | 17-0006051 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | WYANDOTTE-1103 | 102911103 | FUSE | 5427 | 20170108 | 1430 | 1627346 | 1768 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 18803 | 39.5932 | -121.4447 | MTR1008140943 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006051 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245792 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006341&numberofmonths=24&showchangehistorylog=1 | 17-0006341 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BIG MEADOWS-2101 | 102812101 | RECLOSER | 2476 | 20170109 | 2236 | 1632352 | 4787 | Distribution Circuit | Vegetation | Tree - fell into line | 2747 | 1407309 | 40.1713 | -121.0871 | 10POLESSSOF18685 | Overcast-Fog-Snow-Strong Winds-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0006341 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1246047 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006215&numberofmonths=24&showchangehistorylog=1 | 17-0006215 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KANAKA-1101 | 103221101 | JUMPER | OJCORNEWYORKANDSESAME | 20170109 | 1547 | 1631669 | 128 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 512 | 39.4483 | -121.2571 | CORNEROFNEWYORKSESAME | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006215 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245911 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006353&numberofmonths=24&showchangehistorylog=1 | 17-0006353 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WYANDOTTE-1107 | 102911107 | RECLOSER | 1510 | 20170109 | 2323 | 1632387 | 1042 | Distribution Circuit | Vegetation | Tree - fell into line | 661 | 381461 | 39.497 | -121.4452 | 1075HURLETONRD1SPANSSOF1510 | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006353 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246059 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006490&numberofmonths=24&showchangehistorylog=1 | 17-0006490 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 1875 | 20170110 | 534 | 1632530 | 689 | Distribution Circuit | Vegetation | Tree - branch fell on line | 42 | 28938 | 39.4363 | -121.326 | 15980VIERRARD | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0006490 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1246164 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006772&numberofmonths=24&showchangehistorylog=1 | 17-0006772 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BIG BEND-1101 | 103751101 | FUSE | 2851 | 20170110 | 1507 | 1633938 | 187 | Distribution Circuit | Vegetation | Tree - fell into line | 65 | 12155 | 39.7857 | -121.5063 | RobbinsJames193413255AMBLESIDE | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006772 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246365 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006828&numberofmonths=24&showchangehistorylog=1 | 17-0006828 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BIG MEADOWS-2101 | 102812101 | JUMPER | WIREDOWNSSIDEOF18145ONMAINLINE | 20170110 | 1413 | 1634235 | 601 | Distribution Circuit | Equipment Failure/Involved | Overhead | 199 | 89910 | 40.1985 | -121.0702 | 1SPANSSOFFUCO18145 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0006828 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Force Out | 1246412 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007278&numberofmonths=24&showchangehistorylog=1 | 17-0007278 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1101 | 103201101 | RECLOSER | 13026 | 20170110 | 1628 | 1634391 | 4379 | Distribution Circuit | Vegetation | Tree - fell into line | 167 | 558905 | 39.6844 | -120.9829 | 15SPANSLDSIDEOF130264SPANSFROMEOLBEYONDSBCO68671 | Overcast-Fog-Snow-Strong Winds-Below 32 F | Crossarm, Wood | Broken, wire on ground | 17-0007278 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1246858 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006595&numberofmonths=24&showchangehistorylog=1 | 17-0006595 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | COTTONWOOD-1102 | 102931102 | FUSE | 2085 | 20170110 | 1247 | 1633298 | 67 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 67 | 40.3805 | -122.437 | MEADOWOAKDRSOGASPOINTRDWOCOTTONWOOD | Overcast-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0006595 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246242 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007245&numberofmonths=24&showchangehistorylog=1 | 17-0007245 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | HAMILTON BRANCH-1101 | 102361101 | JUMPER | LINEBUCKRIPPEDCLEAR | 20170110 | 1922 | 1638026 | 1507 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 10549 | 40.2626 | -121.1352 | 616CEDARCANYONRD | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007245 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Open Circuit | 1246825 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007034&numberofmonths=24&showchangehistorylog=1 | 17-0007034 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KANAKA-1101 | 103221101 | RECLOSER | 79226 | 20170110 | 1848 | 1636626 | 225 | Distribution Circuit | Vegetation | Tree - fell into line | 896 | 70817 | 39.5148 | -121.2644 | 2LDSIDEOFCHALLENGESIDELR5462 | Overcast-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0007034 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Three Phase Fault | 1246619 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0009979&numberofmonths=24&showchangehistorylog=1 | 17-0009979 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | RECLOSER | 1804 | 20170118 | 1350 | 1646317 | 1332 | Distribution Circuit | Vegetation | Tree - fell into line | 433 | 138251 | 39.39 | -121.4043 | SparksMarty3864600Uphamrd | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0009979 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1249037 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0010942&numberofmonths=24&showchangehistorylog=1 | 17-0010942 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | BUCKS CREEK-1103 | 102211103 | RECLOSER | 2414 | 20170118 | 1859 | 1648330 | 6012 | Distribution Circuit | Vegetation | Tree - fell into line | 119 | 704056 | 39.8921 | -121.2043 | BUCKSLAKEATDAM | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0010942 | OH | Sus | 0 | yes | 2017 | JAN | Yes | None | 1249879 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0009937&numberofmonths=24&showchangehistorylog=1 | 17-0009937 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1102 | 103201102 | RECLOSER | 5462 | 20170118 | 1300 | 1646223 | 463 | Distribution Circuit | Vegetation | Tree - branch fell on line | 457 | 209843 | 39.483 | -121.2464 | SparksMarty38643spansLSofmeter1007886392ATFUCO23421ONMAINLINE | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0009937 | OH | Sus | 42928979 | yes | 2017 | JAN | Yes | Line to Ground | 1249014 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0010121&numberofmonths=24&showchangehistorylog=1 | 17-0010121 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KESWICK-1101 | 103451101 | OCB | 11012 | 20170118 | 1558 | 1646895 | 971 | Distribution Circuit | Vegetation | Tree - fell into line | 789 | 207405 | 40.6242 | -122.4619 | MTR5000071488 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0010121 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1249133 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0010452&numberofmonths=24&showchangehistorylog=1 | 17-0010452 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WILDWOOD-1101 | 103611101 | RECLOSER | 1576 | 20170118 | 1859 | 1649034 | 1152 | Distribution Circuit | Vegetation | Tree - fell into line | 107 | 117426 | 40.3851 | -123.0294 | HWY36EOFWILDWOODSUBSSMTR1008299576 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0010452 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1249468 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0010844&numberofmonths=24&showchangehistorylog=1 | 17-0010844 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WILDWOOD-1101 | 103611101 | OTHER | WIREDOWN2SPSSOFMTR1008299576 | 20170118 | 2157 | 1649972 | 1248 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 19544 | 40.4135 | -123.0607 | 2SPANSSSOFMTR1008299576 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010844 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1249807 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0010851&numberofmonths=24&showchangehistorylog=1 | 17-0010851 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | CEDAR CREEK-1101 | 103321101 | FUSE | 8159 | 20170119 | 1145 | 1651052 | 1705 | Distribution Circuit | Equipment Failure/Involved | Overhead | 94 | 157640 | 40.8612 | -121.9174 | 6PLD8159SSOF8085 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010851 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1249813 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011583&numberofmonths=24&showchangehistorylog=1 | 17-0011583 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CEDAR CREEK-1101 | 103321101 | FUSE | 4881 | 20170119 | 1923 | 1653273 | 2709 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 21672 | 40.7865 | -121.9007 | 12PNOFFUCO4881 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011583 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1250441 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0010776&numberofmonths=24&showchangehistorylog=1 | 17-0010776 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1101 | 103201101 | RECLOSER | 98174 | 20170119 | 1001 | 1650579 | 8944 | Distribution Circuit | Vegetation | Tree - fell into line | 458 | 2592877 | 39.6081 | -121.0754 | 2SPANSLDSIDEFUCO13841ONMAINLINE10EOF885752SSOF88575 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010776 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Multi-Fault | 1249762 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0010850&numberofmonths=24&showchangehistorylog=1 | 17-0010850 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | CHESTER-1102 | 103181102 | FUSE | 9337 | 20170119 | 943 | 1650512 | 237 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 1970 | 40.2951 | -121.2415 | WSHWY36OPPWATSONRD | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0010850 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1249812 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011106&numberofmonths=24&showchangehistorylog=1 | 17-0011106 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WILDWOOD-1101 | 103611101 | TRANSFORMER | 117065039030 | 20170119 | 1845 | 1651932 | 1155 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 4575 | 40.3998 | -123.0549 | WILDWOODRDESPLATINA96076 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011106 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Open Circuit | 1250014 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011415&numberofmonths=24&showchangehistorylog=1 | 17-0011415 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BURNEY-1101 | 103311101 | FUSE | 9251 | 20170120 | 1003 | 1653620 | 196 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 392 | 40.8634 | -121.7219 | 3SPANSSSOF7838 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on object | 17-0011415 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1250299 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011812&numberofmonths=24&showchangehistorylog=1 | 17-0011812 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | CEDAR CREEK-1101 | 103321101 | FUSE | 1635 | 20170120 | 1711 | 1655174 | 5360 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 187737 | 40.908 | -121.9112 | 10SPANSSOURCESIDEOFFUCO8427 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0011812 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1250641 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011380&numberofmonths=24&showchangehistorylog=1 | 17-0011380 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | COTTONWOOD-1103 | 102931103 | RECLOSER | 9072 | 20170120 | 812 | 1653526 | 464 | Distribution Circuit | Vegetation | Tree - fell into line | 287 | 128458 | 40.3378 | -122.3717 | ReginatoAaron1820METER1008364183 | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011380 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1250281 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011750&numberofmonths=24&showchangehistorylog=1 | 17-0011750 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | KANAKA-1101 | 103221101 | OTHER | WIREDOWN | 20170120 | 1445 | 1654952 | 1033 | Distribution Circuit | Equipment Failure/Involved | Overhead | 179 | 21676 | 39.5465 | -121.3874 | 1SPANSSOFSW1417 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011750 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1250581 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011771&numberofmonths=24&showchangehistorylog=1 | 17-0011771 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1104 | 103521104 | OTHER | WIREDOWN4SPANSNOF5221 | 20170120 | 1854 | 1655074 | 160 | Distribution Circuit | Vegetation | Tree - fell into line | 983 | 24544 | 40.5815 | -122.302 | 4SPANSNOF5221 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011771 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1250602 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011171&numberofmonths=24&showchangehistorylog=1 | 17-0011171 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ORO FINO-1102 | 103031102 | RECLOSER | 2560 | 20170120 | 412 | 1652273 | 702 | Distribution Circuit | Vegetation | Tree - fell into line | 561 | 327080 | 39.8888 | -121.6648 | PowersDave249912SPSSREG16HWY3212SPANSSSOF2040 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011171 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1250083 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011760&numberofmonths=24&showchangehistorylog=1 | 17-0011760 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | ORO FINO-1102 | 103031102 | OTHER | WIREDOWN | 20170120 | 1618 | 1655046 | 1188 | Distribution Circuit | Vegetation | Tree - branch fell on line | 316 | 368832 | 39.9994 | -121.6306 | HWY3225MIWOFHWYMARKER33BET48211423 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011760 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1250591 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011326&numberofmonths=24&showchangehistorylog=1 | 17-0011326 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | PIT NO 3-2101 | 103732101 | RECLOSER | 1482 | 20170120 | 810 | 1653191 | 9058 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 85733 | 40.9986 | -121.7471 | BET4445AND8497 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0011326 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1250223 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011653&numberofmonths=24&showchangehistorylog=1 | 17-0011653 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | PIT NO 5-1101 | 101321101 | RECLOSER | 1606 | 20170120 | 1311 | 1654321 | 8844 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 344374 | 41.0191 | -121.9095 | MULTIPLELOCATIONSBEYONDLR1606 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011653 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1250503 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011755&numberofmonths=24&showchangehistorylog=1 | 17-0011755 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | PIT NO 5-1101 | 101321101 | RECLOSER | 1618 | 20170120 | 1848 | 1655023 | 7210 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 7210 | 40.9885 | -121.9742 | SEVERALLOCATIONSBET16183881 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011755 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1250586 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011986&numberofmonths=24&showchangehistorylog=1 | 17-0011986 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | PIT NO 5-1101 | 101321101 | RECLOSER | 1658 | 20170120 | 1958 | 1655969 | 2953 | Distribution Circuit | Vegetation | Tree - bark fell into line | 12 | 35206 | 40.9922 | -121.9705 | REEDYCAMPRDWOFHAGENFLATRD | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011986 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1250803 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012538&numberofmonths=24&showchangehistorylog=1 | 17-0012538 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | PIT NO 5-1101 | 101321101 | JUMPER | WIREDWN11SPLDSOFUSE8379 | 20170120 | 1958 | 1657663 | 5593 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 33558 | 40.9906 | -121.9179 | BooneStan143511spansldside8379fuses | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012538 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1251358 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011156&numberofmonths=24&showchangehistorylog=1 | 17-0011156 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | STILLWATER-1101 | 103561101 | RECLOSER | 48950 | 20170120 | 310 | 1652103 | 518 | Distribution Circuit | Vegetation | Tree - fell into line | 626 | 146318 | 40.7039 | -122.3364 | BROKENPOLEWIREDOWN1PNOF4701TREEDOWNATFUCO7133 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0011156 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1250067 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011293&numberofmonths=24&showchangehistorylog=1 | 17-0011293 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | STILLWATER-1101 | 103561101 | JUMPER | OJSLBFEEDING7133 | 20170120 | 405 | 1653087 | 592 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 4144 | 40.7184 | -122.3308 | SSOF7133ONSINGLEPHASE | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011293 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1250192 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011675&numberofmonths=24&showchangehistorylog=1 | 17-0011675 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER | 1640 | 20170120 | 1543 | 1654632 | 3102 | Distribution Circuit | Vegetation | Tree - fell into line | 168 | 800762 | 40.3543 | -121.5766 | 1SPANSSOF3097 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011675 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Multi-Fault | 1250524 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012368&numberofmonths=24&showchangehistorylog=1 | 17-0012368 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | GIRVAN-1101 | 103401101 | FUSE | 96125 | 20170121 | 2025 | 1657241 | 337 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 16176 | 40.5419 | -122.4827 | 15390MIDDLETOWNPARKRD | Partly Cloudy-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012368 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1251186 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013567&numberofmonths=24&showchangehistorylog=1 | 17-0013567 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 1875 | 20170122 | 2355 | 1662593 | 847 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 35574 | 39.4363 | -121.326 | 5PSSMTR100788641 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013567 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1252387 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013702&numberofmonths=24&showchangehistorylog=1 | 17-0013702 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | GANSNER-1101 | 103021101 | FUSE | 18719 | 20170122 | 1912 | 1662164 | 1098 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 18666 | 39.9238 | -121.0771 | MTR5000120240 | Overcast-Fog-Snow-Below 32 F | Crossarm, Wood | Broken, wire on ground | 17-0013702 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1252504 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013557&numberofmonths=24&showchangehistorylog=1 | 17-0013557 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KANAKA-1101 | 103221101 | OTHER | WIREDOWN | 20170122 | 2224 | 1662615 | 971 | Distribution Circuit | Vegetation | Tree - fell into line | 458 | 64158 | 39.5171 | -121.268 | WIREDOWNHOTONMAINLINELOCBET910996851PSSOF91099 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013557 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1252375 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012653&numberofmonths=24&showchangehistorylog=1 | 17-0012653 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WYANDOTTE-1107 | 102911107 | RECLOSER | 1510 | 20170122 | 300 | 1658314 | 622 | Distribution Circuit | Vegetation | Tree - fell into line | 444 | 179089 | 39.497 | -121.4452 | 4SPANSLDSIDEOF4011 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012653 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1251475 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013588&numberofmonths=24&showchangehistorylog=1 | 17-0013588 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ORO LOMA-1102 | 255371102 | RECLOSER | 2560 | 20170123 | 517 | 1662842 | 568 | Distribution Circuit | Vegetation | Tree - fell into line | 561 | 154169 | 39.8888 | -121.6648 | PowersDave2499BEYONDFUSES1945 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013588 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1252412 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013829&numberofmonths=24&showchangehistorylog=1 | 17-0013829 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | PIT NO 3-2101 | 103732101 | RECLOSER | 1386 | 20170123 | 903 | 1663345 | 721 | Distribution Circuit | Environmental/External | Ice or snow | 64 | 45652 | 41.0214 | -121.6772 | 1PLD3681 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0013829 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1252603 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013629&numberofmonths=24&showchangehistorylog=1 | 17-0013629 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | STILLWATER-1101 | 103561101 | FUSE | 7145 | 20170123 | 632 | 1662910 | 333 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 8991 | 40.7249 | -122.3215 | MTR1007279920 | Overcast-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0013629 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1252450 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018641&numberofmonths=24&showchangehistorylog=1 | 17-0018641 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BIG MEADOWS-2101 | 102812101 | RECLOSER | 2248 | 20170207 | 1400 | 1680318 | 136 | Distribution Circuit | Equipment Failure/Involved | Overhead | 975 | 132600 | 40.1705 | -121.0807 | WSIDEOFSW433 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018641 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1256411 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018423&numberofmonths=24&showchangehistorylog=1 | 17-0018423 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KANAKA-1101 | 103221101 | FUSE | 9635 | 20170207 | 419 | 1677732 | 960 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 5172 | 39.5208 | -121.2486 | 282BAMFORDWAY | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018423 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1256246 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018327&numberofmonths=24&showchangehistorylog=1 | 17-0018327 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1104 | 103521104 | FUSE | 11579 | 20170207 | 425 | 1677761 | 769 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 9228 | 40.5637 | -122.2863 | MTR5000074531 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0018327 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1256163 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018125&numberofmonths=24&showchangehistorylog=1 | 17-0018125 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WYANDOTTE-1103 | 102911103 | RECLOSER | 77578 | 20170207 | 418 | 1677739 | 744 | Distribution Circuit | 3rd Party | Vehicle | 3403 | 883011 | 39.5045 | -121.4987 | MEYERSRANCHANDOLIVEHWYSWITCH6619ONGROUND | Overcast-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0018125 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Multi-Fault | 1255988 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018747&numberofmonths=24&showchangehistorylog=1 | 17-0018747 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | WYANDOTTE-1103 | 102911103 | FUSE | 5437 | 20170207 | 1816 | 1680856 | 996 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1278 | 39.6326 | -121.4014 | MaysSean2497treerippedlinedown | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018747 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1256495 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018097&numberofmonths=24&showchangehistorylog=1 | 17-0018097 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WYANDOTTE-1107 | 102911107 | FUSE | 535 | 20170207 | 231 | 1677406 | 451 | Distribution Circuit | Vegetation | Tree - fell into line | 90 | 21054 | 39.4968 | -121.4453 | MTR1007885818 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018097 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1255953 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0019391&numberofmonths=24&showchangehistorylog=1 | 17-0019391 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | ANTLER-1101 | 103271101 | OTHER | WIREDOWNSSMTR1009720193 | 20170209 | 1014 | 1683059 | 232 | Distribution Circuit | Vegetation | Tree - fell into line | 957 | 26340 | 40.8168 | -122.3293 | 3PSSOFMTR1009720193 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019391 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Open Circuit | 1256936 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024762&numberofmonths=24&showchangehistorylog=1 | 17-0024762 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BIG MEADOWS-2101 | 102812101 | FUSE | 18127 | 20170220 | 2139 | 1706186 | 1201 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 25221 | 40.1501 | -120.789 | 9SPANSSSSIDEOFEOLBEYOND18127 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024762 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1261731 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025138&numberofmonths=24&showchangehistorylog=1 | 17-0025138 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BIG MEADOWS-2101 | 102812101 | RECLOSER | 2510 | 20170220 | 1857 | 1708664 | 2655 | Distribution Circuit | Vegetation | Tree - fell into line | 84 | 222027 | 40.2105 | -121.1644 | LDSIDEOFTPOLE515INVICINITYOFMTR10086830755SOF18597LDSIDEOF1809BET463927 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025138 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Multi-Fault | 1262057 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023920&numberofmonths=24&showchangehistorylog=1 | 17-0023920 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | COTTONWOOD-1101 | 102931101 | FUSE | 6005 | 20170220 | 1614 | 1703746 | 1216 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 2789 | 40.3235 | -122.4296 | MTR1008366677 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023920 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1260894 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024697&numberofmonths=24&showchangehistorylog=1 | 17-0024697 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | EAST QUINCY-1101 | 102551101 | FUSE | 3141 | 20170220 | 2149 | 1706525 | 1058 | Distribution Circuit | Vegetation | Tree - fell into line | 180 | 47934 | 39.9288 | -120.8937 | 2535THST | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024697 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1261664 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024102&numberofmonths=24&showchangehistorylog=1 | 17-0024102 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER | 1640 | 20170220 | 2042 | 1705973 | 3975 | Distribution Circuit | Vegetation | Tree - fell into line | 168 | 615828 | 40.3543 | -121.5766 | MULTIPLEDAMAGELOCATIONSLDSIDEOFLR1640 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0024102 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1261066 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024889&numberofmonths=24&showchangehistorylog=1 | 17-0024889 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BIG MEADOWS-2101 | 102812101 | FUSE | 18607 | 20170221 | 521 | 1707440 | 3181 | Distribution Circuit | Vegetation | Tree - fell into line | 90 | 206504 | 40.1499 | -120.9348 | POLE29232POLESSOUTHWESTOFMTR1008298614 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024889 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Three Phase Fault | 1261863 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025633&numberofmonths=24&showchangehistorylog=1 | 17-0025633 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | BUCKS CREEK-1103 | 102211103 | RECLOSER | 2414 | 20170221 | 28 | 1710770 | 3709 | Distribution Circuit | Equipment Failure/Involved | Overhead | 314 | 1164626 | 39.8921 | -121.2043 | 2SPANSSSOF881652SPANSSSOF18617 | Overcast-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0025633 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1262458 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025092&numberofmonths=24&showchangehistorylog=1 | 17-0025092 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1101 | 103201101 | OTHER | WIREDOWN | 20170221 | 1117 | 1708329 | 621 | Distribution Circuit | Vegetation | Tree - fell into line | 358 | 221997 | 39.6393 | -121.0455 | 22SPANSLDSIDEMTR1007888884 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0025092 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Open Circuit | 1262023 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025118&numberofmonths=24&showchangehistorylog=1 | 17-0025118 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | GANSNER-1101 | 103021101 | FUSE | 3067 | 20170221 | 1250 | 1708599 | 1633 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 11431 | 39.9326 | -121.061 | 5SPANSNOF3067 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025118 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1262039 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025080&numberofmonths=24&showchangehistorylog=1 | 17-0025080 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | GRAYS FLAT-0401 | 102530401 | FUSE | 1787 | 20170221 | 938 | 1708126 | 2027 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 24324 | 40.0161 | -121.0868 | 2SPANSSSOFMTR1009119930 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025080 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1262016 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025128&numberofmonths=24&showchangehistorylog=1 | 17-0025128 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | GRAYS FLAT-0401 | 102530401 | FUSE | 3079 | 20170221 | 702 | 1708248 | 666 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 26640 | 40.0218 | -121.0628 | TRANSMISSIONPOLE1810ANDPOLE1811 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0025128 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1262047 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024936&numberofmonths=24&showchangehistorylog=1 | 17-0024936 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KANAKA-1101 | 103221101 | FUSE | 1811 | 20170221 | 210 | 1707259 | 2330 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 22708 | 39.4456 | -121.2771 | MTR1007460274 | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024936 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1261910 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024980&numberofmonths=24&showchangehistorylog=1 | 17-0024980 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KANAKA-1101 | 103221101 | FUSE | 1997 | 20170221 | 119 | 1707121 | 2131 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 17048 | 39.524 | -121.2954 | 4SPANSSSOFMTR1007550543 | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024980 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1261938 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025199&numberofmonths=24&showchangehistorylog=1 | 17-0025199 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | SPANISH CREEK-4401 | 103104401 | OTHER | WIREDOWN3SPANSLDSIDEOF18129 | 20170221 | 547 | 1707859 | 753 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 19179 | 40.147 | -120.79 | 3SPANSLDSIDEOF18129 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025199 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1262100 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025267&numberofmonths=24&showchangehistorylog=1 | 17-0025267 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | SPANISH CREEK-4401 | 103104401 | FUSE | 3051 | 20170221 | 1752 | 1709219 | 2630 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2630 | 40.1205 | -120.8227 | 1SPANLDSIDEOF3051 | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025267 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Three Phase Fault | 1262168 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024840&numberofmonths=24&showchangehistorylog=1 | 17-0024840 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | VOLTA-1102 | 102541102 | FUSE | 10437 | 20170221 | 230 | 1707228 | 612 | Distribution Circuit | Vegetation | Tree - fell into line | 1167 | 163416 | 40.4905 | -121.8867 | ColgateCalem1959RCO10473 | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 17-0024840 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1261810 | PW | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037564&numberofmonths=24&showchangehistorylog=1 | 17-0037564 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CENTERVILLE-1101 | 102021101 | TRIP-SAVER | 1243 | 20170406 | 2224 | 1748364 | 679 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 25918 | 39.7901 | -121.6559 | MTR1009801967 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037564 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1271786 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037446&numberofmonths=24&showchangehistorylog=1 | 17-0037446 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | JESSUP-1102 | 103441102 | RECLOSER | 1550 | 20170406 | 2303 | 1748675 | 345 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1408 | 150746 | 40.4471 | -122.3187 | 1stpolewofLR76068 | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037446 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1271660 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037632&numberofmonths=24&showchangehistorylog=1 | 17-0037632 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KANAKA-1101 | 103221101 | RECLOSER | 65606 | 20170406 | 2304 | 1748789 | 1365 | Distribution Circuit | Vegetation | Tree - fell into line | 425 | 330489 | 39.5291 | -121.2838 | MTR1009397333 | Overcast-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0037632 | OH | Sus | 0 | yes | 2017 | APR | Yes | Three Phase Fault | 1271853 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037563&numberofmonths=24&showchangehistorylog=1 | 17-0037563 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | PARADISE-1103 | 102831103 | FUSE | 17469 | 20170406 | 2224 | 1748319 | 699 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 19799 | 39.7461 | -121.6434 | AngelMichael1769Foothillrdmeter1007907829 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037563 | OH | Sus | 0 | yes | 2017 | APR | Yes | Force Out | 1271785 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0038086&numberofmonths=24&showchangehistorylog=1 | 17-0038086 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1101 | 103201101 | FUSE | 1953 | 20170407 | 1900 | 1751570 | 1120 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 3360 | 39.5767 | -121.1007 | 5LDSIDEOF1953 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0038086 | OH | Sus | 0 | yes | 2017 | APR | Yes | Three Phase Fault | 1272145 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037544&numberofmonths=24&showchangehistorylog=1 | 17-0037544 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | COTTONWOOD-1101 | 102931101 | FUSE | 7185 | 20170407 | 201 | 1749183 | 494 | Distribution Circuit | Vegetation | Tree - branch fell on line | 85 | 9928 | 40.3851 | -122.3213 | 1SSSOFMTR1006279513 | Overcast-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037544 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1271764 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037693&numberofmonths=24&showchangehistorylog=1 | 17-0037693 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KANAKA-1101 | 103221101 | FUSE | 799 | 20170407 | 857 | 1750170 | 523 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 12029 | 39.59 | -121.277 | ATMTR1009361023 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037693 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Line | 1271898 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037522&numberofmonths=24&showchangehistorylog=1 | 17-0037522 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1103 | 102831103 | FUSE | 7025 | 20170407 | 11 | 1748900 | 514 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 1542 | 39.7447 | -121.6266 | 2SLDSOF7025 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037522 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1271739 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037584&numberofmonths=24&showchangehistorylog=1 | 17-0037584 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1103 | 102831103 | FUSE | 4665 | 20170407 | 148 | 1749167 | 544 | Distribution Circuit | Vegetation | Tree - fell into line | 73 | 19312 | 39.7625 | -121.6287 | BischelJason17731007694429 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037584 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1271807 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037908&numberofmonths=24&showchangehistorylog=1 | 17-0037908 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1103 | 102831103 | RECLOSER | 2488 | 20170407 | 1220 | 1750770 | 506 | Distribution Circuit | Vegetation | Tree - fell into line | 769 | 79028 | 39.7411 | -121.6278 | 1SPANLDSIDEOF2488 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037908 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1272034 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037572&numberofmonths=24&showchangehistorylog=1 | 17-0037572 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | WYANDOTTE-1103 | 102911103 | FUSE | 13751 | 20170407 | 19 | 1749374 | 514 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 4112 | 39.6335 | -121.3973 | 5SPANSLDSIDEOFFUCO13751 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037572 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1271794 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0085339&numberofmonths=24&showchangehistorylog=1 | 17-0085339 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BIG BEND-1101 | 103751101 | FUSE | 2851 | 20171008 | 2012 | 1893777 | 943 | Distribution Circuit | Vegetation | Tree - fell into line | 64 | 60352 | 39.7857 | -121.5063 | MTR1007635265 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085339 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1306790 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0085303&numberofmonths=24&showchangehistorylog=1 | 17-0085303 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CENTERVILLE-1101 | 102021101 | RECLOSER | 2592 | 20171008 | 2015 | 1893833 | 372 | Distribution Circuit | Equipment Failure/Involved | Overhead | 409 | 134500 | 39.7889 | -121.6577 | MTR50000690056 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085303 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Line | 1306750 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0085263&numberofmonths=24&showchangehistorylog=1 | 17-0085263 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1102 | 103201102 | RECLOSER | 1064 | 20171008 | 2039 | 1893816 | 2591 | Distribution Circuit | Vegetation | Tree - branch fell on line | 200 | 100195 | 39.482 | -121.2419 | 1PWOF5887 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085263 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1306710 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0085359&numberofmonths=24&showchangehistorylog=1 | 17-0085359 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE | 1835 | 20171008 | 2129 | 1893943 | 2675 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 22535 | 39.4719 | -121.2734 | MTR1006741869 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085359 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1306812 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0085276&numberofmonths=24&showchangehistorylog=1 | 17-0085276 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | CLARK ROAD-1102 | 103091102 | FUSE | 17483 | 20171008 | 2255 | 1894161 | 2535 | Distribution Circuit | Vegetation | Tree - fell into line | 152 | 160479 | 39.6278 | -121.5282 | ONHARDTAP8SOF17483MTR1007767783 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085276 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Force Out | 1306723 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0085039&numberofmonths=24&showchangehistorylog=1 | 17-0085039 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | DESCHUTES-1101 | 103351101 | FUSE | 2593 | 20171008 | 639 | 1892952 | 581 | Distribution Circuit | Vegetation | Tree - fell into line | 94 | 22340 | 40.6873 | -122.0432 | 3SPANSLDSIDEOFMTR5000018326 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0085039 | OH | Sus | 31355701 | yes | 2017 | OCT | Yes | Line to Ground | 1306495 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0085314&numberofmonths=24&showchangehistorylog=1 | 17-0085314 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1103 | 102831103 | FUSE | 1289 | 20171008 | 1917 | 1893731 | 1738 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 50577 | 39.7476 | -121.6268 | MTR1007884116 | Clear-32-90 F | Pole-Wood | Broken, wire on object | 17-0085314 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Force Out | 1306763 | PW | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0085504&numberofmonths=24&showchangehistorylog=1 | 17-0085504 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1103 | 102831103 | JUMPER | HOTWIREDOWN1SSOFMTR1007551383 | 20171008 | 2219 | 1896055 | 2125 | Distribution Circuit | Vegetation | Tree - fell into line | 772 | 42839 | 39.7367 | -121.6466 | 1SSOFMTR1009863950 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085504 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1306959 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0085265&numberofmonths=24&showchangehistorylog=1 | 17-0085265 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1104 | 102831104 | FUSE | 27187 | 20171008 | 1839 | 1894153 | 761 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 6849 | 39.7467 | -121.5891 | 1LDSIDEOFFUSES | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085265 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Line | 1306712 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0085196&numberofmonths=24&showchangehistorylog=1 | 17-0085196 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | WYANDOTTE-1103 | 102911103 | RECLOSER | 1974 | 20171008 | 2039 | 1893810 | 325 | Distribution Circuit | Vegetation | Tree - fell into line | 616 | 181992 | 39.6394 | -121.4297 | MTR1007241162BALDROCK1SOFMTR50000136224 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085196 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Line | 1306641 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0085524&numberofmonths=24&showchangehistorylog=1 | 17-0085524 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | GANSNER-1101 | 103021101 | JUMPER | WIREDOWN2SPANSLDSIDEOF3491 | 20171009 | 834 | 1896296 | 305 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 7625 | 40.0153 | -120.9652 | WIREDOWN2SPANSLDSIDEOF3491 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085524 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1306970 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0088893&numberofmonths=24&showchangehistorylog=1 | 17-0088893 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KANAKA-1101 | 103221101 | RECLOSER | 83288 | 20171020 | 54 | 1904944 | 594 | Distribution Circuit | Vegetation | Tree - fell into line | 214 | 78976 | 39.5275 | -121.2862 | WoodmanseeMatt1751treetookprimarywiredown | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0088893 | OH | Sus | 43198926 | yes | 2017 | OCT | Yes | Line to Line | 1309474 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0088896&numberofmonths=24&showchangehistorylog=1 | 17-0088896 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1101 | 102831101 | FUSE | 693 | 20171020 | 335 | 1905198 | 777 | Distribution Circuit | Vegetation | Tree - bark fell into line | 59 | 45843 | 39.7835 | -121.6001 | MTR1006285610 | Partly Cloudy-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0088896 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1309477 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0088953&numberofmonths=24&showchangehistorylog=1 | 17-0088953 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1104 | 102831104 | FUSE | 17291 | 20171020 | 658 | 1905445 | 597 | Distribution Circuit | Vegetation | Tree - grew into line | 16 | 9552 | 39.7376 | -121.5937 | 1SLDSIDEOF17291 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0088953 | OH | Sus | 43198933 | yes | 2017 | OCT | Yes | Line to Ground | 1309532 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0099731&numberofmonths=24&showchangehistorylog=1 | 17-0099731 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | ORO FINO-1102 | 103031102 | FUSE | 1945 | 20171204 | 1130 | 1935634 | 628 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 46472 | 40.0942 | -121.5178 | AngelMichael176915spansnof69213buttemeadows | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0099731 | OH | Sus | 31368299 | yes | 2017 | DEC | Yes | Line to Ground | 1317481 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0102019&numberofmonths=24&showchangehistorylog=1 | 17-0102019 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | BUCKS CREEK-1103 | 102211103 | RECLOSER | 2414 | 20171216 | 924 | 1944580 | 3250 | Distribution Circuit | Vegetation | Tree - fell into line | 314 | 875514 | 39.8921 | -121.2043 | BET18661AND18449LDSIDEOFFUCO1129 | Clear-Below 32 F | Pole-Wood | Broken, wire on ground | 17-0102019 | OH | Sus | 0 | yes | 2017 | DEC | Yes | Line to Line | 1319929 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0102098&numberofmonths=24&showchangehistorylog=1 | 17-0102098 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | VOLTA-1102 | 102541102 | OTHER | WIREDOWN1SPLDSIDEOF1553 | 20171216 | 1206 | 1944712 | 221 | Distribution Circuit | Vegetation | Tree - fell into line | 1076 | 155662 | 40.5042 | -121.8138 | FUCO1553 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0102098 | OH | Sus | 0 | yes | 2017 | DEC | Yes | Line to Ground | 1320008 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0023263&numberofmonths=24&showchangehistorylog=1 | 18-0023263 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BURNEY-1101 | 103311101 | RECLOSER | 1322 | 20180316 | 644 | 45248 | 188 | Distribution Circuit | Environmental/External | Ice or snow | 66 | 8092 | 40.913 | -121.6469 | 1SPANLDSIDEOFFUSES10115 | Overcast-Fog-Snow-Below 32 F | Crossarm, Wood | Broken, wire on ground | 18-0023263 | OH | Sus | 31384484 | yes | 2018 | MAR | Yes | Line to Ground | 1336159 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0023329&numberofmonths=24&showchangehistorylog=1 | 18-0023329 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | PIT NO 3-2101 | 103732101 | OCB | 21012 | 20180316 | 954 | 45480 | 466 | Distribution Circuit | Vegetation | Tree - branch fell on line | 155 | 57958 | 40.9981 | -121.7476 | 2SPANSSSOF1360 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023329 | OH | Sus | 43302933 | yes | 2018 | MAR | Yes | Line to Ground | 1336222 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0023409&numberofmonths=24&showchangehistorylog=1 | 18-0023409 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | RISING RIVER-1101 | 103551101 | RECLOSER | 1530 | 20180316 | 1013 | 45549 | 429 | Distribution Circuit | Vegetation | Tree - branch fell on line | 536 | 123960 | 40.8713 | -121.5539 | 19558HWY89 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023409 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1336272 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0065462&numberofmonths=24&showchangehistorylog=1 | 18-0065462 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | GIRVAN-1101 | 103401101 | FUSE | 3489 | 20180728 | 449 | 146126 | 14779 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 10 | 80 | 40.505 | -122.5476 | LDSIDEOF3489 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 18-0065462 | OH | Sus | 0 | No | 2018 | JUL | Yes | Force Out | 1368104 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0065468&numberofmonths=24&showchangehistorylog=1 | 18-0065468 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | GIRVAN-1101 | 103401101 | FUSE | 4191 | 20180728 | 449 | 146134 | 14874 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 2 | 30 | 40.5279 | -122.5567 | LDSIDEOF4191 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 18-0065468 | OH | Sus | 0 | No | 2018 | JUL | Yes | Force Out | 1368105 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0065470&numberofmonths=24&showchangehistorylog=1 | 18-0065470 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | GIRVAN-1101 | 103401101 | FUSE | 4855 | 20180728 | 449 | 146141 | 14885 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 31 | 775 | 40.5318 | -122.5561 | LDSIDEOF4855 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 18-0065470 | OH | Sus | 0 | No | 2018 | JUL | Yes | Force Out | 1368107 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0066705&numberofmonths=24&showchangehistorylog=1 | 18-0066705 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | GIRVAN-1101 | 103401101 | FUSE | 1861 | 20180728 | 449 | 148785 | 13955 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 18 | 72 | 40.5008 | -122.57 | MULTIPLELOCATIONSBEYOND1861 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0066705 | OH | Sus | 0 | No | 2018 | JUL | Yes | Multi-Fault | 1369023 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0064616&numberofmonths=24&showchangehistorylog=1 | 18-0064616 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WYANDOTTE-1107 | 102911107 | FUSE | 513 | 20180728 | 1808 | 142676 | 232 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 6264 | 39.4954 | -121.4908 | WoodmanseeMatt1751wiredownat85craneave | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0064616 | OH | Sus | 0 | No | 2018 | JUL | Yes | Line to Line | 1367436 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0090193&numberofmonths=24&showchangehistorylog=1 | 18-0090193 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | COTTONWOOD-1101 | 102931101 | FUSE | 5985 | 20181014 | 1123 | 194784 | 397 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 945 | 40.36 | -122.4266 | 4PLDSIDEOFMTR1008363886 | Clear-Strong Winds-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 18-0090193 | OH | Sus | 0 | yes | 2018 | OCT | Yes | Line to Ground | 1385465 | CSO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0098064&numberofmonths=24&showchangehistorylog=1 | 18-0098064 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | BIG BEND-1101 | 103751101 | SWITCH | 1721 | 20181108 | 746 | 212778 | 42326 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 206 | 8647832 | 39.7633 | -121.5224 | CAMPFIRE | Clear-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 18-0098064 | OH | Sus | 0 | yes | 2018 | NOV | Yes | None | 1391837 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0098208&numberofmonths=24&showchangehistorylog=1 | 18-0098208 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | CLARK ROAD-1102 | 103091102 | RECLOSER | 47006 | 20181108 | 1044 | 211509 | 20092 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 148 | 2672214 | 39.6987 | -121.5742 | CAMPFIRE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0098208 | OH | Sus | 0 | yes | 2018 | NOV | Yes | Force Out | 1391419 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0099384&numberofmonths=24&showchangehistorylog=1 | 18-0099384 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | CLARK ROAD-1102 | 103091102 | FUSE | 815317 | 20181108 | 1050 | 214503 | 10465 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 18 | 188370 | 39.672 | -121.5828 | MULTIPLELOCATIONSLDSIDEOF815317 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 18-0099384 | OH | Sus | 0 | yes | 2018 | NOV | Yes | None | 1392369 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0099388&numberofmonths=24&showchangehistorylog=1 | 18-0099388 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | CLARK ROAD-1102 | 103091102 | JUMPER | OJSONHARDTAP1POLESOF815317 | 20181108 | 1050 | 214521 | 8866 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 2 | 17732 | 39.669 | -121.5821 | MULTIPLELOCATIONSONHARDTAP | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 18-0099388 | OH | Sus | 0 | yes | 2018 | NOV | Yes | Line to Ground | 1392376 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0098438&numberofmonths=24&showchangehistorylog=1 | 18-0098438 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | NOTRE DAME-1104 | 102041104 | TRIP-SAVER | 2537 | 20181108 | 1907 | 211953 | 22615 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 44 | 995060 | 39.7912 | -121.7218 | BISCHEL2498openedtripsaverduetofire | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0098438 | OH | Sus | 0 | yes | 2018 | NOV | Yes | Force Out | 1391519 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0104677&numberofmonths=24&showchangehistorylog=1 | 18-0104677 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ORO FINO-1101 | 103031101 | RECLOSER | 2022 | 20181129 | 114 | 227403 | 171 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1053 | 180063 | 39.8542 | -121.6059 | 1SPANSOUTHOF52315259ONHARDTAP | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | On Ground | 18-0104677 | OH | Sus | 0 | yes | 2018 | NOV | Yes | Line to Ground | 1395992 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005061&numberofmonths=24&showchangehistorylog=1 | 19-0005061 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BIG MEADOWS-2101 | 102812101 | RECLOSER | 2476 | 20190106 | 1147 | 255177 | 760 | Distribution Circuit | Vegetation | Tree - fell into line | 1372 | 622480 | 40.1713 | -121.0871 | BRUNELLEMICHAEL24994spanssourceside18685 | Overcast-Snow-Below 32 F | Crossarm, Wood | Broken, wire on ground | 19-0005061 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1403534 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005266&numberofmonths=24&showchangehistorylog=1 | 19-0005266 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KANAKA-1101 | 103221101 | RECLOSER | 5460 | 20190106 | 1821 | 256415 | 1136 | Distribution Circuit | Vegetation | Tree - fell into line | 457 | 440995 | 39.5444 | -121.1478 | 3SPANSLDSIDEOF5957 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005266 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1403737 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005051&numberofmonths=24&showchangehistorylog=1 | 19-0005051 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ORO FINO-1102 | 103031102 | OTHER | WIREDOWN | 20190106 | 1012 | 255066 | 158 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1086 | 148398 | 39.8877 | -121.6653 | 1SPANEASTOF76008 | Overcast-Fog-Heavy Rain-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0005051 | OH | Sus | 43626761 | yes | 2019 | JAN | Yes | Open Circuit | 1403524 | CSO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005497&numberofmonths=24&showchangehistorylog=1 | 19-0005497 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ORO FINO-1102 | 103031102 | FUSE | 1147 | 20190106 | 2011 | 257518 | 929 | Distribution Circuit | Vegetation | Tree - fell into line | 116 | 107764 | 39.8897 | -121.5781 | 1SLDSIDEOF1147 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005497 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1403946 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005346&numberofmonths=24&showchangehistorylog=1 | 19-0005346 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | PIT NO 5-1101 | 101321101 | RECLOSER | 1606 | 20190106 | 1936 | 257186 | 961 | Distribution Circuit | Environmental/External | Ice or snow | 126 | 93721 | 41.0191 | -121.9095 | brokenswitcharmoverlr1658wiredown4spldside1658 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005346 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Force Out | 1403799 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005794&numberofmonths=24&showchangehistorylog=1 | 19-0005794 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | WYANDOTTE-1103 | 102911103 | OTHER | 5405 | 20190106 | 2255 | 259151 | 895 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 76075 | 39.6801 | -121.3467 | 3SPLDSIDEOF5405 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005794 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Open Circuit | 1404166 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010040&numberofmonths=24&showchangehistorylog=1 | 19-0010040 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | CLARK ROAD-1102 | 103091102 | RECLOSER | 2070 | 20190116 | 1818 | 269193 | 1120 | Distribution Circuit | Vegetation | Tree - fell into line | 403 | 92881 | 39.6565 | -121.5762 | 2SPANSSOUTHOF1689OAKTREETHROUGHLINEWIREDOWN | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | On Ground | 19-0010040 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1406904 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010867&numberofmonths=24&showchangehistorylog=1 | 19-0010867 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CLARK ROAD-1102 | 103091102 | FUSE | 17791 | 20190116 | 2134 | 271174 | 1122 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 28602 | 39.7099 | -121.5235 | ONPOLECAT1STSPANSOFPINEBRAEANDONWENDY1STSPANNOFPINEBRAE | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010867 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1407574 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0009948&numberofmonths=24&showchangehistorylog=1 | 19-0009948 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | GRAYS FLAT-0401 | 102530401 | OTHER | WIREDOWN8SPANSSSOF865983 | 20190116 | 1159 | 266846 | 415 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 12134 | 40.0165 | -121.0565 | 8SPANSSSOF865983 | Overcast-Fog-Drizzle-Strong Winds-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0009948 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1406818 | CSO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010243&numberofmonths=24&showchangehistorylog=1 | 19-0010243 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KANAKA-1101 | 103221101 | RECLOSER | 83288 | 20190116 | 1902 | 270864 | 1427 | Distribution Circuit | Vegetation | Tree - fell into line | 214 | 93211 | 39.5275 | -121.2862 | 1SSOF1997 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010243 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Multi-Fault | 1407108 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010311&numberofmonths=24&showchangehistorylog=1 | 19-0010311 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KANAKA-1101 | 103221101 | RECLOSER | 79226 | 20190116 | 2150 | 271283 | 875 | Distribution Circuit | Vegetation | Tree - fell into line | 1146 | 704347 | 39.5148 | -121.2644 | MAINLINESSFUCO1989 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010311 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1407176 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010386&numberofmonths=24&showchangehistorylog=1 | 19-0010386 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | PARADISE-1104 | 102831104 | FUSE | 17707 | 20190116 | 2313 | 271838 | 1137 | Distribution Circuit | Equipment Failure/Involved | Overhead | 161 | 126335 | 39.7321 | -121.6516 | MTR1008116051 | Overcast-Heavy Rain-Strong Winds-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0010386 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407252 | CSO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011368&numberofmonths=24&showchangehistorylog=1 | 19-0011368 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | BUCKS CREEK-1103 | 102211103 | RECLOSER | 338520 | 20190117 | 834 | 273115 | 1796 | Distribution Circuit | Vegetation | Tree - fell into line | 315 | 517838 | 39.8921 | -121.2043 | 5SOF88165 | Overcast-Fog-Snow-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011368 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407914 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011300&numberofmonths=24&showchangehistorylog=1 | 19-0011300 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WYANDOTTE-1103 | 102911103 | RECLOSER | 1508 | 20190117 | 1659 | 274653 | 641 | Distribution Circuit | 3rd Party | Vehicle | 1365 | 711942 | 39.5046 | -121.4527 | WoodmanseeMatt1751northregulatorpole13869 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 19-0011300 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1407861 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0016836&numberofmonths=24&showchangehistorylog=1 | 19-0016836 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1102 | 103521102 | FUSE | 6857 | 20190202 | 3 | 285901 | 631 | Distribution Circuit | Vegetation | Tree - fell into line | 243 | 7815 | 40.6597 | -122.3291 | 1SPANNORTHOF6857 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0016836 | OH | Sus | 31424435 | yes | 2019 | FEB | Yes | Line to Ground | 1411296 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018159&numberofmonths=24&showchangehistorylog=1 | 19-0018159 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BIG MEADOWS-2101 | 102812101 | RECLOSER | 2476 | 20190204 | 2107 | 291101 | 1025 | Distribution Circuit | Vegetation | Tree - fell into line | 1372 | 645067 | 40.1713 | -121.0871 | MULTIPLELOCATIONBETWEEN24763161 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018159 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1412400 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0017711&numberofmonths=24&showchangehistorylog=1 | 19-0017711 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ORO FINO-1102 | 103031102 | RECLOSER | 2556 | 20190204 | 457 | 289465 | 343 | Distribution Circuit | Vegetation | Tree - fell into line | 181 | 61453 | 39.8903 | -121.5777 | 6SPANSLDSIDEOF17417 | Overcast-Fog-Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0017711 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1412123 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0017942&numberofmonths=24&showchangehistorylog=1 | 19-0017942 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | RISING RIVER-1101 | 103551101 | RECLOSER | 1530 | 20190204 | 1014 | 289947 | 1795 | Distribution Circuit | Vegetation | Tree - fell into line | 536 | 712220 | 40.8713 | -121.5539 | MTR50000022989SPANSSS5995 | Overcast-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0017942 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1412255 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0017688&numberofmonths=24&showchangehistorylog=1 | 19-0017688 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER | 53118 | 20190204 | 225 | 289396 | 621 | Distribution Circuit | Equipment Failure/Involved | Overhead | 784 | 486659 | 40.4011 | -121.875 | MAINLINE1SPLDSIDE850241 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017688 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1412101 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0017998&numberofmonths=24&showchangehistorylog=1 | 19-0017998 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | WYANDOTTE-1103 | 102911103 | FUSE | 1467 | 20190204 | 1157 | 290383 | 325 | Distribution Circuit | Vegetation | Tree - fell into line | 88 | 28600 | 39.6615 | -121.3893 | WoodmanseeMatt1751wiredown10spansldsideoffuco1467 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017998 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1412289 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018269&numberofmonths=24&showchangehistorylog=1 | 19-0018269 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | GIRVAN-1101 | 103401101 | RECLOSER | 323094 | 20190205 | 624 | 291738 | 325 | Distribution Circuit | 3rd Party | Gun Shot | 163 | 47900 | 40.4984 | -122.5727 | LYTLE1785CHURCHSTWOPLATINARDONO | Partly Cloudy-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018269 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1412507 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020401&numberofmonths=24&showchangehistorylog=1 | 19-0020401 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1102 | 103201102 | RECLOSER | 1064 | 20190209 | 1911 | 297357 | 1125 | Distribution Circuit | Vegetation | Tree - fell into line | 202 | 78956 | 39.482 | -121.2419 | 10SPANSSOF5889 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020401 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Three Phase Fault | 1414077 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021674&numberofmonths=24&showchangehistorylog=1 | 19-0021674 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | ANTLER-1101 | 103271101 | RECLOSER | 1376 | 20190212 | 2335 | 301544 | 12306 | Distribution Circuit | Vegetation | Tree - branch fell on line | 67 | 771489 | 40.8524 | -122.3324 | LYTLE17856PEOCO1955STATTONRDLAKEHEAD | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021674 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1415121 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021707&numberofmonths=24&showchangehistorylog=1 | 19-0021707 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | ANTLER-1101 | 103271101 | RECLOSER | 1520 | 20190212 | 2317 | 314747 | 6793 | Distribution Circuit | Vegetation | Tree - branch fell on line | 83 | 563819 | 40.8994 | -122.3862 | SNOWBIRDLN | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0021707 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1417733 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025104&numberofmonths=24&showchangehistorylog=1 | 19-0025104 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | ANTLER-1101 | 103271101 | JUMPER | OJSATSNOWBIRDLNBIGOAKLD | 20190212 | 2317 | 315656 | 9853 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 137942 | 40.9006 | -122.3897 | SparksMarty3864SnowbirdBigOakLn | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025104 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1418181 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025181&numberofmonths=24&showchangehistorylog=1 | 19-0025181 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | ANTLER-1101 | 103271101 | FUSE | 2301 | 20190212 | 2317 | 316031 | 11235 | Distribution Circuit | Environmental/External | Ice or snow | 32 | 359520 | 40.9057 | -122.3864 | LYTLE1785NORTHLAKESHOREDR | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025181 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1418258 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025677&numberofmonths=24&showchangehistorylog=1 | 19-0025677 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | ANTLER-1101 | 103271101 | FUSE | 3319 | 20190212 | 2337 | 317926 | 12212 | Distribution Circuit | Environmental/External | Ice or snow | 99 | 1208988 | 40.8129 | -122.3204 | 1SPANLDSIDE33193SPANSLOADSIDE3319 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025677 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1418723 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024682&numberofmonths=24&showchangehistorylog=1 | 19-0024682 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | COTTONWOOD-1101 | 102931101 | SWITCH | 85689 | 20190212 | 2309 | 314821 | 9426 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 480726 | 40.2749 | -122.4735 | LDSIDEOF85689 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0024682 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1417756 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024710&numberofmonths=24&showchangehistorylog=1 | 19-0024710 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | COTTONWOOD-1102 | 102931102 | FUSE | 2081 | 20190212 | 2242 | 314930 | 6600 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 59400 | 40.3886 | -122.426 | MULTIPLEAREAS | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024710 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1417784 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024712&numberofmonths=24&showchangehistorylog=1 | 19-0024712 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | COTTONWOOD-1102 | 102931102 | FUSE | 5997 | 20190212 | 2242 | 314937 | 8167 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 253177 | 40.3881 | -122.4589 | LDSD5997 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024712 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1417786 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025073&numberofmonths=24&showchangehistorylog=1 | 19-0025073 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | COTTONWOOD-1102 | 102931102 | FUSE | 5405 | 20190212 | 2242 | 315506 | 6569 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 72259 | 40.3838 | -122.4447 | 3113SHANELN | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0025073 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1418148 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021669&numberofmonths=24&showchangehistorylog=1 | 19-0021669 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | COTTONWOOD-1103 | 102931103 | RECLOSER | 1616 | 20190212 | 2329 | 301522 | 5402 | Distribution Circuit | Vegetation | Tree - fell into line | 468 | 2035242 | 40.3561 | -122.3264 | MULTIPLEDAMAGELOCATIONS | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0021669 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1415116 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021680&numberofmonths=24&showchangehistorylog=1 | 19-0021680 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | COTTONWOOD-1103 | 102931103 | RECLOSER | 9072 | 20190212 | 2342 | 301568 | 9452 | Distribution Circuit | Vegetation | Tree - fell into line | 290 | 2662630 | 40.3378 | -122.3717 | SOFMTR1008055772 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021680 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1415127 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022697&numberofmonths=24&showchangehistorylog=1 | 19-0022697 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | COTTONWOOD-1103 | 102931103 | JUMPER | OJGOLDENMEADOWGOLDENDOE | 20190212 | 2329 | 305838 | 5440 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 54400 | 40.2782 | -122.3731 | 17835GOLDENMEADOWTRAIL | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022697 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1415931 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023842&numberofmonths=24&showchangehistorylog=1 | 19-0023842 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | COTTONWOOD-1103 | 102931103 | FUSE | 1369 | 20190212 | 2349 | 311492 | 5526 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 77364 | 40.3327 | -122.3875 | 3RDAND5THSPANSLDSIDEOFFUCO1369 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023842 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Three Phase Fault | 1416982 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024037&numberofmonths=24&showchangehistorylog=1 | 19-0024037 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | COTTONWOOD-1103 | 102931103 | FUSE | 6843 | 20190212 | 2329 | 312121 | 5232 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 181660 | 40.3494 | -122.3265 | LDSIDEOF6843ATMTR1008363452 | Overcast-Fog-Snow-32-90 F | Pole-Wood | Broken, wire on ground | 19-0024037 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1417143 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024173&numberofmonths=24&showchangehistorylog=1 | 19-0024173 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | COTTONWOOD-1103 | 102931103 | FUSE | 6367 | 20190212 | 2329 | 312536 | 5438 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 304528 | 40.2997 | -122.3322 | FROM5LDSIDEOFFUSESTOEOLTOOMANYLOCATIONSTOLIST | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0024173 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1417258 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024689&numberofmonths=24&showchangehistorylog=1 | 19-0024689 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | COTTONWOOD-1103 | 102931103 | JUMPER | OJ | 20190212 | 2329 | 314843 | 6841 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 6841 | 40.2993 | -122.3159 | MTR1008363294 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0024689 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1417764 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021843&numberofmonths=24&showchangehistorylog=1 | 19-0021843 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | DESCHUTES-1101 | 103351101 | RECLOSER | 1380 | 20190212 | 2321 | 301501 | 5446 | Distribution Circuit | Vegetation | Tree - fell into line | 1082 | 2124073 | 40.5607 | -122.1889 | 25281HWY444SPANSLDSIDEOFREGS417327143DERSCHRD28140HWY44 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021843 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1415292 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022438&numberofmonths=24&showchangehistorylog=1 | 19-0022438 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | DESCHUTES-1101 | 103351101 | SWITCH | 9471 | 20190212 | 2321 | 305197 | 9680 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 234492 | 40.5346 | -122.1188 | 20SPANSLDSIDEOF9471 | Overcast-Fog-Snow-32-90 F | Pole-Wood | Broken, wire on ground | 19-0022438 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Multi-Fault | 1415697 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0026190&numberofmonths=24&showchangehistorylog=1 | 19-0026190 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | DESCHUTES-1101 | 103351101 | JUMPER | OJ2SPANSLDSIDEOFMTR1010342071 | 20190212 | 2321 | 319098 | 12320 | Distribution Circuit | Vegetation | Tree - fell into line | 319 | 85814 | 40.5578 | -122.0436 | LDSIDEOFMTR1010342071 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0026190 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1419039 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0026201&numberofmonths=24&showchangehistorylog=1 | 19-0026201 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | FRENCH GULCH-1101 | 103381101 | JUMPER | OJ15173TRINITYMTNRD | 20190212 | 2122 | 319138 | 11251 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 281535 | 40.7293 | -122.6235 | LDSIDEOF15173TRINITYMTNRD | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0026201 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1419046 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0026603&numberofmonths=24&showchangehistorylog=1 | 19-0026603 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | FRENCH GULCH-1101 | 103381101 | JUMPER | OJ15864TRINITYMTNRD | 20190212 | 2315 | 320010 | 13965 | Distribution Circuit | Environmental/External | Ice or snow | 50 | 666330 | 40.7477 | -122.6196 | LDSIDEOF16555TRINITYMTNRD | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0026603 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1419260 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021661&numberofmonths=24&showchangehistorylog=1 | 19-0021661 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | GIRVAN-1101 | 103401101 | RECLOSER | 1330 | 20190212 | 2305 | 301456 | 9607 | Distribution Circuit | Vegetation | Tree - fell into line | 200 | 1654387 | 40.5176 | -122.5059 | PALADEWESLEYmultiplelocationsbeyondopensb346147 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0021661 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1415108 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024070&numberofmonths=24&showchangehistorylog=1 | 19-0024070 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | GIRVAN-1101 | 103401101 | JUMPER | OJSSSOFFMAINLINETWDSMTR1008046102 | 20190212 | 2357 | 312203 | 11203 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 22406 | 40.5318 | -122.4748 | 15821ZEPHYRDR | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 19-0024070 | OH | Sus | 0 | yes | 2019 | FEB | Yes | None | 1417166 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025639&numberofmonths=24&showchangehistorylog=1 | 19-0025639 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | GIRVAN-1101 | 103401101 | FUSE | 1835 | 20190212 | 2305 | 317713 | 9754 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 224342 | 40.5172 | -122.521 | LDSIDEOF1835 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025639 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1418689 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025640&numberofmonths=24&showchangehistorylog=1 | 19-0025640 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | GIRVAN-1101 | 103401101 | FUSE | 3489 | 20190212 | 2305 | 317714 | 11180 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 111800 | 40.505 | -122.5476 | LDSIDEOF3489 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025640 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1418690 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025641&numberofmonths=24&showchangehistorylog=1 | 19-0025641 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | GIRVAN-1101 | 103401101 | FUSE | 5017 | 20190212 | 2305 | 317717 | 9611 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 326774 | 40.5007 | -122.5429 | LDSIDEOF5017 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025641 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1418691 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0026127&numberofmonths=24&showchangehistorylog=1 | 19-0026127 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | GIRVAN-1101 | 103401101 | FUSE | 1837 | 20190212 | 2305 | 318964 | 12277 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 184155 | 40.4547 | -122.6328 | MULTIPLELOCATIONSLDSIDEOF1837 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0026127 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1419006 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0026238&numberofmonths=24&showchangehistorylog=1 | 19-0026238 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | GIRVAN-1101 | 103401101 | FUSE | 2073 | 20190212 | 2305 | 319266 | 12004 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 12004 | 40.4789 | -122.6633 | LDSIDEOF2073 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0026238 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1419067 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021821&numberofmonths=24&showchangehistorylog=1 | 19-0021821 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | GIRVAN-1102 | 103401102 | FUSE | 4407 | 20190212 | 2316 | 302895 | 9687 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 116244 | 40.5869 | -122.4663 | LDSIDEOF4407 | Snow-Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021821 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1415271 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023659&numberofmonths=24&showchangehistorylog=1 | 19-0023659 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | GIRVAN-1102 | 103401102 | FUSE | 9603 | 20190212 | 2356 | 310768 | 5526 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 176832 | 40.5344 | -122.3344 | 6SPANSLDSIDEOF9603 | Snow-Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023659 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1416810 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024143&numberofmonths=24&showchangehistorylog=1 | 19-0024143 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | GIRVAN-1102 | 103401102 | FUSE | 6897 | 20190212 | 132 | 312460 | 5255 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 47295 | 40.5541 | -122.4527 | 6SPANSLDSIDEOFFUCO6897 | Overcast-Fog-Snow-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0024143 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1417235 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021665&numberofmonths=24&showchangehistorylog=1 | 19-0021665 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | JESSUP-1101 | 103441101 | RECLOSER | 41356 | 20190212 | 2312 | 301476 | 10995 | Distribution Circuit | Vegetation | Tree - fell into line | 325 | 2925182 | 40.4772 | -122.4548 | WASSONPHILLIPeverywhere | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021665 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1415112 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021931&numberofmonths=24&showchangehistorylog=1 | 19-0021931 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | JESSUP-1101 | 103441101 | JUMPER | OJ4547HIGHSIDE | 20190212 | 2251 | 303350 | 8382 | Distribution Circuit | Environmental/External | Ice or snow | 103 | 863346 | 40.4782 | -122.4358 | LDSIDE | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021931 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Multi-Fault | 1415364 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024039&numberofmonths=24&showchangehistorylog=1 | 19-0024039 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | JESSUP-1101 | 103441101 | JUMPER | OJSTWDSMTR1008942651 | 20190212 | 2343 | 312125 | 8253 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 8253 | 40.4901 | -122.3584 | MTR1008942651 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024039 | OH | Sus | 0 | yes | 2019 | FEB | Yes | None | 1417144 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024483&numberofmonths=24&showchangehistorylog=1 | 19-0024483 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | JESSUP-1101 | 103441101 | TRIP-SAVER | 2839 | 20190212 | 2343 | 313880 | 9767 | Distribution Circuit | Vegetation | Tree - fell into line | 95 | 848127 | 40.4926 | -122.3677 | MTR1006192668 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0024483 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1417567 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024700&numberofmonths=24&showchangehistorylog=1 | 19-0024700 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | JESSUP-1101 | 103441101 | FUSE | 53313 | 20190212 | 2343 | 314876 | 6886 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 68860 | 40.4891 | -122.3739 | LDSIDEOFFUSES | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024700 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1417773 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024706&numberofmonths=24&showchangehistorylog=1 | 19-0024706 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | JESSUP-1101 | 103441101 | JUMPER | OJSNOFFUCO53313 | 20190212 | 2343 | 314909 | 9591 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 143865 | 40.4896 | -122.3733 | HARDTAPNOFUCO53313 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024706 | OH | Sus | 0 | yes | 2019 | FEB | Yes | None | 1417780 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025315&numberofmonths=24&showchangehistorylog=1 | 19-0025315 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | JESSUP-1101 | 103441101 | FUSE | 6767 | 20190212 | 2342 | 316780 | 9693 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 67851 | 40.4783 | -122.4433 | ALLENDAVE19656654HIGHVALLEYRD | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025315 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1418368 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025638&numberofmonths=24&showchangehistorylog=1 | 19-0025638 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | JESSUP-1101 | 103441101 | JUMPER | OJSSTO5937 | 20190212 | 2312 | 317688 | 11230 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 33690 | 40.4738 | -122.4732 | 5937 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0025638 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1418688 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025656&numberofmonths=24&showchangehistorylog=1 | 19-0025656 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | JESSUP-1101 | 103441101 | JUMPER | OJ6SPANSSSOFCGC118661241120 | 20190212 | 2312 | 317766 | 10868 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 76076 | 40.4638 | -122.4824 | CGC118661241120 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025656 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1418704 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025699&numberofmonths=24&showchangehistorylog=1 | 19-0025699 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | JESSUP-1101 | 103441101 | FUSE | 4089 | 20190212 | 2312 | 318005 | 10983 | Distribution Circuit | Environmental/External | Ice or snow | 9 | 98847 | 40.4805 | -122.4959 | MULTIPLELOCATIONSLDSIDEOFFUCO4089 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025699 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1418745 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0026231&numberofmonths=24&showchangehistorylog=1 | 19-0026231 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | JESSUP-1101 | 103441101 | JUMPER | OJ1EOF88301 | 20190212 | 2356 | 319213 | 10789 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 10789 | 40.491 | -122.4531 | 88301 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0026231 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1419060 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024592&numberofmonths=24&showchangehistorylog=1 | 19-0024592 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | JESSUP-1102 | 103441102 | FUSE | 2377 | 20190212 | 2303 | 314542 | 8372 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 125580 | 40.4598 | -122.3991 | LDSIDEOF2377 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0024592 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1417667 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025250&numberofmonths=24&showchangehistorylog=1 | 19-0025250 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | JESSUP-1102 | 103441102 | SWITCH | 1995 | 20190212 | 2303 | 316487 | 8427 | Distribution Circuit | Vegetation | Tree - fell into line | 111 | 935397 | 40.4689 | -122.4018 | MTR1008968850 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0025250 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1418320 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023874&numberofmonths=24&showchangehistorylog=1 | 19-0023874 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | JESSUP-1103 | 103441103 | JUMPER | OJ1SPANSEOMTR5000009730 | 20190212 | 2358 | 311617 | 3604 | Distribution Circuit | Vegetation | Tree - branch fell on line | 20 | 72080 | 40.4673 | -122.3363 | 1SPANNOMTR5000009730 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023874 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1417008 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022436&numberofmonths=24&showchangehistorylog=1 | 19-0022436 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1103 | 103521103 | SWITCH | 11123 | 20190212 | 2340 | 305193 | 6717 | Distribution Circuit | Vegetation | Tree - fell into line | 99 | 664983 | 40.6325 | -122.4066 | LOMASADRIANATMETERNUMBERANDSOURCESIDEOFHOUSE34SPANS | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022436 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1415695 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024564&numberofmonths=24&showchangehistorylog=1 | 19-0024564 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1103 | 103521103 | FUSE | 11131 | 20190212 | 2340 | 314444 | 9644 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 125372 | 40.6385 | -122.4021 | MTR1008730265 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024564 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1417643 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024624&numberofmonths=24&showchangehistorylog=1 | 19-0024624 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1103 | 103521103 | FUSE | 6151 | 20190212 | 2340 | 314631 | 8243 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 140131 | 40.6257 | -122.416 | 1NOFKESWICKDAMRDNASHRDNOFREDDING | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024624 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1417695 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024625&numberofmonths=24&showchangehistorylog=1 | 19-0024625 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1103 | 103521103 | FUSE | 6149 | 20190212 | 2340 | 314634 | 9415 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 122395 | 40.6255 | -122.4138 | BRADLEYGERALDINESSOKESWICKDAMRDEONASHRDNOREDDING | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024625 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1417696 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024628&numberofmonths=24&showchangehistorylog=1 | 19-0024628 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1103 | 103521103 | FUSE | 6153 | 20190212 | 2340 | 314636 | 9271 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 9271 | 40.6234 | -122.421 | KOTULAJON43436153JakeLn | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024628 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1417699 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025745&numberofmonths=24&showchangehistorylog=1 | 19-0025745 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1103 | 103521103 | FUSE | 6161 | 20190212 | 2340 | 318179 | 9419 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 103609 | 40.6146 | -122.4203 | LDSIDEOF6161 | Overcast-Fog-Heavy Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0025745 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1418790 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025748&numberofmonths=24&showchangehistorylog=1 | 19-0025748 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1103 | 103521103 | FUSE | 6155 | 20190212 | 2340 | 318190 | 9575 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 306400 | 40.6172 | -122.4286 | MULTIPLELDSIDEOF6155 | Overcast-Fog-Heavy Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0025748 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1418793 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022248&numberofmonths=24&showchangehistorylog=1 | 19-0022248 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | ANDERSON-1101 | 103261101 | JUMPER | OJS1LDSIDEOF9573 | 20190213 | 238 | 304559 | 9091 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 63637 | 40.4443 | -122.3062 | 1LDSIDEOF9573 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022248 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1415573 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022862&numberofmonths=24&showchangehistorylog=1 | 19-0022862 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | ANDERSON-1103 | 103261103 | JUMPER | OJS5SSOF3243 | 20190213 | 114 | 307279 | 6754 | Distribution Circuit | Environmental/External | Ice or snow | 41 | 231212 | 40.4765 | -122.2928 | MTR1006237071 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022862 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416104 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025306&numberofmonths=24&showchangehistorylog=1 | 19-0025306 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | ANDERSON-1103 | 103261103 | JUMPER | OJSATLBFEEDINGSINGLEPHASETOTHENORTH | 20190213 | 115 | 316716 | 7952 | Distribution Circuit | Vegetation | Tree - branch fell on line | 18 | 24261 | 40.4701 | -122.2479 | 1SPANLDSIDEOFOJS | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025306 | OH | Sus | 0 | yes | 2019 | FEB | Yes | None | 1418358 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025686&numberofmonths=24&showchangehistorylog=1 | 19-0025686 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ANTLER-1101 | 103271101 | FUSE | 2283 | 20190213 | 57 | 317955 | 11122 | Distribution Circuit | Environmental/External | Ice or snow | 10 | 111220 | 40.8583 | -122.3443 | LYTLE1785LUNGREMNMTNRD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0025686 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1418730 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025688&numberofmonths=24&showchangehistorylog=1 | 19-0025688 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ANTLER-1101 | 103271101 | JUMPER | 5137SSJUMPERS | 20190213 | 57 | 317956 | 13363 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 80178 | 40.8605 | -122.3476 | 5137COUTPOLE | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0025688 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1418732 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025706&numberofmonths=24&showchangehistorylog=1 | 19-0025706 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | ANTLER-1101 | 103271101 | FUSE | 8285 | 20190213 | 57 | 318032 | 11067 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 154938 | 40.8775 | -122.3619 | LYTLE1785HERMANRDLAKEHEAD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0025706 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1418752 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021983&numberofmonths=24&showchangehistorylog=1 | 19-0021983 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | BIG BEND-1102 | 103751102 | OTHER | WIREDOWN1LDSIDEOFMTR1007906658 | 20190213 | 344 | 303383 | 586 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 41238 | 39.69 | -121.3398 | 1LDSIDEOFMTR1007906658 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021983 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1415399 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021704&numberofmonths=24&showchangehistorylog=1 | 19-0021704 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | CEDAR CREEK-1101 | 103321101 | OTHER | WIREDOWNWO27107HWY299 | 20190213 | 1 | 301740 | 5425 | Distribution Circuit | Equipment Failure/Involved | Overhead | 789 | 2031981 | 40.7506 | -122.0486 | WIREDOWNWESTOF6349MTR500006885029475FENDERSFERRYRD | Overcast-Snow-32-90 F | Pole-Wood | Broken, wire on ground | 19-0021704 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1415152 | PW | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023849&numberofmonths=24&showchangehistorylog=1 | 19-0023849 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | COTTONWOOD-1101 | 102931101 | FUSE | 1375 | 20190213 | 202 | 311533 | 3498 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 111936 | 40.3635 | -122.3465 | 2SPANSLDSIDEOF1375 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023849 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1416987 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024258&numberofmonths=24&showchangehistorylog=1 | 19-0024258 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | COTTONWOOD-1101 | 102931101 | JUMPER | OJ | 20190213 | 202 | 312882 | 5187 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 41484 | 40.3485 | -122.4544 | 2LDSIDEOFMTR1008363879 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0024258 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1417336 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022201&numberofmonths=24&showchangehistorylog=1 | 19-0022201 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | COTTONWOOD-1101 | 102931101 | FUSE | 7185 | 20190213 | 202 | 304403 | 3733 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 317305 | 40.3851 | -122.3213 | LDSIDEOF7185FUSESTOOMANYDAMAGELOCATIONSTOLIST | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0022201 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1415540 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023195&numberofmonths=24&showchangehistorylog=1 | 19-0023195 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | COTTONWOOD-1102 | 102931102 | FUSE | 2057 | 20190213 | 216 | 308961 | 8104 | Distribution Circuit | Vegetation | Tree - fell into line | 118 | 853888 | 40.3896 | -122.3229 | MULTIPLEAREASLDSIDEOFFUSE2057 | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023195 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1416384 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023129&numberofmonths=24&showchangehistorylog=1 | 19-0023129 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | DESCHUTES-1101 | 103351101 | JUMPER | OJS1SSOF2707 | 20190213 | 221 | 308505 | 4857 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 63141 | 40.5698 | -122.193 | 1SSOF2707 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023129 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416321 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023136&numberofmonths=24&showchangehistorylog=1 | 19-0023136 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | DESCHUTES-1101 | 103351101 | FUSE | 9463 | 20190213 | 221 | 308515 | 9354 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 9354 | 40.663 | -122.0661 | INGRAMJEFF707495111312999OAKRUNRD | Overcast-Fog-Heavy Rain-32-90 F | Anchor or Guy | Broken, wire on object | 19-0023136 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416327 | ANC | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022339&numberofmonths=24&showchangehistorylog=1 | 19-0022339 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | DESCHUTES-1104 | 103351104 | JUMPER | OJS1SOF7487 | 20190213 | 121 | 304780 | 10631 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 10631 | 40.5981 | -122.2348 | 2SPANSLDSIDE | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022339 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1415633 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022435&numberofmonths=24&showchangehistorylog=1 | 19-0022435 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | DESCHUTES-1104 | 103351104 | FUSE | 6607 | 20190213 | 121 | 305190 | 2419 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 26609 | 40.5932 | -122.2417 | 10SPANSLDSIDEOF6607 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022435 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1415694 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023002&numberofmonths=24&showchangehistorylog=1 | 19-0023002 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | DESCHUTES-1104 | 103351104 | JUMPER | WIREDOWNMTR5000076164 | 20190213 | 2142 | 307194 | 4071 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 38642 | 40.5494 | -122.2448 | 8982MAYNARD | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023002 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416224 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021769&numberofmonths=24&showchangehistorylog=1 | 19-0021769 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | FRENCH GULCH-1101 | 103381101 | OCB | 11012 | 20190213 | 415 | 302628 | 12008 | Distribution Circuit | Environmental/External | Ice or snow | 187 | 1180095 | 40.6869 | -122.6405 | 9SPLSOFR11221 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0021769 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1415221 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022606&numberofmonths=24&showchangehistorylog=1 | 19-0022606 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | GIRVAN-1101 | 103401101 | FUSE | 7959 | 20190213 | 145 | 305742 | 9600 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 153600 | 40.5127 | -122.4423 | ZUNIGAJUAN1655116549TEXASSPRINGSRD | Overcast-Fog-Snow-32-90 F | Pole-Wood | Broken, wire on ground | 19-0022606 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1415840 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022996&numberofmonths=24&showchangehistorylog=1 | 19-0022996 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | GIRVAN-1101 | 103401101 | JUMPER | OJ | 20190213 | 204 | 307993 | 9031 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 18062 | 40.5093 | -122.4461 | SINGLEPHASELINEALONGTEXASSPRINGS | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0022996 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1416218 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021724&numberofmonths=24&showchangehistorylog=1 | 19-0021724 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | GIRVAN-1102 | 103401102 | RECLOSER | 1028 | 20190213 | 154 | 301532 | 3793 | Distribution Circuit | Vegetation | Tree - fell into line | 134 | 508262 | 40.5709 | -122.4263 | ZUNIGAJUAN16338TOWERVIEWCIR | Snow-Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | On Ground | 19-0021724 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1415172 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023902&numberofmonths=24&showchangehistorylog=1 | 19-0023902 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | GIRVAN-1102 | 103401102 | FUSE | 9791 | 20190213 | 108 | 311741 | 9490 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 104390 | 40.5486 | -122.3026 | MTR1006189474 | Snow-Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0023902 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1417032 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023952&numberofmonths=24&showchangehistorylog=1 | 19-0023952 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | GIRVAN-1102 | 103401102 | JUMPER | OJSSSTO2843 | 20190213 | 153 | 311867 | 12387 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 734691 | 40.553 | -122.4454 | 1SSEOF2843 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023952 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1417072 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024179&numberofmonths=24&showchangehistorylog=1 | 19-0024179 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | GIRVAN-1102 | 103401102 | FUSE | 6917 | 20190213 | 119 | 312588 | 11000 | Distribution Circuit | Vegetation | Tree - bark fell into line | 25 | 275000 | 40.5565 | -122.4379 | 16542POWERLINERD | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024179 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1417263 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024182&numberofmonths=24&showchangehistorylog=1 | 19-0024182 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | GIRVAN-1102 | 103401102 | FUSE | 6921 | 20190213 | 153 | 312605 | 12177 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 395417 | 40.5595 | -122.4351 | 16716THOMPSONLN16550THOMPSONLD | Overcast-Fog-Snow-32-90 F | Pole-Wood | Broken, wire on ground | 19-0024182 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1417266 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024194&numberofmonths=24&showchangehistorylog=1 | 19-0024194 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | GIRVAN-1102 | 103401102 | FUSE | 1859 | 20190213 | 153 | 312638 | 11168 | Distribution Circuit | Vegetation | Tree - branch fell on line | 36 | 402048 | 40.5484 | -122.4555 | 2SPANSLDSIDEOFFUCO1859 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024194 | OH | Sus | 0 | yes | 2019 | FEB | Yes | None | 1417275 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0026200&numberofmonths=24&showchangehistorylog=1 | 19-0026200 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | JESSUP-1101 | 103441101 | FUSE | 6959 | 20190213 | 49 | 319132 | 11039 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 430521 | 40.4871 | -122.4514 | 4SPANSLDSIDE6959 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0026200 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1419045 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021709&numberofmonths=24&showchangehistorylog=1 | 19-0021709 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | JESSUP-1102 | 103441102 | RECLOSER | 1550 | 20190213 | 103 | 301726 | 9407 | Distribution Circuit | Vegetation | Tree - fell into line | 860 | 5167335 | 40.4471 | -122.3187 | GONZALESB20776311462MULTIPLELOCATIONS | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021709 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1415157 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023841&numberofmonths=24&showchangehistorylog=1 | 19-0023841 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | JESSUP-1102 | 103441102 | JUMPER | OJS1PSSTO10231 | 20190213 | 29 | 311493 | 8626 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 17252 | 40.443 | -122.324 | 10231 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0023841 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416981 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024433&numberofmonths=24&showchangehistorylog=1 | 19-0024433 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | JESSUP-1102 | 103441102 | FUSE | 10245 | 20190213 | 103 | 313719 | 10027 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 157922 | 40.4344 | -122.4074 | MTR10088920414 | Overcast-Fog-Heavy Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0024433 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1417520 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025629&numberofmonths=24&showchangehistorylog=1 | 19-0025629 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | JESSUP-1102 | 103441102 | JUMPER | OJ1PEOF10257 | 20190213 | 103 | 317655 | 12471 | Distribution Circuit | Vegetation | Tree - fell into line | 98 | 67032 | 40.4513 | -122.4547 | 10257 | Overcast-Fog-Heavy Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0025629 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1418679 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022960&numberofmonths=24&showchangehistorylog=1 | 19-0022960 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | JESSUP-1103 | 103441103 | FUSE | 9903 | 20190213 | 5 | 307864 | 11005 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 22010 | 40.481 | -122.3033 | 1SPANLDSIDEOF9903 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022960 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416188 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023010&numberofmonths=24&showchangehistorylog=1 | 19-0023010 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | JESSUP-1103 | 103441103 | FUSE | 9905 | 20190213 | 5 | 308059 | 11158 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 44632 | 40.48 | -122.3066 | 1SPANLDSIDEOF9905 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023010 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416232 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021700&numberofmonths=24&showchangehistorylog=1 | 19-0021700 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KESWICK-1101 | 103451101 | RECLOSER | 9712 | 20190213 | 47 | 301717 | 6881 | Distribution Circuit | Vegetation | Tree - fell into line | 274 | 1755928 | 40.6166 | -122.4955 | ZUNIGAJUAN800WOBENSONRD900NOWALKERTERRACERDWOKESWICK | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | On Ground | 19-0021700 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1415148 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025112&numberofmonths=24&showchangehistorylog=1 | 19-0025112 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KESWICK-1101 | 103451101 | JUMPER | OJSATMTR1008048270 | 20190213 | 47 | 315717 | 10978 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 21956 | 40.5994 | -122.4892 | MTR1008048270 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025112 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1418191 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025139&numberofmonths=24&showchangehistorylog=1 | 19-0025139 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KESWICK-1101 | 103451101 | JUMPER | OJSONMAINLINEFEEDINGMTR1008044666 | 20190213 | 47 | 315866 | 9583 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 153328 | 40.6096 | -122.5021 | WIREDOWNATLBPOLEFEEDINGMTR1008044666 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025139 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1418217 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025141&numberofmonths=24&showchangehistorylog=1 | 19-0025141 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KESWICK-1101 | 103451101 | FUSE | 2653 | 20190213 | 47 | 315869 | 8083 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 193992 | 40.6133 | -122.4957 | FUCO7105ANDMTR1006231302 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025141 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1418219 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025142&numberofmonths=24&showchangehistorylog=1 | 19-0025142 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KESWICK-1101 | 103451101 | FUSE | 2435 | 20190213 | 23 | 315878 | 8207 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 49242 | 40.6042 | -122.502 | 1SPANLDSIDEOFFUCO2435 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025142 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1418220 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025248&numberofmonths=24&showchangehistorylog=1 | 19-0025248 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KESWICK-1101 | 103451101 | JUMPER | OJSATREDBLUFFRDMIDDLECREEKRD | 20190213 | 44 | 316485 | 11964 | Distribution Circuit | Equipment Failure/Involved | Overhead | 52 | 622128 | 40.5916 | -122.4878 | 10616REDBLUFFRD | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0025248 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1418318 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021795&numberofmonths=24&showchangehistorylog=1 | 19-0021795 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1102 | 103521102 | RECLOSER | 1382 | 20190213 | 314 | 302537 | 9308 | Distribution Circuit | Vegetation | Tree - fell into line | 243 | 1131261 | 40.6539 | -122.3334 | 1SPANSSOF3897 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021795 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Three Phase Fault | 1415246 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023890&numberofmonths=24&showchangehistorylog=1 | 19-0023890 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1102 | 103521102 | RECLOSER | 49144 | 20190213 | 227 | 303048 | 11057 | Distribution Circuit | Vegetation | Tree - fell into line | 414 | 2406517 | 40.6589 | -122.341 | LYTLE17852210TWINVIEWBLVD3SSOF1584WIREDOWN1LOADSIDELR1584BYTREE | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023890 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Multi-Fault | 1417022 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024169&numberofmonths=24&showchangehistorylog=1 | 19-0024169 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1102 | 103521102 | JUMPER | OJSATMTR1008045869 | 20190213 | 227 | 312522 | 9484 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 294004 | 40.632 | -122.3959 | MTR10087578231008045966 | Overcast-Fog-Snow-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0024169 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1417255 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025167&numberofmonths=24&showchangehistorylog=1 | 19-0025167 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1102 | 103521102 | FUSE | 3175 | 20190213 | 227 | 315979 | 11058 | Distribution Circuit | Environmental/External | Ice or snow | 51 | 563958 | 40.6639 | -122.4007 | LDSIDEOF3175 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025167 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1418244 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025208&numberofmonths=24&showchangehistorylog=1 | 19-0025208 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1102 | 103521102 | FUSE | 4623 | 20190213 | 236 | 302490 | 10813 | Distribution Circuit | Vegetation | Tree - branch fell on line | 21 | 227073 | 40.6428 | -122.3336 | MTR1006191740MTR1006233101 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025208 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Three Phase Fault | 1418287 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025587&numberofmonths=24&showchangehistorylog=1 | 19-0025587 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1102 | 103521102 | FUSE | 2891 | 20190213 | 13 | 317477 | 12232 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 61160 | 40.6772 | -122.4082 | 17321FLANAGANRD | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0025587 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1418634 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025595&numberofmonths=24&showchangehistorylog=1 | 19-0025595 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1102 | 103521102 | FUSE | 2413 | 20190213 | 227 | 317513 | 11058 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 77406 | 40.6576 | -122.4215 | 1517AND18SPANSLDSIDEOF2413 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0025595 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1418642 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0026616&numberofmonths=24&showchangehistorylog=1 | 19-0026616 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1102 | 103521102 | JUMPER | OJ1NOF3177 | 20190213 | 227 | 320065 | 12098 | Distribution Circuit | Environmental/External | Ice or snow | 22 | 266156 | 40.668 | -122.4019 | BETOJS2891 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0026616 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1419268 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023411&numberofmonths=24&showchangehistorylog=1 | 19-0023411 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1103 | 103521103 | FUSE | 5377 | 20190213 | 345 | 309799 | 7999 | Distribution Circuit | Vegetation | Tree - fell into line | 131 | 459117 | 40.6314 | -122.2688 | LASTLINEBUCKPOLELDSIDE | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023411 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Multi-Fault | 1416564 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023459&numberofmonths=24&showchangehistorylog=1 | 19-0023459 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1103 | 103521103 | JUMPER | OJSFEEDINGMTR1006191323 | 20190213 | 345 | 310024 | 6345 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 6345 | 40.642 | -122.2971 | 1SSOFMTR1006191323 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023459 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416610 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023545&numberofmonths=24&showchangehistorylog=1 | 19-0023545 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1103 | 103521103 | FUSE | 7009 | 20190213 | 345 | 310314 | 6568 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 85384 | 40.6348 | -122.2965 | 1SPANLDSIDEOF7009 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0023545 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416691 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023548&numberofmonths=24&showchangehistorylog=1 | 19-0023548 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1103 | 103521103 | JUMPER | OJS1WOF5567 | 20190213 | 202 | 310324 | 9216 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 46080 | 40.651 | -122.2979 | 2WOF5567 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023548 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416694 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024635&numberofmonths=24&showchangehistorylog=1 | 19-0024635 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1103 | 103521103 | SWITCH | 1949 | 20190213 | 40 | 314657 | 8279 | Distribution Circuit | Vegetation | Tree - fell into line | 234 | 1937286 | 40.6232 | -122.4207 | SBCO1949 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024635 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1417708 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024697&numberofmonths=24&showchangehistorylog=1 | 19-0024697 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1103 | 103521103 | FUSE | 3491 | 20190213 | 41 | 314872 | 9709 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 29127 | 40.6487 | -122.3973 | LDSIDEOF3491 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024697 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1417770 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021850&numberofmonths=24&showchangehistorylog=1 | 19-0021850 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1104 | 103521104 | OCB | 11042 | 20190213 | 209 | 301902 | 7681 | Distribution Circuit | Vegetation | Tree - fell into line | 687 | 3078183 | 40.619 | -122.3227 | 1SOF831585ONMAINLINESINGLEPHASETAPAT8515MULTIPLEBET551985753817 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021850 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Multi-Fault | 1415298 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022445&numberofmonths=24&showchangehistorylog=1 | 19-0022445 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1104 | 103521104 | FUSE | 8641 | 20190213 | 116 | 305203 | 8284 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 124260 | 40.5882 | -122.307 | 4SPANSLDSIDEOF8641 | Overcast-Fog-Heavy Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0022445 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1415703 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023141&numberofmonths=24&showchangehistorylog=1 | 19-0023141 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1104 | 103521104 | FUSE | 5673 | 20190213 | 209 | 308677 | 4011 | Distribution Circuit | Vegetation | Tree - fell into line | 65 | 260715 | 40.5523 | -122.2765 | MTR1006089463 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023141 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416334 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023489&numberofmonths=24&showchangehistorylog=1 | 19-0023489 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1104 | 103521104 | FUSE | 11485 | 20190213 | 209 | 310127 | 10659 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 42636 | 40.5887 | -122.3013 | 2SPANSLDSIDEOF11485 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023489 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416635 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023686&numberofmonths=24&showchangehistorylog=1 | 19-0023686 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1104 | 103521104 | JUMPER | VJSFEEDING8515 | 20190213 | 209 | 310855 | 10933 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 54665 | 40.5951 | -122.3108 | SINGLEPHASEEOF851510571OLDOREGONTRAIL | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023686 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416836 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024184&numberofmonths=24&showchangehistorylog=1 | 19-0024184 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1104 | 103521104 | FUSE | 11585 | 20190213 | 209 | 312611 | 9135 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 63945 | 40.5632 | -122.2808 | 1SPANAND2SPANSLDSIDEOF11585 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024184 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1417268 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024234&numberofmonths=24&showchangehistorylog=1 | 19-0024234 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1104 | 103521104 | FUSE | 11587 | 20190213 | 209 | 312776 | 7841 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 39205 | 40.5587 | -122.2787 | 2SPANSLDSIDE | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024234 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1417314 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024235&numberofmonths=24&showchangehistorylog=1 | 19-0024235 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1104 | 103521104 | FUSE | 11595 | 20190213 | 204 | 312778 | 8196 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 73764 | 40.553 | -122.2837 | LDSIDEOF11595 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024235 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1417315 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024239&numberofmonths=24&showchangehistorylog=1 | 19-0024239 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1104 | 103521104 | FUSE | 11599 | 20190213 | 51 | 312782 | 8290 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 24870 | 40.553 | -122.2802 | 3SPANSLDSIDEOF11599 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0024239 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1417319 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021783&numberofmonths=24&showchangehistorylog=1 | 19-0021783 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ORO FINO-1101 | 103031101 | OCB | 11012 | 20190213 | 441 | 302659 | 926 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4318 | 1174921 | 39.8716 | -121.6113 | MULTIPLELOCATIONSOFTREEBRANCHESWIREDOWN15185SHADOWWOOD | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021783 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1415234 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022452&numberofmonths=24&showchangehistorylog=1 | 19-0022452 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ORO FINO-1102 | 103031102 | FUSE | 17167 | 20190213 | 634 | 302898 | 971 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 13323 | 39.8661 | -121.5762 | MTR1007239390 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022452 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1415709 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022507&numberofmonths=24&showchangehistorylog=1 | 19-0022507 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ORO FINO-1102 | 103031102 | RECLOSER | 2556 | 20190213 | 837 | 303256 | 895 | Distribution Circuit | Vegetation | Tree - fell into line | 181 | 160987 | 39.8903 | -121.5777 | 4SPANSLDSIDEOFSBCO17419 | Overcast-Fog-Heavy Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0022507 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1415749 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021969&numberofmonths=24&showchangehistorylog=1 | 19-0021969 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | RED BLUFF-1104 | 103541104 | FUSE | 1991 | 20190213 | 652 | 302933 | 655 | Distribution Circuit | Vegetation | Tree - fell into line | 101 | 66155 | 40.3013 | -122.2739 | MTR1008053978 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0021969 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1415387 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021695&numberofmonths=24&showchangehistorylog=1 | 19-0021695 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | STILLWATER-1101 | 103561101 | RECLOSER | 1320 | 20190213 | 33 | 301697 | 8289 | Distribution Circuit | Vegetation | Tree - fell into line | 436 | 1564961 | 40.6959 | -122.3427 | MTR10086706521STHARDTAPNOF3327 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021695 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1415142 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023063&numberofmonths=24&showchangehistorylog=1 | 19-0023063 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | STILLWATER-1101 | 103561101 | FUSE | 55301 | 20190213 | 33 | 308218 | 13671 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 451143 | 40.7378 | -122.3151 | 18AND23SPANSLDSIDEOF55301ONWESTSIDEOFI5 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0023063 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416267 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024118&numberofmonths=24&showchangehistorylog=1 | 19-0024118 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | STILLWATER-1101 | 103561101 | FUSE | 4675 | 20190213 | 33 | 312380 | 11227 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 233622 | 40.7069 | -122.3278 | PALADEWESLEYonespansourceside1006232058 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0024118 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1417205 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024584&numberofmonths=24&showchangehistorylog=1 | 19-0024584 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | STILLWATER-1101 | 103561101 | JUMPER | OJATTAPFEEDING889694697 | 20190213 | 33 | 314532 | 6925 | Distribution Circuit | Equipment Failure/Involved | Overhead | 70 | 484702 | 40.6943 | -122.3186 | MULTIPLELOC | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0024584 | OH | Sus | 0 | yes | 2019 | FEB | Yes | None | 1417659 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025284&numberofmonths=24&showchangehistorylog=1 | 19-0025284 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | STILLWATER-1101 | 103561101 | FUSE | 3307 | 20190213 | 33 | 316532 | 6859 | Distribution Circuit | Vegetation | Tree - fell into line | 83 | 569297 | 40.7163 | -122.3316 | MULTIPLE | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025284 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1418336 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025286&numberofmonths=24&showchangehistorylog=1 | 19-0025286 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | STILLWATER-1101 | 103561101 | FUSE | 7133 | 20190213 | 33 | 316534 | 7981 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 183563 | 40.7185 | -122.3315 | SBCO2560591955TUNNELRD | Overcast-Heavy Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0025286 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1418338 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025323&numberofmonths=24&showchangehistorylog=1 | 19-0025323 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | STILLWATER-1101 | 103561101 | JUMPER | SPANSSOF4695REMOVED | 20190213 | 33 | 316803 | 9517 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 9517 | 40.6953 | -122.3173 | 4695 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0025323 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1418377 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025614&numberofmonths=24&showchangehistorylog=1 | 19-0025614 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | STILLWATER-1101 | 103561101 | FUSE | 3309 | 20190213 | 33 | 317560 | 10835 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 32505 | 40.7191 | -122.3304 | 1STAND2NDSPANSLDSIDEOF330926SPANSSPANSLDSIDEOF3309 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025614 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1418661 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025615&numberofmonths=24&showchangehistorylog=1 | 19-0025615 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | STILLWATER-1101 | 103561101 | FUSE | 3327 | 20190213 | 33 | 317567 | 9361 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 102971 | 40.7251 | -122.3253 | 2SPANSLDSIDE3327 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025615 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1418663 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025616&numberofmonths=24&showchangehistorylog=1 | 19-0025616 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | STILLWATER-1101 | 103561101 | FUSE | 3311 | 20190213 | 33 | 317570 | 8189 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 253859 | 40.7251 | -122.325 | MTR1007054564 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025616 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1418664 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025725&numberofmonths=24&showchangehistorylog=1 | 19-0025725 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | STILLWATER-1101 | 103561101 | JUMPER | OJ2SSOFMTR1007054564 | 20190213 | 33 | 318113 | 9508 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 19016 | 40.7248 | -122.323 | MTR1007054564 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025725 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1418771 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025726&numberofmonths=24&showchangehistorylog=1 | 19-0025726 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | STILLWATER-1101 | 103561101 | JUMPER | OJ1SSOF7145FEEDINGTWDMTR1008045723 | 20190213 | 33 | 318115 | 9729 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 107019 | 40.7245 | -122.3216 | MTR1008045723 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025726 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1418772 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024145&numberofmonths=24&showchangehistorylog=1 | 19-0024145 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | STILLWATER-1102 | 103561102 | JUMPER | TAPTO4713CUTINCLEAR | 20190213 | 249 | 312440 | 10751 | Distribution Circuit | Environmental/External | Ice or snow | 53 | 569803 | 40.6804 | -122.3433 | LDSIDE | Overcast-Fog-Snow-32-90 F | Pole-Wood | Broken, wire on ground | 19-0024145 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Multi-Fault | 1417236 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024166&numberofmonths=24&showchangehistorylog=1 | 19-0024166 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | STILLWATER-1102 | 103561102 | FUSE | 1959 | 20190213 | 249 | 312516 | 6666 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 253318 | 40.6872 | -122.3168 | LABOMICHAELOLDOREGONTRAILLYNNDR | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024166 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1417252 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024215&numberofmonths=24&showchangehistorylog=1 | 19-0024215 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | STILLWATER-1102 | 103561102 | FUSE | 5957 | 20190213 | 249 | 312708 | 10860 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 32580 | 40.6864 | -122.3125 | OHAIRESEAN1788co59572spansloadside | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024215 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1417294 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024741&numberofmonths=24&showchangehistorylog=1 | 19-0024741 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | STILLWATER-1102 | 103561102 | SWITCH | 10389 | 20190213 | 220 | 315012 | 8108 | Distribution Circuit | Vegetation | Tree - branch fell on line | 52 | 374638 | 40.7214 | -122.2416 | 15195SILVERTHORN | Overcast-Fog-Snow-32-90 F | Pole-Wood | Broken, wire on ground | 19-0024741 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1417814 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025041&numberofmonths=24&showchangehistorylog=1 | 19-0025041 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | STILLWATER-1102 | 103561102 | FUSE | 3337 | 20190213 | 220 | 315391 | 8104 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 56728 | 40.7328 | -122.2395 | 1SPANLDSIDEOF3337 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0025041 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1418117 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025695&numberofmonths=24&showchangehistorylog=1 | 19-0025695 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | STILLWATER-1102 | 103561102 | FUSE | 3341 | 20190213 | 220 | 317994 | 9379 | Distribution Circuit | Vegetation | Tree - fell into line | 75 | 703425 | 40.7467 | -122.2402 | EVERYWHERE | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0025695 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1418741 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021731&numberofmonths=24&showchangehistorylog=1 | 19-0021731 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER | 80454 | 20190213 | 221 | 301942 | 6704 | Distribution Circuit | Environmental/External | Ice or snow | 218 | 749622 | 40.4341 | -121.8714 | BELLJ183615DIFFERENTLOCATIONS | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0021731 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1415181 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022489&numberofmonths=24&showchangehistorylog=1 | 19-0022489 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | FUSE | 85533 | 20190213 | 229 | 305354 | 3391 | Distribution Circuit | Environmental/External | Ice or snow | 13 | 44083 | 40.4341 | -121.8723 | 2SPANSLDSIDEOF85533 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022489 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1415737 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022549&numberofmonths=24&showchangehistorylog=1 | 19-0022549 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | FUSE | 850247 | 20190213 | 229 | 305552 | 3677 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 22062 | 40.3571 | -121.9095 | 850273 | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022549 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1415787 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023867&numberofmonths=24&showchangehistorylog=1 | 19-0023867 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER | 65764 | 20190213 | 229 | 311926 | 3679 | Distribution Circuit | Environmental/External | Ice or snow | 149 | 547544 | 40.4014 | -121.8771 | MULTIPLEWIREDOWNLDSIDESB939 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023867 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1417091 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021846&numberofmonths=24&showchangehistorylog=1 | 19-0021846 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | VOLTA-1102 | 102541102 | RECLOSER | 1504 | 20190213 | 725 | 303015 | 6468 | Distribution Circuit | Vegetation | Tree - fell into line | 1169 | 6266140 | 40.4937 | -121.8735 | 1SPSSOFLR1646 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021846 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1415295 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025089&numberofmonths=24&showchangehistorylog=1 | 19-0025089 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WHITMORE-1101 | 103601101 | RECLOSER | 1598 | 20190213 | 823 | 303217 | 7467 | Distribution Circuit | Vegetation | Tree - fell into line | 170 | 1253635 | 40.6208 | -121.9332 | MTR100391336 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025089 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1418165 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025273&numberofmonths=24&showchangehistorylog=1 | 19-0025273 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | WHITMORE-1101 | 103601101 | JUMPER | OJMAINLINESSOF7661 | 20190213 | 823 | 316518 | 7756 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 31024 | 40.6915 | -121.9155 | 7661 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0025273 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1418331 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025997&numberofmonths=24&showchangehistorylog=1 | 19-0025997 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WHITMORE-1101 | 103601101 | FUSE | 2215 | 20190213 | 822 | 318677 | 10748 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 150472 | 40.5896 | -121.9536 | 5387 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025997 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1418957 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0026140&numberofmonths=24&showchangehistorylog=1 | 19-0026140 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WHITMORE-1101 | 103601101 | FUSE | 6699 | 20190213 | 822 | 318982 | 11888 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 47552 | 40.5892 | -121.9357 | 89SPANSLDSIDEOF6699 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0026140 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1419015 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023542&numberofmonths=24&showchangehistorylog=1 | 19-0023542 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | CORNING-1102 | 103331102 | FUSE | 1905 | 20190214 | 1658 | 310308 | 1494 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 7470 | 39.8997 | -122.6118 | 28SPANSLDSIDEOFFUCO1905 | Overcast-Fog-Snow-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0023542 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1416688 | CSO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024567&numberofmonths=24&showchangehistorylog=1 | 19-0024567 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | COTTONWOOD-1102 | 102931102 | FUSE | 10031 | 20190214 | 1511 | 309869 | 3049 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 12196 | 40.3893 | -122.33 | 2SPANSLDSIDEOFFUCO10031 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024567 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1417644 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023665&numberofmonths=24&showchangehistorylog=1 | 19-0023665 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | DESCHUTES-1104 | 103351104 | FUSE | 4303 | 20190214 | 1713 | 308200 | 4362 | Distribution Circuit | Vegetation | Tree - branch fell on line | 46 | 200652 | 40.5703 | -122.272 | ReginatoAaron1820sameness | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023665 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416816 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022876&numberofmonths=24&showchangehistorylog=1 | 19-0022876 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KANAKA-1101 | 103221101 | RECLOSER | 83288 | 20190214 | 429 | 306999 | 896 | Distribution Circuit | Vegetation | Tree - fell into line | 214 | 98132 | 39.5275 | -121.2862 | 6SPANSLDSIDEOFLR83288 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022876 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Multi-Fault | 1416115 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022912&numberofmonths=24&showchangehistorylog=1 | 19-0022912 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KANAKA-1101 | 103221101 | RECLOSER | 1044 | 20190214 | 758 | 307625 | 372 | Distribution Circuit | Vegetation | Tree - fell into line | 249 | 42714 | 39.5749 | -121.3056 | MTR1010455584 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022912 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Multi-Fault | 1416146 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023762&numberofmonths=24&showchangehistorylog=1 | 19-0023762 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1103 | 103521103 | FUSE | 1435 | 20190214 | 2031 | 310841 | 5429 | Distribution Circuit | Vegetation | Tree - branch fell on line | 64 | 47913 | 40.6403 | -122.2403 | MTR1009605790 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023762 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416913 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024190&numberofmonths=24&showchangehistorylog=1 | 19-0024190 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1103 | 103521103 | FUSE | 6377 | 20190214 | 1737 | 310457 | 8687 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 78183 | 40.6764 | -122.196 | LOMASADRIANASSISTTAG | Overcast-Drizzle-32-90 F | Pole - Tower, steel | Broken, wire on ground | 19-0024190 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1417273 | PS | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024240&numberofmonths=24&showchangehistorylog=1 | 19-0024240 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1103 | 103521103 | JUMPER | OJS1LDSIDEOFMTR5000078976 | 20190214 | 1800 | 312797 | 2860 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 11440 | 40.6845 | -122.1433 | AT1475ONMAINLINE | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024240 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1417320 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024711&numberofmonths=24&showchangehistorylog=1 | 19-0024711 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1103 | 103521103 | FUSE | 7835 | 20190214 | 1800 | 314931 | 8568 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 34272 | 40.7119 | -122.0865 | 3SPANSLDSIDEOFFUCO7835 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 19-0024711 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Multi-Fault | 1417785 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023508&numberofmonths=24&showchangehistorylog=1 | 19-0023508 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | VOLTA-1101 | 102541101 | JUMPER | 85534 | 20190214 | 1600 | 310172 | 6881 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 68810 | 40.4553 | -121.8656 | 7SPANSLDSIDEOF85534 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023508 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1416656 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022815&numberofmonths=24&showchangehistorylog=1 | 19-0022815 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WYANDOTTE-1103 | 102911103 | RECLOSER | 1508 | 20190214 | 442 | 306861 | 523 | Distribution Circuit | Vegetation | Tree - fell into line | 1191 | 732699 | 39.5046 | -121.4527 | MTR1007241235 | Partly Cloudy-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022815 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Multi-Fault | 1416061 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023641&numberofmonths=24&showchangehistorylog=1 | 19-0023641 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | WYANDOTTE-1103 | 102911103 | JUMPER | WIREDOWN | 20190214 | 1840 | 310717 | 865 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 73441 | 39.6859 | -121.3416 | ATFUCO1469 | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023641 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1416792 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024211&numberofmonths=24&showchangehistorylog=1 | 19-0024211 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | CEDAR CREEK-1101 | 103321101 | FUSE | 8085 | 20190215 | 1443 | 312463 | 1419 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 18447 | 40.8785 | -121.9332 | 4SPE3SPSEOFFUCO6639 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0024211 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1417290 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024236&numberofmonths=24&showchangehistorylog=1 | 19-0024236 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CEDAR CREEK-1101 | 103321101 | JUMPER | WIREDOWN | 20190215 | 1739 | 312728 | 1131 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 29403 | 40.7417 | -121.9956 | 2SPANSSSOFFUCO3943 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024236 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1417316 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024102&numberofmonths=24&showchangehistorylog=1 | 19-0024102 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1101 | 103201101 | FUSE | 1953 | 20190215 | 1145 | 312250 | 1560 | Distribution Circuit | Environmental/External | Ice or snow | 3 | 4680 | 39.5767 | -121.1007 | 6SPANSLDSIDEOFFUCO1953 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0024102 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1417192 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024612&numberofmonths=24&showchangehistorylog=1 | 19-0024612 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | COTTONWOOD-1101 | 102931101 | FUSE | 43801 | 20190215 | 1922 | 312900 | 1252 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 15024 | 40.3452 | -122.4319 | MTR1008777844 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024612 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1417685 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023868&numberofmonths=24&showchangehistorylog=1 | 19-0023868 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | COTTONWOOD-1102 | 102931102 | FUSE | 1801 | 20190215 | 531 | 311356 | 659 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1318 | 40.3899 | -122.3557 | EVERYPOLELDSIDEOFFUSES | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 19-0023868 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1417005 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024410&numberofmonths=24&showchangehistorylog=1 | 19-0024410 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | ELK CREEK-1101 | 102781101 | FUSE | 2349 | 20190215 | 1917 | 312894 | 2799 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 41985 | 39.6381 | -122.6108 | 6SPANSLDSIDEOFFUCO2349 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024410 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Three Phase Fault | 1417496 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024610&numberofmonths=24&showchangehistorylog=1 | 19-0024610 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | GIRVAN-1101 | 103401101 | FUSE | 3331 | 20190215 | 1423 | 312323 | 7069 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 98966 | 40.5541 | -122.4732 | 5000016641 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 19-0024610 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1417683 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024207&numberofmonths=24&showchangehistorylog=1 | 19-0024207 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1103 | 103521103 | SWITCH | 7823 | 20190215 | 1020 | 310511 | 483 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 16905 | 40.6778 | -122.165 | AT1475ONMAINLINE | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024207 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1417287 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024356&numberofmonths=24&showchangehistorylog=1 | 19-0024356 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | STILLWATER-1102 | 103561102 | FUSE | 6685 | 20190215 | 2205 | 313086 | 3975 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 166950 | 40.6883 | -122.2815 | 13896DANIELSLN | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024356 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Multi-Fault | 1417440 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025320&numberofmonths=24&showchangehistorylog=1 | 19-0025320 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1102 | 103521102 | FUSE | 653 | 20190216 | 1206 | 314128 | 4346 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 22300 | 40.6479 | -122.3597 | 17SPANSLDSIDEOF653 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025320 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1418374 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025285&numberofmonths=24&showchangehistorylog=1 | 19-0025285 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | ANTLER-1101 | 103271101 | RECLOSER | 1520 | 20190217 | 1653 | 316517 | 1142 | Distribution Circuit | Vegetation | Tree - fell into line | 82 | 93644 | 40.8994 | -122.3862 | MTR1009724158 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025285 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1418337 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025611&numberofmonths=24&showchangehistorylog=1 | 19-0025611 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | ANTLER-1101 | 103271101 | JUMPER | OJSATLBFEEDINGMTR1009724158 | 20190217 | 1653 | 317554 | 4352 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 4352 | 40.9052 | -122.383 | MTR1009724158 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025611 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1418658 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0026365&numberofmonths=24&showchangehistorylog=1 | 19-0026365 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | COTTONWOOD-1101 | 102931101 | FUSE | 6861 | 20190217 | 928 | 315481 | 4823 | Distribution Circuit | Environmental/External | Ice or snow | 6 | 28938 | 40.3236 | -122.4399 | 2POLESLDSIDEOFFUCO6861LASTPOLELDSIDEOFFUCO6861 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0026365 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1419179 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025593&numberofmonths=24&showchangehistorylog=1 | 19-0025593 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | COTTONWOOD-1103 | 102931103 | FUSE | 6587 | 20190217 | 821 | 316557 | 2073 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 122307 | 40.3308 | -122.4045 | LDSIDEOF6587 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025593 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1418640 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025684&numberofmonths=24&showchangehistorylog=1 | 19-0025684 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | COTTONWOOD-1103 | 102931103 | FUSE | 7283 | 20190217 | 828 | 316555 | 3172 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 15966 | 40.3311 | -122.4117 | LDSIDEOF7283 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025684 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Three Phase Fault | 1418728 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025150&numberofmonths=24&showchangehistorylog=1 | 19-0025150 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | FRENCH GULCH-1101 | 103381101 | RECLOSER | 1464 | 20190217 | 1306 | 315894 | 3164 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 12656 | 40.7131 | -122.6357 | 2POLESLDSIDEOF1464 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 19-0025150 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1418229 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025086&numberofmonths=24&showchangehistorylog=1 | 19-0025086 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | FRENCH GULCH-1102 | 103381102 | OTHER | WIREDOWN11LDSDLR1462 | 20190217 | 932 | 315566 | 4674 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 135500 | 40.6625 | -122.6219 | HOLLANDDONAVONSAPID101461483 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025086 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1418162 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025130&numberofmonths=24&showchangehistorylog=1 | 19-0025130 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | GIRVAN-1101 | 103401101 | JUMPER | OJ2SPSSOFMTR1009717918 | 20190217 | 1213 | 315816 | 317 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 317 | 40.5148 | -122.5107 | MTR1009717918 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025130 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1418208 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025909&numberofmonths=24&showchangehistorylog=1 | 19-0025909 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | GIRVAN-1101 | 103401101 | JUMPER | 3WIRESDOWN5POLESSSOF2675 | 20190217 | 1623 | 316486 | 4397 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 26382 | 40.4987 | -122.3732 | 5POLESSSOF2675 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025909 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1418912 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025603&numberofmonths=24&showchangehistorylog=1 | 19-0025603 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | JESSUP-1102 | 103441102 | FUSE | 10273 | 20190217 | 1917 | 316792 | 1398 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 27960 | 40.4601 | -122.4016 | 17547CIMMERONTRAILRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025603 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1418650 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025667&numberofmonths=24&showchangehistorylog=1 | 19-0025667 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | JESSUP-1102 | 103441102 | FUSE | 2379 | 20190217 | 1917 | 317812 | 2511 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 10044 | 40.4592 | -122.397 | 7SPANSLDSIDEOF2379 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0025667 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1418715 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025043&numberofmonths=24&showchangehistorylog=1 | 19-0025043 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KESWICK-1101 | 103451101 | FUSE | 2411 | 20190217 | 835 | 315359 | 5860 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 69790 | 40.6146 | -122.519 | MTR1006709936 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 19-0025043 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Three Phase Fault | 1418120 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025889&numberofmonths=24&showchangehistorylog=1 | 19-0025889 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KESWICK-1101 | 103451101 | FUSE | 107703 | 20190217 | 1519 | 318449 | 3041 | Distribution Circuit | Environmental/External | Ice or snow | 2 | 6082 | 40.6603 | -122.4728 | EOLTRANSFORMERPOLELDSIDEOF107703 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 19-0025889 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Multi-Fault | 1418904 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0026780&numberofmonths=24&showchangehistorylog=1 | 19-0026780 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | KESWICK-1101 | 103451101 | FUSE | 2443 | 20190217 | 804 | 320347 | 6326 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 69586 | 40.5974 | -122.5439 | 213151728293034SPANSLDSIDEOF2443ANDAT904183 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0026780 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1419397 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025253&numberofmonths=24&showchangehistorylog=1 | 19-0025253 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1103 | 103521103 | OTHER | WIREDOWNMTR1009767053 | 20190217 | 1619 | 316488 | 1286 | Distribution Circuit | Equipment Failure/Involved | Overhead | 393 | 120656 | 40.6362 | -122.4187 | 17350RHONDALYNRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025253 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1418321 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025327&numberofmonths=24&showchangehistorylog=1 | 19-0025327 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1104 | 103521104 | FUSE | 11591 | 20190217 | 1800 | 316966 | 4122 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 8244 | 40.554 | -122.2886 | 3SPANSLDSIDEOFFUCO11591 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025327 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1418382 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025697&numberofmonths=24&showchangehistorylog=1 | 19-0025697 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | PANORAMA-1102 | 103461102 | RECLOSER | 1632 | 20190217 | 729 | 315319 | 3536 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 35360 | 40.4045 | -122.1217 | 4SOFLR1632 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025697 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1418743 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028060&numberofmonths=24&showchangehistorylog=1 | 19-0028060 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BIG MEADOWS-2101 | 102812101 | RECLOSER | 2510 | 20190226 | 137 | 323788 | 2531 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 7575 | 40.2104 | -121.1644 | 13SPANSFROM18175TWD721 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028060 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1420170 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028347&numberofmonths=24&showchangehistorylog=1 | 19-0028347 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BIG MEADOWS-2101 | 102812101 | FUSE | 2935 | 20190226 | 103 | 323772 | 957 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 4785 | 40.1326 | -120.9565 | 5SPANSSSOFLINEANDBUCKFEEDINGMTR10088292241 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028347 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Three Phase Fault | 1420331 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028356&numberofmonths=24&showchangehistorylog=1 | 19-0028356 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BIG MEADOWS-2101 | 102812101 | JUMPER | OJSLBFEEDINGMTR1008829224 | 20190226 | 58 | 324565 | 3762 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 3762 | 40.1156 | -120.9708 | TAPFEEDINGMTR1008829224 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028356 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1420334 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028296&numberofmonths=24&showchangehistorylog=1 | 19-0028296 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BUCKS CREEK-1102 | 102211102 | FUSE | 1381 | 20190226 | 1217 | 324110 | 4239 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 4239 | 40.0845 | -121.1511 | MULTIPLELOCATIONSBET18597AND18501VERYDIFFICULTTERRAINTODETERMINEACTUALLOCATIONS | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0028296 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Three Phase Fault | 1420308 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028322&numberofmonths=24&showchangehistorylog=1 | 19-0028322 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BUCKS CREEK-1102 | 102211102 | OTHER | WIREDOWNMAINLINESS1809 | 20190226 | 946 | 324441 | 1577 | Distribution Circuit | Equipment Failure/Involved | Overhead | 130 | 52991 | 40.0824 | -121.1538 | ONMAINLINEONSOURCESIDEOF1809FUCO | Overcast-Fog-Snow-Strong Winds-Below 32 F | Conductor, Overhead | Broken, wire on object | 19-0028322 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1420322 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028520&numberofmonths=24&showchangehistorylog=1 | 19-0028520 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1102 | 103201102 | RECLOSER | 1064 | 20190226 | 1849 | 325116 | 1271 | Distribution Circuit | Vegetation | Tree - fell into line | 202 | 197116 | 39.482 | -121.2419 | MTR1007888007 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028520 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1420428 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028273&numberofmonths=24&showchangehistorylog=1 | 19-0028273 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | EAST QUINCY-1101 | 102551101 | FUSE | 3071 | 20190226 | 1005 | 324219 | 360 | Distribution Circuit | Environmental/External | Ice or snow | 1 | 360 | 39.9304 | -121.0617 | LAST2SPANSLDSIDEOF3071 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028273 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1420299 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028383&numberofmonths=24&showchangehistorylog=1 | 19-0028383 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | GANSNER-1101 | 103021101 | FUSE | 1797 | 20190226 | 149 | 324636 | 3783 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 98358 | 40.0027 | -120.9677 | 1POLELDSIDEOFMTR10010376336 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | On Ground | 19-0028383 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Multi-Fault | 1420340 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028069&numberofmonths=24&showchangehistorylog=1 | 19-0028069 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | HAMILTON BRANCH-1101 | 102361101 | RECLOSER | 2046 | 20190226 | 259 | 323824 | 1024 | Distribution Circuit | Vegetation | Tree - fell into line | 203 | 207872 | 40.2694 | -121.0878 | BRUNELLEMICHAEL2499ONMAINLINEFROMTAP48755LOADSIDESPAN | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028069 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1420180 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028501&numberofmonths=24&showchangehistorylog=1 | 19-0028501 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | PANORAMA-1102 | 103461102 | OTHER | WIREDOWNMAINLINEATMTR1006233956 | 20190226 | 1451 | 324969 | 1139 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 92651 | 40.4486 | -122.1978 | MTR1006233956 | Partly Cloudy-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028501 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1420409 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028109&numberofmonths=24&showchangehistorylog=1 | 19-0028109 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER | 80454 | 20190226 | 739 | 323939 | 1902 | Distribution Circuit | Vegetation | Tree - fell into line | 242 | 61868 | 40.4341 | -121.8714 | 3AND4SPANSLOADSIDEOF1571 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028109 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1420206 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028635&numberofmonths=24&showchangehistorylog=1 | 19-0028635 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER | 1640 | 20190226 | 2344 | 325782 | 2472 | Distribution Circuit | Environmental/External | Ice or snow | 784 | 1384234 | 40.3543 | -121.5766 | 12EOF64963ANDSEVERALLOCATIONSBETSW3813ANDLR1640 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028635 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1420541 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028263&numberofmonths=24&showchangehistorylog=1 | 19-0028263 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WYANDOTTE-1110 | 102911110 | TRANSFORMER | 221356467877 | 20190226 | 1016 | 324240 | 390 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 724 | 39.5292 | -121.5199 | MAYSS2497pinefellandtookwiredown | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028263 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1420294 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028746&numberofmonths=24&showchangehistorylog=1 | 19-0028746 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BIG MEADOWS-2101 | 102812101 | OTHER | WIREDOWNLINEANDBUCKFEEDING3157 | 20190227 | 551 | 326416 | 390 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1359 | 94474 | 40.1951 | -121.1214 | HARDTAPFEEDINGFUCO3157 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on object | 19-0028746 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1420656 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028762&numberofmonths=24&showchangehistorylog=1 | 19-0028762 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | CORNING-1101 | 103331101 | FUSE | 85223 | 20190227 | 340 | 326503 | 659 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 6905 | 40.0087 | -122.4149 | MTR1008572385 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on object | 19-0028762 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1420663 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028766&numberofmonths=24&showchangehistorylog=1 | 19-0028766 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KANAKA-1101 | 103221101 | RECLOSER | 83288 | 20190227 | 129 | 326308 | 1145 | Distribution Circuit | Vegetation | Tree - fell into line | 133 | 68258 | 39.5275 | -121.2862 | CUTOUTPOLE1997 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0028766 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1420664 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028696&numberofmonths=24&showchangehistorylog=1 | 19-0028696 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1102 | 103521102 | RECLOSER | 49144 | 20190227 | 209 | 326128 | 1885 | Distribution Circuit | Vegetation | Tree - fell into line | 536 | 293776 | 40.6589 | -122.341 | 4WOFMTR1009985866 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0028696 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1420607 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028938&numberofmonths=24&showchangehistorylog=1 | 19-0028938 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1102 | 103521102 | RECLOSER | 1382 | 20190227 | 1057 | 326877 | 404 | Distribution Circuit | Vegetation | Tree - branch fell on line | 244 | 48120 | 40.6539 | -122.3334 | 2WOF5433 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028938 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1420788 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0029136&numberofmonths=24&showchangehistorylog=1 | 19-0029136 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1103 | 103521103 | FUSE | 2595 | 20190227 | 1442 | 327241 | 1099 | Distribution Circuit | Equipment Failure/Involved | Overhead | 83 | 13086 | 40.6333 | -122.2547 | 2SSOFMTR1008042804 | Partly Cloudy-Rain-32-90 F | Woodpin | Broken, wire on object | 19-0029136 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1420890 | WP | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0029026&numberofmonths=24&showchangehistorylog=1 | 19-0029026 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | SYCAMORE CREEK-1111 | 102971111 | FUSE | 2499 | 20190227 | 1257 | 326778 | 413 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 9912 | 39.9168 | -121.7365 | LDSIDEOF2499 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0029026 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1420832 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0064515&numberofmonths=24&showchangehistorylog=1 | 19-0064515 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | WYANDOTTE-1103 | 102911103 | FUSE | 1487 | 20190608 | 308 | 401169 | 736 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 62560 | 39.6301 | -121.3787 | 4SPANSLDSIDEOF1487 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0064515 | OH | Sus | 31451974 | yes | 2019 | JUN | Yes | Line to Ground | 1446689 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0103372&numberofmonths=24&showchangehistorylog=1 | 19-0103372 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1104 | 103521104 | FUSE | 7033 | 20190925 | 627 | 612845 | 518 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 7066 | 40.6125 | -122.2792 | 1PSOFMTR5000073022 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0103372 | OH | Sus | 0 | yes | 2019 | SEP | Yes | Line to Line | 1472776 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0130373&numberofmonths=24&showchangehistorylog=1 | 19-0130373 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | BIG BEND-1102 | 103751102 | OTHER | WIREDOWN1PEO13759 | 20191126 | 2219 | 720482 | 1143 | Distribution Circuit | Vegetation | Tree - fell into line | 301 | 207583 | 39.6528 | -121.442 | 1PEO13759 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0130373 | OH | Sus | 0 | yes | 2019 | NOV | Yes | Open Circuit | 1495173 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0130575&numberofmonths=24&showchangehistorylog=1 | 19-0130575 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | BANGOR-1101 | 103191101 | JUMPER | OJS1EO709 | 20191127 | 1604 | 721990 | 76 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 76 | 39.4465 | -121.2774 | 2EO709 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0130575 | OH | Sus | 0 | yes | 2019 | NOV | Yes | Force Out | 1495284 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0130351&numberofmonths=24&showchangehistorylog=1 | 19-0130351 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | BIG BEND-1101 | 103751101 | FUSE | 1735 | 20191127 | 47 | 719578 | 1012 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 25300 | 39.6962 | -121.4813 | 15SPLDSIDEOFCOUT | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0130351 | OH | Sus | 0 | yes | 2019 | NOV | Yes | Line to Ground | 1495165 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0129558&numberofmonths=24&showchangehistorylog=1 | 19-0129558 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE | 23415 | 20191127 | 1415 | 721945 | 182 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 546 | 39.4787 | -121.2566 | TX222096365976 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0129558 | OH | Sus | 0 | yes | 2019 | NOV | Yes | Open Circuit | 1495271 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0010251&numberofmonths=24&showchangehistorylog=1 | 20-0010251 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | BIG BEND-1102 | 103751102 | FUSE | 1467 | 20200116 | 1502 | 763226 | 1353 | Distribution Circuit | Vegetation | Tree - fell into line | 90 | 121770 | 39.6615 | -121.3893 | 10SPANSLDSIDEOF1467 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0010251 | OH | Sus | 0 | yes | 2020 | JAN | Yes | Line to Ground | 1506973 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0010211&numberofmonths=24&showchangehistorylog=1 | 20-0010211 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KANAKA-1101 | 103221101 | RECLOSER | 83288 | 20200116 | 1545 | 763291 | 285 | Distribution Circuit | Vegetation | Tree - branch fell on line | 136 | 28120 | 39.5275 | -121.2862 | THORNEALLANWIREDOWNFORBESTOWNWEISSHILLRD | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0010211 | OH | Sus | 0 | yes | 2020 | JAN | Yes | Line to Ground | 1506955 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0010625&numberofmonths=24&showchangehistorylog=1 | 20-0010625 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KANAKA-1101 | 103221101 | FUSE | 1405 | 20200116 | 1600 | 763499 | 1570 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 4710 | 39.5931 | -121.2538 | 10SPANSSOURCESIDEOFCGC222154670240 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 20-0010625 | OH | Sus | 0 | yes | 2020 | JAN | Yes | Line to Line | 1507327 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0009909&numberofmonths=24&showchangehistorylog=1 | 20-0009909 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | WHITMORE-1101 | 103601101 | JUMPER | WIREDOWN1SNOF7649 | 20200116 | 1101 | 762714 | 337 | Distribution Circuit | Vegetation | Tree - fell into line | 119 | 31375 | 40.702 | -121.9215 | 1SNOF7649 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 20-0009909 | OH | Sus | 0 | yes | 2020 | JAN | Yes | Line to Ground | 1506857 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0019320&numberofmonths=24&showchangehistorylog=1 | 20-0019320 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE | 1971 | 20200209 | 1218 | 783724 | 262 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 786 | 39.4833 | -121.2422 | MTR1007641278 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0019320 | OH | Sus | 31490408 | yes | 2020 | FEB | Yes | Line to Ground | 1513348 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0032219&numberofmonths=24&showchangehistorylog=1 | 20-0032219 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1102 | 103201102 | OTHER | WIREDOWNMAINLINE2SOMTR1007888458 | 20200315 | 615 | 851915 | 732 | Distribution Circuit | Vegetation | Tree - fell into line | 201 | 135037 | 39.4504 | -121.2549 | MAINLINE2SPANSLDSIDEOFMTR10078884581SPANSOFMTR1010141246 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0032219 | OH | Sus | 44259032 | yes | 2020 | MAR | Yes | Line to Ground | 1521552 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0085570&numberofmonths=24&showchangehistorylog=1 | 20-0085570 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | SYCAMORE CREEK-1111 | 102971111 | RECLOSER | 2014 | 20200817 | 818 | 1015209 | 391 | Distribution Circuit | Environmental/External | Lightning | 537 | 209967 | 39.8317 | -121.8444 | REGS40 | Partly Cloudy-Lightning-Heat Wave-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0085570 | OH | Sus | 0 | yes | 2020 | AUG | Yes | Three Phase Fault | 1555966 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0094909&numberofmonths=24&showchangehistorylog=1 | 20-0094909 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | STILLWATER-1101 | 103561101 | RECLOSER | 48950 | 20200908 | 1025 | 1060925 | 673 | Distribution Circuit | Vegetation | Tree - fell into line | 256 | 172261 | 40.7039 | -122.3364 | ONMAINLINEEOF76937SPANSSOFSAP101457018 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0094909 | OH | Sus | 0 | yes | 2020 | SEP | Yes | Line to Line | 1562268 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0009558&numberofmonths=24&showchangehistorylog=1 | 21-0009558 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1104 | 102831104 | FUSE | 2755 | 20210118 | 421 | 1212092 | 544 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 9792 | 39.7584 | -121.5738 | 3RDPOLEFROMEOL | Clear-32-90F | Pole-Wood | Broken, wire on ground | 21-0009558 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Line | 1593609 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0010539&numberofmonths=24&showchangehistorylog=1 | 21-0010539 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | ORO FINO-1102 | 103031102 | RECLOSER | 38698 | 20210119 | 944 | 1216245 | 516 | Distribution Circuit | Vegetation | Tree - fell into line | 312 | 82044 | 40.0376 | -121.6179 | 2SPLDSIDEOFMTR1010383199 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0010539 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Line | 1594475 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0013592&numberofmonths=24&showchangehistorylog=1 | 21-0013592 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | OTHER | WIREDOWN5SPANSSS1596 | 20210125 | 502 | 1223363 | 566 | Distribution Circuit | Vegetation | Tree - fell into line | 779 | 429455 | 40.3606 | -121.7947 | 5SPANSSSOF1596 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0013592 | OH | Sus | 44634092 | No | 2021 | JAN | Yes | Line to Ground | 1596581 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0015779&numberofmonths=24&showchangehistorylog=1 | 21-0015779 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | CEDAR CREEK-1101 | 103321101 | FUSE | 5123 | 20210127 | 400 | 1232641 | 603 | Distribution Circuit | Vegetation | Tree - fell into line | 104 | 68050 | 40.7705 | -121.9673 | 5SPANSLDSIDEOF1631 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0015779 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1598322 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0015916&numberofmonths=24&showchangehistorylog=1 | 21-0015916 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | COTTONWOOD-1103 | 102931103 | FUSE | 7283 | 20210127 | 136 | 1231931 | 685 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 3425 | 40.3311 | -122.4117 | WIREDOWNLDSIDEOF7283 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0015916 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Line | 1598428 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0015647&numberofmonths=24&showchangehistorylog=1 | 21-0015647 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | GIRVAN-1102 | 103401102 | FUSE | 2843 | 20210127 | 329 | 1232739 | 542 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 33604 | 40.5527 | -122.4453 | 9126CHAPARRALDR | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0015647 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Line | 1598198 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0015526&numberofmonths=24&showchangehistorylog=1 | 21-0015526 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ORO FINO-1101 | 103031101 | OCB | 11012 | 20210127 | 159 | 1232087 | 891 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2336 | 1346507 | 39.8716 | -121.6113 | PALADEWES1934meter100811273114770colterrd | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0015526 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1598070 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0017650&numberofmonths=24&showchangehistorylog=1 | 21-0017650 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | CORNING-1102 | 103331102 | FUSE | 6081 | 20210128 | 1003 | 1239240 | 445 | Distribution Circuit | Environmental/External | Ice or snow | 8 | 1798 | 39.8467 | -122.59 | LDSIDEOFFU8105 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0017650 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1599751 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0115712&numberofmonths=24&showchangehistorylog=1 | 21-0115712 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | PIT NO 1-1101 | 103721101 | RECLOSER | 11012 | 20210910 | 521 | 1467342 | 785 | Distribution Circuit | Animal | Other | 883 | 299396 | 40.9903 | -121.4964 | 1SPANSSOFLR70952 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0115712 | OH | Sus | 0 | No | 2021 | SEP | Yes | Three Phase Fault | 1664638 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0132188&numberofmonths=24&showchangehistorylog=1 | 21-0132188 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1102 | 103201102 | OCB | 11022 | 20211017 | 2058 | 1500244 | 407 | Distribution Circuit | Equipment Failure/Involved | Overhead | 898 | 145162 | 39.4857 | -121.2202 | KRZYMINSKIWOODY53035630519938laporterd | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0132188 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Ground | 1675001 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0136508&numberofmonths=24&showchangehistorylog=1 | 21-0136508 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | BIG BEND-1102 | 103751102 | FUSE | 1435 | 20211024 | 739 | 1508400 | 616 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 42504 | 39.6441 | -121.4449 | CGC22154807188320STONEROAD | Strong Winds-Heavy Rain-Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0136508 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Ground | 1677986 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0136052&numberofmonths=24&showchangehistorylog=1 | 21-0136052 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1103 | 102831103 | FUSE | 4665 | 20211024 | 906 | 1509005 | 556 | Distribution Circuit | Vegetation | Tree - fell into line | 229 | 90288 | 39.7625 | -121.6287 | MTR1010956273 | Strong Winds-Heavy Rain-Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0136052 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Ground | 1677520 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0137602&numberofmonths=24&showchangehistorylog=1 | 21-0137602 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1104 | 102831104 | FUSE | 272749 | 20211025 | 1532 | 1519479 | 375 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 811 | 39.7413 | -121.5998 | 2LDSIDEOFMTR100000048130 | Strong Winds-Heavy Rain-Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0137602 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Ground | 1678907 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0157006&numberofmonths=24&showchangehistorylog=1 | 21-0157006 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | GIRVAN-1102 | 103401102 | FUSE | 3875 | 20211213 | 826 | 1565969 | 893 | Distribution Circuit | Environmental/External | Water | 16 | 2483 | 40.5668 | -122.4314 | MTR1010466811 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 21-0157006 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Line | 1693911 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0157433&numberofmonths=24&showchangehistorylog=1 | 21-0157433 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ORO FINO-1102 | 103031102 | FUSE | 3357 | 20211213 | 1438 | 1567626 | 312 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 5928 | 39.8583 | -121.6598 | 4SPANSLDSIDEOFFUCO3357 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0157433 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1694331 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0156941&numberofmonths=24&showchangehistorylog=1 | 21-0156941 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | SYCAMORE CREEK-1111 | 102971111 | FUSE | 943 | 20211213 | 424 | 1565729 | 598 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 34086 | 39.8995 | -121.7408 | MTR1007459545 | Clear-32-90F | Conductor, Overhead | On Ground | 21-0156941 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Line | 1693836 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0157724&numberofmonths=24&showchangehistorylog=1 | 21-0157724 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BIG MEADOWS-2101 | 102812101 | OTHER | 1SPANDOWN | 20211214 | 101 | 1569214 | 1253 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 10120 | 40.211 | -121.1633 | GWALTNEYCODY17841poleeastoffuses18495 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0157724 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1694622 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0157716&numberofmonths=24&showchangehistorylog=1 | 21-0157716 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | HAMILTON BRANCH-1101 | 102361101 | RECLOSER | 90334 | 20211214 | 222 | 1569053 | 1062 | Distribution Circuit | Vegetation | Tree - fell into line | 302 | 297104 | 40.2684 | -121.0876 | GWALTNEYCODY17845622hwy147 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 21-0157716 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Line | 1694613 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0157708&numberofmonths=24&showchangehistorylog=1 | 21-0157708 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER | 80454 | 20211214 | 201 | 1569263 | 734 | Distribution Circuit | Vegetation | Tree - fell into line | 239 | 175426 | 40.4341 | -121.8715 | 1SPANLDSIDE1557 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0157708 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Line | 1694604 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0160600&numberofmonths=24&showchangehistorylog=1 | 21-0160600 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | GRAYS FLAT-0401 | 102530401 | JUMPER | WIREDOWN209RIVERVIEWDR | 20211225 | 1642 | 1581491 | 198 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 594 | 40.0158 | -121.0788 | 209RIVERVIEWDR | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0160600 | OH | Sus | 0 | No | 2021 | DEC | Yes | Open Circuit | 1698079 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0160774&numberofmonths=24&showchangehistorylog=1 | 21-0160774 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1101 | 103201101 | OTHER | WIREDOWN15LDSIDEOF55453 | 20211226 | 923 | 1582593 | 377 | Distribution Circuit | Environmental/External | Ice or snow | 6 | 2262 | 39.7141 | -120.9775 | 15LDSIDEOF55453 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0160774 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1698274 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0160981&numberofmonths=24&showchangehistorylog=1 | 21-0160981 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BIG MEADOWS-2101 | 102812101 | OTHER | 1WIREDOWNHOT | 20211227 | 242 | 1584041 | 375 | Distribution Circuit | Equipment Failure/Involved | Overhead | 631 | 236625 | 40.2093 | -121.1605 | 1SSFOLR2016 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0160981 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1698511 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0161578&numberofmonths=24&showchangehistorylog=1 | 21-0161578 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1102 | 103201102 | OTHER | WIREDOWN2LDSIDEOF697 | 20211229 | 1221 | 1588470 | 263 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 5508 | 39.4742 | -121.2442 | 2LDSIDEOF697 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0161578 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1699358 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0161623&numberofmonths=24&showchangehistorylog=1 | 21-0161623 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE | 23199 | 20211229 | 1048 | 1588340 | 379 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1137 | 39.4763 | -121.2172 | 4LDSIDEOF23199 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0161623 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1699442 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0161488&numberofmonths=24&showchangehistorylog=1 | 21-0161488 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ORO FINO-1101 | 103031101 | OTHER | WIREDOWNSSOFFUCO17833 | 20211229 | 639 | 1587908 | 413 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 4776 | 39.835 | -121.5907 | SSOFFUCO17833 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0161488 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1699233 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0161638&numberofmonths=24&showchangehistorylog=1 | 21-0161638 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ORO FINO-1101 | 103031101 | FUSE | 1415 | 20211229 | 1358 | 1588874 | 320 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 960 | 39.8286 | -121.6239 | LDSIDEOFFUCO14151SPANFROMEOL | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0161638 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1699468 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0161537&numberofmonths=24&showchangehistorylog=1 | 21-0161537 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ORO FINO-1102 | 103031102 | FUSE | 27019 | 20211229 | 218 | 1587678 | 892 | Distribution Circuit | Vegetation | Tree - fell into line | 167 | 114987 | 39.8487 | -121.6167 | WIREDOWN15040VORHEISLN | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0161537 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1699310 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0138281&numberofmonths=24&showchangehistorylog=1 | 22-0138281 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | BIG BEND-1101 | 103751101 | RECLOSER | 11012 | 20221210 | 1021 | 1881519 | 545 | Distribution Circuit | Vegetation | Tree - fell into line | 312 | 93362 | 39.6769 | -121.4915 | 9SPANSLDSIDEOF17216SPANSSWOF17135 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0138281 | OH | Sus | 0 | No | 2022 | DEC | Yes | Multi-Fault | 1789115 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0138180&numberofmonths=24&showchangehistorylog=1 | 22-0138180 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1105 | 102831105 | FUSE | 1267 | 20221210 | 909 | 1880603 | 440 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 7632 | 39.816 | -121.5808 | 3SPANSBEYONDRIDGEWAYLINEBUCK | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0138180 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1789014 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0138142&numberofmonths=24&showchangehistorylog=1 | 22-0138142 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | PIT NO 3-2101 | 103732101 | RECLOSER | 1482 | 20221210 | 838 | 1880898 | 735 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 7251 | 40.9984 | -121.7477 | BETWEEN58333815 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0138142 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Line | 1788975 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0138228&numberofmonths=24&showchangehistorylog=1 | 22-0138228 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WILDWOOD-1101 | 103611101 | FUSE | 1671 | 20221210 | 845 | 1881352 | 532 | Distribution Circuit | Equipment Failure/Involved | Overhead | 38 | 20216 | 40.3889 | -123.0589 | 1SPANSS2SPANSLDSIDEOFCGC117050839249 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0138228 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Line | 1789065 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0009775&numberofmonths=24&showchangehistorylog=1 | 23-0009775 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | CLARK ROAD-1102 | 103091102 | RECLOSER | 47006 | 20230108 | 258 | 1932083 | 957 | Distribution Circuit | Vegetation | Tree - fell into line | 147 | 57924 | 39.6988 | -121.5741 | 2LDSIDEOFFUCO1951 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0009775 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1799611 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0009879&numberofmonths=24&showchangehistorylog=1 | 23-0009879 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | RISING RIVER-1101 | 103551101 | RECLOSER | 1532 | 20230108 | 655 | 1932564 | 665 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 19950 | 40.8233 | -121.5024 | 1532 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0009879 | OH | Sus | 0 | No | 2023 | JAN | Yes | Force Out | 1799728 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0010800&numberofmonths=24&showchangehistorylog=1 | 23-0010800 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | ANTLER-1101 | 103271101 | RECLOSER | 1520 | 20230109 | 548 | 1935918 | 489 | Distribution Circuit | Vegetation | Tree - fell into line | 129 | 21225 | 40.8995 | -122.3862 | ATMTR5000073248ONSINGLEPHASEHARDTAP | Clear-32-90F | Pole-Wood | Broken, wire on ground | 23-0010800 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Line | 1800661 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0010755&numberofmonths=24&showchangehistorylog=1 | 23-0010755 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1102 | 103201102 | RECLOSER | 83288 | 20230109 | 414 | 1935571 | 275 | Distribution Circuit | Vegetation | Tree - fell into line | 137 | 36059 | 39.5275 | -121.2861 | 4SPANSWOF1969 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0010755 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Line | 1800621 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0010725&numberofmonths=24&showchangehistorylog=1 | 23-0010725 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ORO FINO-1102 | 103031102 | RECLOSER | 2560 | 20230109 | 236 | 1935039 | 598 | Distribution Circuit | Vegetation | Tree - fell into line | 574 | 239699 | 39.8889 | -121.6646 | 8SPANSSSOFFUCO24075368HEADWATERSFORESTRANCH | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0010725 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1800586 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0011867&numberofmonths=24&showchangehistorylog=1 | 23-0011867 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BUTTE-1105 | 103081105 | RECLOSER | 2511 | 20230110 | 430 | 1942126 | 811 | Distribution Circuit | Vegetation | Tree - fell into line | 200 | 70691 | 39.7281 | -121.7061 | 3SPANSLDSIDEOF264131SPANSOFCGC220970777314 | Partly Cloudy-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 23-0011867 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1801634 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0015833&numberofmonths=24&showchangehistorylog=1 | 23-0015833 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | ANTLER-1101 | 103271101 | FUSE | 2243 | 20230114 | 348 | 1952763 | 891 | Distribution Circuit | Vegetation | Tree - fell into line | 164 | 50380 | 40.886 | -122.3867 | CGC118919356605 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 23-0015833 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Line | 1804679 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0015972&numberofmonths=24&showchangehistorylog=1 | 23-0015972 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BUTTE-1105 | 103081105 | RECLOSER | 612016 | 20230114 | 910 | 1953563 | 442 | Distribution Circuit | Vegetation | Tree - fell into line | 204 | 49075 | 39.7281 | -121.7061 | LUIZPATAtfuses16189 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0015972 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1804797 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0016072&numberofmonths=24&showchangehistorylog=1 | 23-0016072 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | FRENCH GULCH-1101 | 103381101 | TRIP-SAVER | 2905 | 20230114 | 755 | 1953067 | 905 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 13370 | 40.7197 | -122.6293 | 12193EASTFORKRD | Clear-32-90F | Pole-Wood | Broken, wire on ground | 23-0016072 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Line | 1804876 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0034188&numberofmonths=24&showchangehistorylog=1 | 23-0034188 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | BIG BEND-1102 | 103751102 | FUSE | 1449 | 20230224 | 814 | 2004402 | 350 | Distribution Circuit | Equipment Failure/Involved | Overhead | 85 | 29750 | 39.6529 | -121.4452 | FAILEDSPLICE1SPANLDSIDEFUCO1449WIREDOWN | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 23-0034188 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Ground | 1817093 | CSO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0033847&numberofmonths=24&showchangehistorylog=1 | 23-0033847 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CLARK ROAD-1102 | 103091102 | JUMPER | WIREDOWN1SPLDSIDEOF1711 | 20230224 | 741 | 2003573 | 494 | Distribution Circuit | Environmental/External | Ice or snow | 160 | 74763 | 39.6959 | -121.5245 | WallaceBob1sploadsideSw1711 | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0033847 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Ground | 1816859 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0034485&numberofmonths=24&showchangehistorylog=1 | 23-0034485 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | DESCHUTES-1101 | 103351101 | OTHER | 3001 | 20230224 | 1746 | 2006654 | 216 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 432 | 40.5375 | -122.159 | 3POLEFROM3001LDSIDE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0034485 | OH | Sus | 0 | No | 2023 | FEB | Yes | Open Circuit | 1817336 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0034256&numberofmonths=24&showchangehistorylog=1 | 23-0034256 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | GIRVAN-1102 | 103401102 | FUSE | 2469 | 20230224 | 724 | 2003277 | 435 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 10440 | 40.593 | -122.4887 | LOVERCHECK5302600410OKTOHOLDOWNFROMOPENJUMPERS1SPANNORTHOF1031TOEOLMAKEREPAIRSWHENCOMPLETEOKTORTCLOJ | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0034256 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Ground | 1817148 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0034107&numberofmonths=24&showchangehistorylog=1 | 23-0034107 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KANAKA-1101 | 103221101 | FUSE | 9635 | 20230224 | 835 | 2004251 | 588 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 3552 | 39.5208 | -121.2494 | 222125167428 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 23-0034107 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Line | 1817050 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0033662&numberofmonths=24&showchangehistorylog=1 | 23-0033662 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1102 | 103521102 | RECLOSER | 49144 | 20230224 | 506 | 2002710 | 539 | Distribution Circuit | Equipment Failure/Involved | Overhead | 536 | 248719 | 40.6599 | -122.3419 | 6POLESSSOFLR1584 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0033662 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Ground | 1816700 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0034298&numberofmonths=24&showchangehistorylog=1 | 23-0034298 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1103 | 103521103 | FUSE | 5721 | 20230224 | 437 | 2002466 | 837 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 11084 | 40.6614 | -122.1963 | CGC100000032785 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0034298 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Ground | 1817183 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0034169&numberofmonths=24&showchangehistorylog=1 | 23-0034169 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | RED BLUFF-1101 | 103541101 | FUSE | 85811 | 20230224 | 520 | 2005593 | 831 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 7479 | 40.2208 | -122.3799 | 17525HWY36W3SPANSWOF17525HWY36W | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0034169 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Ground | 1817083 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0033935&numberofmonths=24&showchangehistorylog=1 | 23-0033935 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WYANDOTTE-1107 | 102911107 | RECLOSER | 38438 | 20230224 | 959 | 2004228 | 1184 | Distribution Circuit | Vegetation | Tree - fell into line | 268 | 47397 | 39.4932 | -121.3706 | LDSIDEOFCGC221874467176 | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0033935 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Ground | 1816923 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0035489&numberofmonths=24&showchangehistorylog=1 | 23-0035489 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | TYLER-1105 | 103571105 | FUSE | 2069 | 20230225 | 1802 | 2009088 | 302 | Distribution Circuit | 3rd Party | Gun Shot | 5 | 1422 | 40.1065 | -122.3521 | 6SPLDSDOFFUCO2069 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0035489 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Ground | 1818336 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0036472&numberofmonths=24&showchangehistorylog=1 | 23-0036472 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | SYCAMORE CREEK-1111 | 102971111 | FUSE | 685 | 20230227 | 1126 | 2011973 | 274 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 2740 | 39.9377 | -121.724 | 2SPANSEOF685BETFIRSTPOTANDNEXTANGLEPOLE | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0036472 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Line | 1819090 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0037149&numberofmonths=24&showchangehistorylog=1 | 23-0037149 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1105 | 102831105 | RECLOSER | 829194 | 20230228 | 855 | 2014509 | 674 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3565 | 174884 | 39.8256 | -121.5974 | CG221118378549 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 23-0037149 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Ground | 1819626 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0037480&numberofmonths=24&showchangehistorylog=1 | 23-0037480 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | VOLTA-1102 | 102541102 | FUSE | 10629 | 20230228 | 1136 | 2015110 | 563 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 563 | 40.4903 | -121.8697 | EOL | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 23-0037480 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Ground | 1819854 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0045523&numberofmonths=24&showchangehistorylog=1 | 23-0045523 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | WYANDOTTE-1103 | 102911103 | RECLOSER | 640652 | 20230314 | 1604 | 2043133 | 294 | Distribution Circuit | Vegetation | Tree - fell into line | 442 | 129948 | 39.6394 | -121.4295 | RCO380565ONMAINLINE | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0045523 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1825486 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0045625&numberofmonths=24&showchangehistorylog=1 | 23-0045625 | NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WYANDOTTE-1107 | 102911107 | RECLOSER | 38438 | 20230314 | 1659 | 2043638 | 118 | Distribution Circuit | Equipment Failure/Involved | Overhead | 243 | 28674 | 39.4932 | -121.3706 | MTR1010357570 | Strong Winds-Clear-32-90 F | Pole-Wood | Broken, wire on ground | 23-0045625 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1825570 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0049162&numberofmonths=24&showchangehistorylog=1 | 23-0049162 | NORTH VALLEY | FIELD OPS NORTH | Tier 3 | BIG BEND-1101 | 103751101 | OTHER | 7031 | 20230321 | 643 | 2053576 | 272 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 1632 | 39.7737 | -121.5067 | 2SPANSLDSIDEOF7031 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on object | 23-0049162 | OH | Sus | 0 | No | 2023 | MAR | Yes | Open Circuit | 1828068 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0022762&numberofmonths=24&showchangehistorylog=1 | 13-0022762 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 1097 | 20130408 | 530 | 768882 | 780 | Distribution Circuit | Vegetation | Tree - branch fell on line | 66 | 69630 | 37.383 | -122.2632 | 314877532668 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0022762 | OH | Sus | 0 | yes | 2013 | APR | Yes | Line to Ground | 99291890 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0022777&numberofmonths=24&showchangehistorylog=1 | 13-0022777 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 8319 | 20130408 | 651 | 769004 | 1209 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 37479 | 37.3833 | -122.2487 | 314912332479 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0022777 | OH | Sus | 0 | yes | 2013 | APR | Yes | None | 99291878 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0022831&numberofmonths=24&showchangehistorylog=1 | 13-0022831 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 12917 | 20130408 | 416 | 768700 | 1336 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 8016 | 37.373 | -122.2577 | 314900832294 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0022831 | OH | Sus | 0 | yes | 2013 | APR | Yes | Line to Ground | 99291835 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078168&numberofmonths=24&showchangehistorylog=1 | 13-0078168 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | OTHER |  | 20131121 | 2105 | 909907 | 453 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 11325 | 37.3132 | -122.2723 | CLARK1076241866redwood | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078168 | OH | Sus | 41991611 | yes | 2013 | NOV | Yes | Open Circuit | 99251942 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0073444&numberofmonths=24&showchangehistorylog=1 | 14-0073444 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 8981 | 20141203 | 1132 | 1123022 | 676 | Distribution Circuit | Vegetation | Tree - bark fell into line | 60 | 39445 | 37.388 | -122.267 | CRAMERCHRIS307BlakewoodWayRedwoodCityWoodsidearea | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073444 | OH | Sus | 31118268 | yes | 2014 | DEC | Yes | Line to Ground | 99196797 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0073538&numberofmonths=24&showchangehistorylog=1 | 14-0073538 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 5417 | 20141203 | 1100 | 1122489 | 1029 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 44247 | 37.3891 | -122.2663 | CRAMERCHRIS85StadlerWoodside | Heavy rain-32 - 90 F | Conductor, Overhead | On Ground | 14-0073538 | OH | Sus | 42283848 | yes | 2014 | DEC | Yes | Line to Ground | 99196726 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075835&numberofmonths=24&showchangehistorylog=1 | 14-0075835 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | HALF MOON BAY-1101 | 24101101 | FUSE | 8607 | 20141211 | 812 | 1131405 | 2198 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 17584 | 37.4451 | -122.3314 | 13424SKYLINEBLVDWS | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075835 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194258 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075453&numberofmonths=24&showchangehistorylog=1 | 14-0075453 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 4279 | 20141211 | 653 | 1131371 | 380 | Distribution Circuit | Vegetation | Tree - branch fell on line | 93 | 27093 | 37.318 | -122.3007 | EPPERSONCHAD83216748129lahondardlahonda | Rain-32 - 90 F | Anchor or Guy | Broken, wire on object | 14-0075453 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194861 | ANC | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075467&numberofmonths=24&showchangehistorylog=1 | 14-0075467 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 1067 | 20141211 | 823 | 1131545 | 887 | Distribution Circuit | Equipment Failure/Involved | Other | 13 | 11531 | 37.1848 | -122.385 | LDSIDECOUTS1067 | Rain-32 - 90 F | Conductor, Overhead | On Ground | 14-0075467 | OH | Sus | 0 | yes | 2014 | DEC | Yes |  | 99194851 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075510&numberofmonths=24&showchangehistorylog=1 | 14-0075510 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | OTHER |  | 20141211 | 1320 | 1133906 | 532 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 12768 | 37.3138 | -122.276 | 3NOFLR8898 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075510 | OH | Sus | 31120659 | yes | 2014 | DEC | Yes | Line to Ground | 99194818 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075627&numberofmonths=24&showchangehistorylog=1 | 14-0075627 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 1127 | 20141211 | 752 | 1133548 | 758 | Distribution Circuit | Equipment Failure/Involved | Other | 34 | 25772 | 37.2549 | -122.3458 | SERINITYVALLEYRDRANCHRDPESCADERO | Rain-32 - 90 F | Conductor, Overhead | On Ground | 14-0075627 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194736 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075639&numberofmonths=24&showchangehistorylog=1 | 14-0075639 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | OTHER |  | 20141211 | 835 | 1134718 | 1210 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 20570 | 37.2376 | -122.321 | 675REDWOOD | Rain-32 - 90 F | Conductor, Overhead | On Ground | 14-0075639 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194727 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076299&numberofmonths=24&showchangehistorylog=1 | 14-0076299 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 7687 | 20141211 | 529 | 1138004 | 2596 | Distribution Circuit | Equipment Failure/Involved | Other | 20 | 51920 | 37.1697 | -122.2993 | 6SPANLDSIDE7687 | Rain-32 - 90 F | Conductor, Overhead | On Ground | 14-0076299 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99193490 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076301&numberofmonths=24&showchangehistorylog=1 | 14-0076301 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 13213 | 20141211 | 936 | 1132317 | 3529 | Distribution Circuit | Equipment Failure/Involved | Other | 5 | 14960 | 37.1703 | -122.2999 | WIREDOWNWHITEHOUSESYNRDPESCADERO | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076301 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99193489 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075502&numberofmonths=24&showchangehistorylog=1 | 14-0075502 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | RECLOSER | 8512 | 20141211 | 1323 | 1133890 | 197 | Distribution Circuit | Equipment Failure/Involved | Other | 143 | 27170 | 37.2891 | -122.213 | 1SOF65911PHASEDOWNONGRD | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075502 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194823 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076457&numberofmonths=24&showchangehistorylog=1 | 14-0076457 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | FUSE | 13331 | 20141211 | 1922 | 1135637 | 1748 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 24472 | 37.2567 | -122.2159 | PORTOLASTATEPARKMAINTENANCEYARDTOTHERIGHTOFTHECAMPGROUNDS | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076457 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99193909 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075181&numberofmonths=24&showchangehistorylog=1 | 14-0075181 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | RECLOSER | 8972 | 20141211 | 848 | 1131818 | 95 | Distribution Circuit | Equipment Failure/Involved | Other | 68 | 6460 | 37.4184 | -122.3223 | 10SPANSLDSIDEOFLR8972 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 14-0075181 | OH | Sus | 0 | yes | 2014 | DEC | Yes |  | 99195080 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075739&numberofmonths=24&showchangehistorylog=1 | 14-0075739 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 8615 | 20141211 | 1138 | 1135029 | 1686 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 23604 | 37.4249 | -122.3135 | 1942KINGSMTRDWOODSIDE | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075739 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194293 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075765&numberofmonths=24&showchangehistorylog=1 | 14-0075765 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 7487 | 20141211 | 1818 | 1135345 | 1047 | Distribution Circuit | Equipment Failure/Involved | Other | 6 | 6282 | 37.3818 | -122.2646 | 200KEBETRDWOODSIDE | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075765 | OH | Sus | 0 | yes | 2014 | DEC | Yes | None | 99194285 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076355&numberofmonths=24&showchangehistorylog=1 | 14-0076355 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 7969 | 20141211 | 1537 | ODB-9919 | 3078 | Distribution Circuit | Equipment Failure/Involved | Other | 2 | 6156 | 37.3833 | -122.2727 | RO14591LAHONDARDVERYENDKEBETRIDGERDWOODSIDE | Clear-32 - 90 F | Conductor, Overhead | On Ground | 14-0076355 | OH | Sus | 0 | yes | 2014 | DEC | Yes |  | 99193482 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076629&numberofmonths=24&showchangehistorylog=1 | 14-0076629 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 4099 | 20141212 | 2215 | 1139311 | 807 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 10491 | 37.3932 | -122.2705 | LDSIDE4099 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076629 | OH | Sus | 31120659 | yes | 2014 | DEC | Yes | Line to Ground | 99193426 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079526&numberofmonths=24&showchangehistorylog=1 | 14-0079526 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | BERESFORD-0403 | 24040403 | OTHER |  | 20141230 | 1950 | 1155308 | 1412 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1412 | 37.5548 | -122.3429 | 1SPANLDSIDEOF9225 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079526 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99190117 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079363&numberofmonths=24&showchangehistorylog=1 | 14-0079363 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | OTHER |  | 20141230 | 1557 | 1153668 | 1386 | Distribution Circuit | Vegetation | Tree - branch fell on line | 55 | 75738 | 37.2653 | -122.2106 | 5PLDSIDELR8982 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079363 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Open Circuit | 99190152 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079243&numberofmonths=24&showchangehistorylog=1 | 14-0079243 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 4429 | 20141230 | 1432 | 1153418 | 1488 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 40176 | 37.3875 | -122.2745 | WIREDOWN4429 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079243 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99190176 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010578&numberofmonths=24&showchangehistorylog=1 | 15-0010578 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | OTHER |  | 20150206 | 1407 | 1177361 | 3068 | Distribution Circuit | Equipment Failure/Involved | Other | 376 | 161503 | 37.2876 | -122.2731 | CLARK1076241811000vpescaderocrkrdjonesgulchymcacamp | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010578 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183411 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010125&numberofmonths=24&showchangehistorylog=1 | 15-0010125 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | PACIFICA-1103 | 22811103 | RECLOSER | 3907 | 20150206 | 1229 | 1174920 | 917 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 13755 | 37.5843 | -122.4997 | CLARK10762418mcneeranchR340to6007and1spanNorth | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010125 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99184647 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010652&numberofmonths=24&showchangehistorylog=1 | 15-0010652 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1104 | 24251104 | FUSE | 3575 | 20150206 | 1858 | 1177970 | 972 | Distribution Circuit | Equipment Failure/Involved | Other | 27 | 26244 | 37.4303 | -122.2787 | KUHLS8361865treetopfellintolinebrokearmandwiredwn | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010652 | OH | Sus | 31132845 | yes | 2015 | FEB | Yes | Line to Line | 99184575 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011148&numberofmonths=24&showchangehistorylog=1 | 15-0011148 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | SWITCH | 2031 | 20150207 | 939 | 1180953 | 431 | Distribution Circuit | Equipment Failure/Involved | Other | 66 | 28446 | 37.3109 | -122.2759 | 1MILESOF2031 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 15-0011148 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99184372 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011160&numberofmonths=24&showchangehistorylog=1 | 15-0011160 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 4279 | 20150207 | 941 | 1180796 | 139 | Distribution Circuit | Equipment Failure/Involved | Other | 93 | 12927 | 37.318 | -122.3007 | 1MILES2031 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 15-0011160 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99184365 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011719&numberofmonths=24&showchangehistorylog=1 | 15-0011719 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | BERESFORD-0403 | 24040403 | OTHER |  | 20150208 | 1814 | 1183727 | 716 | Distribution Circuit | Vegetation | Tree - fell into line | 625 | 46772 | 37.553 | -122.339 | CrystalSprings2PEofElCerritoSanMateo | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 15-0011719 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183327 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011987&numberofmonths=24&showchangehistorylog=1 | 15-0011987 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | CAROLANDS-0404 | 24060404 | FUSE | 1723 | 20150208 | 2200 | 1185226 | 869 | Distribution Circuit | Equipment Failure/Involved | Other | 64 | 55616 | 37.5591 | -122.3547 | 400BLKELCENTROHILLSBOROUGH | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011987 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183241 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011941&numberofmonths=24&showchangehistorylog=1 | 15-0011941 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | EMERALD LAKE-0401 | 24080401 | TRANSFORMER |  | 20150208 | 1744 | 1185526 | 1387 | Distribution Circuit | Equipment Failure/Involved | Other | 37 | 33687 | 37.4535 | -122.2671 | ODRISCOLL84016734147JEFFERSONAVERWC | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011941 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183264 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011695&numberofmonths=24&showchangehistorylog=1 | 15-0011695 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 8981 | 20150208 | 1544 | 1183225 | 1546 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 50146 | 37.388 | -122.267 | IRO16995SKYLINE | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 15-0011695 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183332 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0084772&numberofmonths=24&showchangehistorylog=1 | 15-0084772 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | BERESFORD-0403 | 24040403 | OTHER | WIREDOWN | 20151213 | 1014 | 1361230 | 276 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 3334 | 37.5506 | -122.3479 | 975LASENDA | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084772 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1174440 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0084641&numberofmonths=24&showchangehistorylog=1 | 15-0084641 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1102 | 24131102 | FUSE | 4963 | 20151213 | 919 | 1360775 | 504 | Distribution Circuit | Vegetation | Tree - fell into line | 333 | 167832 | 37.3512 | -122.1983 | HULGAN83718624spansloadsideofsw4963 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084641 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1174307 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0084881&numberofmonths=24&showchangehistorylog=1 | 15-0084881 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 4133 | 20151213 | 1100 | 1361605 | 575 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2300 | 37.3882 | -122.2633 | 3SPANLDSIDEOFFICO4133 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084881 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1174548 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0087178&numberofmonths=24&showchangehistorylog=1 | 15-0087178 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | BELMONT-1103 | 24031103 | FUSE | 4913 | 20151224 | 1958 | 1371392 | 945 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 45285 | 37.4949 | -122.2783 | 255WINDINGWAY | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0087178 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1177258 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017669&numberofmonths=24&showchangehistorylog=1 | 16-0017669 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 12185 | 20160305 | 1610 | 1417315 | 717 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 25095 | 37.3752 | -122.3774 | 8POLENORTHOFFUSE12185 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017669 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1189525 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017983&numberofmonths=24&showchangehistorylog=1 | 16-0017983 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 8739 | 20160305 | 1751 | 1417798 | 424 | Distribution Circuit | Equipment Failure/Involved | Overhead | 67 | 12904 | 37.4311 | -122.3842 | 8939 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017983 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1189854 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0018008&numberofmonths=24&showchangehistorylog=1 | 16-0018008 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | OTHER | WIREDOWN9NOF8898 | 20160305 | 2101 | 1419333 | 470 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 9225 | 37.316 | -122.2745 | 9NOFLR8898 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018008 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Open Circuit | 1189879 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0018045&numberofmonths=24&showchangehistorylog=1 | 16-0018045 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | RECLOSER | 98440 | 20160305 | 1614 | 1417174 | 1256 | Distribution Circuit | Vegetation | Tree - branch fell on line | 153 | 189248 | 37.2667 | -122.3225 | 1W4247WIREDOWN2SOSW81321 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | On Ground | 16-0018045 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1189916 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017753&numberofmonths=24&showchangehistorylog=1 | 16-0017753 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 8311 | 20160305 | 1627 | 1417226 | 1240 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 1240 | 37.3837 | -122.2468 | EPPERSONCHAD8321674rear485oldlahondard | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017753 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1189607 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017826&numberofmonths=24&showchangehistorylog=1 | 16-0017826 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1104 | 24251104 | FUSE | 3585 | 20160305 | 1627 | 1417227 | 381 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 6096 | 37.424 | -122.2753 | 1PSOFFUSE3585 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017826 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1189680 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0003329&numberofmonths=24&showchangehistorylog=1 | 17-0003329 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | FUSE | 3217 | 20170103 | 2009 | 1616723 | 913 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 14608 | 37.294 | -122.2409 | 2SPANSLDSIDEOFFU3217 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003329 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1243503 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0003321&numberofmonths=24&showchangehistorylog=1 | 17-0003321 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 8605 | 20170103 | 2041 | 1616773 | 1111 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 17776 | 37.4343 | -122.3232 | IFO347RIDGERD | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003321 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1243496 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005286&numberofmonths=24&showchangehistorylog=1 | 17-0005286 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | HALF MOON BAY-1101 | 24101101 | RECLOSER | 8972 | 20170108 | 1251 | 1626502 | 1650 | Distribution Circuit | Vegetation | Tree - branch fell on line | 68 | 92895 | 37.4185 | -122.3224 | SWETTRD2SPANSEOFSTARHILLRD | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | On Ground | 17-0005286 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245076 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005168&numberofmonths=24&showchangehistorylog=1 | 17-0005168 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | OTHER | WIREDOWNMTR10058597405 | 20170108 | 1009 | 1625271 | 1556 | Distribution Circuit | Vegetation | Tree - branch fell on line | 29 | 39020 | 37.3132 | -122.2723 | IFO105REDWOOD | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005168 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1244963 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005329&numberofmonths=24&showchangehistorylog=1 | 17-0005329 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 4265 | 20170108 | 1236 | 1626875 | 1409 | Distribution Circuit | Vegetation | Tree - branch fell on line | 53 | 57153 | 37.3182 | -122.2718 | SCHLOCKERJEFF32sequoialahonda | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005329 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245119 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005515&numberofmonths=24&showchangehistorylog=1 | 17-0005515 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | RECLOSER | 98440 | 20170108 | 1126 | 1627946 | 1754 | Distribution Circuit | Equipment Failure/Involved | Overhead | 142 | 63454 | 37.2667 | -122.3224 | WIREDOWNLINESIDE10463TWD5585 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005515 | OH | Sus | 0 | yes | 2017 | JAN | Yes | None | 1245298 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005965&numberofmonths=24&showchangehistorylog=1 | 17-0005965 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 1127 | 20170108 | 1450 | 1627471 | 3146 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 102792 | 37.2549 | -122.3459 | CLARK10762418851nativesonrdpescader | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005965 | OH | Sus | 31294580 | yes | 2017 | JAN | Yes | Line to Ground | 1245732 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005971&numberofmonths=24&showchangehistorylog=1 | 17-0005971 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 5523 | 20170108 | 859 | 1623846 | 3381 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 10143 | 37.3128 | -122.2899 | SCHLOCKERJEFF7255lahondardlahonda | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005971 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245737 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006049&numberofmonths=24&showchangehistorylog=1 | 17-0006049 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 8465 | 20170108 | 1530 | 1630921 | 1167 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 7002 | 37.2619 | -122.3363 | unknown | Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0006049 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245790 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005033&numberofmonths=24&showchangehistorylog=1 | 17-0005033 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-0401 | 24130401 | OTHER | WIREDOWN | 20170108 | 113 | 1623835 | 1091 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 58679 | 37.267 | -122.2112 | INFRONTOFPORTOLASTATEPARKENTRANCE | Strong Winds-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005033 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1244831 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005507&numberofmonths=24&showchangehistorylog=1 | 17-0005507 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | PACIFICA-1103 | 22811103 | JUMPER | WIREDOWNCUTLDSDDE | 20170108 | 1531 | 1628055 | 1389 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 16821 | 37.5829 | -122.4971 | 1637HIGGINSWAY | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005507 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245290 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0004910&numberofmonths=24&showchangehistorylog=1 | 17-0004910 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 8615 | 20170108 | 320 | 1622495 | 716 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 10024 | 37.4248 | -122.3133 | KingsMtnRd4PEOSkylinetoT1306Woodside | Overcast-Fog-Heavy Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0004910 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1244711 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005177&numberofmonths=24&showchangehistorylog=1 | 17-0005177 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | OTHER | WIREDOWNMTR1003838035 | 20170108 | 833 | 1623805 | 899 | Distribution Circuit | Vegetation | Tree - fell into line | 110 | 82091 | 37.3821 | -122.2387 | EPPERSONCHAD8321674171trinity | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005177 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1244971 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005275&numberofmonths=24&showchangehistorylog=1 | 17-0005275 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 7487 | 20170108 | 1012 | 1624697 | 4798 | Distribution Circuit | Vegetation | Tree - fell into line | 65 | 201521 | 37.3818 | -122.2647 | HIGHTOWERWILLIAMCO7487 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005275 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245065 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005339&numberofmonths=24&showchangehistorylog=1 | 17-0005339 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 13255 | 20170108 | 944 | 1624335 | 1522 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 18264 | 37.379 | -122.2608 | SCHAPPERT258922681priwireand1secwiredown | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | On Ground | 17-0005339 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245129 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005665&numberofmonths=24&showchangehistorylog=1 | 17-0005665 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | OTHER | WIREDOWNMARINERD | 20170108 | 1817 | 1628988 | 1351 | Distribution Circuit | Vegetation | Tree - fell into line | 193 | 26371 | 37.4335 | -122.323 | LDSIDEOF8605 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005665 | OH | Sus | 31294580 | yes | 2017 | JAN | Yes | Line to Ground | 1245446 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005927&numberofmonths=24&showchangehistorylog=1 | 17-0005927 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 4433 | 20170108 | 2217 | 1629643 | 3020 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 33220 | 37.3844 | -122.2611 | LOADSIDEOF4433 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005927 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245705 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006088&numberofmonths=24&showchangehistorylog=1 | 17-0006088 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 4241 | 20170109 | 1145 | 1631090 | 20 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 60 | 37.2624 | -122.3234 | unknown | Strong Winds-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0006088 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245817 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006008&numberofmonths=24&showchangehistorylog=1 | 17-0006008 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-0401 | 24130401 | SWITCH | 6743 | 20170109 | 952 | 1630373 | 748 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2244 | 37.2943 | -122.1687 | 6SPANNORTHOF6743 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0006008 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245756 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006295&numberofmonths=24&showchangehistorylog=1 | 17-0006295 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 4431 | 20170109 | 1930 | 1632155 | 1758 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 25516 | 37.3856 | -122.2614 | 950ESPINOZA | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006295 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245993 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007206&numberofmonths=24&showchangehistorylog=1 | 17-0007206 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | EMERALD LAKE-0401 | 24080401 | FUSE | 267759 | 20170110 | 1745 | 1637906 | 1681 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1681 | 37.4699 | -122.3151 | JUSTLDSIDEOFFU267759 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007206 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246786 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006851&numberofmonths=24&showchangehistorylog=1 | 17-0006851 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 7985 | 20170110 | 1724 | 1634683 | 2670 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 5340 | 37.2086 | -122.3251 | 20SPANSLOADSIDEOFFUSE7985 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006851 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246432 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006973&numberofmonths=24&showchangehistorylog=1 | 17-0006973 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | JUMPER | WIREDOWNLAFONDARDEOF4133 | 20170110 | 1937 | 1636276 | 2999 | Distribution Circuit | Vegetation | Tree - fell into line | 246 | 25597 | 37.3887 | -122.2636 | LAHONDARDEOFFU4133 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006973 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Force Out | 1246555 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007175&numberofmonths=24&showchangehistorylog=1 | 17-0007175 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | JUMPER | WIREDOWN17000SKYLINE | 20170110 | 1742 | 1637400 | 1688 | Distribution Circuit | Vegetation | Tree - fell into line | 1692 | 805011 | 37.3914 | -122.2729 | 17000SKYLINE | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007175 | OH | Sus | 31294580 | yes | 2017 | JAN | Yes | Force Out | 1246760 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006723&numberofmonths=24&showchangehistorylog=1 | 17-0006723 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1104 | 24251104 | FUSE | 9169 | 20170110 | 1414 | 1633654 | 868 | Distribution Circuit | Vegetation | Tree - branch fell on line | 74 | 64232 | 37.4234 | -122.277 | LOADSIDECROSSARM | Overcast-Heavy Rain-32-90 F | Crossarm, Wood | Broken, wire on object | 17-0006723 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246331 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007870&numberofmonths=24&showchangehistorylog=1 | 17-0007870 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | HALF MOON BAY-1101 | 24101101 | FUSE | 8607 | 20170111 | 1649 | 1640373 | 1423 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 11384 | 37.4452 | -122.3314 | SCHLOCKERJEFFtwospansloadside8607woodside | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007870 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247329 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007567&numberofmonths=24&showchangehistorylog=1 | 17-0007567 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | SWITCH | 1015 | 20170111 | 1107 | 1639568 | 8 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 472 | 37.2717 | -122.2987 | WURRRD | Overcast-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0007567 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247096 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007567&numberofmonths=24&showchangehistorylog=1 | 17-0007567 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | SWITCH | 517 | 20170111 | 1130 | 1639630 | 674 | Distribution Circuit | Vegetation | Tree - fell into line | 81 | 54594 | 37.2833 | -122.2835 | WURRRD | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0007567 | OH | Sus | 42913270 | yes | 2017 | JAN | Yes | Line to Ground | 1247107 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007876&numberofmonths=24&showchangehistorylog=1 | 17-0007876 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 1097 | 20170111 | 1148 | 1639760 | 381 | Distribution Circuit | Vegetation | Tree - branch fell on line | 41 | 15621 | 37.383 | -122.2634 | LDSIDEOF8607 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007876 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247333 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0008382&numberofmonths=24&showchangehistorylog=1 | 17-0008382 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 4429 | 20170111 | 2041 | 1641184 | 2104 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 10520 | 37.3876 | -122.2746 | 2PSOUTHOF4429 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0008382 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247782 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0010229&numberofmonths=24&showchangehistorylog=1 | 17-0010229 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1102 | 24131102 | FUSE | 4945 | 20170118 | 1533 | 1646768 | 1490 | Distribution Circuit | Equipment Failure/Involved | Overhead | 39 | 58110 | 37.3329 | -122.2306 | 2SPANE11527 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | On Ground | 17-0010229 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1249234 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0010356&numberofmonths=24&showchangehistorylog=1 | 17-0010356 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | RECLOSER | 47872 | 20170118 | 1923 | 1648539 | 618 | Distribution Circuit | Vegetation | Tree - branch fell on line | 226 | 148279 | 37.4182 | -122.3194 | 1SLR39480 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010356 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1249368 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011429&numberofmonths=24&showchangehistorylog=1 | 17-0011429 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 11229 | 20170120 | 736 | 1653033 | 508 | Distribution Circuit | Vegetation | Tree - branch fell on line | 67 | 34036 | 37.2307 | -122.3261 | 520REDWOODAVE | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011429 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1250312 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011669&numberofmonths=24&showchangehistorylog=1 | 17-0011669 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | FUSE | 4311 | 20170120 | 1359 | 1654381 | 1056 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 15840 | 37.3049 | -122.268 | 8SPANSLDSIDEOF4311 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011669 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Three Phase Fault | 1250518 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012704&numberofmonths=24&showchangehistorylog=1 | 17-0012704 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 5703 | 20170122 | 315 | 1658576 | 772 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2316 | 37.2697 | -122.3158 | SCHLOCKERJEFF1eastofcutouts5703 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0012704 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1251527 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012809&numberofmonths=24&showchangehistorylog=1 | 17-0012809 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | OTHER | WIREDOWN | 20170122 | 426 | 1658740 | 507 | Distribution Circuit | Vegetation | Tree - branch fell on line | 579 | 9755 | 37.317 | -122.3028 | SCHLOCKERJEFF1sof4933cutouts111peekaboolnlahonda | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012809 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1251631 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013115&numberofmonths=24&showchangehistorylog=1 | 17-0013115 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | JUMPER | 1117 | 20170122 | 1200 | 1660898 | 705 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 2820 | 37.2878 | -122.2728 | LDSIDE1117 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013115 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1251934 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013217&numberofmonths=24&showchangehistorylog=1 | 17-0013217 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 1067 | 20170122 | 914 | 1660216 | 811 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 10543 | 37.1848 | -122.385 | SCHLOCKERJEFFthreelocations17linesideco77131spansonmainlinefromco1067 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013217 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1252026 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013347&numberofmonths=24&showchangehistorylog=1 | 17-0013347 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 4995 | 20170122 | 1603 | 1661628 | 4484 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 98648 | 37.2876 | -122.2464 | ODRISCOLL8401673UPDRIVEWAYOF9700ALPINERDLAHONDA | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013347 | OH | Sus | 42928223 | yes | 2017 | JAN | Yes | Line to Line | 1252162 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012863&numberofmonths=24&showchangehistorylog=1 | 17-0012863 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | FUSE | 1721 | 20170122 | 447 | 1658815 | 528 | Distribution Circuit | Equipment Failure/Involved | Overhead | 50 | 26400 | 37.318 | -122.1911 | 1MILELDSIDEOFCOUTS1721 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012863 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1251686 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013075&numberofmonths=24&showchangehistorylog=1 | 17-0013075 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | OTHER | WIREDOWN4SPLINESIDE4737 | 20170122 | 949 | 1660198 | 790 | Distribution Circuit | Vegetation | Tree - fell into line | 68 | 19915 | 37.4036 | -122.3352 | 2SPSO1STTXON3PHASELINE4SPANSLINESIDEOF4737 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013075 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Open Circuit | 1251893 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018292&numberofmonths=24&showchangehistorylog=1 | 17-0018292 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 1127 | 20170207 | 601 | 1678185 | 1010 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 34340 | 37.2549 | -122.3459 | CLARK107624184thpolefromco1127NativeSonspescaderocrkrd | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018292 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1256132 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018614&numberofmonths=24&showchangehistorylog=1 | 17-0018614 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 8125 | 20170207 | 906 | -1680268 | 1048 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 39824 | 37.1459 | -122.3363 | CLARK1076241831poleeastofco812523milesinonwhitehousecyn |  | Conductor, Overhead | Broken, wire on ground | 17-0018614 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1256385 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018195&numberofmonths=24&showchangehistorylog=1 | 17-0018195 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 1097 | 20170207 | 639 | 1678242 | 837 | Distribution Circuit | Equipment Failure/Involved | Overhead | 314 | 69594 | 37.383 | -122.2634 | 14150HYWY84 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0018195 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1256056 | PW | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018462&numberofmonths=24&showchangehistorylog=1 | 17-0018462 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 4737 | 20170207 | 942 | 1679537 | 708 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 14160 | 37.4023 | -122.3361 | 1492STARHILL | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | On Ground | 17-0018462 | OH | Sus | 31304022 | yes | 2017 | FEB | Yes | Line to Ground | 1256274 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018677&numberofmonths=24&showchangehistorylog=1 | 17-0018677 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | SWITCH | 11417 | 20170207 | 941 | 1680647 | 1818 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 54540 | 37.3884 | -122.2722 | MULTIPLECASESOFWIREDOWN | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018677 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1256443 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0019634&numberofmonths=24&showchangehistorylog=1 | 17-0019634 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 8125 | 20170209 | 1900 | 1684093 | 1252 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 47576 | 37.1459 | -122.3363 | 27spansLDSIDEOF8125 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019634 | OH | Sus | 31304022 | yes | 2017 | FEB | Yes | Line to Ground | 1257105 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0019761&numberofmonths=24&showchangehistorylog=1 | 17-0019761 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 1127 | 20170209 | 2302 | 1684331 | 1058 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 15215 | 37.2549 | -122.3459 | 2SPANSLDSIDEOF1127 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019761 | OH | Sus | 42939220 | yes | 2017 | FEB | Yes | Line to Ground | 1257232 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0019480&numberofmonths=24&showchangehistorylog=1 | 17-0019480 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | RECLOSER | 8884 | 20170209 | 1345 | 1683562 | 524 | Distribution Circuit | Environmental/External | Flood/Erosion | 341 | 29789 | 37.3895 | -122.2687 | 12MILELDSIDEOFLR8884 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019480 | OH | Sus | 42939220 | yes | 2017 | FEB | Yes | Force Out | 1256994 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0021980&numberofmonths=24&showchangehistorylog=1 | 17-0021980 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | RECLOSER | 8512 | 20170217 | 951 | 1693622 | 204 | Distribution Circuit | Vegetation | Tree - fell into line | 142 | 24271 | 37.2891 | -122.2132 | 1POLESS6591 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0021980 | OH | Sus | 42950847 | yes | 2017 | FEB | Yes | Line to Ground | 1259083 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0022113&numberofmonths=24&showchangehistorylog=1 | 17-0022113 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | FUSE | 4961 | 20170217 | 938 | 1693429 | 844 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 3354 | 37.2944 | -122.1639 | 4SPANSO6743 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022113 | OH | Sus | 31306686 | yes | 2017 | FEB | Yes | Line to Ground | 1259196 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0022911&numberofmonths=24&showchangehistorylog=1 | 17-0022911 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | JUMPER | 4279 | 20170218 | 614 | 1699086 | 468 | Distribution Circuit | Vegetation | Tree - fell into line | 160 | 36457 | 37.3172 | -122.2946 | 10SPLDSIDE4279 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022911 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1259925 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024267&numberofmonths=24&showchangehistorylog=1 | 17-0024267 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | BERESFORD-0403 | 24040403 | JUMPER | WIREDOWNIFO773ELCERRITOAVE | 20170220 | 2026 | 1705900 | 394 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 4291 | 37.553 | -122.3399 | 773ELCERRITOAVE | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024267 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1261232 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023767&numberofmonths=24&showchangehistorylog=1 | 17-0023767 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | JUMPER | UNNUMBEREDDISC | 20170220 | 1040 | 1702873 | 903 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 34314 | 37.166 | -122.3224 | 34POLESLDSIDEOF8125HMB | Clear-32-90 F | Conductor, Overhead | On Ground | 17-0023767 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1260757 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024165&numberofmonths=24&showchangehistorylog=1 | 17-0024165 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 4319 | 20170220 | 1804 | 1705161 | 2743 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 21944 | 37.2992 | -122.2642 | VARIOUSLOCATIONSLDSIDEOF4319 | Overcast-Heavy Rain-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0024165 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1261131 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024680&numberofmonths=24&showchangehistorylog=1 | 17-0024680 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | TRIP-SAVER | 8089 | 20170220 | 1635 | 1704608 | 1443 | Distribution Circuit | Equipment Failure/Involved | Overhead | 106 | 152958 | 37.2193 | -122.3422 | 22SPANSLDSIDEOF8089 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0024680 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1261646 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024802&numberofmonths=24&showchangehistorylog=1 | 17-0024802 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | FUSE | 1721 | 20170220 | 2044 | 1706007 | 2447 | Distribution Circuit | Vegetation | Tree - branch fell on line | 50 | 122350 | 37.318 | -122.1911 | ONSKYLINERD1MILESOFALPINERD | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024802 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1261771 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023662&numberofmonths=24&showchangehistorylog=1 | 17-0023662 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | RECLOSER | 8974 | 20170220 | 639 | 1702537 | 527 | Distribution Circuit | Vegetation | Tree - fell into line | 314 | 44742 | 37.3881 | -122.2669 | LAHONDARDSOF11493 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023662 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1260665 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023943&numberofmonths=24&showchangehistorylog=1 | 17-0023943 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | OTHER | WIREDOWN16995SKYLINEBLVD | 20170220 | 1647 | 1704369 | 782 | Distribution Circuit | Vegetation | Tree - fell into line | 341 | 58195 | 37.3911 | -122.2746 | 16995SKYLINEBLVD | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023943 | OH | Sus | 0 | yes | 2017 | FEB | Yes | None | 1260917 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025078&numberofmonths=24&showchangehistorylog=1 | 17-0025078 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 4737 | 20170220 | 2029 | 1705908 | 1421 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 28420 | 37.4023 | -122.3361 | 1492STARHILL | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025078 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1262014 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025169&numberofmonths=24&showchangehistorylog=1 | 17-0025169 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1101 | 24101101 | FUSE | 10695 | 20170221 | 1341 | 1708768 | 349 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 5933 | 37.4861 | -122.4191 | CLARK10762418diggscyn6spansloadsideco10695 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025169 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Three Phase Fault | 1262080 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024948&numberofmonths=24&showchangehistorylog=1 | 17-0024948 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | RECLOSER | 6018 | 20170221 | 829 | 1707906 | 432 | Distribution Circuit | Vegetation | Tree - fell into line | 927 | 156962 | 37.3265 | -122.3875 | IRO2550PESCADEROCREEKRDPESC | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024948 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1261919 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037356&numberofmonths=24&showchangehistorylog=1 | 17-0037356 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | RECLOSER | 8982 | 20170406 | 1939 | 1748111 | 1358 | Distribution Circuit | Equipment Failure/Involved | Overhead | 55 | 74690 | 37.2682 | -122.2113 | WIREDOWN2SPANSLDSIDEOFLR8982 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037356 | OH | Sus | 0 | yes | 2017 | APR | Yes | Force Out | 1271566 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037279&numberofmonths=24&showchangehistorylog=1 | 17-0037279 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | RECLOSER | 8972 | 20170406 | 2028 | 1746810 | 1412 | Distribution Circuit | Vegetation | Tree - fell into line | 68 | 96016 | 37.4185 | -122.3224 | OKRYDONNIE2413treebroketopofpole345SWETTRD | Overcast-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0037279 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1271497 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037971&numberofmonths=24&showchangehistorylog=1 | 17-0037971 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | TRIP-SAVER | 8601 | 20170406 | 2039 | 1746939 | 1366 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 57372 | 37.4388 | -122.3234 | IRO235OLDRANCHRD | Overcast-Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0037971 | OH | Sus | 31316082 | yes | 2017 | APR | Yes | Line to Ground | 1272068 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0075505&numberofmonths=24&showchangehistorylog=1 | 17-0075505 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1102 | 24131102 | JUMPER | WIREONGROUNDTWD7550ALPINERD | 20170903 | 828 | 1867889 | 1231 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2750 | 37.283 | -122.224 | SourceSOF7550AlpineRd | Clear-Heat Wave-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0075505 | OH | Sus | 0 | yes | 2017 | SEP | Yes | Line to Ground | 1299794 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0075627&numberofmonths=24&showchangehistorylog=1 | 17-0075627 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1102 | 24131102 | JUMPER | OJ8POLES13329 | 20170903 | 1626 | 1869183 | 1341 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 4023 | 37.2539 | -122.2183 | 8POLESLDSIDEOF13329 | Clear-Heat Wave-Above 90 | Conductor, Overhead | Broken, wire on ground | 17-0075627 | OH | Sus | 0 | yes | 2017 | SEP | Yes | Line to Ground | 1299910 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0077883&numberofmonths=24&showchangehistorylog=1 | 17-0077883 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | SNEATH LANE-1106 | 22721106 | OTHER | WIREDOWNJUSTLDSIDEOF11089 | 20170911 | 1904 | 1876236 | 488 | Distribution Circuit | Environmental/External | Lightning | 4032 | 116781 | 37.6249 | -122.4461 | SNEATHLANEBETEARLAVECLAREMONTDR | Partly Cloudy-Drizzle-Lightning-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0077883 | OH | Sus | 0 | yes | 2017 | SEP | Yes | Line to Ground | 1301650 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0099791&numberofmonths=24&showchangehistorylog=1 | 17-0099791 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1101 | 24101101 | FUSE | 10695 | 20171204 | 1650 | 1935846 | 604 | Distribution Circuit | Vegetation | Tree - branch fell on line | 34 | 13838 | 37.4861 | -122.4191 | 9SPNSNCO6127APANOLIA75MINO0F92HalfMoonBay | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0099791 | OH | Sus | 43227146 | yes | 2017 | DEC | Yes | Open Circuit | 1317534 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0102222&numberofmonths=24&showchangehistorylog=1 | 17-0102222 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | SWITCH | 7483 | 20171216 | 1527 | 1945909 | 525 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 8218 | 37.4005 | -122.2919 | LDSIDEOF760BEARGULCH | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0102222 | OH | Sus | 0 | yes | 2017 | DEC | Yes | Line to Ground | 1320130 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0098441&numberofmonths=24&showchangehistorylog=1 | 18-0098441 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | HALF MOON BAY-1101 | 24101101 | FUSE | 8607 | 20181108 | 1644 | 211874 | 148 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 1184 | 37.4452 | -122.3314 | 13385SLYLINEBLVDWOODSIDE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0098441 | OH | Sus | 0 | yes | 2018 | NOV | Yes | Line to Ground | 1391522 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0104871&numberofmonths=24&showchangehistorylog=1 | 18-0104871 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 13253 | 20181129 | 737 | 227952 | 633 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 32283 | 37.378 | -122.2613 | FULLERLLOYD15SKYLINEDR | Overcast-Heavy Rain-Lightning-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0104871 | OH | Sus | 43587430 | yes | 2018 | NOV | Yes | Line to Ground | 1396166 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005295&numberofmonths=24&showchangehistorylog=1 | 19-0005295 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | RECLOSER | 98440 | 20190106 | 1732 | 255924 | 1088 | Distribution Circuit | Vegetation | Tree - branch fell on line | 154 | 19102 | 37.2667 | -122.3224 | WOF10463 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005295 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1403761 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005121&numberofmonths=24&showchangehistorylog=1 | 19-0005121 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | OTHER | SLATECREEKPORTOLASTATEPARKRD | 20190106 | 1310 | 255461 | 608 | Distribution Circuit | Vegetation | Tree - branch fell on line | 55 | 31685 | 37.2662 | -122.2108 | SLATECREEKPORTOLASTATEPARKRD | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005121 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1403593 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005246&numberofmonths=24&showchangehistorylog=1 | 19-0005246 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 13253 | 20190106 | 1727 | 255922 | 1574 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 80274 | 37.378 | -122.2613 | 34SKYLINEDROFFOFBIGTREE | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005246 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1403716 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005477&numberofmonths=24&showchangehistorylog=1 | 19-0005477 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 1099 | 20190106 | 1934 | 257428 | 1219 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 70600 | 37.3829 | -122.2629 | KUHLSSTEVE2spansldside8983treeinpri20medwaytreepriservice | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005477 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1403925 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010096&numberofmonths=24&showchangehistorylog=1 | 19-0010096 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1102 | 24131102 | TRIP-SAVER | 12249 | 20190116 | 1728 | 268656 | 1402 | Distribution Circuit | Vegetation | Tree - branch fell on line | 27 | 37854 | 37.3532 | -122.2644 | 11801LAHONDARDWOODSIDE | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010096 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1406963 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010421&numberofmonths=24&showchangehistorylog=1 | 19-0010421 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1102 | 24131102 | OTHER | WIREDOWN2NO12249 | 20190116 | 1838 | 272060 | 1807 | Distribution Circuit | Vegetation | Tree - fell into line | 1157 | 603505 | 37.3536 | -122.2641 | 2SPANLDSIDEW80255HEACOXRD2NO12249 | Overcast-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0010421 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Three Phase Fault | 1407286 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010086&numberofmonths=24&showchangehistorylog=1 | 19-0010086 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 4737 | 20190116 | 1542 | 268252 | 1458 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 29160 | 37.4023 | -122.3361 | FULLERLLOYDSAMEAS | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010086 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1406952 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010441&numberofmonths=24&showchangehistorylog=1 | 19-0010441 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | TRIP-SAVER | 8601 | 20190116 | 2105 | 270948 | 1172 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 49224 | 37.4388 | -122.3234 | 5SPANSLDSIDEOF8601 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010441 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407305 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010563&numberofmonths=24&showchangehistorylog=1 | 19-0010563 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | OTHER | WIREDOWNSOURCESIDE13253 | 20190116 | 2302 | 271784 | 938 | Distribution Circuit | Vegetation | Tree - fell into line | 310 | 96394 | 37.3782 | -122.2611 | SOURCELDSIDE13253 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 19-0010563 | OH | Sus | 31422194 | yes | 2019 | JAN | Yes | Line to Ground | 1407425 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011180&numberofmonths=24&showchangehistorylog=1 | 19-0011180 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 8615 | 20190116 | 2343 | 272010 | 1503 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 21042 | 37.4248 | -122.3133 | KINGSMOUNTAINRDATSKYLINEWOODSIDE | Overcast-Fog-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011180 | OH | Sus | 31422194 | yes | 2019 | JAN | Yes | Line to Ground | 1407783 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011907&numberofmonths=24&showchangehistorylog=1 | 19-0011907 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 7683 | 20190117 | 833 | 275982 | 1922 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 5766 | 37.3528 | -122.3342 | LDSIDEOF7683 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011907 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1408258 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0012088&numberofmonths=24&showchangehistorylog=1 | 19-0012088 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | JUMPER | OJLINESIDE4277 | 20190117 | 812 | 276596 | 6241 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 18723 | 37.3164 | -122.3026 | LDSIDE4277 | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0012088 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1408439 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011332&numberofmonths=24&showchangehistorylog=1 | 19-0011332 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | SAN CARLOS-1103 | 24181103 | FUSE | 6693 | 20190117 | 1744 | 274742 | 1373 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 6865 | 37.4558 | -122.3065 | 102CANADARD | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011332 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407883 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010501&numberofmonths=24&showchangehistorylog=1 | 19-0010501 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | JUMPER | WIREDOWNLDSIDE7483 | 20190117 | 40 | 272190 | 890 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 22998 | 37.4006 | -122.2909 | LDSIDE7483 | Overcast-Fog-32-90 F | Conductor, Overhead | On Ground | 19-0010501 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407366 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0017359&numberofmonths=24&showchangehistorylog=1 | 19-0017359 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | JUMPER | WIREBROKEN1POLENO11769 | 20190202 | 1832 | 288022 | 537 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 15573 | 37.3145 | -122.2724 | 1POLENO11769LINESOURCESIDE | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on object | 19-0017359 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1411771 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0017036&numberofmonths=24&showchangehistorylog=1 | 19-0017036 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | JUMPER | WIREDOWN6SPANSSOURCESIDE4737 | 20190202 | 405 | 286993 | 474 | Distribution Circuit | Vegetation | Tree - branch fell on line | 68 | 12927 | 37.4062 | -122.3329 | 6SPANSSOURCESIDE4737STARHILLRD | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017036 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1411490 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018303&numberofmonths=24&showchangehistorylog=1 | 19-0018303 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 1123 | 20190205 | 559 | 291671 | 661 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 3966 | 37.2717 | -122.3078 | 10SPANSLOADSIDEOFFUSE1123 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0018303 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Multi-Fault | 1412527 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018773&numberofmonths=24&showchangehistorylog=1 | 19-0018773 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | OTHER | WIREDOWN2SSREDWOODSHELDON | 20190205 | 1956 | 293676 | 464 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 11634 | 37.3138 | -122.2736 | 2SSREDWOODDRSHELDONDR | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0018773 | OH | Sus | 31424639 | yes | 2019 | FEB | Yes | Open Circuit | 1412839 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020853&numberofmonths=24&showchangehistorylog=1 | 19-0020853 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | OTHER | WIREDOWNNO7867 | 20190210 | 2028 | 299395 | 2993 | Distribution Circuit | Vegetation | Tree - fell into line | 343 | 153185 | 37.3945 | -122.2918 | FUSES7481NO7867 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 19-0020853 | OH | Sus | 31425315 | yes | 2019 | FEB | Yes | Line to Ground | 1414555 | PW | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021721&numberofmonths=24&showchangehistorylog=1 | 19-0021721 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 1123 | 20190212 | 2315 | 301628 | 917 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 5502 | 37.2717 | -122.3078 | MULTIPULESPANSOFWIREDOWNBEYOND11238879PESCADEROCRKRD | Overcast-Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0021721 | OH | Sus | 31425520 | yes | 2019 | FEB | Yes | Three Phase Fault | 1415169 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022190&numberofmonths=24&showchangehistorylog=1 | 19-0022190 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1101 | 24101101 | FUSE | 4149 | 20190213 | 746 | 303068 | 674 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 1348 | 37.4967 | -122.4298 | 2SPANSLDSIDEOFFU4149 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022190 | OH | Sus | 43677704 | yes | 2019 | FEB | Yes | Line to Line | 1415531 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022410&numberofmonths=24&showchangehistorylog=1 | 19-0022410 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 4263 | 20190213 | 1315 | 304592 | 605 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 5315 | 37.3154 | -122.272 | SCHLOCKERJEFF71lagunadrivelahonda | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022410 | OH | Sus | 31425418 | yes | 2019 | FEB | Yes | Line to Ground | 1415677 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022524&numberofmonths=24&showchangehistorylog=1 | 19-0022524 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 1621 | 20190213 | 1550 | 305146 | 4240 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 12720 | 37.3202 | -122.3741 | LDSIDE1621 | Overcast-Drizzle-32-90 F | Conductor, Overhead | On Ground | 19-0022524 | OH | Sus | 31425418 | yes | 2019 | FEB | Yes | Line to Ground | 1415763 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023318&numberofmonths=24&showchangehistorylog=1 | 19-0023318 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 14653 | 20190213 | 1029 | 304425 | 3643 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 32787 | 37.2402 | -122.3366 | SCHLOCKERJEFF300southranchroad | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023318 | OH | Sus | 43677704 | yes | 2019 | FEB | Yes | Line to Ground | 1416497 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021938&numberofmonths=24&showchangehistorylog=1 | 19-0021938 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | FUSE | 4309 | 20190213 | 616 | 302878 | 601 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 7212 | 37.3104 | -122.276 | SCHLOCKERJEFF68poperdlahonda | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021938 | OH | Sus | 31425418 | yes | 2019 | FEB | Yes | Line to Ground | 1415367 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023372&numberofmonths=24&showchangehistorylog=1 | 19-0023372 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | FUSE | 8549 | 20190213 | 2319 | 308290 | 2340 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 71108 | 37.2628 | -122.2119 | LDSIDE5741 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023372 | OH | Sus | 43677704 | yes | 2019 | FEB | Yes | Line to Ground | 1416526 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022945&numberofmonths=24&showchangehistorylog=1 | 19-0022945 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 1043 | 20190214 | 145 | 307798 | 3506 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 3506 | 37.3111 | -122.3868 | WIREDOWN | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | On Ground | 19-0022945 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416175 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023599&numberofmonths=24&showchangehistorylog=1 | 19-0023599 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | HALF MOON BAY-1103 | 24101103 | FUSE | 6093 | 20190214 | 718 | 310489 | 2017 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 34333 | 37.3984 | -122.3643 | LDSIDE6093 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023599 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416747 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023737&numberofmonths=24&showchangehistorylog=1 | 19-0023737 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | RECLOSER | 6018 | 20190214 | 1221 | 310866 | 4637 | Distribution Circuit | Vegetation | Tree - fell into line | 953 | 691981 | 37.3265 | -122.3875 | BRODERIUS15049779cabrillohwy | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023737 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416887 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023500&numberofmonths=24&showchangehistorylog=1 | 19-0023500 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | RALSTON-1101 | 24141101 | FUSE | 8603 | 20190214 | 12 | 306027 | 3991 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 63856 | 37.4474 | -122.3345 | LDSIDE8603 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023500 | OH | Sus | 31425418 | yes | 2019 | FEB | Yes | Line to Ground | 1416648 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022723&numberofmonths=24&showchangehistorylog=1 | 19-0022723 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | RECLOSER | 8972 | 20190214 | 30 | 306070 | 1162 | Distribution Circuit | Vegetation | Tree - branch fell on line | 69 | 80178 | 37.4185 | -122.3224 | STARHILLRDSOFSWETTRD | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022723 | OH | Sus | 43677704 | yes | 2019 | FEB | Yes | Line to Ground | 1415958 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022743&numberofmonths=24&showchangehistorylog=1 | 19-0022743 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | JUMPER | PRIWIREDOWN1480LAHONDARD | 20190214 | 37 | 306275 | 844 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 3230 | 37.3893 | -122.2637 | NA | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022743 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1415982 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025121&numberofmonths=24&showchangehistorylog=1 | 19-0025121 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 6973 | 20190217 | 1014 | 315558 | 1790 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 5540 | 37.3174 | -122.3331 | SCHLOCKERJEFF4310lahondaroad5sfromcutouts6973 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025121 | OH | Sus | 31425418 | yes | 2019 | FEB | Yes | Line to Ground | 1418201 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025737&numberofmonths=24&showchangehistorylog=1 | 19-0025737 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 7985 | 20190217 | 1151 | 318142 | 3079 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 6158 | 37.2086 | -122.3251 | NEAREOLPAST7985 | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 19-0025737 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1418781 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028725&numberofmonths=24&showchangehistorylog=1 | 19-0028725 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | WOODSIDE-1104 | 24251104 | TRIP-SAVER | 3583 | 20190227 | 41 | 325954 | 710 | Distribution Circuit | Vegetation | Tree - fell into line | 100 | 54746 | 37.4245 | -122.2736 | 5SPLDSIDEOF9173 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028725 | OH | Sus | 43684677 | yes | 2019 | FEB | Yes | Line to Ground | 1420636 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0009621&numberofmonths=24&showchangehistorylog=1 | 20-0009621 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | RECLOSER | 8972 | 20200116 | 839 | 762280 | 535 | Distribution Circuit | Vegetation | Tree - branch fell on line | 69 | 36915 | 37.4185 | -122.3224 | 2PNO410STARHILLRD | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0009621 | OH | Sus | 0 | yes | 2020 | JAN | Yes | Line to Ground | 1506733 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0084802&numberofmonths=24&showchangehistorylog=1 | 20-0084802 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 8125 | 20200816 | 903 | 1011595 | 507 | Distribution Circuit | Vegetation | Tree - branch fell on line | 38 | 16445 | 37.1459 | -122.3363 | CLARKDON65086736783015Whitehousecyn3milefromHWY1 | Partly Cloudy-Drizzle-Lightning-Heat Wave-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0084802 | OH | Sus | 0 | yes | 2020 | AUG | Yes | Line to Ground | 1555279 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0085352&numberofmonths=24&showchangehistorylog=1 | 20-0085352 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 12457 | 20200816 | 2134 | 1014238 | 1119 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1119 | 37.524 | -122.488 | CLARKDON6508673678rearofdennisoncyn | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0085352 | OH | Sus | 0 | yes | 2020 | AUG | Yes | Force Out | 1555783 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0009656&numberofmonths=24&showchangehistorylog=1 | 21-0009656 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | OTHER | WIREDOWN6SPANLINESIDEOF8549 | 20210118 | 1007 | 1212401 | 532 | Distribution Circuit | Vegetation | Tree - branch fell on line | 55 | 29140 | 37.2653 | -122.211 | 6SPANSLINESIDEOF8549 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0009656 | OH | Sus | 44628037 | No | 2021 | JAN | Yes | Open Circuit | 1593672 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0010195&numberofmonths=24&showchangehistorylog=1 | 21-0010195 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | SNEATH LANE-1106 | 22721106 | FUSE | 3185 | 20210119 | 454 | 1214799 | 567 | Distribution Circuit | Equipment Failure/Involved | Overhead | 120 | 68040 | 37.6264 | -122.4421 | WIREDOWNAT1570CLAREMONTDR | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0010195 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1594162 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0010039&numberofmonths=24&showchangehistorylog=1 | 21-0010039 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 5417 | 20210119 | 32 | 1214103 | 569 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 22100 | 37.3888 | -122.2663 | WIREDOWNIFO60STANDLER | Strong Winds-Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 21-0010039 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1594003 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0010078&numberofmonths=24&showchangehistorylog=1 | 21-0010078 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 8327 | 20210119 | 30 | 1213674 | 379 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 1895 | 37.3813 | -122.2546 | FULLERLLOYD5109092893579OLDLAHONDA | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0010078 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1594045 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0015827&numberofmonths=24&showchangehistorylog=1 | 21-0015827 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 12917 | 20210127 | 712 | 1233425 | 339 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 2373 | 37.3734 | -122.258 | SABAPAUL6506427081tree | Strong Winds- | Conductor, Overhead | Broken, wire on ground | 21-0015827 | OH | Sus | 0 | No | 2021 | JAN | Yes | Force Out | 1598357 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0157413&numberofmonths=24&showchangehistorylog=1 | 21-0157413 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 4279 | 20211213 | 952 | 1567887 | 671 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 53246 | 37.3178 | -122.3 | 7POLESEOF14513 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0157413 | OH | Sus | 0 | No | 2021 | DEC | Yes | Multi-Fault | 1694311 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0138490&numberofmonths=24&showchangehistorylog=1 | 22-0138490 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 8615 | 20221210 | 1116 | 1881728 | 467 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 6538 | 37.4248 | -122.3133 | LDSIDE8615 | Heavy Rain-Strong Winds-Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0138490 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1789319 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0007745&numberofmonths=24&showchangehistorylog=1 | 23-0007745 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1104 | 24251104 | FUSE | 3575 | 20230105 | 118 | 1920693 | 1444 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 38988 | 37.4304 | -122.2787 | 250GREERRD | Strong Winds-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0007745 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Line | 1797922 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0012235&numberofmonths=24&showchangehistorylog=1 | 23-0012235 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1101 | 24101101 | FUSE | 10695 | 20230110 | 406 | 1943256 | 869 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 11297 | 37.4884 | -122.42 | 5SPANSLDSIDEOF10695 | Strong Winds- | Conductor, Overhead | Broken, wire on ground | 23-0012235 | OH | Sus | 0 | No | 2023 | JAN | Yes | Force Out | 1801997 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0016185&numberofmonths=24&showchangehistorylog=1 | 23-0016185 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 4245 | 20230114 | 749 | 1954337 | 600 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1800 | 37.2716 | -122.2968 | LDSIDE4245 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0016185 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1804959 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0016493&numberofmonths=24&showchangehistorylog=1 | 23-0016493 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | RECLOSER | H80 | 20230114 | 2342 | 1955338 | 1033 | Distribution Circuit | Vegetation | Tree - fell into line | 647 | 178905 | 37.3302 | -122.375 | TheHondaRoadadsapID100269599 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 23-0016493 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1805249 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0016057&numberofmonths=24&showchangehistorylog=1 | 23-0016057 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | RECLOSER | 8884 | 20230114 | 824 | 1953267 | 468 | Distribution Circuit | Vegetation | Tree - fell into line | 343 | 85298 | 37.3894 | -122.2686 | 16363SKYLINEBLVD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0016057 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Line | 1804866 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0016957&numberofmonths=24&showchangehistorylog=1 | 23-0016957 | PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | RECLOSER | 8974 | 20230116 | 624 | 1956755 | 406 | Distribution Circuit | Vegetation | Tree - fell into line | 314 | 7438 | 37.3881 | -122.267 | 191BLAKEWOODWYREDWOODCITY | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0016957 | OH | Sus | 0 | No | 2023 | JAN | Yes | Force Out | 1805662 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0017018&numberofmonths=24&showchangehistorylog=1 | 23-0017018 | PENINSULA | FIELD OPS CENTRAL | Tier 2 | WOODSIDE-1104 | 24251104 | TRIP-SAVER | 3583 | 20230116 | 734 | 1957216 | 709 | Distribution Circuit | Vegetation | Tree - fell into line | 103 | 47976 | 37.4245 | -122.2736 | 558PATROLRD573PATROLRD532PATROLRD | Strong Winds-Heavy Rain-Clear-32-90F | Pole-Wood | Broken, wire on ground | 23-0017018 | OH | Sus | 0 | No | 2023 | JAN | Yes | Multi-Fault | 1805722 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078622&numberofmonths=24&showchangehistorylog=1 | 13-0078622 | SACRAMENTO | FIELD OPS NORTH | Tier 2 | VACA DIXON-1105 | 63591105 | FUSE | 40983 | 20131122 | 1225 | 912077 | 545 | Distribution Circuit | Equipment Failure/Involved | Other | 95 | 18781 | 38.4401 | -122.0019 | 1HARDTAPLDSIDEOF40983 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on object | 13-0078622 | OH | Sus | 0 | yes | 2013 | NOV | Yes | Line to Ground | 99251528 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0078910&numberofmonths=24&showchangehistorylog=1 | 14-0078910 | SACRAMENTO | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | RECLOSER | 7446 | 20141230 | 840 | 1150530 | 449 | Distribution Circuit | Vegetation | Tree - fell into line | 520 | 79320 | 39.3517 | -121.3275 | 1SPANSOUTHOF9823 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0078910 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99190754 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079333&numberofmonths=24&showchangehistorylog=1 | 14-0079333 | SACRAMENTO | FIELD OPS NORTH | Tier 2 | BROWNS VALLEY-1101 | 152921101 | FUSE | 6811 | 20141230 | 1630 | 1153984 | 300 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2400 | 39.2297 | -121.3968 | 4POLESSO6811WIREDOWNTREE | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 14-0079333 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99190422 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005344&numberofmonths=24&showchangehistorylog=1 | 17-0005344 | SACRAMENTO | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 1895 | 20170108 | 1227 | 1626017 | 257 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 7710 | 39.3376 | -121.3754 | FIELD | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005344 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245134 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005482&numberofmonths=24&showchangehistorylog=1 | 17-0005482 | SACRAMENTO | FIELD OPS NORTH | Tier 2 | NARROWS-2101 | 153132101 | FUSE | 36129 | 20170108 | 1239 | 1626357 | 453 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 12606 | 39.2423 | -121.357 | PALADEWESLEY6678turkeyhollow | Partly Cloudy-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005482 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245265 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007253&numberofmonths=24&showchangehistorylog=1 | 17-0007253 | SACRAMENTO | FIELD OPS NORTH | Tier 2 | VACAVILLE-1108 | 63601108 | FUSE | 1475 | 20170110 | 1917 | 1636080 | 930 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 5580 | 38.4093 | -122.0652 | 3SPANSLDSIDEOF1475 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | On Ground | 17-0007253 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246833 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0010068&numberofmonths=24&showchangehistorylog=1 | 17-0010068 | SACRAMENTO | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | JUMPER | WIREDOWNBEYOND459277 | 20170118 | 1527 | 1646735 | 229 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 458 | 39.3212 | -121.3964 | BEYOND459277 | Overcast-Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0010068 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1249096 | PW | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025868&numberofmonths=24&showchangehistorylog=1 | 17-0025868 | SACRAMENTO | FIELD OPS NORTH | Tier 2 | PUTAH CREEK-1102 | 63681102 | RECLOSER | 67858 | 20170222 | 2134 | 1711452 | 956 | Distribution Circuit | Vegetation | Tree - fell into line | 101 | 30897 | 38.4806 | -122.0272 | MTR1009335905 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025868 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1262664 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0075611&numberofmonths=24&showchangehistorylog=1 | 17-0075611 | SACRAMENTO | FIELD OPS NORTH | Tier 2 | BROWNS VALLEY-1101 | 152921101 | JUMPER | WIREDOWN | 20170903 | 1855 | 1869070 | 115 | Distribution Circuit | Equipment Failure/Involved | Overhead | 582 | 55325 | 39.2401 | -121.4091 | MARYSVILLERDNOBROWNSVALLEYSCHOOLRD1SNOF18219 | Partly Cloudy-Heat Wave-Above 90 | Conductor, Overhead | Broken, wire on ground | 17-0075611 | OH | Sus | 0 | yes | 2017 | SEP | Yes | Line to Ground | 1299892 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0085755&numberofmonths=24&showchangehistorylog=1 | 17-0085755 | SACRAMENTO | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 5807 | 20171008 | 2322 | 1896866 | 6701 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 69 | 462369 | 39.332 | -121.3646 | MULTIPLE | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0085755 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Force Out | 1307078 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0086750&numberofmonths=24&showchangehistorylog=1 | 17-0086750 | SACRAMENTO | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 18539 | 20171008 | 2322 | 1899357 | 8197 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 4 | 32788 | 39.3529 | -121.3302 | VARIOUS | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086750 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1307822 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0086819&numberofmonths=24&showchangehistorylog=1 | 17-0086819 | SACRAMENTO | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 173629 | 20171008 | 2322 | 1899487 | 6858 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 3 | 20574 | 39.3211 | -121.3949 | VARIOUS | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086819 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1307869 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0086820&numberofmonths=24&showchangehistorylog=1 | 17-0086820 | SACRAMENTO | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 459277 | 20171008 | 2322 | 1899490 | 6991 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 2 | 13982 | 39.3215 | -121.3958 | VAROIUS | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086820 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1307870 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0086821&numberofmonths=24&showchangehistorylog=1 | 17-0086821 | SACRAMENTO | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 188009 | 20171008 | 2322 | 1899491 | 7601 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 1 | 7601 | 39.3221 | -121.3952 | MTR1006522363 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086821 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1307871 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0086822&numberofmonths=24&showchangehistorylog=1 | 17-0086822 | SACRAMENTO | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 307759 | 20171008 | 2322 | 1899493 | 8123 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 1 | 8123 | 39.3224 | -121.3945 | MTR1006522390 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086822 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1307872 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0086823&numberofmonths=24&showchangehistorylog=1 | 17-0086823 | SACRAMENTO | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 693385 | 20171008 | 2322 | 1899495 | 7863 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 29 | 228027 | 39.3243 | -121.392 | VAROIUS | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086823 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1307873 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0086825&numberofmonths=24&showchangehistorylog=1 | 17-0086825 | SACRAMENTO | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 527809 | 20171008 | 2322 | 1899496 | 6703 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 2 | 13406 | 39.3281 | -121.3862 | VARIOUS | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086825 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1307874 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0086826&numberofmonths=24&showchangehistorylog=1 | 17-0086826 | SACRAMENTO | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 1803 | 20171008 | 2322 | 1899498 | 6839 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 151 | 897785 | 39.3286 | -121.3832 | VARIOUS | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086826 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1307875 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0086827&numberofmonths=24&showchangehistorylog=1 | 17-0086827 | SACRAMENTO | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | JUMPER | OJS1NEOF17889 | 20171008 | 2308 | 1899500 | 6882 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 1 | 6882 | 39.3302 | -121.3825 | MTR1007537152 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086827 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1307876 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0086828&numberofmonths=24&showchangehistorylog=1 | 17-0086828 | SACRAMENTO | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 15803 | 20171008 | 2308 | 1899501 | 6502 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 4 | 26008 | 39.3314 | -121.382 | VARIOIUS | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086828 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1307877 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0086829&numberofmonths=24&showchangehistorylog=1 | 17-0086829 | SACRAMENTO | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 15805 | 20171008 | 2316 | 1899504 | 6894 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 1 | 6894 | 39.3325 | -121.3817 | VARIOUS | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086829 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1307878 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0086830&numberofmonths=24&showchangehistorylog=1 | 17-0086830 | SACRAMENTO | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 15807 | 20171008 | 2316 | 1899506 | 6874 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 1 | 6874 | 39.333 | -121.3813 | VARIOUS | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086830 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1307879 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0086833&numberofmonths=24&showchangehistorylog=1 | 17-0086833 | SACRAMENTO | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 15809 | 20171008 | 2316 | 1899516 | 6884 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 1 | 6884 | 39.3355 | -121.3801 | LOADSIDE | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086833 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1307882 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0086835&numberofmonths=24&showchangehistorylog=1 | 17-0086835 | SACRAMENTO | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | JUMPER | OJS1NEOF15809 | 20171008 | 2308 | 1899517 | 6939 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 1 | 6939 | 39.3359 | -121.3798 | MTR1007535560 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086835 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1307883 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0086837&numberofmonths=24&showchangehistorylog=1 | 17-0086837 | SACRAMENTO | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 15811 | 20171008 | 2322 | 1899520 | 6886 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 1 | 6886 | 39.3373 | -121.377 | LOADSIDE | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086837 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1307884 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0086838&numberofmonths=24&showchangehistorylog=1 | 17-0086838 | SACRAMENTO | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 15813 | 20171008 | 2322 | 1899523 | 6890 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 11 | 75790 | 39.3377 | -121.3756 | LOADSIDE | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086838 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1307885 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0086839&numberofmonths=24&showchangehistorylog=1 | 17-0086839 | SACRAMENTO | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 1895 | 20171008 | 2322 | 1894286 | 8085 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 30 | 242550 | 39.3376 | -121.3754 | LOADSIDE | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086839 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1307886 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0086840&numberofmonths=24&showchangehistorylog=1 | 17-0086840 | SACRAMENTO | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 15815 | 20171008 | 2322 | 1899525 | 6669 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 3 | 20007 | 39.3363 | -121.3717 | LOADSIDE15815 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086840 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1307887 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0086841&numberofmonths=24&showchangehistorylog=1 | 17-0086841 | SACRAMENTO | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 15819 | 20171008 | 2322 | 1899526 | 6662 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 3 | 19986 | 39.3356 | -121.3708 | LOADSIDE15819 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086841 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1307888 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0086842&numberofmonths=24&showchangehistorylog=1 | 17-0086842 | SACRAMENTO | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 15821 | 20171008 | 2322 | 1899529 | 6893 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 2 | 13786 | 39.3351 | -121.3702 | LOADSIDE | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086842 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1307889 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0086845&numberofmonths=24&showchangehistorylog=1 | 17-0086845 | SACRAMENTO | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 15823 | 20171008 | 2316 | 1899530 | 6779 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 2 | 13558 | 39.3346 | -121.3694 | LOADSIDE | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086845 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1307891 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0086846&numberofmonths=24&showchangehistorylog=1 | 17-0086846 | SACRAMENTO | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 15825 | 20171008 | 2322 | 1899532 | 6768 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 1 | 6768 | 39.3339 | -121.3684 | LOADSIDE | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086846 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1307892 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0086847&numberofmonths=24&showchangehistorylog=1 | 17-0086847 | SACRAMENTO | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 15827 | 20171008 | 2322 | 1899533 | 6758 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 3 | 20274 | 39.3338 | -121.3681 | LOADSIDE | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086847 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1307893 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0086849&numberofmonths=24&showchangehistorylog=1 | 17-0086849 | SACRAMENTO | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 15829 | 20171008 | 2308 | 1899536 | 6767 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 2 | 13534 | 39.3329 | -121.3665 | LOADSIDE | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086849 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1307894 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0085274&numberofmonths=24&showchangehistorylog=1 | 17-0085274 | SACRAMENTO | FIELD OPS NORTH | Tier 2 | DOBBINS-1101 | 153741101 | RECLOSER | 1808 | 20171008 | 2205 | 1894014 | 3750 | Distribution Circuit | Vegetation | Tree - fell into line | 169 | 426606 | 39.3745 | -121.2339 | MTR1007106801 | Strong Winds-Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085274 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1306721 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0086135&numberofmonths=24&showchangehistorylog=1 | 17-0086135 | SACRAMENTO | FIELD OPS NORTH | Tier 2 | DOBBINS-1101 | 153741101 | FUSE | 17309 | 20171008 | 2145 | 1893968 | 4099 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 4099 | 39.3967 | -121.2196 | 3POLESNOFMTR1007535860 | Strong Winds-Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086135 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1307300 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0089070&numberofmonths=24&showchangehistorylog=1 | 17-0089070 | SACRAMENTO | FIELD OPS NORTH | Tier 3 | DOBBINS-1101 | 153741101 | FUSE | 18445 | 20171020 | 59 | 1905604 | 771 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 1542 | 39.3671 | -121.204 | 1SPANSOUTH1SPANEASTOF18445 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0089070 | OH | Sus | 43199090 | yes | 2017 | OCT | Yes | Line to Ground | 1309628 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011107&numberofmonths=24&showchangehistorylog=1 | 19-0011107 | SACRAMENTO | FIELD OPS NORTH | Tier 2 | NARROWS-2101 | 153132101 | FUSE | 18555 | 20190117 | 146 | 272280 | 714 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 8568 | 39.288 | -121.3512 | CGC221833559078TAP | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011107 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1407730 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0136382&numberofmonths=24&showchangehistorylog=1 | 21-0136382 | SACRAMENTO | FIELD OPS NORTH | Tier 2 | DOBBINS-1101 | 153741101 | OTHER | WIREDOWN2SSOFMTR1008859464 | 20211024 | 1444 | 1512993 | 277 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 554 | 39.3858 | -121.2524 | 2SSMTR1008859464 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0136382 | OH | Sus | 0 | No | 2021 | OCT | Yes | Force Out | 1677862 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0007542&numberofmonths=24&showchangehistorylog=1 | 23-0007542 | SACRAMENTO | FIELD OPS NORTH | Tier 2 | NARROWS-2101 | 153132101 | FUSE | 2527 | 20230105 | 10 | 1920285 | 1368 | Distribution Circuit | Vegetation | Tree - branch fell on line | 21 | 28728 | 39.2509 | -121.35 | 3POLESLDSIDEOF2527 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0007542 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1797757 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0045549&numberofmonths=24&showchangehistorylog=1 | 23-0045549 | SACRAMENTO | FIELD OPS NORTH | Tier 3 | DOBBINS-1101 | 153741101 | FUSE | 15911 | 20230314 | 1437 | 2042432 | 320 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2560 | 39.3703 | -121.207 | CGC222244562061 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0045549 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Line | 1825506 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0010247&numberofmonths=24&showchangehistorylog=1 | 17-0010247 | SAN FRANCISCO | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | OTHER | WIREDOWN8SPANSLDSOFUSE4737 | 20170118 | 1759 | s1249610 | 694 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 9920 | 37.3999 | -122.3414 | WIREDOWN6SLINESIDEOF37570 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010247 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Open Circuit | 1249610 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075959&numberofmonths=24&showchangehistorylog=1 | 14-0075959 | SAN JOSE | FIELD OPS SOUTH | Tier 2 | LLAGAS-2103 | 83182103 | FUSE | 14201 | 20141211 | 2140 | 1136215 | 620 | Distribution Circuit | Equipment Failure/Involved | Other | 2 | 1240 | 37.0461 | -121.65 | Knapp38233115DAYRD | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075959 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194228 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076326&numberofmonths=24&showchangehistorylog=1 | 14-0076326 | SAN JOSE | FIELD OPS SOUTH | Tier 2 | MILPITAS-1109 | 82831109 | OTHER |  | 20141212 | 1115 | 1138128 | 150 | Distribution Circuit | Equipment Failure/Involved | Other | 2 | 300 | 37.4375 | -121.8213 |  | Drizzle-32 - 90 F | Conductor, Overhead | On Ground | 14-0076326 | OH | Sus | 0 | yes | 2014 | DEC | Yes | None | 99194002 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079602&numberofmonths=24&showchangehistorylog=1 | 14-0079602 | SAN JOSE | FIELD OPS SOUTH | Tier 2 | SWIFT-2110 | 83392110 | FUSE | 6263 | 20141230 | 1843 | 1156068 | 1342 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 22396 | 37.3407 | -121.7701 | 3875QUAILCANYONCT | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079602 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99189378 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007155&numberofmonths=24&showchangehistorylog=1 | 17-0007155 | SAN JOSE | FIELD OPS SOUTH | Tier 2 | MORGAN HILL-2105 | 83242105 | FUSE | 28315 | 20170110 | 2051 | 1637040 | 2529 | Distribution Circuit | Vegetation | Tree - branch fell on line | 86 | 15704 | 37.0597 | -121.663 | Moyano3707treefellandtookoutprimary | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007155 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246739 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007249&numberofmonths=24&showchangehistorylog=1 | 17-0007249 | SAN JOSE | FIELD OPS SOUTH | Tier 2 | MORGAN HILL-2111 | 83242111 | FUSE | 3761 | 20170110 | 2002 | 1636629 | 2428 | Distribution Circuit | Vegetation | Tree - fell into line | 123 | 246744 | 37.1085 | -121.7322 | 1POLELDSIDEOF4461 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007249 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246829 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0010809&numberofmonths=24&showchangehistorylog=1 | 17-0010809 | SAN JOSE | FIELD OPS SOUTH | Tier 2 | SWIFT-2110 | 83392110 | RECLOSER | XR254 | 20170119 | 1010 | 1650603 | 1664 | Distribution Circuit | Environmental/External | Lightning | 194 | 189436 | 37.334 | -121.7559 | 4805QUIMBYRD | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010809 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1249782 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018354&numberofmonths=24&showchangehistorylog=1 | 17-0018354 | SAN JOSE | FIELD OPS SOUTH | Tier 2 | LLAGAS-2101 | 83182101 | FUSE | 3843 | 20170207 | 736 | 1678652 | 439 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 6146 | 37.0696 | -121.5205 | Guillen4644JUSTSO10840COYOTELAKERDA | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018354 | OH | Sus | 0 | yes | 2017 | FEB | Yes | None | 1256191 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018660&numberofmonths=24&showchangehistorylog=1 | 17-0018660 | SAN JOSE | FIELD OPS SOUTH | Tier 2 | MORGAN HILL-2105 | 83242105 | OTHER | WIREDOWN1SSOFUCOS4889 | 20170207 | 1126 | 1679934 | 664 | Distribution Circuit | Equipment Failure/Involved | Overhead | 98 | 17648 | 37.075 | -121.6716 | 1SSOFUCOS4889 | Strong Winds-Rain-Heavy Rain-Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018660 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1256428 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018740&numberofmonths=24&showchangehistorylog=1 | 17-0018740 | SAN JOSE | FIELD OPS SOUTH | Tier 3 | MORGAN HILL-2111 | 83242111 | TRIP-SAVER | 4461 | 20170207 | 1723 | 1680858 | 4728 | Distribution Circuit | Environmental/External | Flood/Erosion | 63 | 297864 | 37.0838 | -121.7754 | 2PWOF4461 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018740 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1256488 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023138&numberofmonths=24&showchangehistorylog=1 | 17-0023138 | SAN JOSE | FIELD OPS SOUTH | Tier 2 | MC KEE-1111 | 83531111 | FUSE | 14289 | 20170217 | 827 | 1693487 | 1969 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 11814 | 37.3537 | -121.7775 | LOADSIDEOF14289 | Overcast-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023138 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1260145 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005517&numberofmonths=24&showchangehistorylog=1 | 19-0005517 | SAN JOSE | FIELD OPS SOUTH | Tier 3 | MORGAN HILL-2111 | 83242111 | FUSE | 2153 | 20190106 | 1954 | 257386 | 1536 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 18432 | 37.0885 | -121.7564 | 6SPANSSOUTHOF215310SPANSSOUTHOF2153 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005517 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1403966 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018584&numberofmonths=24&showchangehistorylog=1 | 19-0018584 | SAN JOSE | FIELD OPS SOUTH | Tier 2 | MILPITAS-1109 | 82831109 | FUSE | 25457 | 20190202 | 1352 | 287562 | 4368 | Distribution Circuit | Vegetation | Tree - bark fell into line | 4 | 17472 | 37.4005 | -121.7645 | ATEOL | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0018584 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1412700 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022427&numberofmonths=24&showchangehistorylog=1 | 19-0022427 | SAN JOSE | FIELD OPS SOUTH | Tier 3 | LLAGAS-2107 | 83182107 | FUSE | 4459 | 20190213 | 1319 | 304628 | 546 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 8736 | 37.0052 | -121.6689 | Riggins464240848354597485WHITEHURSTRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022427 | OH | Sus | 31425399 | yes | 2019 | FEB | Yes | Line to Ground | 1415686 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024737&numberofmonths=24&showchangehistorylog=1 | 19-0024737 | SAN JOSE | FIELD OPS SOUTH | Tier 2 | HICKS-2101 | 83432101 | FUSE | 25065 | 20190216 | 1743 | 314870 | 448 | Distribution Circuit | Equipment Failure/Involved | Overhead | 53 | 23744 | 37.18 | -121.8163 | 21400BERTRAMRD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024737 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1417810 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0085670&numberofmonths=24&showchangehistorylog=1 | 20-0085670 | SAN JOSE | FIELD OPS SOUTH | Tier 3 | MORGAN HILL-2105 | 83242105 | OTHER | OJSNWO73299 | 20200817 | 645 | 1015257 | 316 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 13858 | 37.0369 | -121.7129 | 6630REDWOODRETREATRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0085670 | OH | Sus | 0 | yes | 2020 | AUG | Yes | Line to Ground | 1556063 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0161149&numberofmonths=24&showchangehistorylog=1 | 21-0161149 | SAN JOSE | FIELD OPS SOUTH | Tier 2 | MORGAN HILL-2105 | 83242105 | FUSE | 27285 | 20211227 | 1446 | 1585919 | 390 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 16380 | 37.0889 | -121.6648 | RIGGINSAARON4084835459SYCAMOREDRWESTOFOAKGLENAVE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0161149 | OH | Sus | 45102203 | No | 2021 | DEC | Yes | Force Out | 1698726 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0138452&numberofmonths=24&showchangehistorylog=1 | 22-0138452 | SAN JOSE | FIELD OPS SOUTH | Tier 2 | MORGAN HILL-2111 | 83242111 | FUSE | 2501 | 20221210 | 1103 | 1881688 | 412 | Distribution Circuit | Equipment Failure/Involved | Overhead | 32 | 11967 | 37.1502 | -121.7491 | 325CASALOMARD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0138452 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1789278 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0022600&numberofmonths=24&showchangehistorylog=1 | 13-0022600 | SIERRA | FIELD OPS NORTH | Tier 2 | GRASS VALLEY-1103 | 152031103 | RECLOSER | 2180 | 20130408 | 1324 | 770213 | 567 | Distribution Circuit | Vegetation | Tree - fell into line | 481 | 92952 | 39.1531 | -121.077 | 3sof2180 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0022600 | OH | Sus | 30988246 | yes | 2013 | APR | Yes | Line to Ground | 99292015 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078484&numberofmonths=24&showchangehistorylog=1 | 13-0078484 | SIERRA | FIELD OPS NORTH | Tier 3 | ALLEGHANY-1102 | 152101102 | FUSE | 6747 | 20131121 | 2129 | 911665 | 2681 | Distribution Circuit | Equipment Failure/Involved | Other | 4 | 10724 | 39.3602 | -120.7849 | 13178SCOTCHMANFALLSRD | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078484 | OH | Sus | 0 | yes | 2013 | NOV | Yes | Line to Ground | 99251226 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078113&numberofmonths=24&showchangehistorylog=1 | 13-0078113 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | OCB | OCB | 20131121 | 2047 | 909364 | 21 | Distribution Circuit | Equipment Failure/Involved | Other | 5436 | 114156 | 38.7393 | -120.6769 | SINGLEPHASELEADINGTONOCUSTOMERSNOTMAPPED | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 13-0078113 | OH | Sus | 0 | yes | 2013 | NOV | Yes | Line to Ground | 99251969 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078998&numberofmonths=24&showchangehistorylog=1 | 13-0078998 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | OTHER |  | 20131121 | 2154 | 909799 | 2511 | Distribution Circuit | Equipment Failure/Involved | Other | 2 | 5022 | 38.7062 | -120.6712 | 4120SNOWRD | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078998 | OH | Sus | 0 | yes | 2013 | NOV | Yes | Line to Ground | 99251074 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078249&numberofmonths=24&showchangehistorylog=1 | 13-0078249 | SIERRA | FIELD OPS NORTH | Tier 3 | DRUM-1101 | 152321101 | RECLOSER | 1602 | 20131121 | 2127 | 909663 | 1323 | Distribution Circuit | Vegetation | Tree - fell into line | 320 | 225275 | 39.2516 | -120.7505 | LDSIDESBCO30691 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on object | 13-0078249 | OH | Sus | 0 | yes | 2013 | NOV | Yes | Line to Ground | 99251726 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078237&numberofmonths=24&showchangehistorylog=1 | 13-0078237 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE | 18511 | 20131121 | 1915 | 908474 | 1555 | Distribution Circuit | Equipment Failure/Involved | Other | 84 | 105254 | 38.7538 | -120.5751 | FLECKLINPAUL62353090631424SPANSSOURCESIDE11051 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 13-0078237 | OH | Sus | 0 | yes | 2013 | NOV | Yes | Line to Ground | 99251731 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0077956&numberofmonths=24&showchangehistorylog=1 | 13-0077956 | SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | RECLOSER | 2224 | 20131121 | 1609 | 907493 | 1269 | Distribution Circuit | Vegetation | Tree - fell into line | 967 | 565491 | 38.9053 | -120.8372 | 8800WENTWORTH | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0077956 | OH | Sus | 0 | yes | 2013 | NOV | Yes | Line to Line | 99251796 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078701&numberofmonths=24&showchangehistorylog=1 | 13-0078701 | SIERRA | FIELD OPS NORTH | Tier 2 | ALLEGHANY-1101 | 152101101 | FUSE | 7905 | 20131122 | 1508 | 912541 | 2872 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 31592 | 39.5654 | -120.6389 | BETWEEN79053223 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078701 | OH | Sus | 0 | yes | 2013 | NOV | Yes | Line to Ground | 99250913 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078675&numberofmonths=24&showchangehistorylog=1 | 13-0078675 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1102 | 152481102 | FUSE | 3919 | 20131122 | 1259 | 912551 | 1847 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 59320 | 39.2005 | -120.9193 | STEPHENSON1588530913148220818REDDOG | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078675 | OH | Sus | 0 | yes | 2013 | NOV | Yes | Line to Ground | 99251212 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078615&numberofmonths=24&showchangehistorylog=1 | 13-0078615 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1106 | 152481106 | RECLOSER | 51486 | 20131122 | 1237 | 912181 | 1632 | Distribution Circuit | Vegetation | Tree - fell into line | 1038 | 630848 | 39.1911 | -120.9964 | 17006HWY174EO50047 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078615 | OH | Sus | 0 | yes | 2013 | NOV | Yes | Three Phase Fault | 99251215 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078726&numberofmonths=24&showchangehistorylog=1 | 13-0078726 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 9795 | 20131122 | 1531 | 912620 | 1515 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 81810 | 39.1905 | -120.9889 | 13367CRAWFORDLN | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078726 | OH | Sus | 0 | yes | 2013 | NOV | Yes | Line to Ground | 99251204 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078583&numberofmonths=24&showchangehistorylog=1 | 13-0078583 | SIERRA | FIELD OPS NORTH | Tier 3 | DRUM-1101 | 152321101 | FUSE | 9215 | 20131122 | 734 | 911141 | 2241 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 40338 | 39.276 | -120.7167 | JOHNSTONM1508530906556312707zeibrightrd | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 13-0078583 | OH | Sus | 0 | yes | 2013 | NOV | Yes | Line to Ground | 99251219 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078241&numberofmonths=24&showchangehistorylog=1 | 13-0078241 | SIERRA | FIELD OPS NORTH | Tier 2 | EL DORADO PH-2101 | 152762101 | RECLOSER | 52456 | 20131122 | 43 | 910278 | 1049 | Distribution Circuit | Equipment Failure/Involved | Other | 189 | 109436 | 38.7756 | -120.4024 | LARCHLNHWY50 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078241 | OH | Sus | 0 | yes | 2013 | NOV | Yes | Line to Ground | 99251728 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078541&numberofmonths=24&showchangehistorylog=1 | 13-0078541 | SIERRA | FIELD OPS NORTH | Tier 2 | EL DORADO PH-2101 | 152762101 | FUSE | 1571 | 20131122 | 43 | 911857 | 3837 | Distribution Circuit | Vegetation | Tree - fell into line | 65 | 249405 | 38.7744 | -120.2979 | WIREDOWNATEOLBEYOND1571 | Strong winds-Below 32 F | Conductor, Overhead | Broken, wire on ground | 13-0078541 | OH | Sus | 0 | yes | 2013 | NOV | Yes | Line to Ground | 99250918 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078771&numberofmonths=24&showchangehistorylog=1 | 13-0078771 | SIERRA | FIELD OPS NORTH | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 9351 | 20131122 | 1900 | 913036 | 1385 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 6925 | 38.8966 | -120.8913 | 3201ARGONAUT | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0078771 | OH | Sus | 0 | yes | 2013 | NOV | Yes |  | 99251195 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078837&numberofmonths=24&showchangehistorylog=1 | 13-0078837 | SIERRA | FIELD OPS NORTH | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 4489 | 20131122 | 2046 | 913186 | 1092 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 58968 | 38.9142 | -120.9385 | 6POLESLDSIDEOF4489 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078837 | OH | Sus | 0 | yes | 2013 | NOV | Yes |  | 99251181 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078568&numberofmonths=24&showchangehistorylog=1 | 13-0078568 | SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | RECLOSER | 9712 | 20131122 | 1141 | 911991 | 2290 | Distribution Circuit | Vegetation | Tree - fell into line | 1107 | 425449 | 38.8323 | -120.8174 | RENFREESAM150553090621105500AMERICANFLATRD | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078568 | OH | Sus | 0 | yes | 2013 | NOV | Yes | Line to Ground | 99250916 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078552&numberofmonths=24&showchangehistorylog=1 | 13-0078552 | SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | RECLOSER | 7522 | 20131122 | 1114 | 911910 | 735 | Distribution Circuit | Vegetation | Tree - fell into line | 1012 | 126224 | 38.816 | -120.8219 | 6160VEERCAMPRDGARDENVALLEY | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078552 | OH | Sus | 0 | yes | 2013 | NOV | Yes | Line to Line | 99251564 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078544&numberofmonths=24&showchangehistorylog=1 | 13-0078544 | SIERRA | FIELD OPS NORTH | Tier 2 | TAMARACK-1101 | 152291101 | FUSE | 6619 | 20131122 | 933 | 911606 | 2562 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 77256 | 39.3182 | -120.4548 | HARTEMMETT1506530906203150432ConiferDr | Strong winds-Below 32 F | Conductor, Overhead | Broken, wire on ground | 13-0078544 | OH | Sus | 0 | yes | 2013 | NOV | Yes |  | 99250917 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078691&numberofmonths=24&showchangehistorylog=1 | 13-0078691 | SIERRA | FIELD OPS NORTH | Tier 2 | TAMARACK-1101 | 152291101 | FUSE | 6617 | 20131122 | 1540 | 912375 | 1697 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 17253 | 39.3203 | -120.433 | HARTEMMETT150653090620311polessideofcos6653HessaveKingave | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078691 | OH | Sus | 0 | yes | 2013 | NOV | Yes | Open Circuit | 99251209 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078862&numberofmonths=24&showchangehistorylog=1 | 13-0078862 | SIERRA | FIELD OPS NORTH | Tier 2 | TAMARACK-1101 | 152291101 | FUSE | 6631 | 20131122 | 2131 | 913244 | 1317 | Distribution Circuit | Vegetation | Tree - fell into line | 119 | 36519 | 39.3199 | -120.4407 | 51559TAMARACKCRESCENT | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 13-0078862 | OH | Sus | 0 | yes | 2013 | NOV | Yes | None | 99251167 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078891&numberofmonths=24&showchangehistorylog=1 | 13-0078891 | SIERRA | FIELD OPS NORTH | Tier 2 | TAMARACK-1101 | 152291101 | FUSE | 6635 | 20131122 | 1253 | 912242 | 2167 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 31816 | 39.3198 | -120.4336 | RUSTYLNOLDHWY40 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 13-0078891 | OH | Sus | 0 | yes | 2013 | NOV | Yes | Three Phase Fault | 99251156 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0052913&numberofmonths=24&showchangehistorylog=1 | 14-0052913 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 10019 | 20140824 | 1928 | 1072340 | 283 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 19736 | 38.5698 | -120.6939 | LIZARRAGAA62053090631314545GRINDINGROCKRD | Clear-32 - 90 F | Conductor, Overhead | On Ground | 14-0052913 | OH | Sus | 31096822 | No | 2014 | AUG | Yes | Line to Line | 99210692 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0073345&numberofmonths=24&showchangehistorylog=1 | 14-0073345 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 21355 | 20141203 | 958 | 1122204 | 817 | Distribution Circuit | Equipment Failure/Involved | Other | 14 | 11438 | 38.5478 | -120.7104 | 2SPANSLOADSIDEOF21355 | Rain-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0073345 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99196863 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0073530&numberofmonths=24&showchangehistorylog=1 | 14-0073530 | SIERRA | FIELD OPS NORTH | Tier 2 | BRUNSWICK-1103 | 152481103 | FUSE | 31321 | 20141203 | 1428 | 1123470 | 691 | Distribution Circuit | Vegetation | Tree - fell into line | 99 | 33713 | 39.2693 | -121.0085 | BETWEEN559331843MAINLINE | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073530 | OH | Sus | 0 | yes | 2014 | DEC | Yes |  | 99196732 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0073563&numberofmonths=24&showchangehistorylog=1 | 14-0073563 | SIERRA | FIELD OPS NORTH | Tier 3 | COLUMBIA HILL-1101 | 152471101 | FUSE | 8035 | 20141203 | 1418 | 1123401 | 1337 | Distribution Circuit | Equipment Failure/Involved | Other | 41 | 20689 | 39.3445 | -121.077 | TASSONELOUIS1262682630212543SHADYCRRD | Fog-32 - 90 F | Conductor, Underground | Broken, wire on ground | 14-0073563 | OH | Sus | 0 | yes | 2014 | DEC | Yes |  | 99196569 | CU | UG | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0073194&numberofmonths=24&showchangehistorylog=1 | 14-0073194 | SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1103 | 152261103 | FUSE | 1113 | 20141203 | 609 | 1121757 | 421 | Distribution Circuit | Vegetation | Tree - fell into line | 76 | 31996 | 38.7309 | -120.8418 | 2450COLDSPRINGSRD | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073194 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99196967 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0073415&numberofmonths=24&showchangehistorylog=1 | 14-0073415 | SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1101 | 152241101 | FUSE | 5781 | 20141203 | 1149 | 1122888 | 259 | Distribution Circuit | Vegetation | Tree - fell into line | 173 | 43781 | 39.0177 | -121.0297 | 17505HILLCRESTDRMEADOVISTA | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073415 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99196816 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0073135&numberofmonths=24&showchangehistorylog=1 | 14-0073135 | SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1102 | 152241102 | RECLOSER | 39104 | 20141203 | 306 | 1121664 | 607 | Distribution Circuit | Vegetation | Tree - fell into line | 875 | 150128 | 38.9734 | -121.0139 | RENFREESAM150553090621103POLESSOUTHOFSW1901ONMAINLINE | Rain-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 14-0073135 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99197005 | CAW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0073166&numberofmonths=24&showchangehistorylog=1 | 14-0073166 | SIERRA | FIELD OPS NORTH | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 18861 | 20141203 | 511 | 1121716 | 332 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 7636 | 38.795 | -120.884 | 6770JohnsonRanchRd | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073166 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99196985 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075037&numberofmonths=24&showchangehistorylog=1 | 14-0075037 | SIERRA | FIELD OPS NORTH | Tier 3 | ALLEGHANY-1102 | 152101102 | OCB | OCB | 20141211 | 556 | 1129858 | 2284 | Distribution Circuit | Vegetation | Tree - fell into line | 153 | 49907 | 39.4653 | -120.8449 | 5SPANSSSOF80849 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075037 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99193083 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075426&numberofmonths=24&showchangehistorylog=1 | 14-0075426 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 7959 | 20141211 | 949 | 1132513 | 511 | Distribution Circuit | Vegetation | Tree - fell into line | 192 | 70642 | 38.6431 | -120.5261 | BEYOND20105 | Rain-32 - 90 F | Conductor, Overhead | On Ground | 14-0075426 | OH | Sus | 0 | yes | 2014 | DEC | Yes |  | 99194881 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075600&numberofmonths=24&showchangehistorylog=1 | 14-0075600 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 21345 | 20141211 | 833 | 1131657 | 1597 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 11179 | 38.5986 | -120.7508 | DERYKKEVIN6215303865111loadsideofcouts21345 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on object | 14-0075600 | OH | Sus | 0 | yes | 2014 | DEC | Yes |  | 99194322 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075553&numberofmonths=24&showchangehistorylog=1 | 14-0075553 | SIERRA | FIELD OPS NORTH | Tier 3 | BONNIE NOOK-1102 | 152301102 | FUSE | 9593 | 20141211 | 1030 | 1132899 | 765 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 25180 | 39.2173 | -120.8093 | COUT34367 | Strong winds-32 - 90 F | Cutout, Fused, Distribution | Broken, wire on ground | 14-0075553 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99194784 | COF | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075130&numberofmonths=24&showchangehistorylog=1 | 14-0075130 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE | 6279 | 20141211 | 729 | 1130716 | 339 | Distribution Circuit | Equipment Failure/Involved | Other | 53 | 17967 | 39.3185 | -120.8895 | 6SPANSLDSIDEOF3419 | Drizzle-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 14-0075130 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99195126 | CSO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075022&numberofmonths=24&showchangehistorylog=1 | 14-0075022 | SIERRA | FIELD OPS NORTH | Tier 3 | CLARKSVILLE-2103 | 153612103 | FUSE | 11049 | 20141211 | 620 | 1129852 | 275 | Distribution Circuit | Vegetation | Tree - fell into line | 84 | 19377 | 38.6059 | -121.0221 | 1007652580 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075022 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99195201 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075279&numberofmonths=24&showchangehistorylog=1 | 14-0075279 | SIERRA | FIELD OPS NORTH | Tier 3 | COLUMBIA HILL-1101 | 152471101 | RECLOSER | 2212 | 20141211 | 638 | 1130009 | 628 | Distribution Circuit | Vegetation | Tree - fell into line | 72 | 45216 | 39.3849 | -121.0318 | JIMENEZAL1586530913796318287BEARCANYONRD | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075279 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99195002 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075342&numberofmonths=24&showchangehistorylog=1 | 14-0075342 | SIERRA | FIELD OPS NORTH | Tier 3 | COLUMBIA HILL-1101 | 152471101 | FUSE | 8129 | 20141211 | 955 | 1132485 | 290 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 4060 | 39.3693 | -121.1074 | JIMENEZAL1586530913796310244OLDRD | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075342 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194947 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075221&numberofmonths=24&showchangehistorylog=1 | 14-0075221 | SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1102 | 152241102 | FUSE | 8469 | 20141211 | 717 | 1130439 | 538 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 10576 | 38.9764 | -121.0193 | 232CRYSTALLN | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075221 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99195050 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0074819&numberofmonths=24&showchangehistorylog=1 | 14-0074819 | SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2102 | 153132102 | OTHER |  | 20141211 | 125 | 1128899 | 305 | Distribution Circuit | Equipment Failure/Involved | Other | 85 | 25925 | 39.2527 | -121.1139 | WIREDOWN4EOF32993 | Partly cloudy-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 14-0074819 | OH | Sus | 0 | yes | 2014 | DEC | Yes | None | 99195314 | CSO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075552&numberofmonths=24&showchangehistorylog=1 | 14-0075552 | SIERRA | FIELD OPS NORTH | Tier 3 | PIKE CITY-1101 | 152201101 | FUSE | 8213 | 20141211 | 1048 | 1132493 | 700 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 15400 | 39.4689 | -121.0853 | 15SPANSLDSIDEOF8213 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075552 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194785 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0074971&numberofmonths=24&showchangehistorylog=1 | 14-0074971 | SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2108 | 153652108 | RECLOSER | 19622 | 20141211 | 554 | 1129635 | 1951 | Distribution Circuit | Vegetation | Tree - fell into line | 1667 | 212744 | 38.6568 | -120.9932 | 3680MILLBRAEMTR1006551129 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 14-0074971 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99194391 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075377&numberofmonths=24&showchangehistorylog=1 | 14-0075377 | SIERRA | FIELD OPS NORTH | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 11997 | 20141211 | 921 | 1132264 | 307 | Distribution Circuit | Equipment Failure/Involved | Other | 2039 | 49545 | 38.7521 | -120.9359 | WIREDOWNLDSIDEOF11997 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075377 | OH | Sus | 0 | yes | 2014 | DEC | Yes |  | 99194916 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075446&numberofmonths=24&showchangehistorylog=1 | 14-0075446 | SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2110 | 153652110 | FUSE | 22331 | 20141211 | 1026 | 1132860 | 1089 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 50094 | 38.6541 | -120.9296 | 4420CREEKSIDEDRIVE | Rain-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0075446 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99194867 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076193&numberofmonths=24&showchangehistorylog=1 | 14-0076193 | SIERRA | FIELD OPS NORTH | Tier 3 | ALLEGHANY-1101 | 152101101 | RECLOSER | 806 | 20141212 | 719 | 1137348 | 109 | Distribution Circuit | Equipment Failure/Involved | Other | 81 | 8829 | 39.4881 | -120.8574 | 6SPANSSSOFSW833 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076193 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Three Phase Fault | 99194110 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076542&numberofmonths=24&showchangehistorylog=1 | 14-0076542 | SIERRA | FIELD OPS NORTH | Tier 2 | ALLEGHANY-1101 | 152101101 | RECLOSER | 978 | 20141212 | 1519 | 1138694 | 2844 | Distribution Circuit | Equipment Failure/Involved | Other | 198 | 142613 | 39.6079 | -120.6067 | 6POLESLOADSIDEOF7931 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076542 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99193206 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076149&numberofmonths=24&showchangehistorylog=1 | 14-0076149 | SIERRA | FIELD OPS NORTH | Tier 3 | DRUM-1101 | 152321101 | RECLOSER | 75874 | 20141212 | 454 | 1137073 | 2361 | Distribution Circuit | Equipment Failure/Involved | Other | 103 | 86102 | 39.2908 | -120.6779 | WIREDOWNLDSIDE83643WIREDOWNHWY20BOWMANTURNOFFWIREDOWN3SWOF1205BROKENGUYMTR1008935922BROKENPOLE10PNMO | Snow-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076149 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99193509 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076356&numberofmonths=24&showchangehistorylog=1 | 14-0076356 | SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 18215 | 20141212 | 1125 | 1138145 | 335 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 1910 | 38.7293 | -120.9601 | 1SPANWIREDOWNLEADINGTO1007392168 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076356 | OH | Sus | 0 | yes | 2014 | DEC | Yes |  | 99193978 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076114&numberofmonths=24&showchangehistorylog=1 | 14-0076114 | SIERRA | FIELD OPS NORTH | Tier 2 | SUMMIT-1101 | 152591101 | OCB | OCB | 20141212 | 250 | 1136968 | 1130 | Distribution Circuit | Vegetation | Tree - fell into line | 1046 | 411830 | 39.3194 | -120.3788 | 14spans12kvdown4WOF66492ATCOUTS64185wirelayingoncrossarm | Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 14-0076114 | OH | Sus | 0 | yes | 2014 | DEC | Yes |  | 99193514 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076718&numberofmonths=24&showchangehistorylog=1 | 14-0076718 | SIERRA | FIELD OPS NORTH | Tier 2 | TAMARACK-1101 | 152291101 | FUSE | 6653 | 20141212 | 907 | 1137709 | 1733 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 10398 | 39.3219 | -120.4286 | 4SPANSLOADSIDE | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076718 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99193370 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079527&numberofmonths=24&showchangehistorylog=1 | 14-0079527 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 11943 | 20141230 | 1022 | 1151136 | 846 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 4230 | 38.6795 | -120.6902 | 3SPANSLOADSIDEOF11943 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079527 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99190288 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079102&numberofmonths=24&showchangehistorylog=1 | 14-0079102 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1102 | 152481102 | FUSE | 9779 | 20141230 | 922 | 1150847 | 550 | Distribution Circuit | Equipment Failure/Involved | Other | 110 | 60500 | 39.2088 | -120.9467 | LDSIDEOF9779 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079102 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99190589 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079003&numberofmonths=24&showchangehistorylog=1 | 14-0079003 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1106 | 152481106 | RECLOSER | 51486 | 20141230 | 842 | 1150810 | 1278 | Distribution Circuit | Vegetation | Tree - fell into line | 993 | 560377 | 39.1911 | -120.9964 | JCTTO694875FUCO | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079003 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Multi-Fault | 99190217 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079252&numberofmonths=24&showchangehistorylog=1 | 14-0079252 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 6759 | 20141230 | 842 | 1153922 | 1751 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 105060 | 39.1894 | -120.9612 | MTR100750055 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079252 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99190173 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079477&numberofmonths=24&showchangehistorylog=1 | 14-0079477 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 3935 | 20141230 | 1601 | 1153724 | 1438 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 18694 | 39.152 | -121.0262 | 19775NOATAKCANYONRDGRASSVALLEY | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079477 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99190130 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0078959&numberofmonths=24&showchangehistorylog=1 | 14-0078959 | SIERRA | FIELD OPS NORTH | Tier 2 | BRUNSWICK-1110 | 152481110 | FUSE | 3907 | 20141230 | 952 | 1150873 | 797 | Distribution Circuit | Vegetation | Tree - fell into line | 113 | 69303 | 39.2223 | -121.0817 | 10791WALKERDRGRASSVALLEY | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0078959 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99190710 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079256&numberofmonths=24&showchangehistorylog=1 | 14-0079256 | SIERRA | FIELD OPS NORTH | Tier 3 | COLUMBIA HILL-1101 | 152471101 | FUSE | 4373 | 20141230 | 1003 | 1150967 | 2926 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 27680 | 39.3829 | -121.0482 | MTR1007665827 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079256 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99189729 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079528&numberofmonths=24&showchangehistorylog=1 | 14-0079528 | SIERRA | FIELD OPS NORTH | Tier 3 | COLUMBIA HILL-1101 | 152471101 | FUSE | 4493 | 20141230 | 1602 | 1153754 | 1508 | Distribution Circuit | Equipment Failure/Involved | Other | 52 | 78416 | 39.3922 | -121.0977 | MTR1007523053 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079528 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99190116 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079318&numberofmonths=24&showchangehistorylog=1 | 14-0079318 | SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | OTHER |  | 20141230 | 1049 | 1154477 | 1251 | Distribution Circuit | Vegetation | Tree - fell into line | 118 | 136278 | 38.6745 | -120.7866 | 2SPANSNWOF1006650207 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079318 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99190161 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079441&numberofmonths=24&showchangehistorylog=1 | 14-0079441 | SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 2177 | 20141230 | 1040 | 1151257 | 1150 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 9200 | 38.6916 | -120.7371 | 4807WOODLANDDR | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079441 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99190138 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079203&numberofmonths=24&showchangehistorylog=1 | 14-0079203 | SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1107 | 152261107 | FUSE | 10287 | 20141230 | 1040 | 1151251 | 1212 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 13980 | 38.7207 | -120.8803 | MTR1007477600 | Strong winds-32 - 90 F | Transformer | Broken, wire on object | 14-0079203 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99190186 | TX | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079272&numberofmonths=24&showchangehistorylog=1 | 14-0079272 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 2417 | 20141230 | 1630 | 1154043 | 1140 | Distribution Circuit | Equipment Failure/Involved | Other | 22 | 25080 | 38.7703 | -120.4942 | 4SPANSLOADSIDE2417 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on object | 14-0079272 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99190170 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079386&numberofmonths=24&showchangehistorylog=1 | 14-0079386 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 20835 | 20141230 | 1830 | 1155026 | 580 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1160 | 38.7718 | -120.5783 | 2POLESLOADSIDEOF20835 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079386 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99190384 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079488&numberofmonths=24&showchangehistorylog=1 | 14-0079488 | SIERRA | FIELD OPS NORTH | Tier 2 | GRASS VALLEY-1103 | 152031103 | FUSE | 3225 | 20141230 | 2121 | 1155662 | 1077 | Distribution Circuit | Equipment Failure/Involved | Other | 2 | 2154 | 39.1402 | -121.1112 | MTR1009742866 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 14-0079488 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99190126 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079200&numberofmonths=24&showchangehistorylog=1 | 14-0079200 | SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1103 | 152691103 | RECLOSER | 995672 | 20141230 | 1035 | 1151235 | 1751 | Distribution Circuit | Vegetation | Tree - fell into line | 216 | 210631 | 39.1337 | -121.0716 | MULTIPLE | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079200 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99190187 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079241&numberofmonths=24&showchangehistorylog=1 | 14-0079241 | SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1109 | 152691109 | FUSE | 9935 | 20141230 | 1147 | 1151659 | 1639 | Distribution Circuit | Equipment Failure/Involved | Other | 6 | 4298 | 39.0303 | -121.0973 | 23779HWY49AUBURN | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079241 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99190177 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0078904&numberofmonths=24&showchangehistorylog=1 | 14-0078904 | SIERRA | FIELD OPS NORTH | Tier 3 | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 1184 | 20141230 | 902 | 1150699 | 928 | Distribution Circuit | Vegetation | Tree - fell into line | 306 | 270317 | 38.8991 | -120.855 | 1WO52067 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0078904 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Three Phase Fault | 99190761 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079082&numberofmonths=24&showchangehistorylog=1 | 14-0079082 | SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2102 | 153132102 | FUSE | 32995 | 20141230 | 1013 | 1151157 | 1074 | Distribution Circuit | Vegetation | Tree - fell into line | 240 | 257760 | 39.2528 | -121.1151 | 2PNO32999 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079082 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99190603 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079281&numberofmonths=24&showchangehistorylog=1 | 14-0079281 | SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2105 | 153132105 | FUSE | 4599 | 20141230 | 1116 | 1151512 | 1723 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 37906 | 39.1824 | -121.196 | MTR10070677501007523780 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079281 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99190167 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079518&numberofmonths=24&showchangehistorylog=1 | 14-0079518 | SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2105 | 153132105 | OTHER |  | 20141230 | 1657 | 1154574 | 1231 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 4924 | 39.2014 | -121.241 | WILKINSARMANDO158991350571SPANSOUTHOFC030699 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079518 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99190121 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079558&numberofmonths=24&showchangehistorylog=1 | 14-0079558 | SIERRA | FIELD OPS NORTH | Tier 3 | PIKE CITY-1101 | 152201101 | FUSE | 4197 | 20141230 | 1007 | 1151658 | 3237 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 61503 | 39.4195 | -121.066 | 15623CELESTIALVALLEYRD | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0079558 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99189716 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0078955&numberofmonths=24&showchangehistorylog=1 | 14-0078955 | SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | RECLOSER | 9712 | 20141230 | 1048 | 1151193 | 1137 | Distribution Circuit | Vegetation | Tree - fell into line | 1375 | 353622 | 38.8323 | -120.8174 | BETWEEN31153AND31155ANDBEYOND5851 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0078955 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Three Phase Fault | 99190222 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079071&numberofmonths=24&showchangehistorylog=1 | 14-0079071 | SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 32365 | 20141230 | 1029 | 1152210 | 1217 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2434 | 38.8414 | -120.815 | 1SPANLDSIDEOF32365 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079071 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99190209 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079146&numberofmonths=24&showchangehistorylog=1 | 14-0079146 | SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | SWITCH | 5851 | 20141230 | 1029 | 1152978 | 1217 | Distribution Circuit | Vegetation | Tree - fell into line | 127 | 154559 | 38.84 | -120.8191 | 1SPANLDSIDEOF5851 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079146 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99190195 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079469&numberofmonths=24&showchangehistorylog=1 | 14-0079469 | SIERRA | FIELD OPS NORTH | Tier 2 | PLACERVILLE-2106 | 153082106 | FUSE | 6053 | 20141230 | 1019 | 1154418 | 915 | Distribution Circuit | Vegetation | Tree - fell into line | 81 | 59485 | 38.84 | -120.8753 | 4SPLDSIDEOF6053 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079469 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99190323 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079438&numberofmonths=24&showchangehistorylog=1 | 14-0079438 | SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 20749 | 20141230 | 1246 | 1153941 | 964 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 16388 | 38.8319 | -120.8169 | 5SPANSEOF20749 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079438 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99190139 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079464&numberofmonths=24&showchangehistorylog=1 | 14-0079464 | SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 1445 | 20141230 | 1455 | 1153156 | 1405 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 8054 | 38.8108 | -120.8048 | CGC223425541680 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079464 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99190133 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079550&numberofmonths=24&showchangehistorylog=1 | 14-0079550 | SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 2197 | 20141230 | 1037 | 1151241 | 1948 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 21324 | 38.8283 | -120.8131 | MTR1007203195 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079550 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99190110 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079563&numberofmonths=24&showchangehistorylog=1 | 14-0079563 | SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 11359 | 20141230 | 1123 | 1151556 | 1460 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 17520 | 38.8215 | -120.7922 | 4SPANSNORTHWESTOF11359 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079563 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99190105 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079011&numberofmonths=24&showchangehistorylog=1 | 14-0079011 | SIERRA | FIELD OPS NORTH | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 9103 | 20141230 | 1209 | 1151755 | 916 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 14607 | 38.8115 | -120.9105 | 7292HEMLOCKLR | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079011 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99190664 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079078&numberofmonths=24&showchangehistorylog=1 | 14-0079078 | SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 20451 | 20141230 | 1215 | 1151794 | 615 | Distribution Circuit | Equipment Failure/Involved | Other | 20 | 4300 | 38.7375 | -120.9703 | LOADSIDEOFMTR1009704574 | Strong winds-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 14-0079078 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99190607 | CSO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079209&numberofmonths=24&showchangehistorylog=1 | 14-0079209 | SIERRA | FIELD OPS NORTH | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 10077 | 20141230 | 957 | 1153521 | 978 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 38694 | 38.7968 | -120.9107 | 4741MOUNTIANVIEW | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079209 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99190501 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079311&numberofmonths=24&showchangehistorylog=1 | 14-0079311 | SIERRA | FIELD OPS NORTH | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 10321 | 20141230 | 957 | 1154411 | 1388 | Distribution Circuit | Equipment Failure/Involved | Other | 87 | 115198 | 38.8031 | -120.9301 | 5950CLARKMOUNTAINRD | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079311 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99190162 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0078949&numberofmonths=24&showchangehistorylog=1 | 14-0078949 | SIERRA | FIELD OPS NORTH | Tier 2 | WEIMAR-1102 | 152491102 | FUSE | 6175 | 20141230 | 1000 | 1150948 | 307 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 18113 | 39.0361 | -121.0041 | 1SPLDSIDEOF6175 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0078949 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99190719 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010532&numberofmonths=24&showchangehistorylog=1 | 15-0010532 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-1104 | 153661104 | RECLOSER | 97086 | 20150206 | 1357 | 1175598 | 1641 | Distribution Circuit | Vegetation | Tree - fell into line | 443 | 598787 | 38.7654 | -120.704 | BETWEEN1230518055 | Strong winds-32 - 90 F | Conductor, Underground | Broken, wire on ground | 15-0010532 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99184598 | CU | UG | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010100&numberofmonths=24&showchangehistorylog=1 | 15-0010100 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 2005 | 20150206 | 605 | 1173272 | 1825 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 31025 | 38.635 | -120.6947 | 6360MEYERLNSOMERSET | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010100 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99184648 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010458&numberofmonths=24&showchangehistorylog=1 | 15-0010458 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 20861 | 20150206 | 1412 | 1176109 | 1528 | Distribution Circuit | Equipment Failure/Involved | Other | 58 | 88376 | 38.6379 | -120.5665 | DERYKKEVIN62153038651115431cosumnesminerd | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on object | 15-0010458 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99184611 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010285&numberofmonths=24&showchangehistorylog=1 | 15-0010285 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1102 | 152481102 | RECLOSER | 940 | 20150206 | 1250 | 1175132 | 1761 | Distribution Circuit | Vegetation | Tree - fell into line | 1219 | 635170 | 39.2191 | -121.0227 | 7PEO7005MTR1007534345 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010285 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183954 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0009836&numberofmonths=24&showchangehistorylog=1 | 15-0009836 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1103 | 152481103 | FUSE | 6597 | 20150206 | 422 | 1173180 | 503 | Distribution Circuit | Vegetation | Tree - branch fell on line | 43 | 8509 | 39.2914 | -121.031 | MUELLERANDY1585530863680716996LAKEVERAPURDONRDNEVADACITY | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0009836 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99184663 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010527&numberofmonths=24&showchangehistorylog=1 | 15-0010527 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1103 | 152481103 | FUSE | 7117 | 20150206 | 1227 | 1175745 | 2749 | Distribution Circuit | Vegetation | Tree - fell into line | 157 | 431593 | 39.2849 | -121.0217 | 2PEO33615 | Strong winds-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 15-0010527 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183944 | CAW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010684&numberofmonths=24&showchangehistorylog=1 | 15-0010684 | SIERRA | FIELD OPS NORTH | Tier 2 | BRUNSWICK-1103 | 152481103 | FUSE | 33111 | 20150206 | 1321 | 1175365 | 1529 | Distribution Circuit | Vegetation | Tree - fell into line | 86 | 131494 | 39.254 | -121.0121 | 33113COUTS3PLDSIDE | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010684 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Three Phase Fault | 99184566 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011142&numberofmonths=24&showchangehistorylog=1 | 15-0011142 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1103 | 152481103 | FUSE | 7119 | 20150206 | 1238 | 1179246 | 4381 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 198813 | 39.3124 | -121.0352 | 18221roundmtnranchrdNevadaCity | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011142 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183381 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011312&numberofmonths=24&showchangehistorylog=1 | 15-0011312 | SIERRA | FIELD OPS NORTH | Tier 2 | BRUNSWICK-1104 | 152481104 | FUSE | 9861 | 20150206 | 1243 | 1175015 | 1861 | Distribution Circuit | Equipment Failure/Involved | Other | 14 | 26054 | 39.2452 | -121.0376 | EOL | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011312 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Open Circuit | 99184274 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010341&numberofmonths=24&showchangehistorylog=1 | 15-0010341 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1105 | 152481105 | RECLOSER | 1030 | 20150206 | 1230 | 1174902 | 1597 | Distribution Circuit | Vegetation | Tree - fell into line | 1202 | 532333 | 39.2408 | -121.0301 | 31741POLEBROKENCONDUCTORDOWNONBOTHSIDES | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0010341 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99184630 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010731&numberofmonths=24&showchangehistorylog=1 | 15-0010731 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE | 34175 | 20150206 | 1237 | 1175199 | 1463 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 24871 | 39.2406 | -120.9243 | BUCKEYERDKEANTONLN | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010731 | OH | Sus | 42328531 | yes | 2015 | FEB | Yes | Line to Line | 99184557 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0009826&numberofmonths=24&showchangehistorylog=1 | 15-0009826 | SIERRA | FIELD OPS NORTH | Tier 2 | CLARKSVILLE-2103 | 153612103 | OTHER |  | 20150206 | 602 | 1173302 | 796 | Distribution Circuit | Vegetation | Tree - fell into line | 2001 | 244527 | 38.6058 | -121.0231 | 13099 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0009826 | OH | Sus | 31132929 | yes | 2015 | FEB | Yes | Line to Ground | 99185327 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010035&numberofmonths=24&showchangehistorylog=1 | 15-0010035 | SIERRA | FIELD OPS NORTH | Tier 3 | COLUMBIA HILL-1101 | 152471101 | OTHER |  | 20150206 | 952 | 1173968 | 3068 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 9420 | 39.3663 | -121.0376 | MTR1004463004 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010035 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183958 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011115&numberofmonths=24&showchangehistorylog=1 | 15-0011115 | SIERRA | FIELD OPS NORTH | Tier 2 | COLUMBIA HILL-1101 | 152471101 | FUSE | 8115 | 20150206 | 1914 | 1177774 | 1327 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 49099 | 39.3253 | -121.1121 | TASSONELOUIS1262682630222101ROOSTERHILLRD | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011115 | OH | Sus | 31132899 | yes | 2015 | FEB | Yes | Line to Ground | 99184392 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010248&numberofmonths=24&showchangehistorylog=1 | 15-0010248 | SIERRA | FIELD OPS NORTH | Tier 3 | DRUM-1101 | 152321101 | OCB | OCB | 20150206 | 1353 | 1175581 | 1615 | Distribution Circuit | Vegetation | Tree - branch fell on line | 193 | 22175 | 39.2559 | -120.7674 | JOHNSTONM150853090655635spanswofLR75874 | Clear-32 - 90 F | Crossarm, Wood | Broken, wire on object | 15-0010248 | OH | Sus | 0 | yes | 2015 | FEB | Yes |  | 99184635 | CAW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010365&numberofmonths=24&showchangehistorylog=1 | 15-0010365 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 22771 | 20150206 | 1222 | 1175368 | 1678 | Distribution Circuit | Vegetation | Tree - fell into line | 450 | 129316 | 38.7169 | -120.5801 | LIZARRAGAA62053090631316326GREYLINGWAY | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010365 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99184628 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010649&numberofmonths=24&showchangehistorylog=1 | 15-0010649 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | SWITCH | 22399 | 20150206 | 1542 | 1176263 | 3175 | Distribution Circuit | Vegetation | Tree - fell into line | 275 | 29718 | 38.714 | -120.6222 | LDSIDESPANOF22399 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010649 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183935 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0009919&numberofmonths=24&showchangehistorylog=1 | 15-0009919 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE | 18407 | 20150206 | 637 | 1173384 | 324 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 2916 | 38.7681 | -120.5915 | SAMANIEGOS62653090631226154dropoffrdPOLLOCKPINES | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0009919 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99185262 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010510&numberofmonths=24&showchangehistorylog=1 | 15-0010510 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE | 21023 | 20150206 | 1631 | 1176562 | 1669 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 5333 | 38.7534 | -120.5944 | LIZARRAGAA62053090631313640POOLHOUSERDA | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010510 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99184602 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0009882&numberofmonths=24&showchangehistorylog=1 | 15-0009882 | SIERRA | FIELD OPS NORTH | Tier 3 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 9383 | 20150206 | 639 | 1173390 | 364 | Distribution Circuit | Vegetation | Tree - branch fell on line | 50 | 12375 | 38.9077 | -120.8457 | MTR1004686762 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 15-0009882 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99185294 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010334&numberofmonths=24&showchangehistorylog=1 | 15-0010334 | SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2105 | 153132105 | RECLOSER | 2748 | 20150206 | 1202 | 1174623 | 1121 | Distribution Circuit | Vegetation | Tree - fell into line | 880 | 375194 | 39.2081 | -121.2034 | BARKERBILL12565303622077NotatsceneofincidentAndyMuellerprimaryscene | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 15-0010334 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99184632 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010297&numberofmonths=24&showchangehistorylog=1 | 15-0010297 | SIERRA | FIELD OPS NORTH | Tier 3 | PIKE CITY-1101 | 152201101 | OTHER |  | 20150206 | 1231 | 1175866 | 2870 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 14350 | 39.406 | -121.0574 | MTR1007600446 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0010297 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183953 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010485&numberofmonths=24&showchangehistorylog=1 | 15-0010485 | SIERRA | FIELD OPS NORTH | Tier 3 | PIKE CITY-1101 | 152201101 | FUSE | 8211 | 20150206 | 1231 | 1176836 | 3219 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 3219 | 39.4692 | -121.0864 | MTR1007744566 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0010485 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99183946 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0009898&numberofmonths=24&showchangehistorylog=1 | 15-0009898 | SIERRA | FIELD OPS NORTH | Tier 2 | PLACERVILLE-2106 | 153082106 | FUSE | 31163 | 20150206 | 747 | 1173489 | 486 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 486 | 38.8186 | -120.8241 | HARTEMMETT150653090620316461GardenValleyRdcos31163 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0009898 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99185285 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010083&numberofmonths=24&showchangehistorylog=1 | 15-0010083 | SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 3773 | 20150206 | 653 | 1173408 | 1033 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2066 | 38.884 | -120.8299 | 6957HWY193 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010083 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99185173 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0009821&numberofmonths=24&showchangehistorylog=1 | 15-0009821 | SIERRA | FIELD OPS NORTH | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | RECLOSER | 13322 | 20150206 | 605 | 1173314 | 272 | Distribution Circuit | Equipment Failure/Involved | Other | 624 | 118178 | 38.769 | -120.9274 | 1SPANWOMET1007389045 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0009821 | OH | Sus | 0 | yes | 2015 | FEB | Yes |  | 99185330 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011119&numberofmonths=24&showchangehistorylog=1 | 15-0011119 | SIERRA | FIELD OPS NORTH | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 4651 | 20150206 | 1958 | 1178209 | 1352 | Distribution Circuit | Vegetation | Tree - fell into line | 158 | 202456 | 38.7712 | -120.9324 | SAMANIEGOS6265309063122arrowbeeandcasualct | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011119 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Three Phase Fault | 99184390 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011604&numberofmonths=24&showchangehistorylog=1 | 15-0011604 | SIERRA | FIELD OPS NORTH | Tier 2 | ALLEGHANY-1101 | 152101101 | FUSE | 30317 | 20150207 | 709 | 1183003 | 2286 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 2286 | 39.618 | -120.5927 | MTR1007739725 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011604 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183689 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011412&numberofmonths=24&showchangehistorylog=1 | 15-0011412 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 21135 | 20150207 | 2050 | 1181895 | 910 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 3640 | 38.6419 | -120.7027 | BEYOOND21135 | Rain-32 - 90 F | Conductor, Overhead | On Ground | 15-0011412 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99183822 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011338&numberofmonths=24&showchangehistorylog=1 | 15-0011338 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1105 | 152481105 | SWITCH | 9821 | 20150207 | 1614 | 1181653 | 1426 | Distribution Circuit | Equipment Failure/Involved | Other | 167 | 238142 | 39.3083 | -120.9321 | 1EO318872EO31887 | Overcast-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 15-0011338 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183844 | CAW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011345&numberofmonths=24&showchangehistorylog=1 | 15-0011345 | SIERRA | FIELD OPS NORTH | Tier 2 | BRUNSWICK-1110 | 152481110 | FUSE | 7259 | 20150207 | 1732 | 1181675 | 1243 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 1477 | 39.2277 | -121.101 | 10596DIXONRD | Drizzle-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0011345 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Open Circuit | 99183841 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011227&numberofmonths=24&showchangehistorylog=1 | 15-0011227 | SIERRA | FIELD OPS NORTH | Tier 3 | COLUMBIA HILL-1101 | 152471101 | FUSE | 4493 | 20150207 | 1232 | 1181149 | 1553 | Distribution Circuit | Equipment Failure/Involved | Other | 52 | 12620 | 39.3922 | -121.0977 | MTR1007523065 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011227 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183870 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011318&numberofmonths=24&showchangehistorylog=1 | 15-0011318 | SIERRA | FIELD OPS NORTH | Tier 3 | PIKE CITY-1101 | 152201101 | FUSE | 8223 | 20150207 | 1351 | 1181589 | 1704 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 5752 | 39.4567 | -121.037 | MTR1007742510 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0011318 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183851 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011019&numberofmonths=24&showchangehistorylog=1 | 15-0011019 | SIERRA | FIELD OPS NORTH | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 18319 | 20150207 | 213 | 1180346 | 846 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 32890 | 38.8085 | -120.9437 | 5250WAGGONERMINERD | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011019 | OH | Sus | 0 | yes | 2015 | FEB | Yes | None | 99184451 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011037&numberofmonths=24&showchangehistorylog=1 | 15-0011037 | SIERRA | FIELD OPS NORTH | Tier 2 | SUMMIT-1101 | 152591101 | OCB | OCB | 20150207 | 319 | 1180207 | 529 | Distribution Circuit | Vegetation | Tree - fell into line | 1036 | 502076 | 39.3194 | -120.3788 | 2SPANSSSOFLR2304 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011037 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99184441 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011797&numberofmonths=24&showchangehistorylog=1 | 15-0011797 | SIERRA | FIELD OPS NORTH | Tier 3 | COLUMBIA HILL-1101 | 152471101 | FUSE | 8197 | 20150208 | 2007 | 1183975 | 938 | Distribution Circuit | Equipment Failure/Involved | Other | 3 | 2814 | 39.3374 | -121.0899 | BUCKTOTHEEAST | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011797 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99183311 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0084850&numberofmonths=24&showchangehistorylog=1 | 15-0084850 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE | 12615 | 20151213 | 1123 | 1361721 | 642 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 43014 | 38.7995 | -120.7287 | MTR1009642459 | Overcast-Fog-Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 15-0084850 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Line | 1174517 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0084894&numberofmonths=24&showchangehistorylog=1 | 15-0084894 | SIERRA | FIELD OPS NORTH | Tier 2 | PLACERVILLE-1110 | 153081110 | FUSE | 12989 | 20151213 | 1111 | 1361650 | 296 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 9472 | 38.7472 | -120.821 | EOMTR1007476217 | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084894 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1174562 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0087106&numberofmonths=24&showchangehistorylog=1 | 15-0087106 | SIERRA | FIELD OPS NORTH | Tier 2 | PENRYN-1107 | 152561107 | FUSE | 5259 | 20151224 | 1150 | 1370952 | 167 | Distribution Circuit | 3rd Party | Vehicle | 97 | 11766 | 38.8267 | -121.1242 | 5203 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0087106 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1177178 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0013867&numberofmonths=24&showchangehistorylog=1 | 16-0013867 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-1103 | 153661103 | FUSE | 1433 | 20160217 | 1952 | 1408518 | 2741 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 16446 | 38.7498 | -120.7564 | 2165SHADOWRUNRD | Partly Cloudy-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013867 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Line to Ground | 1186862 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0013786&numberofmonths=24&showchangehistorylog=1 | 16-0013786 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-1104 | 153661104 | FUSE | 1313 | 20160217 | 2041 | 1407581 | 1385 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 34625 | 38.7588 | -120.7204 | 1SPANSO20857 | Overcast-Heavy Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 16-0013786 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Line to Ground | 1186819 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0013521&numberofmonths=24&showchangehistorylog=1 | 16-0013521 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 13253 | 20160217 | 1955 | 1407634 | 1508 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 24128 | 38.6762 | -120.6611 | 1007391839 | Partly Cloudy-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013521 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Line to Line | 1186607 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0013615&numberofmonths=24&showchangehistorylog=1 | 16-0013615 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 21161 | 20160217 | 2015 | 1407847 | 1378 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2756 | 38.5664 | -120.7109 | 1SPANLDSIDE | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013615 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Line to Ground | 1186694 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0013475&numberofmonths=24&showchangehistorylog=1 | 16-0013475 | SIERRA | FIELD OPS NORTH | Tier 2 | AUBURN-1102 | 152161102 | FUSE | 8611 | 20160217 | 2059 | 1407233 | 255 | Distribution Circuit | Vegetation | Tree - fell into line | 185 | 47175 | 38.9083 | -121.0618 | 2SPANSLOADSIDEOF8611 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013475 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Line to Line | 1186561 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0013188&numberofmonths=24&showchangehistorylog=1 | 16-0013188 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1102 | 152481102 | JUMPER | 3POLEFROMEOLOPENJUMPERS | 20160217 | 1301 | 1405446 | 577 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 2540 | 39.2126 | -121.0123 | TREETHRULINEWIREPULLEDCLEANLYAWAYFROMJUMPERSBASICALLYOPENEDJUMPERSFORUS | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013188 | OH | Sus | 31219754 | yes | 2016 | FEB | Yes | Line to Ground | 1186299 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0012990&numberofmonths=24&showchangehistorylog=1 | 16-0012990 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1105 | 152481105 | JUMPER | 3PHASEWIREDOWN2LDSIDEOF2130 | 20160217 | 749 | 1404658 | 443 | Distribution Circuit | Vegetation | Tree - fell into line | 203 | 36514 | 39.2734 | -120.9681 | SCOTTSVALLEYRDANDBURJERRD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0012990 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Line to Ground | 1186144 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0013009&numberofmonths=24&showchangehistorylog=1 | 16-0013009 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 9075 | 20160217 | 944 | 1404585 | 269 | Distribution Circuit | Vegetation | Tree - branch fell on line | 50 | 13450 | 39.1857 | -120.9722 | HWY174COLFAX | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013009 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Line to Ground | 1186181 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0013396&numberofmonths=24&showchangehistorylog=1 | 16-0013396 | SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 1333 | 20160217 | 2015 | 1407534 | 1284 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 32100 | 38.6747 | -120.7232 | 5261GOLDDUST5301GOLDDUSTDR | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013396 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Line to Ground | 1186566 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0013566&numberofmonths=24&showchangehistorylog=1 | 16-0013566 | SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1107 | 152261107 | FUSE | 41463 | 20160217 | 2027 | 1407069 | 1753 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 20485 | 38.7171 | -120.825 | MTR1007481243 | Overcast-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 16-0013566 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Line to Line | 1186649 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0013111&numberofmonths=24&showchangehistorylog=1 | 16-0013111 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE | 6647 | 20160217 | 731 | 1404530 | 663 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 29835 | 38.7648 | -120.5838 | 1SPANLDSIDEOF6647 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013111 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Line to Ground | 1186249 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0013390&numberofmonths=24&showchangehistorylog=1 | 16-0013390 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2102 | 152762102 | RECLOSER | 6852 | 20160217 | 1959 | 1406901 | 1322 | Distribution Circuit | Vegetation | Tree - fell into line | 3294 | 1569268 | 38.7604 | -120.5769 | PAGANVICTOR7076893441FUSEPOLE2869SBCO11825POLE | Overcast-Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 16-0013390 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Line to Ground | 1186473 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0012962&numberofmonths=24&showchangehistorylog=1 | 16-0012962 | SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1101 | 152241101 | FUSE | 3147 | 20160217 | 725 | 1404729 | 598 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 5382 | 39.0027 | -121.0201 | HARTEMMETT15065309062031Rearof1075WoodlandDr | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 16-0012962 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Line to Ground | 1186175 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0012962&numberofmonths=24&showchangehistorylog=1 | 16-0012962 | SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1101 | 152241101 | FUSE | 7535 | 20160217 | 725 | 1404730 | 414 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 3726 | 39.0021 | -121.0208 | HARTEMMETT150653090620312spansseastofcos753517120placerhills | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0012962 | OH | Sus | 0 | yes | 2016 | FEB | Yes | None | 1186176 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0013479&numberofmonths=24&showchangehistorylog=1 | 16-0013479 | SIERRA | FIELD OPS NORTH | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 4491 | 20160217 | 2006 | 1407048 | 1058 | Distribution Circuit | Vegetation | Tree - fell into line | 170 | 165496 | 38.9134 | -120.9316 | HARTEMMETT150653090620311polenofcos8561SecretLaketrlLoynscreekct | Partly Cloudy-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 16-0013479 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Line to Ground | 1186565 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0013392&numberofmonths=24&showchangehistorylog=1 | 16-0013392 | SIERRA | FIELD OPS NORTH | Tier 2 | PLACERVILLE-1111 | 153081111 | JUMPER | OPENJUMPERS4NOF2503 | 20160217 | 1910 | 1406951 | 921 | Distribution Circuit | Equipment Failure/Involved | Overhead | 80 | 17295 | 38.7247 | -120.7972 | 4NOF2503 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013392 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Line to Ground | 1186475 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0013499&numberofmonths=24&showchangehistorylog=1 | 16-0013499 | SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 9375 | 20160217 | 1956 | 1406733 | 876 | Distribution Circuit | Vegetation | Tree - fell into line | 90 | 55382 | 38.8468 | -120.7948 | 3SPANSNWOF5591 | Partly Cloudy-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013499 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Line to Line | 1186586 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0012964&numberofmonths=24&showchangehistorylog=1 | 16-0012964 | SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | RECLOSER | 7522 | 20160217 | 731 | 1404541 | 618 | Distribution Circuit | Vegetation | Tree - fell into line | 1015 | 161119 | 38.8155 | -120.8221 | 4970BLACKOAKMINERD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0012964 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Line to Ground | 1186118 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0013097&numberofmonths=24&showchangehistorylog=1 | 16-0013097 | SIERRA | FIELD OPS NORTH | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 22943 | 20160217 | 738 | 1404550 | 514 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 5140 | 38.8059 | -120.9074 | 1SPANLDSIDEOF22943 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013097 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Line to Ground | 1186237 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0013561&numberofmonths=24&showchangehistorylog=1 | 16-0013561 | SIERRA | FIELD OPS NORTH | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 11479 | 20160217 | 1944 | 1406632 | 525 | Distribution Circuit | Vegetation | Tree - fell into line | 129 | 67725 | 38.8062 | -120.9254 | MTR1007648733 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013561 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Line to Ground | 1186644 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0013605&numberofmonths=24&showchangehistorylog=1 | 16-0013605 | SIERRA | FIELD OPS NORTH | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 21799 | 20160217 | 2111 | 1407292 | 1507 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 19378 | 38.7933 | -120.9047 | 4800MTNVIEWDR | Partly Cloudy-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013605 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Line to Line | 1186685 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0013669&numberofmonths=24&showchangehistorylog=1 | 16-0013669 | SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 11437 | 20160217 | 1949 | 1406645 | 1336 | Distribution Circuit | Vegetation | Tree - fell into line | 111 | 131360 | 38.7111 | -120.9456 | 8POLESNO11437 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013669 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Line to Ground | 1186735 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0013524&numberofmonths=24&showchangehistorylog=1 | 16-0013524 | SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2110 | 153652110 | FUSE | 1555 | 20160217 | 1957 | 1406788 | 1201 | Distribution Circuit | Vegetation | Tree - fell into line | 258 | 119826 | 38.6476 | -120.9178 | MTR1007653215 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013524 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Line to Ground | 1186610 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0018340&numberofmonths=24&showchangehistorylog=1 | 16-0018340 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1103 | 152481103 | FUSE | 4665 | 20160305 | 2245 | 1421177 | 1198 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 23960 | 39.2955 | -121.0152 | MULTIPLE | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018340 | OH | Sus | 31223007 | yes | 2016 | MAR | Yes | Line to Ground | 1190193 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017839&numberofmonths=24&showchangehistorylog=1 | 16-0017839 | SIERRA | FIELD OPS NORTH | Tier 2 | BRUNSWICK-1105 | 152481105 | FUSE | 30029 | 20160305 | 2014 | 1418826 | 1157 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 34710 | 39.234 | -121.0291 | 10938BUBBLINGWELLSRDUPCRYSTALSPRINGSRD | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017839 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1189693 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0018400&numberofmonths=24&showchangehistorylog=1 | 16-0018400 | SIERRA | FIELD OPS NORTH | Tier 3 | COLUMBIA HILL-1101 | 152471101 | FUSE | 4493 | 20160305 | 2237 | 1421366 | 2538 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 51774 | 39.3927 | -121.0981 | MTR74E950 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018400 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190248 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0018459&numberofmonths=24&showchangehistorylog=1 | 16-0018459 | SIERRA | FIELD OPS NORTH | Tier 3 | COLUMBIA HILL-1101 | 152471101 | JUMPER | OJS1SSOFMTR1009800191 | 20160305 | 2237 | 1422204 | 2543 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2543 | 39.3941 | -121.0981 | MTR1009800191 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018459 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190297 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017988&numberofmonths=24&showchangehistorylog=1 | 16-0017988 | SIERRA | FIELD OPS NORTH | Tier 3 | FORESTHILL-1102 | 152181102 | FUSE | 6005 | 20160305 | 2102 | 1419429 | 809 | Distribution Circuit | Vegetation | Tree - branch fell on line | 298 | 224099 | 39.0191 | -120.8972 | 12140SPRINGGARDENRDFORESTHILL | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017988 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1189859 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0018433&numberofmonths=24&showchangehistorylog=1 | 16-0018433 | SIERRA | FIELD OPS NORTH | Tier 2 | GRASS VALLEY-1103 | 152031103 | FUSE | 7825 | 20160305 | 2119 | 1421530 | 2296 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 34188 | 39.1363 | -121.1167 | MTR1007602114 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018433 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190271 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017621&numberofmonths=24&showchangehistorylog=1 | 16-0017621 | SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1102 | 152241102 | FUSE | 8469 | 20160305 | 1719 | 1417619 | 316 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 6952 | 38.9765 | -121.0191 | 300CRYSTALLN | Partly Cloudy-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017621 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1189475 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0018360&numberofmonths=24&showchangehistorylog=1 | 16-0018360 | SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1104 | 152691104 | FUSE | 6875 | 20160305 | 2150 | 1419747 | 1005 | Distribution Circuit | Vegetation | Tree - fell into line | 262 | 263310 | 39.1046 | -121.0589 | 2SPANSEO7937 | Strong Winds-Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018360 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Three Phase Fault | 1190212 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017820&numberofmonths=24&showchangehistorylog=1 | 16-0017820 | SIERRA | FIELD OPS NORTH | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 2422 | 20160305 | 2042 | 1419150 | 207 | Distribution Circuit | Vegetation | Tree - fell into line | 602 | 45367 | 38.9 | -120.9075 | 1SPEOSW1121 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017820 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1189673 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0018350&numberofmonths=24&showchangehistorylog=1 | 16-0018350 | SIERRA | FIELD OPS NORTH | Tier 3 | PIKE CITY-1101 | 152201101 | RECLOSER | 1730 | 20160305 | 2157 | 1421605 | 2481 | Distribution Circuit | Vegetation | Tree - fell into line | 142 | 154286 | 39.4332 | -121.0754 | 1NO2SOMET1007582011 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 16-0018350 | OH | Sus | 31223007 | yes | 2016 | MAR | Yes | Line to Ground | 1190202 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0071922&numberofmonths=24&showchangehistorylog=1 | 16-0071922 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE | 4821 | 20161014 | 705 | 1558419 | 580 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 6960 | 39.2426 | -120.9999 | MUELLERANDY1585530863680712143BIGBLUERD | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 16-0071922 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Line | 1229110 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0002880&numberofmonths=24&showchangehistorylog=1 | 17-0002880 | SIERRA | FIELD OPS NORTH | Tier 3 | BONNIE NOOK-1101 | 152301101 | OCB | 11012 | 20170103 | 548 | 1615292 | 404 | Distribution Circuit | Vegetation | Tree - fell into line | 513 | 90044 | 39.214 | -120.8098 | JOHNSTONM15085309065563copole6375 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0002880 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1243200 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0002967&numberofmonths=24&showchangehistorylog=1 | 17-0002967 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1105 | 152481105 | RECLOSER | 2210 | 20170103 | 1056 | 1615646 | 1999 | Distribution Circuit | Vegetation | Tree - branch fell on line | 652 | 471639 | 39.261 | -120.9817 | MTR1008660552BRANCHONLINEOPENJUMPERATHIGHSIDEOFSBCO9803ATMTR10076066BROKENCROSSARMANDWIREDOWN | Overcast-Fog-Snow-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0002967 | OH | Sus | 42908603 | yes | 2017 | JAN | Yes | Line to Ground | 1243260 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0003403&numberofmonths=24&showchangehistorylog=1 | 17-0003403 | SIERRA | FIELD OPS NORTH | Tier 3 | COLUMBIA HILL-1101 | 152471101 | RECLOSER | 35424 | 20170103 | 2309 | 1617255 | 1248 | Distribution Circuit | Vegetation | Tree - fell into line | 237 | 187104 | 39.3432 | -121.1212 | 3SPEO19847OAKTREELN | Overcast-Heavy Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0003403 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1243589 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0002908&numberofmonths=24&showchangehistorylog=1 | 17-0002908 | SIERRA | FIELD OPS NORTH | Tier 3 | PIKE CITY-1101 | 152201101 | FUSE | 38373 | 20170103 | 536 | 1615461 | 831 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 9141 | 39.478 | -121.0421 | 1SPAN3SPANSLDSIDEOF38373 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0002908 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1243222 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0003215&numberofmonths=24&showchangehistorylog=1 | 17-0003215 | SIERRA | FIELD OPS NORTH | Tier 3 | PIKE CITY-1101 | 152201101 | RECLOSER | 1720 | 20170103 | 1927 | 1616634 | 4448 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 133251 | 39.455 | -121.0529 | MUELLERANDY15855308636807PIKECITYSUB | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003215 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1243384 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005783&numberofmonths=24&showchangehistorylog=1 | 17-0005783 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-1104 | 153661104 | RECLOSER | 12832 | 20170108 | 2019 | 1629044 | 1118 | Distribution Circuit | Vegetation | Tree - fell into line | 760 | 315709 | 38.7523 | -120.682 | 3945NCANYON | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005783 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Three Phase Fault | 1245570 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005435&numberofmonths=24&showchangehistorylog=1 | 17-0005435 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 18843 | 20170108 | 1016 | 1626858 | 604 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 8456 | 38.5358 | -120.6969 | 2SPANSSOUTHOFCGC223733031865 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005435 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1245219 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005727&numberofmonths=24&showchangehistorylog=1 | 17-0005727 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | RECLOSER | 186912 | 20170108 | 2115 | 1629283 | 1352 | Distribution Circuit | Vegetation | Tree - fell into line | 1226 | 309908 | 38.641 | -120.7043 | 1SEOF484633SPANSLDSIDEOF21323 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0005727 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1245511 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0004980&numberofmonths=24&showchangehistorylog=1 | 17-0004980 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1103 | 152481103 | RECLOSER | 2200 | 20170108 | 657 | 1622900 | 252 | Distribution Circuit | Vegetation | Tree - branch fell on line | 114 | 19722 | 39.275 | -121.0207 | WIREDOWNBETMTR1007523075FUCO3550 | Strong Winds-Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004980 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1244781 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005157&numberofmonths=24&showchangehistorylog=1 | 17-0005157 | SIERRA | FIELD OPS NORTH | Tier 2 | BRUNSWICK-1106 | 152481106 | FUSE | 4637 | 20170108 | 1024 | 1624846 | 344 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 15136 | 39.1678 | -121.0464 | FUSE46375LDSIDEOFFUSE46374LDSIDEOFFUSE4637 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005157 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1244952 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005426&numberofmonths=24&showchangehistorylog=1 | 17-0005426 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1106 | 152481106 | RECLOSER | 2104 | 20170108 | 1216 | 1627010 | 1464 | Distribution Circuit | Vegetation | Tree - fell into line | 2032 | 789644 | 39.1994 | -121.0173 | TASSONELOUIS12626826302BTWNROLLINSVI | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0005426 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Three Phase Fault | 1245209 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005737&numberofmonths=24&showchangehistorylog=1 | 17-0005737 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 33773 | 20170108 | 1453 | 1627510 | 1197 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 56259 | 39.134 | -121.0182 | 18142DOGBARRD | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005737 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1245521 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005422&numberofmonths=24&showchangehistorylog=1 | 17-0005422 | SIERRA | FIELD OPS NORTH | Tier 2 | COLUMBIA HILL-1101 | 152471101 | FUSE | 8115 | 20170108 | 1219 | 1626111 | 1510 | Distribution Circuit | Vegetation | Tree - branch fell on line | 37 | 55870 | 39.3255 | -121.1124 | WILKINSARMANDO1589913505723883ROOSTERHILLRD | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005422 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Force Out | 1245205 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005730&numberofmonths=24&showchangehistorylog=1 | 17-0005730 | SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1103 | 152261103 | SWITCH | 1257 | 20170108 | 2129 | 1628985 | 1153 | Distribution Circuit | Vegetation | Tree - fell into line | 197 | 24281 | 38.7287 | -120.8412 | SAMANIEGOS6265309063122debbielane | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005730 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245514 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005057&numberofmonths=24&showchangehistorylog=1 | 17-0005057 | SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 20383 | 20170108 | 722 | 1623078 | 283 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 2830 | 38.6907 | -120.7532 | 2SWOFMETER1007371854 | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005057 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1244855 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005377&numberofmonths=24&showchangehistorylog=1 | 17-0005377 | SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 21913 | 20170108 | 1205 | 1625997 | 543 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 14706 | 38.6719 | -120.8218 | METER1006550634 | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005377 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1245163 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005243&numberofmonths=24&showchangehistorylog=1 | 17-0005243 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 18417 | 20170108 | 1017 | 1624755 | 557 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 11140 | 38.7651 | -120.5785 | 1SPANLDSIDEOF18417 | Partly Cloudy-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005243 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245032 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005126&numberofmonths=24&showchangehistorylog=1 | 17-0005126 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2102 | 152762102 | JUMPER | OJ2EOF7085 | 20170108 | 815 | 1624970 | 268 | Distribution Circuit | Environmental/External | Lightning | 572 | 98692 | 38.7574 | -120.5866 | OJ2EOF7085OPEN | Overcast-Fog-Rain-Lightning-Strong Winds-32-90 F | Jumper | Broken, wire on object | 17-0005126 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Open Circuit | 1244925 | JMP | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005704&numberofmonths=24&showchangehistorylog=1 | 17-0005704 | SIERRA | FIELD OPS NORTH | Tier 2 | GRASS VALLEY-1101 | 152031101 | FUSE | 32729 | 20170108 | 1351 | 1627090 | 1486 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 29720 | 39.16 | -121.058 | 100SSMTR1007533698 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0005704 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1245486 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006004&numberofmonths=24&showchangehistorylog=1 | 17-0006004 | SIERRA | FIELD OPS NORTH | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 6585 | 20170108 | 2209 | 1629610 | 2398 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 38368 | 38.9292 | -120.8903 | 5085SPANISHDRYDIGGINSGREENWOOD | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006004 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245753 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005732&numberofmonths=24&showchangehistorylog=1 | 17-0005732 | SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 4115 | 20170108 | 1904 | 1628748 | 2730 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 20778 | 38.8659 | -120.8221 | HARTEMMETT150653090620314441WabassoLn | Overcast-Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0005732 | OH | Sus | 31294707 | yes | 2017 | JAN | Yes | Line to Ground | 1245516 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005757&numberofmonths=24&showchangehistorylog=1 | 17-0005757 | SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | RECLOSER | 7522 | 20170108 | 2202 | 1629607 | 1390 | Distribution Circuit | Vegetation | Tree - fell into line | 1019 | 1011862 | 38.8155 | -120.8221 | 1SPN1SPSO32331 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005757 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1245542 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005683&numberofmonths=24&showchangehistorylog=1 | 17-0005683 | SIERRA | FIELD OPS NORTH | Tier 2 | SHINGLE SPRINGS-2108 | 153652108 | FUSE | 2659 | 20170108 | 1729 | 1628414 | 2684 | Distribution Circuit | Vegetation | Tree - fell into line | 150 | 214164 | 38.6611 | -120.9907 | MTR1009375415 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005683 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245466 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005586&numberofmonths=24&showchangehistorylog=1 | 17-0005586 | SIERRA | FIELD OPS NORTH | Tier 2 | SHINGLE SPRINGS-2110 | 153652110 | FUSE | 12965 | 20170108 | 1757 | 1627977 | 1054 | Distribution Circuit | Vegetation | Tree - fell into line | 116 | 12814 | 38.6667 | -120.9134 | JESSEEBEN6209168268237BUCKEYESCHOOL | Overcast-Fog-Rain-32-90 F | Anchor or Guy | Broken, wire on ground | 17-0005586 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1245366 | ANC | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005234&numberofmonths=24&showchangehistorylog=1 | 17-0005234 | SIERRA | FIELD OPS NORTH | Tier 2 | SUMMIT-1102 | 152591102 | FUSE | 6829 | 20170108 | 1020 | 1625922 | 7734 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 30936 | 39.3175 | -120.3525 | MTR37538R | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0005234 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245023 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005295&numberofmonths=24&showchangehistorylog=1 | 17-0005295 | SIERRA | FIELD OPS NORTH | Tier 2 | WISE-1102 | 152271102 | FUSE | 5401 | 20170108 | 1218 | 1626097 | 222 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 4392 | 38.8988 | -121.096 | 1061MILLERTOWNRD | Partly Cloudy-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0005295 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1245085 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005433&numberofmonths=24&showchangehistorylog=1 | 17-0005433 | SIERRA | FIELD OPS NORTH | Tier 2 | WISE-1102 | 152271102 | RECLOSER | 307494 | 20170108 | 1502 | 1627596 | 683 | Distribution Circuit | Vegetation | Tree - grew into line | 267 | 63858 | 38.9339 | -121.1791 | 6311MTVERNONRD | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005433 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245217 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005861&numberofmonths=24&showchangehistorylog=1 | 17-0005861 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE | 6931 | 20170109 | 135 | 1629925 | 2133 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 12137 | 39.2292 | -121.0018 | 5SPANSLDSIDEOFFUCO6931 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005861 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245644 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006205&numberofmonths=24&showchangehistorylog=1 | 17-0006205 | SIERRA | FIELD OPS NORTH | Tier 2 | BRUNSWICK-1106 | 152481106 | FUSE | 8949 | 20170109 | 1524 | 1631582 | 1279 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 5025 | 39.1637 | -120.9686 | 34SSOFCGC222922454666 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006205 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245896 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006597&numberofmonths=24&showchangehistorylog=1 | 17-0006597 | SIERRA | FIELD OPS NORTH | Tier 2 | ECHO SUMMIT-1101 | 158031101 | FUSE | 2429 | 20170109 | 657 | 1633309 | 6208 | Distribution Circuit | Environmental/External | Flood/Erosion | 6 | 37248 | 38.7746 | -120.4 | SAMANIEGOS626530906312210972hwy50 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006597 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246244 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005942&numberofmonths=24&showchangehistorylog=1 | 17-0005942 | SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1107 | 152691107 | FUSE | 80845 | 20170109 | 357 | 1630021 | 827 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 10751 | 39.0362 | -121.0775 | 1SPANSO80845FUCO | Strong Winds-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005942 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Three Phase Fault | 1245714 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005979&numberofmonths=24&showchangehistorylog=1 | 17-0005979 | SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1109 | 152691109 | FUSE | 7863 | 20170109 | 558 | 1630218 | 1670 | Distribution Circuit | Vegetation | Tree - branch fell on line | 48 | 27672 | 39.0916 | -121.1772 | MTR1007518412 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0005979 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245742 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006249&numberofmonths=24&showchangehistorylog=1 | 17-0006249 | SIERRA | FIELD OPS NORTH | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 38111 | 20170109 | 607 | 1630221 | 2344 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 9376 | 38.8961 | -120.9192 | 5001LAFAILLELNGREENWOOD | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006249 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245942 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006005&numberofmonths=24&showchangehistorylog=1 | 17-0006005 | SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2102 | 153132102 | FUSE | 7251 | 20170109 | 626 | 1630242 | 711 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 25477 | 39.2634 | -121.1984 | MTR1009251387 | Overcast-Fog-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 17-0006005 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245754 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005598&numberofmonths=24&showchangehistorylog=1 | 17-0005598 | SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | JUMPER | WIREDOWN2PWO1008964630 | 20170109 | 2021 | 1632219 | 1224 | Distribution Circuit | Vegetation | Tree - fell into line | 166 | 9051 | 38.966 | -120.714 | HARTEMMETT150653090620312poleswomtr1008964630 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005598 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246031 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005829&numberofmonths=24&showchangehistorylog=1 | 17-0005829 | SIERRA | FIELD OPS NORTH | Tier 2 | SHADY GLEN-1102 | 152431102 | FUSE | 59355 | 20170109 | 38 | 1629879 | 2349 | Distribution Circuit | Equipment Failure/Involved | Overhead | 752 | 37353 | 39.116 | -120.9517 | RENFREESAM15055309062110mtr100489703325281hwy174colfax | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005829 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245614 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005978&numberofmonths=24&showchangehistorylog=1 | 17-0005978 | SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2110 | 153652110 | FUSE | 18223 | 20170109 | 925 | 1630275 | 1770 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 4857 | 38.6303 | -120.9242 | 5400CONNIELANE | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005978 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Force Out | 1245741 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005932&numberofmonths=24&showchangehistorylog=1 | 17-0005932 | SIERRA | FIELD OPS NORTH | Tier 2 | WEIMAR-1101 | 152491101 | FUSE | 6185 | 20170109 | 311 | 1629982 | 1248 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 19968 | 39.056 | -120.982 | 351ORCHARDLNCOLFAX | Strong Winds-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0005932 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Three Phase Fault | 1245709 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0008227&numberofmonths=24&showchangehistorylog=1 | 17-0008227 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE | 3369 | 20170110 | 2124 | 1637618 | 2476 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 14856 | 38.7521 | -120.6285 | 4995DOUGLASFIRCTMTR1007477136 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0008227 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Force Out | 1247670 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006879&numberofmonths=24&showchangehistorylog=1 | 17-0006879 | SIERRA | FIELD OPS NORTH | Tier 2 | BRUNSWICK-1110 | 152481110 | FUSE | 3907 | 20170110 | 1727 | 1634697 | 1533 | Distribution Circuit | Vegetation | Tree - fell into line | 114 | 14641 | 39.2224 | -121.0816 | IFO10664OAKST | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006879 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1246457 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007467&numberofmonths=24&showchangehistorylog=1 | 17-0007467 | SIERRA | FIELD OPS NORTH | Tier 3 | COLUMBIA HILL-1101 | 152471101 | OCB | 11012 | 20170110 | 1936 | 1636324 | 2670 | Distribution Circuit | Vegetation | Tree - fell into line | 1130 | 1246286 | 39.3313 | -121.1015 | WIREDOWN3LDSIDEOFSB314273LDSIDEOFSB31427 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007467 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247062 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0008336&numberofmonths=24&showchangehistorylog=1 | 17-0008336 | SIERRA | FIELD OPS NORTH | Tier 2 | COLUMBIA HILL-1101 | 152471101 | FUSE | 919149 | 20170110 | 1500 | 1633879 | 2914 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 17484 | 39.3366 | -121.1173 | MTR5000054660 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0008336 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1247760 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006912&numberofmonths=24&showchangehistorylog=1 | 17-0006912 | SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1103 | 152261103 | FUSE | 7431 | 20170110 | 1747 | 1634447 | 1588 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 15117 | 38.7251 | -120.8482 | CGC223305438740 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006912 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1246493 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0008527&numberofmonths=24&showchangehistorylog=1 | 17-0008527 | SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1103 | 152261103 | FUSE | 18615 | 20170110 | 2102 | 1637108 | 2773 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 5546 | 38.7281 | -120.8437 | 3SPANSLDSIDEOFFUCO | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0008527 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247887 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006894&numberofmonths=24&showchangehistorylog=1 | 17-0006894 | SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1105 | 152261105 | FUSE | 6661 | 20170110 | 1646 | 1634503 | 2979 | Distribution Circuit | Vegetation | Tree - fell into line | 169 | 257366 | 38.5894 | -120.8462 | ATMTR1007477018 | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0006894 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246473 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007848&numberofmonths=24&showchangehistorylog=1 | 17-0007848 | SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1105 | 152261105 | FUSE | 21593 | 20170110 | 2043 | 1636978 | 2823 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 26585 | 38.6871 | -120.8569 | 2SPANSWOFMTR1007391288 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0007848 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247308 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006795&numberofmonths=24&showchangehistorylog=1 | 17-0006795 | SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 21931 | 20170110 | 1533 | 1634068 | 2950 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 29950 | 38.6839 | -120.7929 | 2SPANSNEOF21931MTR1005221632 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006795 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1246383 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007580&numberofmonths=24&showchangehistorylog=1 | 17-0007580 | SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 2167 | 20170110 | 2119 | 1637575 | 2394 | Distribution Circuit | Equipment Failure/Involved | Overhead | 118 | 282492 | 38.67 | -120.7776 | 5SPANSLOADSIDEOF2167 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007580 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247104 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006395&numberofmonths=24&showchangehistorylog=1 | 17-0006395 | SIERRA | FIELD OPS NORTH | Tier 3 | DRUM-1101 | 152321101 | RECLOSER | 75874 | 20170110 | 631 | 1632529 | 3645 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 270882 | 39.2911 | -120.6782 | BET9231AND1213 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006395 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246101 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006803&numberofmonths=24&showchangehistorylog=1 | 17-0006803 | SIERRA | FIELD OPS NORTH | Tier 3 | DRUM-1101 | 152321101 | JUMPER | 1602 | 20170110 | 1514 | 1634159 | 1589 | Distribution Circuit | Vegetation | Tree - fell into line | 151 | 86286 | 39.2816 | -120.7089 | 1EO1211 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006803 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Open Circuit | 1246390 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007913&numberofmonths=24&showchangehistorylog=1 | 17-0007913 | SIERRA | FIELD OPS NORTH | Tier 3 | DRUM-1101 | 152321101 | FUSE | 9215 | 20170110 | 942 | 1632834 | 5248 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 94464 | 39.276 | -120.7173 | BET9215AND9227 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0007913 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247365 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0008310&numberofmonths=24&showchangehistorylog=1 | 17-0008310 | SIERRA | FIELD OPS NORTH | Tier 3 | DRUM-1101 | 152321101 | FUSE | 9213 | 20170110 | 548 | 1632510 | 6290 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 106930 | 39.2816 | -120.7087 | LuizPatrick5305306634fusecos5213 | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0008310 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247738 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007794&numberofmonths=24&showchangehistorylog=1 | 17-0007794 | SIERRA | FIELD OPS NORTH | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE | 4151 | 20170110 | 2005 | 1636661 | 2783 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 33396 | 38.9879 | -120.9062 | 3SPANSLDSIDEOF4151 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0007794 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247263 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007027&numberofmonths=24&showchangehistorylog=1 | 17-0007027 | SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1101 | 152241101 | FUSE | 36679 | 20170110 | 1738 | 1634764 | 1602 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 6408 | 39.0055 | -121.0581 | AT36679 | Overcast-Fog-Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0007027 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Open Circuit | 1246612 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007107&numberofmonths=24&showchangehistorylog=1 | 17-0007107 | SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1101 | 152241101 | FUSE | 4763 | 20170110 | 1913 | 1636038 | 1224 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 35496 | 39.0192 | -121.0298 | T14JEDA4PNOOFCO4763 | Partly Cloudy-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007107 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246692 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007233&numberofmonths=24&showchangehistorylog=1 | 17-0007233 | SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1101 | 152241101 | RECLOSER | 2414 | 20170110 | 2119 | 1637588 | 248 | Distribution Circuit | Vegetation | Tree - fell into line | 382 | 45873 | 38.9661 | -121.0354 | 3WO9975 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007233 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246812 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007264&numberofmonths=24&showchangehistorylog=1 | 17-0007264 | SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1101 | 152241101 | FUSE | 9957 | 20170110 | 2046 | 1636999 | 1249 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 14454 | 38.9987 | -121.01 | RENFREESAM15055309062110376goldenoak | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007264 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246844 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007172&numberofmonths=24&showchangehistorylog=1 | 17-0007172 | SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1109 | 152691109 | FUSE | 7863 | 20170110 | 1907 | 1637690 | 1273 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 61104 | 39.0916 | -121.1772 | 4NOF36431 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007172 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1246757 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006646&numberofmonths=24&showchangehistorylog=1 | 17-0006646 | SIERRA | FIELD OPS NORTH | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 9345 | 20170110 | 1207 | 1633157 | 3127 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 10600 | 38.8966 | -120.9607 | HARTEMMETT150653090620312328Hwy1937670Brushrocksln | Partly Cloudy-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006646 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246275 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007000&numberofmonths=24&showchangehistorylog=1 | 17-0007000 | SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2105 | 153132105 | TRIP-SAVER | 7203 | 20170110 | 1840 | 1635621 | 982 | Distribution Circuit | Vegetation | Tree - fell into line | 226 | 221932 | 39.1808 | -121.1894 | 2OF3SPANSOFWIREDOWN7877 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007000 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Three Phase Fault | 1246582 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006508&numberofmonths=24&showchangehistorylog=1 | 17-0006508 | SIERRA | FIELD OPS NORTH | Tier 3 | OLETA-1102 | 163541102 | FUSE | 20527 | 20170110 | 946 | 1632898 | 190 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 570 | 38.6557 | -120.602 | 5761BOUQUETCANYONRDSOMERSET | Heavy Rain-Strong Winds-Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006508 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246173 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007276&numberofmonths=24&showchangehistorylog=1 | 17-0007276 | SIERRA | FIELD OPS NORTH | Tier 2 | PENRYN-1103 | 152561103 | FUSE | 5253 | 20170110 | 1822 | 1635361 | 1336 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 73480 | 38.8342 | -121.1096 | 3290HECTORRD | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007276 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Three Phase Fault | 1246856 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006867&numberofmonths=24&showchangehistorylog=1 | 17-0006867 | SIERRA | FIELD OPS NORTH | Tier 2 | PENRYN-1105 | 152561105 | FUSE | 9143 | 20170110 | 1620 | 1634282 | 1122 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 33666 | 38.9014 | -121.1876 | ATCOUTS9143 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006867 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Open Circuit | 1246447 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007113&numberofmonths=24&showchangehistorylog=1 | 17-0007113 | SIERRA | FIELD OPS NORTH | Tier 2 | PLACERVILLE-1111 | 153081111 | OTHER | WIREDOWN | 20170110 | 1855 | 1635762 | 493 | Distribution Circuit | Vegetation | Tree - fell into line | 616 | 150379 | 38.7263 | -120.8234 | I41REGSONFORNIRD | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007113 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1246698 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006989&numberofmonths=24&showchangehistorylog=1 | 17-0006989 | SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | RECLOSER | 9372 | 20170110 | 1937 | 1636509 | 2965 | Distribution Circuit | Vegetation | Tree - fell into line | 1272 | 265975 | 38.714 | -120.9394 | 21789 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006989 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Three Phase Fault | 1246571 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007314&numberofmonths=24&showchangehistorylog=1 | 17-0007314 | SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 11705 | 20170110 | 2038 | 1636915 | 879 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 35160 | 38.6884 | -120.9241 | 6SPLDSIDEOF11705 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007314 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246895 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007783&numberofmonths=24&showchangehistorylog=1 | 17-0007783 | SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 11703 | 20170110 | 1844 | 1635609 | 2793 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 34080 | 38.6903 | -120.9293 | 4008BLACKOAKDR | Overcast-Fog-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007783 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247252 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006476&numberofmonths=24&showchangehistorylog=1 | 17-0006476 | SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2110 | 153652110 | FUSE | 22355 | 20170110 | 659 | 1632548 | 1900 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 34079 | 38.6321 | -120.9242 | MTR1007199612 | Heavy Rain-Strong Winds-Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0006476 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246159 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006729&numberofmonths=24&showchangehistorylog=1 | 17-0006729 | SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2110 | 153652110 | JUMPER | OJS1SPANSOFCGC223091035721 | 20170110 | 1155 | 1633126 | 1653 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1653 | 38.6422 | -120.9193 | CGC223091035721 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006729 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Force Out | 1246335 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0008250&numberofmonths=24&showchangehistorylog=1 | 17-0008250 | SIERRA | FIELD OPS NORTH | Tier 2 | SUMMIT-1101 | 152591101 | FUSE | 6627 | 20170110 | 2251 | 1637987 | 3879 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 170972 | 39.3246 | -120.3841 | HARTEMMETT1506530906203121689TBarCtendofcton3phaseline | Overcast-Snow-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0008250 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Three Phase Fault | 1247689 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0008785&numberofmonths=24&showchangehistorylog=1 | 17-0008785 | SIERRA | FIELD OPS NORTH | Tier 2 | TAMARACK-1101 | 152291101 | FUSE | 6617 | 20170110 | 2141 | 1643785 | 5573 | Distribution Circuit | Vegetation | Tree - grew into line | 54 | 300942 | 39.3202 | -120.4334 | MULITPLELOCATIONSEIREDOWNBEYONDFUCO6617OPERATORFIELDDIDNOTCAPTURESPECIFICINFOPERREPORTINGSTANDARDS | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0008785 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1248411 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007889&numberofmonths=24&showchangehistorylog=1 | 17-0007889 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 22021 | 20170111 | 732 | 1638868 | 2229 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 11145 | 38.6188 | -120.7186 | 2SPANSNORTHOF22021 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007889 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247347 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007372&numberofmonths=24&showchangehistorylog=1 | 17-0007372 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE | 2585 | 20170111 | 111 | 1638319 | 1372 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 79576 | 38.7552 | -120.602 | 2840LOYALLN | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007372 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246959 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007365&numberofmonths=24&showchangehistorylog=1 | 17-0007365 | SIERRA | FIELD OPS NORTH | Tier 3 | FORESTHILL-1102 | 152181102 | FUSE | 6005 | 20170111 | 126 | 1638376 | 1304 | Distribution Circuit | Vegetation | Tree - fell into line | 288 | 256170 | 39.019 | -120.8972 | 1SPANSOUTHOFMTR5000047917 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007365 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Three Phase Fault | 1246950 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007524&numberofmonths=24&showchangehistorylog=1 | 17-0007524 | SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1104 | 152691104 | FUSE | 4935 | 20170111 | 817 | 1639018 | 543 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 11138 | 39.1227 | -121.0532 | MTR1007546702 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007524 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1247068 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007320&numberofmonths=24&showchangehistorylog=1 | 17-0007320 | SIERRA | FIELD OPS NORTH | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 2422 | 20170111 | 104 | 1638322 | 1321 | Distribution Circuit | Vegetation | Tree - fell into line | 604 | 171496 | 38.9 | -120.9075 | JOHNSTONM150853090655632spansso5301uppermanhattancreekgeorgetown | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007320 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1246901 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007809&numberofmonths=24&showchangehistorylog=1 | 17-0007809 | SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2105 | 153132105 | FUSE | 5247 | 20170111 | 1343 | 1639923 | 395 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 5730 | 39.2053 | -121.2335 | 10227VISTAPOINTLOOP | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007809 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247273 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007765&numberofmonths=24&showchangehistorylog=1 | 17-0007765 | SIERRA | FIELD OPS NORTH | Tier 2 | SHADY GLEN-1102 | 152431102 | FUSE | 33317 | 20170111 | 929 | 1639249 | 1658 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 16580 | 39.1342 | -120.9407 | 2SPANSSSOF40527 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007765 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Three Phase Fault | 1247235 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007639&numberofmonths=24&showchangehistorylog=1 | 17-0007639 | SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 20469 | 20170111 | 1040 | 1639501 | 485 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 4063 | 38.7664 | -120.9343 | MTR1009669063 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007639 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247149 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0008220&numberofmonths=24&showchangehistorylog=1 | 17-0008220 | SIERRA | FIELD OPS NORTH | Tier 2 | TAMARACK-1101 | 152291101 | FUSE | 6633 | 20170111 | 1736 | 1640476 | 1921 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 95086 | 39.3171 | -120.4498 | HARTEMMETT150653090620313spansEofcos6633onConiferLn | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0008220 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1247663 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0008417&numberofmonths=24&showchangehistorylog=1 | 17-0008417 | SIERRA | FIELD OPS NORTH | Tier 2 | TAMARACK-1101 | 152291101 | FUSE | 6619 | 20170111 | 743 | 1638902 | 2593 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 72604 | 39.318 | -120.4546 | 50247CONIFERDR | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0008417 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247806 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007746&numberofmonths=24&showchangehistorylog=1 | 17-0007746 | SIERRA | FIELD OPS NORTH | Tier 2 | WEIMAR-1101 | 152491101 | FUSE | 6227 | 20170111 | 929 | 1639330 | 589 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 9424 | 38.999 | -120.9854 | CHORJELED9168376299640BoolerdApplegate | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007746 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Open Circuit | 1247222 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007650&numberofmonths=24&showchangehistorylog=1 | 17-0007650 | SIERRA | FIELD OPS NORTH | Tier 2 | WEIMAR-1102 | 152491102 | FUSE | 7795 | 20170111 | 24 | 1638181 | 957 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 22968 | 39.0046 | -120.9954 | MTR1004692250 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007650 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247157 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0010566&numberofmonths=24&showchangehistorylog=1 | 17-0010566 | SIERRA | FIELD OPS NORTH | Tier 3 | COLUMBIA HILL-1101 | 152471101 | FUSE | 4373 | 20170118 | 2116 | 1649065 | 1339 | Distribution Circuit | Vegetation | Tree - branch fell on line | 36 | 48204 | 39.3822 | -121.0482 | TASSONELOUIS12626826302JUNGLETR | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010566 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1249582 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0010132&numberofmonths=24&showchangehistorylog=1 | 17-0010132 | SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1109 | 152691109 | FUSE | 172971 | 20170118 | 1539 | 1646985 | 635 | Distribution Circuit | Equipment Failure/Involved | Overhead | 93 | 34335 | 39.0348 | -121.0985 | MTR1007602815 | Partly Cloudy-Rain-32-90 F | Pole-Wood | Broken, wire on object | 17-0010132 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1249145 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0010489&numberofmonths=24&showchangehistorylog=1 | 17-0010489 | SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2102 | 153132102 | FUSE | 32993 | 20170118 | 2058 | 1648991 | 934 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 79390 | 39.2528 | -121.115 | MTR5000023644 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010489 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1249507 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0010100&numberofmonths=24&showchangehistorylog=1 | 17-0010100 | SIERRA | FIELD OPS NORTH | Tier 2 | PENRYN-1103 | 152561103 | FUSE | 8909 | 20170118 | 1507 | 1646633 | 279 | Distribution Circuit | Vegetation | Tree - fell into line | 633 | 27919 | 38.8548 | -121.1078 | MTR1004894654 | Partly Cloudy-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010100 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1249114 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0010225&numberofmonths=24&showchangehistorylog=1 | 17-0010225 | SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2110 | 153652110 | FUSE | 21045 | 20170118 | 1541 | 1646804 | 1474 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 5896 | 38.6214 | -120.924 | 3SPANSWO21045 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010225 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1249230 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0010698&numberofmonths=24&showchangehistorylog=1 | 17-0010698 | SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2110 | 153652110 | FUSE | 1555 | 20170118 | 2342 | 1649578 | 816 | Distribution Circuit | Vegetation | Tree - fell into line | 258 | 151576 | 38.6476 | -120.9178 | 2SOF20205IFO4440HOLLYDR | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010698 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Three Phase Fault | 1249704 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0010188&numberofmonths=24&showchangehistorylog=1 | 17-0010188 | SIERRA | FIELD OPS NORTH | Tier 2 | WEIMAR-1101 | 152491101 | FUSE | 30745 | 20170118 | 1554 | 1646615 | 1066 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 58630 | 39.0435 | -120.9862 | JOHNSTONM15085309065563copole33851 | Partly Cloudy-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010188 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Force Out | 1249197 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0010264&numberofmonths=24&showchangehistorylog=1 | 17-0010264 | SIERRA | FIELD OPS NORTH | Tier 2 | WEIMAR-1102 | 152491102 | FUSE | 6175 | 20170118 | 1731 | 1646477 | 380 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 22420 | 39.0361 | -121.0041 | 1330PLEASANTRIDGERDCOLFAX | Partly Cloudy-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010264 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1249265 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0010218&numberofmonths=24&showchangehistorylog=1 | 17-0010218 | SIERRA | FIELD OPS NORTH | Tier 2 | WISE-1102 | 152271102 | FUSE | 5365 | 20170118 | 1558 | 1646766 | 625 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 33750 | 38.8911 | -121.1257 | SATTERLEEM15315303204435broken12kvpolecrewtoreplace | Partly Cloudy-Fog-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 17-0010218 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Force Out | 1249223 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0010326&numberofmonths=24&showchangehistorylog=1 | 17-0010326 | SIERRA | FIELD OPS NORTH | Tier 2 | WISE-1102 | 152271102 | FUSE | 3255 | 20170118 | 1546 | 1646832 | 3130 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 62600 | 38.9402 | -121.1612 | 3885SAILORSRAVINERDAUBURN | Rain-Strong Winds-Fog-32-90 F | Pole-Wood | Broken, wire on ground | 17-0010326 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1249336 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0010437&numberofmonths=24&showchangehistorylog=1 | 17-0010437 | SIERRA | FIELD OPS NORTH | Tier 2 | WISE-1102 | 152271102 | RECLOSER | 307494 | 20170118 | 2042 | 1648942 | 2527 | Distribution Circuit | Equipment Failure/Involved | Overhead | 266 | 196977 | 38.9339 | -121.1791 | DERYKKEVIN62153038651114991amina1WOF64151 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010437 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1249452 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0010744&numberofmonths=24&showchangehistorylog=1 | 17-0010744 | SIERRA | FIELD OPS NORTH | Tier 3 | BONNIE NOOK-1101 | 152301101 | FUSE | 6375 | 20170119 | 133 | 1649725 | 2176 | Distribution Circuit | Vegetation | Tree - fell into line | 121 | 245124 | 39.2008 | -120.8355 | 2SPANSSO63753SPANSOFWIREDOWN | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010744 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1249738 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0010628&numberofmonths=24&showchangehistorylog=1 | 17-0010628 | SIERRA | FIELD OPS NORTH | Tier 2 | BRUNSWICK-1104 | 152481104 | FUSE | 69925 | 20170119 | 12 | 1649609 | 1110 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 31080 | 39.263 | -121.0409 | 3LDSIDEOFMTR1009725982 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010628 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Three Phase Fault | 1249641 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0010786&numberofmonths=24&showchangehistorylog=1 | 17-0010786 | SIERRA | FIELD OPS NORTH | Tier 2 | LINCOLN-1104 | 153701104 | FUSE | 37461 | 20170119 | 1023 | 1650642 | 1500 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 4500 | 38.952 | -121.2515 | 1650BIGBENDRD | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010786 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1249768 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0010918&numberofmonths=24&showchangehistorylog=1 | 17-0010918 | SIERRA | FIELD OPS NORTH | Tier 2 | TAMARACK-1101 | 152291101 | FUSE | 6631 | 20170119 | 1227 | 1651144 | 586 | Distribution Circuit | Vegetation | Tree - fell into line | 119 | 69734 | 39.32 | -120.4408 | 51104CONIFERDRSODASPRINGS | Clear-Below 32 F | Conductor, Overhead | Broken, wire on object | 17-0010918 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1249862 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011142&numberofmonths=24&showchangehistorylog=1 | 17-0011142 | SIERRA | FIELD OPS NORTH | Tier 2 | TAMARACK-1101 | 152291101 | FUSE | 6617 | 20170119 | 1555 | 1651558 | 1271 | Distribution Circuit | Equipment Failure/Involved | Overhead | 54 | 68634 | 39.3202 | -120.4334 | BET66176653 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0011142 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1250053 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011549&numberofmonths=24&showchangehistorylog=1 | 17-0011549 | SIERRA | FIELD OPS NORTH | Tier 2 | BELL-1107 | 152701107 | FUSE | 9429 | 20170120 | 1030 | 1653713 | 1594 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 7300 | 38.9226 | -121.121 | MTR1004193078 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 17-0011549 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1250412 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011445&numberofmonths=24&showchangehistorylog=1 | 17-0011445 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1105 | 152481105 | JUMPER | 1PHASEWIREDOWN4SOF31909 | 20170120 | 827 | 1653712 | 505 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2020 | 39.3198 | -120.8655 | 4SOF31909 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011445 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Open Circuit | 1250328 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011592&numberofmonths=24&showchangehistorylog=1 | 17-0011592 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE | 4753 | 20170120 | 718 | 1652948 | 787 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 5509 | 39.3123 | -120.8824 | TASSONELOUIS12626826302G | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011592 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1250449 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011145&numberofmonths=24&showchangehistorylog=1 | 17-0011145 | SIERRA | FIELD OPS NORTH | Tier 2 | ECHO SUMMIT-1101 | 158031101 | RECLOSER | 2500 | 20170120 | 203 | 1652044 | 2589 | Distribution Circuit | Equipment Failure/Involved | Overhead | 246 | 327105 | 38.8236 | -120.0305 | SAMANIEGOS6265309063122abovestrawberry | Overcast-Snow-Below 32 F | Connector or Splice (OH) | Broken, wire on ground | 17-0011145 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1250056 | CSO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013190&numberofmonths=24&showchangehistorylog=1 | 17-0013190 | SIERRA | FIELD OPS NORTH | Tier 3 | ALLEGHANY-1101 | 152101101 | JUMPER | JUMPERS3WOF7939 | 20170121 | 428 | 1661218 | 5041 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 15123 | 39.4667 | -120.8475 | 3WOF7939 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0013190 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Open Circuit | 1252001 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011949&numberofmonths=24&showchangehistorylog=1 | 17-0011949 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1105 | 152481105 | JUMPER | WIREDOWNEOF31909 | 20170121 | 648 | 1655705 | 575 | Distribution Circuit | Vegetation | Tree - fell into line | 154 | 68015 | 39.3223 | -120.8836 | EOF31909 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0011949 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Open Circuit | 1250775 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012930&numberofmonths=24&showchangehistorylog=1 | 17-0012930 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE | 6521 | 20170121 | 1831 | 1659879 | 1350 | Distribution Circuit | Equipment Failure/Involved | Overhead | 123 | 166050 | 39.3087 | -120.909 | 2spanssource9819CROSSARMSTRIPPEDLDSIDEOF31909 | Overcast-Fog-Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0012930 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1251750 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012948&numberofmonths=24&showchangehistorylog=1 | 17-0012948 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1105 | 152481105 | SWITCH | 6523 | 20170121 | 1713 | 1659965 | 1469 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 45077 | 39.3237 | -120.8819 | 2SSOF98191LDSIDEOF31909 | Strong Winds-Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012948 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1251768 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011873&numberofmonths=24&showchangehistorylog=1 | 17-0011873 | SIERRA | FIELD OPS NORTH | Tier 2 | BRUNSWICK-1106 | 152481106 | RECLOSER | 2416 | 20170121 | 115 | 1655395 | 614 | Distribution Circuit | Vegetation | Tree - fell into line | 1309 | 160761 | 39.159 | -121.0398 | 1NOF22044OAKMEADOW | Overcast-Fog-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on object | 17-0011873 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1250700 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011882&numberofmonths=24&showchangehistorylog=1 | 17-0011882 | SIERRA | FIELD OPS NORTH | Tier 3 | DRUM-1101 | 152321101 | FUSE | 30479 | 20170121 | 420 | 1655484 | 755 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 3775 | 39.2518 | -120.7483 | NOCOUT308245 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 17-0011882 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1250709 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011867&numberofmonths=24&showchangehistorylog=1 | 17-0011867 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 22771 | 20170121 | 13 | 1655343 | 1045 | Distribution Circuit | Vegetation | Tree - fell into line | 450 | 300438 | 38.7169 | -120.5802 | 4878GOLDENST | Overcast-Fog-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 17-0011867 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1250694 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0010893&numberofmonths=24&showchangehistorylog=1 | 17-0010893 | SIERRA | FIELD OPS NORTH | Tier 2 | EL DORADO PH-2101 | 152762101 | SWITCH | 13141 | 20170121 | 1154 | 1655261 | 7312 | Distribution Circuit | Vegetation | Tree - branch fell on line | 443 | 598639 | 38.7889 | -120.1686 | 17280ELDORADOHWY | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010893 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1250827 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011929&numberofmonths=24&showchangehistorylog=1 | 17-0011929 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE | 93529 | 20170121 | 557 | 1655615 | 518 | Distribution Circuit | Vegetation | Tree - branch fell on line | 28 | 8409 | 38.7599 | -120.5768 | MTR1007204060 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011929 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1250757 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012150&numberofmonths=24&showchangehistorylog=1 | 17-0012150 | SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 35987 | 20170121 | 1117 | 1656404 | 623 | Distribution Circuit | Vegetation | Tree - fell into line | 78 | 48594 | 38.9205 | -120.6953 | 1E1WOF2990HARMONYLANEGEORGETOWN | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0012150 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1250965 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012943&numberofmonths=24&showchangehistorylog=1 | 17-0012943 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-1104 | 153661104 | RECLOSER | 12832 | 20170122 | 651 | 1659939 | 969 | Distribution Circuit | Vegetation | Tree - fell into line | 760 | 303638 | 38.7523 | -120.682 | HYLANDTRAVIS53029570763945northcanyon | Partly Cloudy-Fog-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012943 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1251763 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013485&numberofmonths=24&showchangehistorylog=1 | 17-0013485 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 8661 | 20170122 | 1951 | 1662238 | 882 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 35280 | 39.1881 | -121.0177 | 1EOFWOFMTR1007532693 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013485 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1252302 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013519&numberofmonths=24&showchangehistorylog=1 | 17-0013519 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1106 | 152481106 | JUMPER | WIREDOWN1LDSIDEOF7047 | 20170122 | 1920 | 1662532 | 1244 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 15011 | 39.1916 | -121.0024 | 1LDSIDEOF7047 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013519 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Open Circuit | 1252337 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013239&numberofmonths=24&showchangehistorylog=1 | 17-0013239 | SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 20371 | 20170122 | 1403 | 1661177 | 1737 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3474 | 38.6942 | -120.7715 | LDSIDEOF20371 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013239 | OH | Sus | 0 | yes | 2017 | JAN | Yes | None | 1252049 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013373&numberofmonths=24&showchangehistorylog=1 | 17-0013373 | SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | JUMPER | WIREONGRD112SPANWO18585 | 20170122 | 1854 | 1662147 | 383 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1174 | 304136 | 38.6771 | -120.761 | 112SPANWO18585 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013373 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Open Circuit | 1252187 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013185&numberofmonths=24&showchangehistorylog=1 | 17-0013185 | SIERRA | FIELD OPS NORTH | Tier 3 | DRUM-1101 | 152321101 | FUSE | 9217 | 20170122 | 330 | 1659270 | 2107 | Distribution Circuit | Vegetation | Tree - fell into line | 88 | 185416 | 39.2582 | -120.7311 | 3SLDSIDEOF92171SPANLDSIDEOFFLOATER | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013185 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1251995 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013537&numberofmonths=24&showchangehistorylog=1 | 17-0013537 | SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | OTHER | WIREDOWNSSPANSLDSD5829 | 20170122 | 2101 | 1662269 | 1407 | Distribution Circuit | Vegetation | Tree - fell into line | 83 | 116781 | 38.9432 | -120.7189 | HATTRUPJIM153353090628884miBeyondSB5829onWentworthSpringsRD | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013537 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Open Circuit | 1252355 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012764&numberofmonths=24&showchangehistorylog=1 | 17-0012764 | SIERRA | FIELD OPS NORTH | Tier 2 | WISE-1102 | 152271102 | RECLOSER | 307494 | 20170122 | 450 | 1658832 | 435 | Distribution Circuit | Vegetation | Tree - fell into line | 267 | 53545 | 38.9339 | -121.1791 | 1PNO9453FUCO | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012764 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1251586 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013710&numberofmonths=24&showchangehistorylog=1 | 17-0013710 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-1104 | 153661104 | FUSE | 6685 | 20170123 | 721 | 1663029 | 2162 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 13164 | 38.7401 | -120.6704 | MTR1007476787 | Snow-Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013710 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1252508 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013612&numberofmonths=24&showchangehistorylog=1 | 17-0013612 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | RECLOSER | 8372 | 20170123 | 710 | 1662972 | 1786 | Distribution Circuit | Vegetation | Tree - fell into line | 696 | 396322 | 38.6092 | -120.7025 | POWELLBRYAN51038574962471sluggulch | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013612 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1252433 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013628&numberofmonths=24&showchangehistorylog=1 | 17-0013628 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 1051 | 20170123 | 403 | 1663102 | 765 | Distribution Circuit | Vegetation | Tree - fell into line | 68 | 52020 | 38.6339 | -120.5653 | 7SPANSLDSIDEOFCOUTS1051 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0013628 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1252449 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013630&numberofmonths=24&showchangehistorylog=1 | 17-0013630 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 22399 | 20170123 | 319 | 1662930 | 5194 | Distribution Circuit | Vegetation | Tree - fell into line | 254 | 986037 | 38.6858 | -120.6418 | 1SPANSSOF22399MTR1005204028 | Partly Cloudy-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 17-0013630 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1252451 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013686&numberofmonths=24&showchangehistorylog=1 | 17-0013686 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 20553 | 20170123 | 354 | 1663455 | 836 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 836 | 38.6266 | -120.5696 | 3SPANLDSIDEOFCOUTS | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0013686 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Force Out | 1252487 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013698&numberofmonths=24&showchangehistorylog=1 | 17-0013698 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 21153 | 20170123 | 723 | 1663566 | 1808 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 19888 | 38.6004 | -120.6437 | 2SPANSLOADSIDEOF21153 | Drizzle-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013698 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1252501 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013876&numberofmonths=24&showchangehistorylog=1 | 17-0013876 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 21393 | 20170123 | 319 | 1664337 | 3713 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 33417 | 38.6947 | -120.639 | MTR1007386289 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 17-0013876 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1252641 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013887&numberofmonths=24&showchangehistorylog=1 | 17-0013887 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 20911 | 20170123 | 406 | 1664354 | 2129 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 6387 | 38.5923 | -120.6085 | 2SPANSLOADSIDEOFCUTOUTS | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013887 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1252649 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0014000&numberofmonths=24&showchangehistorylog=1 | 17-0014000 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 5121 | 20170123 | 1157 | 1663933 | 465 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 8835 | 38.6235 | -120.5877 | 3SPANSLOADSIDEOF5121 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0014000 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1252748 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013995&numberofmonths=24&showchangehistorylog=1 | 17-0013995 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE | 6761 | 20170123 | 1759 | 1664762 | 931 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2793 | 39.3229 | -120.8858 | 3NEOF6761 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0013995 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1252744 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013655&numberofmonths=24&showchangehistorylog=1 | 17-0013655 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1106 | 152481106 | RECLOSER | 51486 | 20170123 | 800 | 1663148 | 449 | Distribution Circuit | Vegetation | Tree - fell into line | 1007 | 209089 | 39.1909 | -120.9967 | R26214426YOUBETRD | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013655 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Multi-Fault | 1252465 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013975&numberofmonths=24&showchangehistorylog=1 | 17-0013975 | SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 2177 | 20170123 | 1429 | 1664345 | 1444 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 11552 | 38.6912 | -120.7371 | ATMTR5000050374 | Partly Cloudy-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013975 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1252728 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013556&numberofmonths=24&showchangehistorylog=1 | 17-0013556 | SIERRA | FIELD OPS NORTH | Tier 3 | DRUM-1101 | 152321101 | RECLOSER | 75874 | 20170123 | 110 | 1662624 | 2563 | Distribution Circuit | Equipment Failure/Involved | Overhead | 87 | 222981 | 39.2911 | -120.6782 | NEAR30691 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0013556 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Force Out | 1252374 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013558&numberofmonths=24&showchangehistorylog=1 | 17-0013558 | SIERRA | FIELD OPS NORTH | Tier 3 | DRUM-1101 | 152321101 | RECLOSER | 1602 | 20170123 | 121 | 1662642 | 2429 | Distribution Circuit | Equipment Failure/Involved | Overhead | 105 | 203778 | 39.2517 | -120.75 | WIREDOWNINMULTIPLELOCATIONS | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0013558 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Force Out | 1252376 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0014026&numberofmonths=24&showchangehistorylog=1 | 17-0014026 | SIERRA | FIELD OPS NORTH | Tier 2 | ECHO SUMMIT-1101 | 158031101 | RECLOSER | 2500 | 20170123 | 1829 | 1664813 | 1351 | Distribution Circuit | Equipment Failure/Involved | Overhead | 640 | 830590 | 38.8236 | -120.0305 | WIREDOWNLDSIDE8975WIREDOWN5SEOF12333 | Overcast-Below 32 F | Crossarm, Wood | Broken, wire on ground | 17-0014026 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1252772 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013576&numberofmonths=24&showchangehistorylog=1 | 17-0013576 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | RECLOSER | 19752 | 20170123 | 416 | 1662767 | 983 | Distribution Circuit | Vegetation | Tree - fell into line | 1142 | 383946 | 38.7139 | -120.5835 | MTR1009711742 | Partly Cloudy-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0013576 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1252397 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0014356&numberofmonths=24&showchangehistorylog=1 | 17-0014356 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 11791 | 20170123 | 349 | 1662723 | 3253 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 24010 | 38.7727 | -120.59 | BEYONDTHEHARDTAP3PSO11791 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0014356 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1253081 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013678&numberofmonths=24&showchangehistorylog=1 | 17-0013678 | SIERRA | FIELD OPS NORTH | Tier 3 | FORESTHILL-1101 | 152181101 | SECTIONALIZER | 1762 | 20170123 | 830 | 1663209 | 330 | Distribution Circuit | Vegetation | Tree - fell into line | 591 | 121954 | 39.0186 | -120.8288 | 1PNO31603FUCO | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0013678 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Three Phase Fault | 1252485 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013563&numberofmonths=24&showchangehistorylog=1 | 17-0013563 | SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | RECLOSER | 2224 | 20170123 | 153 | 1662476 | 2115 | Distribution Circuit | Vegetation | Tree - fell into line | 896 | 491372 | 38.9052 | -120.8373 | VOLCANOVILLERDWIREDOWN | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | On Ground | 17-0013563 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1252382 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018350&numberofmonths=24&showchangehistorylog=1 | 17-0018350 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1103 | 152481103 | RECLOSER | 2200 | 20170207 | 633 | 1678716 | 938 | Distribution Circuit | Vegetation | Tree - fell into line | 114 | 66747 | 39.275 | -121.0207 | METER1009371742 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018350 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Three Phase Fault | 1256187 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018437&numberofmonths=24&showchangehistorylog=1 | 17-0018437 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1104 | 152481104 | FUSE | 7121 | 20170207 | 801 | 1678913 | 1837 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 99198 | 39.2851 | -121.0578 | WILKINSARMANDO1589913505718444AUGUSTINE | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018437 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1256255 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018698&numberofmonths=24&showchangehistorylog=1 | 17-0018698 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 7053 | 20170207 | 1548 | 1680568 | 1403 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 75762 | 39.1909 | -120.9934 | MTR1007546714 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018698 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1256452 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018900&numberofmonths=24&showchangehistorylog=1 | 17-0018900 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 9487 | 20170207 | 431 | 1677779 | 2016 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 26208 | 39.1843 | -120.9369 | 2SPANSLOADSIDE | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018900 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1256629 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018596&numberofmonths=24&showchangehistorylog=1 | 17-0018596 | SIERRA | FIELD OPS NORTH | Tier 2 | BRUNSWICK-1110 | 152481110 | FUSE | 3673 | 20170207 | 708 | 1678445 | 1770 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 4770 | 39.2223 | -121.1055 | MUELLERANDY15855308636807THISADDRESS | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018596 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1256367 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018623&numberofmonths=24&showchangehistorylog=1 | 17-0018623 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE | 18497 | 20170207 | 1229 | 1680149 | 335 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 3685 | 38.7583 | -120.5764 | 4SPANSLOADSIDEOF18497 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018623 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1256395 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018308&numberofmonths=24&showchangehistorylog=1 | 17-0018308 | SIERRA | FIELD OPS NORTH | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE | 5929 | 20170207 | 559 | 1678016 | 1997 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 15827 | 39.0221 | -120.81 | TREESINLINE | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018308 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1256145 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018042&numberofmonths=24&showchangehistorylog=1 | 17-0018042 | SIERRA | FIELD OPS NORTH | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 4487 | 20170207 | 48 | 1677300 | 997 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 24411 | 38.9132 | -120.9627 | 2601WILLOWCREEKTRAIL | Partly Cloudy-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018042 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1255895 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018258&numberofmonths=24&showchangehistorylog=1 | 17-0018258 | SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2105 | 153132105 | FUSE | 4715 | 20170207 | 613 | 1678069 | 637 | Distribution Circuit | Vegetation | Tree - fell into line | 105 | 66885 | 39.1645 | -121.1515 | MUELLERANDY1585530863680713256LONGVALLEYRDPENNVALLEY | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018258 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1256106 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018358&numberofmonths=24&showchangehistorylog=1 | 17-0018358 | SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-1104 | 153651104 | FUSE | 20629 | 20170207 | 735 | 1678787 | 340 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 9520 | 38.5899 | -120.9619 | 6400FERNWOODDR | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0018358 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1256194 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0019741&numberofmonths=24&showchangehistorylog=1 | 17-0019741 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 1149 | 20170209 | 2320 | 1684439 | 1101 | Distribution Circuit | Vegetation | Tree - fell into line | 96 | 105696 | 38.7122 | -120.6675 | LUNAMARCOS62453029574074700Pasoway | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019741 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1257212 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0019423&numberofmonths=24&showchangehistorylog=1 | 17-0019423 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1105 | 152481105 | JUMPER | OJ34451 | 20170209 | 1244 | 1683408 | 229 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 229 | 39.2779 | -120.9456 | 34451 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019423 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Open Circuit | 1256956 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0019708&numberofmonths=24&showchangehistorylog=1 | 17-0019708 | SIERRA | FIELD OPS NORTH | Tier 2 | ECHO SUMMIT-1101 | 158031101 | RECLOSER | 8922 | 20170209 | 2159 | 1684259 | 1239 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 59472 | 38.8228 | -120.0296 | 2SPANSLDSIDEOF8922 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019708 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1257179 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0019309&numberofmonths=24&showchangehistorylog=1 | 17-0019309 | SIERRA | FIELD OPS NORTH | Tier 2 | WEIMAR-1101 | 152491101 | FUSE | 6293 | 20170209 | 911 | 1682879 | 398 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 2944 | 39.0588 | -120.9906 | EDENFORESTDR | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019309 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1256896 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024784&numberofmonths=24&showchangehistorylog=1 | 17-0024784 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-1104 | 153661104 | RECLOSER | 12832 | 20170220 | 2327 | 1706706 | 1081 | Distribution Circuit | Equipment Failure/Involved | Overhead | 759 | 111751 | 38.7523 | -120.682 | NESPANSINGLEPHASELDSIDEOF18525 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024784 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1261754 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024798&numberofmonths=24&showchangehistorylog=1 | 17-0024798 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE | 3277 | 20170220 | 2301 | 1706611 | 1061 | Distribution Circuit | Vegetation | Tree - fell into line | 224 | 237664 | 38.753 | -120.6124 | 1SPANWO32771SO7963 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024798 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1261767 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025187&numberofmonths=24&showchangehistorylog=1 | 17-0025187 | SIERRA | FIELD OPS NORTH | Tier 3 | BONNIE NOOK-1102 | 152301102 | FUSE | 6417 | 20170220 | 2036 | 1708834 | 2590 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 118828 | 39.2105 | -120.8017 | MAINLINEBETWEEN6425AND6421 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025187 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Three Phase Fault | 1262091 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025005&numberofmonths=24&showchangehistorylog=1 | 17-0025005 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1103 | 152481103 | RECLOSER | 2200 | 20170220 | 2310 | 1707254 | 2622 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 149454 | 39.275 | -121.0207 | MTR1009371742 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025005 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Three Phase Fault | 1261960 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024796&numberofmonths=24&showchangehistorylog=1 | 17-0024796 | SIERRA | FIELD OPS NORTH | Tier 2 | BRUNSWICK-1104 | 152481104 | FUSE | 33683 | 20170220 | 2258 | 1707124 | 1091 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 50186 | 39.2465 | -121.0455 | 11809MARIONDR | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024796 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1261765 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024364&numberofmonths=24&showchangehistorylog=1 | 17-0024364 | SIERRA | FIELD OPS NORTH | Tier 2 | CLARKSVILLE-2104 | 153612104 | FUSE | 2039 | 20170220 | 1947 | 1705719 | 1257 | Distribution Circuit | Vegetation | Tree - fell into line | 205 | 184993 | 38.6987 | -121.0239 | 86979 | Overcast-Heavy Rain-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0024364 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Three Phase Fault | 1261329 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024714&numberofmonths=24&showchangehistorylog=1 | 17-0024714 | SIERRA | FIELD OPS NORTH | Tier 2 | ECHO SUMMIT-1101 | 158031101 | RECLOSER | 2500 | 20170220 | 2312 | 1706647 | 3899 | Distribution Circuit | Equipment Failure/Involved | Overhead | 293 | 450134 | 38.8236 | -120.0305 | 4WOF2605TWOMORELOCATIONSWITHFLOATERS | Overcast-Heavy Rain-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0024714 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1261682 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024080&numberofmonths=24&showchangehistorylog=1 | 17-0024080 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 18411 | 20170220 | 1943 | 1705704 | 996 | Distribution Circuit | Vegetation | Tree - fell into line | 73 | 72708 | 38.7722 | -120.5821 | MTR1005221296 | Overcast-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0024080 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1261045 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024082&numberofmonths=24&showchangehistorylog=1 | 17-0024082 | SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1101 | 152241101 | RECLOSER | 76178 | 20170220 | 2019 | 1705858 | 1505 | Distribution Circuit | Vegetation | Tree - fell into line | 613 | 649253 | 39.0015 | -121.0224 | 1137COMBIRRD | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024082 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1261047 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024721&numberofmonths=24&showchangehistorylog=1 | 17-0024721 | SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1102 | 152241102 | FUSE | 6225 | 20170220 | 2113 | 1706118 | 1336 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 13360 | 38.9999 | -120.9889 | 2SPANSLDSIDE | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024721 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1261689 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024793&numberofmonths=24&showchangehistorylog=1 | 17-0024793 | SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1109 | 152691109 | FUSE | 7863 | 20170220 | 2205 | 1706301 | 883 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 42384 | 39.0916 | -121.1772 | 3SPANSNO36431 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024793 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1261762 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024815&numberofmonths=24&showchangehistorylog=1 | 17-0024815 | SIERRA | FIELD OPS NORTH | Tier 2 | PLACERVILLE-1111 | 153081111 | FUSE | 2507 | 20170220 | 2341 | 1706752 | 844 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 10256 | 38.7223 | -120.7976 | MTR1007297901 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024815 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1261784 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024047&numberofmonths=24&showchangehistorylog=1 | 17-0024047 | SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | RECLOSER | 1104 | 20170220 | 1924 | 1705555 | 1481 | Distribution Circuit | Equipment Failure/Involved | Overhead | 645 | 573918 | 38.9124 | -120.8201 | HARTEMMETT150653090620311761RubiconRd | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024047 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1261013 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024857&numberofmonths=24&showchangehistorylog=1 | 17-0024857 | SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 4655 | 20170220 | 2153 | 1706251 | 1777 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 56864 | 38.7689 | -120.9511 | BEYONDMTR1007389331 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024857 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1261827 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025679&numberofmonths=24&showchangehistorylog=1 | 17-0025679 | SIERRA | FIELD OPS NORTH | Tier 2 | SIERRA CITY DIESEL-1101 | 158011101 | RECLOSER | 978 | 20170220 | 2006 | 1707364 | 14116 | Distribution Circuit | Vegetation | Tree - fell into line | 554 | 1789554 | 39.608 | -120.6068 | 1DEPOLELDSIDEOFFU546926SPANSCONDUCTORDOWNLDSIDEOF2628 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025679 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1262503 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024705&numberofmonths=24&showchangehistorylog=1 | 17-0024705 | SIERRA | FIELD OPS NORTH | Tier 2 | SUMMIT-1101 | 152591101 | SECTIONALIZER | 48632 | 20170220 | 2040 | 1706415 | 3965 | Distribution Circuit | Vegetation | Tree - fell into line | 238 | 505460 | 39.3201 | -120.3791 | SATTERLEEM1531530320443512kvmainlinedownduetotreecrewtoreplace | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024705 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1261673 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023949&numberofmonths=24&showchangehistorylog=1 | 17-0023949 | SIERRA | FIELD OPS NORTH | Tier 2 | SUMMIT-1102 | 152591102 | FUSE | 6813 | 20170220 | 909 | 1702805 | 4973 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 14919 | 39.3109 | -120.3361 | 58620OLDDONNERSUMMITRD | Overcast-Snow-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0023949 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Force Out | 1260921 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024702&numberofmonths=24&showchangehistorylog=1 | 17-0024702 | SIERRA | FIELD OPS NORTH | Tier 2 | SUMMIT-1102 | 152591102 | RECLOSER | 49484 | 20170220 | 2303 | 1706446 | 2397 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 89981 | 39.3174 | -120.329 | 1PSO7895 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024702 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1261669 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024960&numberofmonths=24&showchangehistorylog=1 | 17-0024960 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE | 4383 | 20170221 | 204 | 1707324 | 723 | Distribution Circuit | Vegetation | Tree - fell into line | 81 | 58563 | 39.2341 | -120.9849 | MTR1007580729 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024960 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1261925 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025071&numberofmonths=24&showchangehistorylog=1 | 17-0025071 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE | 6279 | 20170221 | 150 | 1707161 | 1042 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 55226 | 39.3185 | -120.8894 | 3PEOF3419 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0025071 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1262009 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024881&numberofmonths=24&showchangehistorylog=1 | 17-0024881 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 7025 | 20170221 | 223 | 1707223 | 687 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 20307 | 39.1988 | -121.0104 | MTR1007662735 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024881 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1261855 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025160&numberofmonths=24&showchangehistorylog=1 | 17-0025160 | SIERRA | FIELD OPS NORTH | Tier 2 | BRUNSWICK-1106 | 152481106 | FUSE | 33279 | 20170221 | 1145 | 1708413 | 1648 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 19776 | 39.1678 | -120.966 | MTR1009283757 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025160 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Three Phase Fault | 1262072 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024972&numberofmonths=24&showchangehistorylog=1 | 17-0024972 | SIERRA | FIELD OPS NORTH | Tier 2 | BRUNSWICK-1110 | 152481110 | FUSE | 33687 | 20170221 | 737 | 1707723 | 1798 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 26970 | 39.243 | -121.0558 | MARINOTONY6134530682641814901ECHORIDGEDRNEVADACITY | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0024972 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1261934 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025739&numberofmonths=24&showchangehistorylog=1 | 17-0025739 | SIERRA | FIELD OPS NORTH | Tier 2 | ECHO SUMMIT-1101 | 158031101 | FUSE | 12861 | 20170221 | 1452 | 1711171 | 4195 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 20975 | 38.8245 | -120.0447 | 2SPANSLOADSIDEOF12861 | Partly Cloudy-Below 32 F | Crossarm, Wood | Broken, wire on ground | 17-0025739 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1262526 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025147&numberofmonths=24&showchangehistorylog=1 | 17-0025147 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 18415 | 20170221 | 1217 | 1708496 | 1493 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 19409 | 38.7719 | -120.5758 | SAMANIEGOS6265309063122randolphcanyonrd | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025147 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1262063 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025185&numberofmonths=24&showchangehistorylog=1 | 17-0025185 | SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1104 | 152691104 | FUSE | 7583 | 20170221 | 224 | 1708238 | 1981 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 8798 | 39.0875 | -121.0463 | MTR1007532554 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025185 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1262088 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024864&numberofmonths=24&showchangehistorylog=1 | 17-0024864 | SIERRA | FIELD OPS NORTH | Tier 2 | LINCOLN-1101 | 153701101 | FUSE | 9415 | 20170221 | 153 | 1707165 | 2347 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 4694 | 38.8972 | -121.2193 | RANDDAN15085309136400900fowlerrd | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024864 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1261835 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025166&numberofmonths=24&showchangehistorylog=1 | 17-0025166 | SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 6943 | 20170221 | 620 | 1707480 | 1858 | Distribution Circuit | Equipment Failure/Involved | Overhead | 23 | 42734 | 38.8447 | -120.8224 | 5545PORTERRANCHGARDENVALLEYCA | Overcast-Fog-Rain-Lightning-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025166 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1262077 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024990&numberofmonths=24&showchangehistorylog=1 | 17-0024990 | SIERRA | FIELD OPS NORTH | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 1261 | 20170221 | 351 | 1707321 | 2042 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 55134 | 38.8011 | -120.8914 | 6673CARVERSRD | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024990 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1261947 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025175&numberofmonths=24&showchangehistorylog=1 | 17-0025175 | SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2110 | 153652110 | FUSE | 20679 | 20170221 | 1011 | 1708200 | 912 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 7296 | 38.6039 | -120.9275 | 5700SEMORDR | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025175 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1262083 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0026002&numberofmonths=24&showchangehistorylog=1 | 17-0026002 | SIERRA | FIELD OPS NORTH | Tier 2 | SUMMIT-1102 | 152591102 | FUSE | 6829 | 20170221 | 2308 | 1709592 | 2580 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 10320 | 39.3175 | -120.3525 | WIREDOWN2POLESLDSIDE | Overcast-Snow-Below 32 F | Conductor, Overhead | On Ground | 17-0026002 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1262750 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025208&numberofmonths=24&showchangehistorylog=1 | 17-0025208 | SIERRA | FIELD OPS NORTH | Tier 2 | WEIMAR-1101 | 152491101 | FUSE | 6193 | 20170221 | 26 | 1706854 | 2503 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 120144 | 39.0713 | -120.9761 | 1SPANNORTHOF33991 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025208 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1262110 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024841&numberofmonths=24&showchangehistorylog=1 | 17-0024841 | SIERRA | FIELD OPS NORTH | Tier 2 | WEIMAR-1102 | 152491102 | FUSE | 6399 | 20170221 | 142 | 1707147 | 993 | Distribution Circuit | Vegetation | Tree - fell into line | 221 | 165903 | 39.0372 | -121.0037 | HATTRUPJIM15335309062888oneNOCO6261seconeoneSOSw1273 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0024841 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Three Phase Fault | 1261811 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025604&numberofmonths=24&showchangehistorylog=1 | 17-0025604 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 21461 | 20170222 | 1236 | 1710649 | 514 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1542 | 38.5707 | -120.7149 | JESSEEBEN62091682682378161DORADOCANYONRD | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025604 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Multi-Fault | 1262442 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025542&numberofmonths=24&showchangehistorylog=1 | 17-0025542 | SIERRA | FIELD OPS NORTH | Tier 2 | ECHO SUMMIT-1101 | 158031101 | OTHER | 8922 | 20170222 | 1129 | 1710507 | 238 | Distribution Circuit | Equipment Failure/Involved | Overhead | 47 | 11186 | 38.8228 | -120.0296 | 10SOF8922 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025542 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Open Circuit | 1262410 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037397&numberofmonths=24&showchangehistorylog=1 | 17-0037397 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | RECLOSER | 97982 | 20170406 | 2233 | 1748398 | 842 | Distribution Circuit | Vegetation | Tree - fell into line | 753 | 422384 | 38.6216 | -120.5867 | JESSEEBEN62091682682371WO7005 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037397 | OH | Sus | 31318176 | yes | 2017 | APR | Yes | Line to Line | 1271609 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037746&numberofmonths=24&showchangehistorylog=1 | 17-0037746 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1103 | 152481103 | FUSE | 7117 | 20170406 | 2222 | 1748343 | 1299 | Distribution Circuit | Vegetation | Tree - fell into line | 155 | 201345 | 39.2846 | -121.022 | BET4651AND33619 | Overcast-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0037746 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1271938 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037304&numberofmonths=24&showchangehistorylog=1 | 17-0037304 | SIERRA | FIELD OPS NORTH | Tier 2 | BRUNSWICK-1104 | 152481104 | RECLOSER | 2112 | 20170406 | 2102 | 1747359 | 1033 | Distribution Circuit | Vegetation | Tree - fell into line | 505 | 277904 | 39.2416 | -121.0566 | 11612DEERPARKDR | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037304 | OH | Sus | 42985912 | yes | 2017 | APR | Yes | Line to Line | 1271520 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037315&numberofmonths=24&showchangehistorylog=1 | 17-0037315 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE | 7079 | 20170406 | 2009 | 1746543 | 840 | Distribution Circuit | Vegetation | Tree - branch fell on line | 308 | 258720 | 38.7533 | -120.5967 | 5945PNYEXPRESS | Partly Cloudy-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037315 | OH | Sus | 42985909 | yes | 2017 | APR | Yes | Line to Line | 1271531 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037317&numberofmonths=24&showchangehistorylog=1 | 17-0037317 | SIERRA | FIELD OPS NORTH | Tier 2 | GRASS VALLEY-1101 | 152031101 | FUSE | 8185 | 20170406 | 2115 | 1747621 | 1054 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 5620 | 39.1801 | -121.0656 | 1PEO14394JASPERLN | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0037317 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Line | 1271533 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037945&numberofmonths=24&showchangehistorylog=1 | 17-0037945 | SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2102 | 153132102 | FUSE | 7437 | 20170406 | 2347 | 1750120 | 1643 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 23002 | 39.2473 | -121.1858 | 1SPANWO7759 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037945 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1272052 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037675&numberofmonths=24&showchangehistorylog=1 | 17-0037675 | SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1110 | 152691110 | JUMPER | HOTWIREDOWNATMTR1009741819 | 20170407 | 809 | 1750085 | 227 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 2985 | 39.0595 | -121.0236 | MTR1009741819 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037675 | OH | Sus | 0 | yes | 2017 | APR | Yes | Open Circuit | 1271889 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037549&numberofmonths=24&showchangehistorylog=1 | 17-0037549 | SIERRA | FIELD OPS NORTH | Tier 2 | SHADY GLEN-1101 | 152431101 | FUSE | 6303 | 20170407 | 51 | 1749080 | 974 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 22138 | 39.0896 | -120.9656 | SATTERLEEM1531530320443512blwn6303crewtorepairbroken12kvTXpolewire | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0037549 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1271769 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0038159&numberofmonths=24&showchangehistorylog=1 | 17-0038159 | SIERRA | FIELD OPS NORTH | Tier 2 | SHINGLE SPRINGS-2110 | 153652110 | FUSE | 22595 | 20170407 | 2052 | 1751947 | 934 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 15878 | 38.6645 | -120.9192 | 3SPSO22595 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0038159 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1272218 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0075507&numberofmonths=24&showchangehistorylog=1 | 17-0075507 | SIERRA | FIELD OPS NORTH | Tier 2 | PLACER-1103 | 152461103 | JUMPER | OJMTR1009206068 | 20170903 | 717 | 1867829 | 218 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 218 | 38.9046 | -121.1008 | mtr1009206068 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0075507 | OH | Sus | 31349005 | yes | 2017 | SEP | Yes | Open Circuit | 1299796 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0085778&numberofmonths=24&showchangehistorylog=1 | 17-0085778 | SIERRA | FIELD OPS NORTH | Tier 2 | BRUNSWICK-1104 | 152481104 | FUSE | 7123 | 20171008 | 2303 | 1894177 | 2350 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 30550 | 39.254 | -121.057 | 10877MORNINGSTARLNNEVADACITY | Clear-32-90 F | Pole-Wood | Broken, wire on object | 17-0085778 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Line | 1307098 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0085266&numberofmonths=24&showchangehistorylog=1 | 17-0085266 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE | 31865 | 20171008 | 2209 | 1894021 | 2127 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2229 | 39.2954 | -120.9808 | 16578COOPERRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085266 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1306713 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0085282&numberofmonths=24&showchangehistorylog=1 | 17-0085282 | SIERRA | FIELD OPS NORTH | Tier 2 | BRUNSWICK-1110 | 152481110 | RECLOSER | 2664 | 20171008 | 2325 | 1894346 | 1044 | Distribution Circuit | Vegetation | Tree - fell into line | 1759 | 252040 | 39.235 | -121.0604 | WILKINSARMANDO15899135057SSANDLSOFCO7163 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085282 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1306729 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0085204&numberofmonths=24&showchangehistorylog=1 | 17-0085204 | SIERRA | FIELD OPS NORTH | Tier 3 | COLUMBIA HILL-1101 | 152471101 | FUSE | 5357 | 20171008 | 1931 | 1893744 | 2723 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 46291 | 39.3711 | -120.9959 | NOMTR100760471417455SKYLANDRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085204 | OH | Sus | 43169673 | yes | 2017 | OCT | Yes | Line to Line | 1306650 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0085355&numberofmonths=24&showchangehistorylog=1 | 17-0085355 | SIERRA | FIELD OPS NORTH | Tier 3 | COLUMBIA HILL-1101 | 152471101 | SWITCH | 879 | 20171008 | 2258 | 1894156 | 978 | Distribution Circuit | Vegetation | Tree - fell into line | 223 | 198802 | 39.3504 | -121.1236 | MUELLERANDY1585530863680728764HWY49HEESCHERDSNSJ | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0085355 | OH | Sus | 31355729 | yes | 2017 | OCT | Yes | Force Out | 1306806 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0086029&numberofmonths=24&showchangehistorylog=1 | 17-0086029 | SIERRA | FIELD OPS NORTH | Tier 2 | GRASS VALLEY-1103 | 152031103 | FUSE | 7835 | 20171008 | 2347 | 1894921 | 4128 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 41 | 169248 | 39.1992 | -121.0865 | 3POLESSO7835 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0086029 | OH | Sus | 0 | yes | 2017 | OCT | Yes | None | 1307258 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0086150&numberofmonths=24&showchangehistorylog=1 | 17-0086150 | SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2102 | 153132102 | JUMPER | JUMPERS1SEOF3987 | 20171008 | 2327 | 1897902 | 5463 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 29043 | 39.2336 | -121.1102 | TASSONELOUIS1262682630210122BTNYSPR | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0086150 | OH | Sus | 31360786 | yes | 2017 | OCT | Yes | Line to Ground | 1307313 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0086143&numberofmonths=24&showchangehistorylog=1 | 17-0086143 | SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2105 | 153132105 | JUMPER | JUMPERS1NEOFMTR1007521741 | 20171008 | 2343 | 1897875 | 3677 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 5 | 18385 | 39.2392 | -121.1426 | FIELD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0086143 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Line | 1307307 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0086158&numberofmonths=24&showchangehistorylog=1 | 17-0086158 | SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2105 | 153132105 | FUSE | 4529 | 20171008 | 2352 | 1897935 | 5230 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 125520 | 39.227 | -121.1412 | 14851ROUGHREADYHWY | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0086158 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1307325 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0085261&numberofmonths=24&showchangehistorylog=1 | 17-0085261 | SIERRA | FIELD OPS NORTH | Tier 3 | PIKE CITY-1101 | 152201101 | JUMPER | WIREDOWNATSPRINGANDMILL | 20171008 | 2110 | 1894011 | 1098 | Distribution Circuit | Vegetation | Tree - fell into line | 258 | 255784 | 39.4551 | -121.0499 | MUELLERANDY15855308636807CORNEROFSPRINGMILLSTSCMPTNVL | Clear-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0085261 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1306707 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0085527&numberofmonths=24&showchangehistorylog=1 | 17-0085527 | SIERRA | FIELD OPS NORTH | Tier 3 | PIKE CITY-1101 | 152201101 | FUSE | 3579 | 20171008 | 2153 | 1896299 | 1357 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 17773 | 39.4112 | -121.0673 | 9SPANSLDSIDEOF3579 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085527 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Line | 1306972 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0085600&numberofmonths=24&showchangehistorylog=1 | 17-0085600 | SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 5801 | 20171008 | 2108 | 1893857 | 1312 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 10496 | 38.8844 | -120.8498 | 4SPANSLDSIDE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085600 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1307004 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0085492&numberofmonths=24&showchangehistorylog=1 | 17-0085492 | SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 21931 | 20171009 | 920 | 1896202 | 408 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 2438 | 38.6839 | -120.7929 | 4770RINGOLD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085492 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Line | 1306953 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0085795&numberofmonths=24&showchangehistorylog=1 | 17-0085795 | SIERRA | FIELD OPS NORTH | Tier 3 | FORESTHILL-1102 | 152181102 | FUSE | 6003 | 20171009 | 1945 | 1897030 | 174 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 174 | 39.02 | -120.8486 | POWERELINE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085795 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Force Out | 1307109 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0085336&numberofmonths=24&showchangehistorylog=1 | 17-0085336 | SIERRA | FIELD OPS NORTH | Tier 2 | GRASS VALLEY-1103 | 152031103 | OCB | 11032 | 20171009 | 124 | 1894576 | 4031 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 1424 | 2445169 | 39.2093 | -121.0615 | LDSIDEOF31365brokenpolewiredownatMTR1007517075 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085336 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1306787 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0086141&numberofmonths=24&showchangehistorylog=1 | 17-0086141 | SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2105 | 153132105 | JUMPER | JUMPERSLDSIDEOFMTR1008936587 | 20171009 | 104 | 1897872 | 5033 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 56 | 281848 | 39.2337 | -121.1541 | NOTREPORTEDBYDOANYWHEREINOUTAGEOQTHADTOENTERSOMETHINGTOCOMPLETEOUTAGE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0086141 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Open Circuit | 1307306 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0086747&numberofmonths=24&showchangehistorylog=1 | 17-0086747 | SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2105 | 153132105 | SWITCH | 34463 | 20171009 | 104 | 1899353 | 5488 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 1 | 5488 | 39.242 | -121.1535 | 11616PICNPANLANE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0086747 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1307821 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0085436&numberofmonths=24&showchangehistorylog=1 | 17-0085436 | SIERRA | FIELD OPS NORTH | Tier 2 | SUMMIT-1101 | 152591101 | TRIP-SAVER | 6627 | 20171009 | 427 | 1895640 | 507 | Distribution Circuit | Vegetation | Tree - branch fell on line | 46 | 23322 | 39.3246 | -120.3841 | TurneyRobert530205656321753TBarCt | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085436 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Force Out | 1306885 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0088957&numberofmonths=24&showchangehistorylog=1 | 17-0088957 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1103 | 152481103 | OTHER | WIREDOWN1CONDUCTOR2PWO33617 | 20171020 | 119 | 1905467 | 706 | Distribution Circuit | Equipment Failure/Involved | Overhead | 155 | 102410 | 39.2925 | -121.0154 | 2PSOURCESIDEOF33617 | Overcast-Fog-Heavy Rain-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0088957 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1309538 | CSO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0089061&numberofmonths=24&showchangehistorylog=1 | 17-0089061 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 7053 | 20171020 | 108 | 1904968 | 2488 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 47369 | 39.1909 | -120.9934 | MTR1007546719 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0089061 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1309621 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0099679&numberofmonths=24&showchangehistorylog=1 | 17-0099679 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 7645 | 20171204 | 1032 | 1934860 | 1328 | Distribution Circuit | Vegetation | Tree - fell into line | 112 | 30299 | 39.1514 | -121.029 | RENFREESAM1505530906211022044oakmeadowsrd | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0099679 | OH | Sus | 0 | yes | 2017 | DEC | Yes | Line to Line | 1317445 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0102021&numberofmonths=24&showchangehistorylog=1 | 17-0102021 | SIERRA | FIELD OPS NORTH | Tier 3 | ALLEGHANY-1102 | 152101102 | RECLOSER | 11022 | 20171216 | 1122 | 1944589 | 3283 | Distribution Circuit | Vegetation | Tree - fell into line | 162 | 58853 | 39.4655 | -120.8443 | NUMEROUSLOCATIONBET889AND809DESOLATEAREA | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0102021 | OH | Sus | 0 | yes | 2017 | DEC | Yes | Line to Line | 1319931 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0102185&numberofmonths=24&showchangehistorylog=1 | 17-0102185 | SIERRA | FIELD OPS NORTH | Tier 2 | BELL-1108 | 152701108 | FUSE | 9927 | 20171216 | 1611 | 1945541 | 163 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 2659 | 38.9692 | -121.1046 | 4555CHRISLN | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0102185 | OH | Sus | 0 | yes | 2017 | DEC | Yes | Line to Ground | 1320096 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0102011&numberofmonths=24&showchangehistorylog=1 | 17-0102011 | SIERRA | FIELD OPS NORTH | Tier 2 | SUMMIT-1101 | 152591101 | FUSE | 6625 | 20171216 | 940 | 1944327 | 393 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 6288 | 39.3232 | -120.3782 | FatorTravis5302177961Donnerpassrd | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0102011 | OH | Sus | 0 | yes | 2017 | DEC | Yes | Line to Line | 1319921 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0102266&numberofmonths=24&showchangehistorylog=1 | 17-0102266 | SIERRA | FIELD OPS NORTH | Tier 2 | TAMARACK-1101 | 152291101 | FUSE | 6631 | 20171216 | 2221 | 1946009 | 1138 | Distribution Circuit | Vegetation | Tree - fell into line | 118 | 30601 | 39.32 | -120.4408 | MTR1004691349 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0102266 | OH | Sus | 35024126 | yes | 2017 | DEC | Yes | Line to Line | 1320176 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0023258&numberofmonths=24&showchangehistorylog=1 | 18-0023258 | SIERRA | FIELD OPS NORTH | Tier 3 | ALLEGHANY-1101 | 152101101 | RECLOSER | 804 | 20180316 | 516 | 45306 | 848 | Distribution Circuit | Vegetation | Tree - fell into line | 603 | 157730 | 39.5598 | -120.8239 | 4SPANSSOURCESIDEOF2730 | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023258 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Three Phase Fault | 1336156 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0023498&numberofmonths=24&showchangehistorylog=1 | 18-0023498 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 2825 | 20180316 | 859 | 45398 | 1192 | Distribution Circuit | Vegetation | Tree - fell into line | 126 | 198450 | 38.6327 | -120.5458 | HILLTOPHILLTOP6949PIONEERDR | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023498 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Multi-Fault | 1336316 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0023752&numberofmonths=24&showchangehistorylog=1 | 18-0023752 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 2491 | 20180316 | 1523 | 46098 | 1541 | Distribution Circuit | Vegetation | Tree - fell into line | 247 | 65694 | 38.6467 | -120.5259 | 2491 | Overcast-Fog-Heavy Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 18-0023752 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1336545 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0023318&numberofmonths=24&showchangehistorylog=1 | 18-0023318 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE | 6521 | 20180316 | 804 | 45335 | 2068 | Distribution Circuit | Vegetation | Tree - fell into line | 125 | 102268 | 39.3087 | -120.909 | ATFUCO4753 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023318 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1336216 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0023501&numberofmonths=24&showchangehistorylog=1 | 18-0023501 | SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 20685 | 20180316 | 1333 | 45927 | 1532 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 12256 | 38.6587 | -120.7561 | LAFFONDDANIEL5325Metatetrail | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023501 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1336317 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0023361&numberofmonths=24&showchangehistorylog=1 | 18-0023361 | SIERRA | FIELD OPS NORTH | Tier 2 | ECHO SUMMIT-1101 | 158031101 | FUSE | 1571 | 20180316 | 738 | 45625 | 4673 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 322437 | 38.7743 | -120.298 | CGC224865340794 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 18-0023361 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1336248 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0023399&numberofmonths=24&showchangehistorylog=1 | 18-0023399 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | OCB | 21012 | 20180316 | 1225 | 45766 | 1706 | Distribution Circuit | Vegetation | Tree - fell into line | 2184 | 777200 | 38.7934 | -120.62 | 2921FOREBAYRD | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023399 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Three Phase Fault | 1336267 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0023538&numberofmonths=24&showchangehistorylog=1 | 18-0023538 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 6797 | 20180316 | 950 | 46111 | 3337 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 90099 | 38.7603 | -120.5749 | 2NDAND3RDSPANSLOADSIDEOF6797 | Overcast-Fog-Snow-32-90 F | Crossarm, Wood | Broken, wire on ground | 18-0023538 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1336337 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0023539&numberofmonths=24&showchangehistorylog=1 | 18-0023539 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 6799 | 20180316 | 1140 | 46114 | 1979 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 120719 | 38.7602 | -120.5687 | JESSEEBEN6209168268237SLYPARKROCKYRD1EOCGC224088740117 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 18-0023539 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1336338 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0023563&numberofmonths=24&showchangehistorylog=1 | 18-0023563 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 2391 | 20180316 | 842 | 46170 | 3015 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 93465 | 38.7387 | -120.5731 | 3902GARNETRD | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023563 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Multi-Fault | 1336355 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0023873&numberofmonths=24&showchangehistorylog=1 | 18-0023873 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 1385 | 20180316 | 834 | 47271 | 3461 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 10383 | 38.7642 | -120.5488 | 2SOF1385 | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023873 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1336674 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0023279&numberofmonths=24&showchangehistorylog=1 | 18-0023279 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2102 | 152762102 | RECLOSER | 19612 | 20180316 | 820 | 45315 | 3571 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1257 | 2290224 | 38.7621 | -120.5586 | AT212311WESTOF227791NOF196122NOF19612AT2963AT39433 | Overcast-Fog-Snow-32-90 F | Crossarm, Wood | Broken, wire on object | 18-0023279 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1336176 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0023411&numberofmonths=24&showchangehistorylog=1 | 18-0023411 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE | 18511 | 20180316 | 1003 | 45615 | 3470 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 262819 | 38.7537 | -120.575 | 11015 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023411 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1336274 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0023586&numberofmonths=24&showchangehistorylog=1 | 18-0023586 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE | 10987 | 20180316 | 1141 | 45734 | 1913 | Distribution Circuit | Environmental/External | Ice or snow | 95 | 181735 | 38.7439 | -120.5658 | GUTIERREZMIGUEL70724914526835diamonddr | Overcast-Fog-Snow-32-90 F | Pole-Wood | Broken, wire on ground | 18-0023586 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Multi-Fault | 1336375 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0023620&numberofmonths=24&showchangehistorylog=1 | 18-0023620 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2102 | 152762102 | OCB | 21022 | 20180316 | 2036 | 46283 | 1476 | Distribution Circuit | Vegetation | Tree - fell into line | 3242 | 622369 | 38.7934 | -120.6201 | WIREDOWN1EO6681ANDPOLEBROKENDOWNCGC224030940164 | Overcast-Fog-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 18-0023620 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1336398 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0023723&numberofmonths=24&showchangehistorylog=1 | 18-0023723 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE | 13059 | 20180316 | 1533 | 46268 | 2749 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 131952 | 38.753 | -120.5682 | FatorTravis53021779616751OnyxdrPollackPines | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023723 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1336516 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0023750&numberofmonths=24&showchangehistorylog=1 | 18-0023750 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE | 20829 | 20180316 | 1145 | 45676 | 3268 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 13072 | 38.7666 | -120.5849 | 1SPLDSIDEOF20829 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023750 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1336543 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0023800&numberofmonths=24&showchangehistorylog=1 | 18-0023800 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2102 | 152762102 | JUMPER | OJSATMTR1007479834 | 20180316 | 1141 | 46981 | 2936 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 23488 | 38.7401 | -120.5609 | 3703GARNETTRD | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 18-0023800 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Multi-Fault | 1336591 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0023446&numberofmonths=24&showchangehistorylog=1 | 18-0023446 | SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 787997 | 20180316 | 918 | 45439 | 975 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 10725 | 38.9156 | -120.6876 | MET1005563852 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 18-0023446 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1336299 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0064545&numberofmonths=24&showchangehistorylog=1 | 18-0064545 | SIERRA | FIELD OPS NORTH | Tier 2 | PLACERVILLE-2106 | 153082106 | FUSE | 92903 | 20180728 | 633 | 142227 | 417 | Distribution Circuit | Vegetation | Tree - branch fell on line | 37 | 15429 | 38.7451 | -120.7825 | 2418MEADOWLN | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0064545 | OH | Sus | 0 | No | 2018 | JUL | Yes | Line to Ground | 1367317 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0090287&numberofmonths=24&showchangehistorylog=1 | 18-0090287 | SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2105 | 153132105 | FUSE | 4819 | 20181014 | 1815 | 194986 | 1048 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 8688 | 39.2382 | -121.1558 | 5SOCGC222388257594 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0090287 | OH | Sus | 43506621 | yes | 2018 | OCT | Yes | Line to Ground | 1385493 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0104944&numberofmonths=24&showchangehistorylog=1 | 18-0104944 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 7673 | 20181129 | 1000 | 228573 | 483 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 6762 | 39.1484 | -121.0332 | 5SPLDSIDEOFCOUT7673 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 18-0104944 | OH | Sus | 31416672 | yes | 2018 | NOV | Yes | Line to Ground | 1396217 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0105035&numberofmonths=24&showchangehistorylog=1 | 18-0105035 | SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1103 | 152691103 | FUSE | 7755 | 20181129 | 1032 | 228677 | 656 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 11152 | 39.078 | -121.0865 | 4PSOFEOL | Partly Cloudy-Fog-Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 18-0105035 | OH | Sus | 0 | yes | 2018 | NOV | Yes | Force Out | 1396276 | CAW | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0105014&numberofmonths=24&showchangehistorylog=1 | 18-0105014 | SIERRA | FIELD OPS NORTH | Tier 2 | SUMMIT-1102 | 152591102 | OCB | 11022 | 20181129 | 1133 | 228831 | 1448 | Distribution Circuit | Equipment Failure/Involved | Overhead | 292 | 64558 | 39.3193 | -120.3785 | WIREDOWN1SPSSBUCKTWDLR2302ONTAPFEEDINGCOUT6841NOCAUSEFOUND | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0105014 | OH | Sus | 0 | yes | 2018 | NOV | Yes | Multi-Fault | 1396264 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005388&numberofmonths=24&showchangehistorylog=1 | 19-0005388 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 11427 | 20190106 | 1854 | 256757 | 1013 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 8448 | 38.6858 | -120.6419 | MTR5000053072 | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005388 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1403837 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005098&numberofmonths=24&showchangehistorylog=1 | 19-0005098 | SIERRA | FIELD OPS NORTH | Tier 2 | BELL-1108 | 152701108 | FUSE | 5773 | 20190106 | 1408 | 255378 | 467 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 18213 | 39.011 | -121.1043 | MTR1004894475 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005098 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1403571 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005481&numberofmonths=24&showchangehistorylog=1 | 19-0005481 | SIERRA | FIELD OPS NORTH | Tier 3 | BONNIE NOOK-1102 | 152301102 | FUSE | 6415 | 20190106 | 2105 | 258055 | 1051 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 21233 | 39.2132 | -120.7805 | 2LDSIDE | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005481 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1403930 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005419&numberofmonths=24&showchangehistorylog=1 | 19-0005419 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1103 | 152481103 | FUSE | 4693 | 20190106 | 2014 | 257526 | 963 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 5778 | 39.2862 | -121.0057 | 2NO4693 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005419 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1403871 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005255&numberofmonths=24&showchangehistorylog=1 | 19-0005255 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1105 | 152481105 | RECLOSER | 2130 | 20190106 | 1811 | 256324 | 987 | Distribution Circuit | Equipment Failure/Involved | Overhead | 207 | 19399 | 39.2741 | -120.9695 | WILKINSARMANDO158991350572PSOSBCO63513 | Snow-Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005255 | OH | Sus | 43626490 | yes | 2019 | JAN | Yes | Line to Line | 1403726 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005852&numberofmonths=24&showchangehistorylog=1 | 19-0005852 | SIERRA | FIELD OPS NORTH | Tier 3 | PIKE CITY-1102 | 152201102 | FUSE | 8801 | 20190106 | 1801 | 256154 | 2934 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 79218 | 39.4945 | -120.9977 | 10NO8803 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005852 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1404217 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005457&numberofmonths=24&showchangehistorylog=1 | 19-0005457 | SIERRA | FIELD OPS NORTH | Tier 2 | PLACERVILLE-1110 | 153081110 | JUMPER | OJ1EO21681 | 20190106 | 2019 | 257563 | 1028 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 6168 | 38.7449 | -120.821 | 2414COLOMARD | Overcast-Fog-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005457 | OH | Sus | 0 | yes | 2019 | JAN | Yes | None | 1403909 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005518&numberofmonths=24&showchangehistorylog=1 | 19-0005518 | SIERRA | FIELD OPS NORTH | Tier 2 | WEIMAR-1101 | 152491101 | RECLOSER | 2058 | 20190106 | 2033 | 257875 | 1091 | Distribution Circuit | Vegetation | Tree - fell into line | 408 | 107385 | 39.0444 | -120.9858 | 1125SIERRADAWNDR | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005518 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1403967 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010662&numberofmonths=24&showchangehistorylog=1 | 19-0010662 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-1104 | 153661104 | OTHER | WIREDOWN3777DOGWOOD | 20190116 | 2333 | 272041 | 2762 | Distribution Circuit | Vegetation | Tree - fell into line | 450 | 291918 | 38.7885 | -120.7039 | 3777DOGWOODLN | Overcast-Fog-Heavy Rain-Lightning-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0010662 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Open Circuit | 1407481 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010402&numberofmonths=24&showchangehistorylog=1 | 19-0010402 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | RECLOSER | 186912 | 20190116 | 2325 | 271904 | 2462 | Distribution Circuit | Vegetation | Tree - fell into line | 1172 | 754567 | 38.641 | -120.7043 | MAINLINEBET22759AND55945 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0010402 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407267 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010542&numberofmonths=24&showchangehistorylog=1 | 19-0010542 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 11937 | 20190116 | 2336 | 271987 | 2391 | Distribution Circuit | Vegetation | Tree - fell into line | 173 | 165864 | 38.7137 | -120.6232 | MTR1005051464 | Overcast-Fog-Heavy Rain-Lightning-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0010542 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407406 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010884&numberofmonths=24&showchangehistorylog=1 | 19-0010884 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 2019 | 20190116 | 2329 | 273570 | 2456 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 50671 | 38.5875 | -120.6614 | MTR1007479702 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010884 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407591 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010901&numberofmonths=24&showchangehistorylog=1 | 19-0010901 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | JUMPER | OJS1EO18833 | 20190116 | 2325 | 273614 | 1300 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 11700 | 38.5867 | -120.7058 | 18833 | Overcast-Fog-Heavy Rain-Lightning-32-90 F | Pole-Wood | Broken, wire on ground | 19-0010901 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407598 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010989&numberofmonths=24&showchangehistorylog=1 | 19-0010989 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 20033 | 20190116 | 2338 | 272817 | 1357 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 16284 | 38.6929 | -120.7149 | 4SPANSSWO20033 | Partly Cloudy-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010989 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407654 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010995&numberofmonths=24&showchangehistorylog=1 | 19-0010995 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 10303 | 20190116 | 2329 | 273883 | 2504 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 12520 | 38.6016 | -120.6988 | 7080DORADOCANYON | Overcast-Fog-Heavy Rain-Lightning-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0010995 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407660 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010999&numberofmonths=24&showchangehistorylog=1 | 19-0010999 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 95655 | 20190116 | 2329 | 273898 | 2381 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 4762 | 38.6109 | -120.6692 | 7211PERRYCREEKRD | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0010999 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407664 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011110&numberofmonths=24&showchangehistorylog=1 | 19-0011110 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 11657 | 20190116 | 2325 | 274204 | 2463 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 78816 | 38.5741 | -120.735 | AT21347 | Overcast-Fog-Snow-Strong Winds-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0011110 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407732 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011168&numberofmonths=24&showchangehistorylog=1 | 19-0011168 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 1055 | 20190116 | 2345 | 272796 | 2477 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 86695 | 38.6516 | -120.6283 | 6POLESLDSIDEOF1055 | Partly Cloudy-Fog-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 19-0011168 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1407773 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010352&numberofmonths=24&showchangehistorylog=1 | 19-0010352 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE | 37441 | 20190116 | 2134 | 271170 | 821 | Distribution Circuit | Vegetation | Tree - fell into line | 98 | 80458 | 39.2377 | -121.0215 | 11835BLACKOAKRD | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010352 | OH | Sus | 31422233 | yes | 2019 | JAN | Yes | Line to Ground | 1407217 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010448&numberofmonths=24&showchangehistorylog=1 | 19-0010448 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE | 31887 | 20190116 | 2259 | 271766 | 1371 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2742 | 39.3086 | -120.9316 | ATCGC223026859934 | Lightning-Fog-Heavy Rain-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0010448 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1407311 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010290&numberofmonths=24&showchangehistorylog=1 | 19-0010290 | SIERRA | FIELD OPS NORTH | Tier 3 | COLUMBIA HILL-1101 | 152471101 | RECLOSER | 764 | 20190116 | 2132 | 271190 | 1388 | Distribution Circuit | Vegetation | Tree - fell into line | 256 | 337277 | 39.367 | -121.0461 | JIMENEZAL530913796319263MAIDURIDGE | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010290 | OH | Sus | 43635519 | yes | 2019 | JAN | Yes | Three Phase Fault | 1407155 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011802&numberofmonths=24&showchangehistorylog=1 | 19-0011802 | SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1105 | 152261105 | FUSE | 13217 | 20190116 | 2332 | 271920 | 2386 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 11930 | 38.5951 | -120.8106 | 2POLESNO13217 | Overcast-Fog-Heavy Rain-Lightning-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011802 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1408214 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010424&numberofmonths=24&showchangehistorylog=1 | 19-0010424 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | RECLOSER | 63464 | 20190116 | 2346 | 272052 | 3719 | Distribution Circuit | Vegetation | Tree - fell into line | 1155 | 196676 | 38.7607 | -120.5049 | HYLANDTRAVIS530295707610121highway50 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010424 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407289 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010711&numberofmonths=24&showchangehistorylog=1 | 19-0010711 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 9991 | 20190116 | 2315 | 271824 | 2238 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 40284 | 38.6392 | -120.5262 | FIRSTSPANLDSIDEOF9991 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010711 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407506 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010493&numberofmonths=24&showchangehistorylog=1 | 19-0010493 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE | 18401 | 20190116 | 2334 | 272263 | 979 | Distribution Circuit | Vegetation | Tree - fell into line | 117 | 37439 | 38.7676 | -120.596 | AT18401 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010493 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1407357 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010162&numberofmonths=24&showchangehistorylog=1 | 19-0010162 | SIERRA | FIELD OPS NORTH | Tier 3 | FORESTHILL-1102 | 152181102 | RECLOSER | 11022 | 20190116 | 1956 | 270326 | 938 | Distribution Circuit | Equipment Failure/Involved | Overhead | 423 | 100008 | 39.02 | -120.8294 | JOHNSTONM150853090655632spansnoco308731 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010162 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407031 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010268&numberofmonths=24&showchangehistorylog=1 | 19-0010268 | SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1103 | 152691103 | FUSE | 32761 | 20190116 | 2003 | 270324 | 1286 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 10288 | 39.148 | -121.0682 | 5SPANSLDSIDEOF32761 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0010268 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407133 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010488&numberofmonths=24&showchangehistorylog=1 | 19-0010488 | SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1103 | 152691103 | FUSE | 9737 | 20190116 | 2229 | 271618 | 1118 | Distribution Circuit | Vegetation | Tree - fell into line | 72 | 80496 | 39.1108 | -121.0824 | 10682EASTLIMEKILNRD | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010488 | OH | Sus | 31422233 | yes | 2019 | JAN | Yes | Line to Line | 1407352 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010946&numberofmonths=24&showchangehistorylog=1 | 19-0010946 | SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1109 | 152691109 | FUSE | 3173 | 20190116 | 2350 | 272043 | 1327 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 14764 | 39.0433 | -121.0977 | 2SPANSLDSIDEOFCGC222567450543 | Partly Cloudy-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010946 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1407625 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011009&numberofmonths=24&showchangehistorylog=1 | 19-0011009 | SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1109 | 152691109 | TRIP-SAVER | 7831 | 20190116 | 2159 | 271401 | 2489 | Distribution Circuit | Vegetation | Tree - fell into line | 154 | 151810 | 39.0948 | -121.1523 | MTR1007518412 | Overcast-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0011009 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407673 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010314&numberofmonths=24&showchangehistorylog=1 | 19-0010314 | SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1110 | 152691110 | OTHER | WIREDOWN1SO35307 | 20190116 | 1922 | 269727 | 935 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 18813 | 39.0793 | -121.018 | 1SO35307 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010314 | OH | Sus | 43635519 | yes | 2019 | JAN | Yes | Line to Ground | 1407179 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0009441&numberofmonths=24&showchangehistorylog=1 | 19-0009441 | SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2102 | 153132102 | RECLOSER | 2718 | 20190116 | 823 | 266550 | 689 | Distribution Circuit | Vegetation | Tree - fell into line | 1173 | 78141 | 39.2354 | -121.2209 | 12052WAXWINGCTPENNVALLEY | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0009441 | OH | Sus | 31422068 | yes | 2019 | JAN | Yes | Line to Ground | 1406524 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0009451&numberofmonths=24&showchangehistorylog=1 | 19-0009451 | SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2105 | 153132105 | RECLOSER | 2748 | 20190116 | 849 | 266596 | 622 | Distribution Circuit | Vegetation | Tree - fell into line | 886 | 65200 | 39.2081 | -121.2033 | 1PSO4403 | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0009451 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1406529 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0009985&numberofmonths=24&showchangehistorylog=1 | 19-0009985 | SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | RECLOSER | 7522 | 20190116 | 1747 | 268772 | 1579 | Distribution Circuit | Vegetation | Tree - fell into line | 1026 | 265796 | 38.8155 | -120.8221 | 1SPANWOR147 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009985 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1406851 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011166&numberofmonths=24&showchangehistorylog=1 | 19-0011166 | SIERRA | FIELD OPS NORTH | Tier 2 | WEIMAR-1101 | 152491101 | FUSE | 6161 | 20190116 | 2324 | 271875 | 2301 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 62127 | 39.0229 | -120.9584 | 1950SUNVALLEYRD | Partly Cloudy-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011166 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407771 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011849&numberofmonths=24&showchangehistorylog=1 | 19-0011849 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE | 12573 | 20190117 | 1335 | 275935 | 2880 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 11520 | 38.7629 | -120.6129 | 2LDSIDEOF12573 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0011849 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1408232 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010996&numberofmonths=24&showchangehistorylog=1 | 19-0010996 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | TRIP-SAVER | 12025 | 20190117 | 1100 | 273887 | 1679 | Distribution Circuit | Vegetation | Tree - fell into line | 108 | 71964 | 38.6276 | -120.7439 | 5SPANSSWO21315 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010996 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407661 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011242&numberofmonths=24&showchangehistorylog=1 | 19-0011242 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 21319 | 20190117 | 8 | 272652 | 2431 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 13340 | 38.6184 | -120.7371 | MTR1007297886 | Overcast-Fog-Heavy Rain-Lightning-32-90 F | Pole-Wood | Broken, wire on ground | 19-0011242 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407818 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010979&numberofmonths=24&showchangehistorylog=1 | 19-0010979 | SIERRA | FIELD OPS NORTH | Tier 2 | BELL-1107 | 152701107 | FUSE | 4857 | 20190117 | 1124 | 273831 | 494 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 2214 | 38.9393 | -121.1305 | LYNNLANE | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010979 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407643 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011243&numberofmonths=24&showchangehistorylog=1 | 19-0011243 | SIERRA | FIELD OPS NORTH | Tier 3 | BONNIE NOOK-1101 | 152301101 | FUSE | 6379 | 20190117 | 2 | 272663 | 2247 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 31458 | 39.2049 | -120.8309 | MTR100458736 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011243 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1407819 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011808&numberofmonths=24&showchangehistorylog=1 | 19-0011808 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE | 31895 | 20190117 | 747 | 272918 | 1718 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3436 | 39.3162 | -120.8964 | 3NOF31895 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011808 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1408217 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010875&numberofmonths=24&showchangehistorylog=1 | 19-0010875 | SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1101 | 152241101 | FUSE | 8483 | 20190117 | 205 | 272316 | 764 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 40478 | 39.0185 | -121.0223 | 1810WALGRAMEADOWSCIRCLE | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010875 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1407582 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011388&numberofmonths=24&showchangehistorylog=1 | 19-0011388 | SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1103 | 152691103 | FUSE | 41595 | 20190117 | 350 | 273552 | 1875 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3750 | 39.1482 | -121.1438 | TASSONELOUIS5306826302FUSE41595 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011388 | OH | Sus | 43635519 | yes | 2019 | JAN | Yes | Line to Ground | 1407933 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011945&numberofmonths=24&showchangehistorylog=1 | 19-0011945 | SIERRA | FIELD OPS NORTH | Tier 3 | PIKE CITY-1101 | 152201101 | FUSE | 5503 | 20190117 | 804 | 276146 | 2005 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 6015 | 39.44 | -121.0755 | 1NOF5503 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011945 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1408278 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010912&numberofmonths=24&showchangehistorylog=1 | 19-0010912 | SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 4105 | 20190117 | 950 | 273445 | 1504 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 16544 | 38.9137 | -120.6793 | TurneyRobert5302056563SAP1000392941spanwoBlodgettForestRd | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010912 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1407603 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011302&numberofmonths=24&showchangehistorylog=1 | 19-0011302 | SIERRA | FIELD OPS NORTH | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 20865 | 20190117 | 622 | 272650 | 1908 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 9540 | 38.8279 | -120.9415 | 1SPANNWO20865 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011302 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407863 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010870&numberofmonths=24&showchangehistorylog=1 | 19-0010870 | SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2110 | 153652110 | FUSE | 21033 | 20190117 | 432 | 272492 | 793 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 25376 | 38.6412 | -120.9109 | 4800TROTTER | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 19-0010870 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407577 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010857&numberofmonths=24&showchangehistorylog=1 | 19-0010857 | SIERRA | FIELD OPS NORTH | Tier 2 | WEIMAR-1102 | 152491102 | FUSE | 6263 | 20190117 | 651 | 272716 | 459 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2295 | 39.0393 | -121.0009 | 20499PLACERHILLS | Partly Cloudy-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010857 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1407569 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010881&numberofmonths=24&showchangehistorylog=1 | 19-0010881 | SIERRA | FIELD OPS NORTH | Tier 2 | WISE-1102 | 152271102 | FUSE | 30657 | 20190117 | 50 | 272208 | 863 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 14671 | 38.899 | -121.095 | FATORTRAVIS530217796110765VoyiatzesrdAuburn | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010881 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1407588 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018389&numberofmonths=24&showchangehistorylog=1 | 19-0018389 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-1103 | 153661103 | FUSE | 6413 | 20190204 | 2314 | 291191 | 6336 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 272706 | 38.71 | -120.7151 | 3220HUMEGLENNDR | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0018389 | OH | Sus | 31424310 | yes | 2019 | FEB | Yes | Line to Ground | 1412588 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018728&numberofmonths=24&showchangehistorylog=1 | 19-0018728 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE | 22085 | 20190204 | 2120 | 291112 | 2701 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 216439 | 38.7408 | -120.6534 | 3801MEYERSLN2SPNOMTR1009714036 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0018728 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1412793 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018147&numberofmonths=24&showchangehistorylog=1 | 19-0018147 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | OCB | 21022 | 20190204 | 2005 | 290949 | 5496 | Distribution Circuit | Vegetation | Tree - fell into line | 3456 | 14931003 | 38.7394 | -120.6774 | MULTIPLELOCATIONS | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0018147 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Multi-Fault | 1412391 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018188&numberofmonths=24&showchangehistorylog=1 | 19-0018188 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 13247 | 20190204 | 2005 | 291125 | 4244 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 72148 | 38.6982 | -120.6704 | LDSIDEOF13247 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018188 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1412430 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018747&numberofmonths=24&showchangehistorylog=1 | 19-0018747 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 1333 | 20190204 | 2005 | 293649 | 4002 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 100050 | 38.6747 | -120.7232 | 2781SPRINGER | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018747 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1412813 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018781&numberofmonths=24&showchangehistorylog=1 | 19-0018781 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 2133 | 20190204 | 2005 | 293740 | 4016 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 124496 | 38.685 | -120.6662 | FUCO18247WIREDOWN2SPANSLDSIDEOF18247 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0018781 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1412846 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019027&numberofmonths=24&showchangehistorylog=1 | 19-0019027 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 13243 | 20190204 | 2005 | 294010 | 3966 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 106890 | 38.7017 | -120.6689 | 3085PLEASANTGROVERD | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0019027 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1413069 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019176&numberofmonths=24&showchangehistorylog=1 | 19-0019176 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 24137 | 20190204 | 2005 | 294332 | 6834 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 20502 | 38.6779 | -120.6634 | LDSIDEOF24137 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0019176 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1413176 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019177&numberofmonths=24&showchangehistorylog=1 | 19-0019177 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | JUMPER | OJ1SPANNWOCGC5185 | 20190204 | 2005 | 294337 | 6798 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 115566 | 38.6262 | -120.7371 | CGC223611335185 | Overcast-Fog-Snow-32-90 F | Pole-Wood | Broken, wire on ground | 19-0019177 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1413178 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019193&numberofmonths=24&showchangehistorylog=1 | 19-0019193 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 11491 | 20190204 | 2005 | 294365 | 5363 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 316417 | 38.6359 | -120.7207 | 4201SANDRIDGERD | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0019193 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1413183 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019309&numberofmonths=24&showchangehistorylog=1 | 19-0019309 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 12187 | 20190204 | 2005 | 294581 | 8451 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 267929 | 38.7074 | -120.6802 | WIREDOWNMTR10088857602952FORTJIMCT5035NEWTOWNRDBROKENXARM5046NEWTOWNRD | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0019309 | OH | Sus | 31424310 | yes | 2019 | FEB | Yes | Line to Line | 1413248 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019331&numberofmonths=24&showchangehistorylog=1 | 19-0019331 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 12691 | 20190204 | 2005 | 294665 | 5579 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 89264 | 38.626 | -120.7374 | 2PSO3780SANDRIDGERD | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0019331 | OH | Sus | 0 | yes | 2019 | FEB | Yes | None | 1413266 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019340&numberofmonths=24&showchangehistorylog=1 | 19-0019340 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | JUMPER | OJ1SPANEOCGC5160 | 20190204 | 2005 | 294691 | 5365 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 10730 | 38.625 | -120.7376 | HALFSPANEOCGC5160 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0019340 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1413274 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019438&numberofmonths=24&showchangehistorylog=1 | 19-0019438 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 11793 | 20190204 | 2005 | 294948 | 4911 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 39288 | 38.6226 | -120.76 | 3100DAWNROSE | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0019438 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1413372 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019444&numberofmonths=24&showchangehistorylog=1 | 19-0019444 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 10597 | 20190204 | 2005 | 294961 | 5382 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 113022 | 38.6003 | -120.6565 | 1PNO10597 | Clear-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0019444 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1413378 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019448&numberofmonths=24&showchangehistorylog=1 | 19-0019448 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 21415 | 20190204 | 1805 | 291035 | 10056 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 181008 | 38.7131 | -120.6321 | KRZYMINSKIWOODYco21415toeol | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0019448 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1413382 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019500&numberofmonths=24&showchangehistorylog=1 | 19-0019500 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 21407 | 20190204 | 2005 | 295068 | 9972 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 129636 | 38.7116 | -120.6264 | 21407 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0019500 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1413400 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019538&numberofmonths=24&showchangehistorylog=1 | 19-0019538 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 10225 | 20190204 | 2005 | 295030 | 7080 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 182939 | 38.6712 | -120.6685 | 6233SILVERRIDGELN | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0019538 | OH | Sus | 31424310 | yes | 2019 | FEB | Yes | Line to Line | 1413438 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019731&numberofmonths=24&showchangehistorylog=1 | 19-0019731 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 21403 | 20190204 | 2005 | 295530 | 9917 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 29751 | 38.7068 | -120.6269 | 12SPANLDSIDEOF21403 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0019731 | OH | Sus | 31424310 | yes | 2019 | FEB | Yes | Open Circuit | 1413533 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021148&numberofmonths=24&showchangehistorylog=1 | 19-0021148 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 21393 | 20190204 | 2005 | 300051 | 10365 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 93285 | 38.6947 | -120.639 | MULTIPLE | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0021148 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Multi-Fault | 1414762 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0017821&numberofmonths=24&showchangehistorylog=1 | 19-0017821 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1105 | 152481105 | OTHER | WIREDOWN1EO38643 | 20190204 | 801 | 289699 | 464 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 4440 | 39.2625 | -120.9392 | 1EO38643 | Overcast-Fog-Heavy Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0017821 | OH | Sus | 31424257 | yes | 2019 | FEB | Yes | Open Circuit | 1412182 | CAW | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0017722&numberofmonths=24&showchangehistorylog=1 | 19-0017722 | SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 1299 | 20190204 | 457 | 289476 | 533 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 36777 | 38.6932 | -120.766 | 1845QUARRYRDPLACERVILLE | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017722 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1412132 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0017832&numberofmonths=24&showchangehistorylog=1 | 19-0017832 | SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 18797 | 20190204 | 835 | 289722 | 650 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 21450 | 38.665 | -120.749 | 2400NOWALKDR2600RANCHRD | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017832 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1412189 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018008&numberofmonths=24&showchangehistorylog=1 | 19-0018008 | SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 13097 | 20190204 | 1225 | 290256 | 1340 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 21081 | 38.6922 | -120.7931 | 986DOWNINGLN | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0018008 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1412295 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019079&numberofmonths=24&showchangehistorylog=1 | 19-0019079 | SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 21933 | 20190204 | 2313 | 294151 | 2557 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 25570 | 38.6828 | -120.7546 | 5280HIDDENHOLLOWDR | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0019079 | OH | Sus | 0 | yes | 2019 | FEB | Yes | None | 1413123 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018081&numberofmonths=24&showchangehistorylog=1 | 19-0018081 | SIERRA | FIELD OPS NORTH | Tier 2 | EL DORADO PH-2101 | 152762101 | RECLOSER | 507864 | 20190204 | 1607 | 290684 | 7371 | Distribution Circuit | Environmental/External | Ice or snow | 1487 | 6904706 | 38.7731 | -120.2934 | FLECKLINPAUL6235309063142CAMPSACRAMENTOMULTIPLE | Overcast-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018081 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Three Phase Fault | 1412332 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018240&numberofmonths=24&showchangehistorylog=1 | 19-0018240 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | OTHER | WIREDOWN1SOMTR1005208316 | 20190204 | 2205 | 291576 | 4030 | Distribution Circuit | Vegetation | Tree - fell into line | 66 | 247513 | 38.6862 | -120.6072 | 1SPANSOCGC223979137457 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0018240 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1412478 | PW | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018681&numberofmonths=24&showchangehistorylog=1 | 19-0018681 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 12645 | 20190204 | 1608 | 291138 | 2943 | Distribution Circuit | Vegetation | Tree - fell into line | 88 | 258984 | 38.7126 | -120.6007 | MULTIPLEALONGSIERRASPRINGSDR | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018681 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1412762 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019229&numberofmonths=24&showchangehistorylog=1 | 19-0019229 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 13251 | 20190204 | 2337 | 291206 | 3352 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 97208 | 38.6883 | -120.6256 | 1546CLEARCREEKCT | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0019229 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1413200 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0017836&numberofmonths=24&showchangehistorylog=1 | 19-0017836 | SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1102 | 152241102 | FUSE | 311367 | 20190204 | 755 | 289665 | 312 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 2216 | 38.9627 | -121.0105 | 1SPANSSOFCGC22821247313 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017836 | OH | Sus | 31424320 | yes | 2019 | FEB | Yes | Line to Ground | 1412194 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018225&numberofmonths=24&showchangehistorylog=1 | 19-0018225 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-1103 | 153661103 | OTHER | WIREDOWN1SPANLDSIDEOFCGC22367243816 | 20190205 | 15 | 291233 | 806 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2418 | 38.7077 | -120.7146 | WIREDOWN1SPANLDSIDEOFCGC223672438165 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018225 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1412465 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018446&numberofmonths=24&showchangehistorylog=1 | 19-0018446 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-1103 | 153661103 | JUMPER | OJS1PWO11445ONTAP | 20190205 | 600 | 292502 | 2040 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 4080 | 38.7047 | -120.7084 | 1PNWO11445 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018446 | OH | Sus | 31424310 | yes | 2019 | FEB | Yes | Line to Ground | 1412631 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018585&numberofmonths=24&showchangehistorylog=1 | 19-0018585 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-1103 | 153661103 | FUSE | 18469 | 20190205 | 1347 | 292792 | 2938 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 5876 | 38.7208 | -120.7197 | 4167HALFMOON | Overcast-Fog-Snow-32-90 F | Pole-Wood | Broken, wire on ground | 19-0018585 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1412701 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018656&numberofmonths=24&showchangehistorylog=1 | 19-0018656 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-1103 | 153661103 | FUSE | 12097 | 20190205 | 1237 | 292672 | 399 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 26 | 10374 | 38.7304 | -120.7157 |  | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0018656 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1412741 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018706&numberofmonths=24&showchangehistorylog=1 | 19-0018706 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-1103 | 153661103 | FUSE | 41067 | 20190205 | 1400 | 292936 | 1485 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 5430 | 38.7366 | -120.7354 | SPANTOTHESOUTHOFCORNERPOLE6SPANSLDSIDEOF41067 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0018706 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1412775 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018707&numberofmonths=24&showchangehistorylog=1 | 19-0018707 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-1103 | 153661103 | FUSE | 6387 | 20190205 | 1348 | 293048 | 4467 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 56457 | 38.737 | -120.7268 | 2800HWY50 | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 19-0018707 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1412776 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018750&numberofmonths=24&showchangehistorylog=1 | 19-0018750 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-1103 | 153661103 | FUSE | 1427 | 20190205 | 1351 | 293066 | 2769 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 11076 | 38.739 | -120.7497 | 1SPANLDSIDEOF1427 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018750 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1412817 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019096&numberofmonths=24&showchangehistorylog=1 | 19-0019096 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-1103 | 153661103 | FUSE | 18475 | 20190205 | 1415 | 294177 | 3233 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 64660 | 38.7131 | -120.7126 | AT18475ANDSS18477 | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 19-0019096 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1413132 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019102&numberofmonths=24&showchangehistorylog=1 | 19-0019102 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-1103 | 153661103 | FUSE | 18473 | 20190205 | 328 | 291689 | 3699 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 77679 | 38.7141 | -120.7124 | 1SPANLDSIDEOF18473 | Overcast-Fog-Snow-Below 32 F | Crossarm, Wood | Broken, wire on ground | 19-0019102 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1413136 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019175&numberofmonths=24&showchangehistorylog=1 | 19-0019175 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-1103 | 153661103 | OTHER | HOTWIREDOWN7SO6633 | 20190205 | 1412 | 294330 | 2965 | Distribution Circuit | Vegetation | Tree - fell into line | 64 | 125536 | 38.7693 | -120.7512 | 7POLESSO6633 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 19-0019175 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1413175 | PW | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019209&numberofmonths=24&showchangehistorylog=1 | 19-0019209 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-1103 | 153661103 | FUSE | 1467 | 20190205 | 1348 | 292795 | 1602 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 86508 | 38.7046 | -120.7072 | LD1467FORTJIMRDALCARD | Overcast-Fog-Snow-Below 32 F | Crossarm, Wood | Broken, wire on object | 19-0019209 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1413192 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019791&numberofmonths=24&showchangehistorylog=1 | 19-0019791 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-1103 | 153661103 | FUSE | 18477 | 20190205 | 1359 | 295750 | 4321 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 25926 | 38.7129 | -120.7116 | LOADSIDEOFFUCO18477 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0019791 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1413577 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018316&numberofmonths=24&showchangehistorylog=1 | 19-0018316 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-1104 | 153661104 | RECLOSER | 12832 | 20190205 | 808 | 291613 | 5953 | Distribution Circuit | Vegetation | Tree - fell into line | 423 | 1188276 | 38.7523 | -120.682 | HYLANDTRAVIS53029570763765chutecamprd | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018316 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1412533 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018506&numberofmonths=24&showchangehistorylog=1 | 19-0018506 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-1104 | 153661104 | FUSE | 1313 | 20190205 | 142 | 292643 | 2622 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 65550 | 38.7588 | -120.7204 | 2PWO18535 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0018506 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1412666 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018699&numberofmonths=24&showchangehistorylog=1 | 19-0018699 | SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1103 | 152261103 | FUSE | 94593 | 20190205 | 523 | 291644 | 2182 | Distribution Circuit | Vegetation | Tree - bark fell into line | 11 | 24002 | 38.7267 | -120.8459 | 2920TELEMARKCT | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018699 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1412770 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018273&numberofmonths=24&showchangehistorylog=1 | 19-0018273 | SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | RECLOSER | 2100 | 20190205 | 632 | 291764 | 1868 | Distribution Circuit | Environmental/External | Ice or snow | 633 | 801734 | 38.6935 | -120.7678 | MAINLINEFU411854729OAKHILL4730OAKHILL4941DOWELLLNFUCO20429 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018273 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1412510 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018726&numberofmonths=24&showchangehistorylog=1 | 19-0018726 | SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 2167 | 20190205 | 632 | 293117 | 3605 | Distribution Circuit | Vegetation | Tree - fell into line | 122 | 439810 | 38.67 | -120.7776 | AT20429 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018726 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1412790 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018799&numberofmonths=24&showchangehistorylog=1 | 19-0018799 | SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 20351 | 20190205 | 2259 | 293786 | 1006 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 8048 | 38.6791 | -120.7724 | MTR5000001446 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0018799 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1412865 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018886&numberofmonths=24&showchangehistorylog=1 | 19-0018886 | SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 11321 | 20190205 | 1358 | 292986 | 2976 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 32736 | 38.706 | -120.7628 | FULTONERIC2pwo2020CampNauvooRdPlacerville | Overcast-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0018886 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1412952 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019070&numberofmonths=24&showchangehistorylog=1 | 19-0019070 | SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 1161 | 20190205 | 119 | 294139 | 5082 | Distribution Circuit | Vegetation | Tree - fell into line | 137 | 696234 | 38.6755 | -120.7512 | MELLOADAM5304015814T5429manytrbllocWIREDOWN4LDSD1161 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0019070 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1413117 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019265&numberofmonths=24&showchangehistorylog=1 | 19-0019265 | SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 18797 | 20190205 | 119 | 294496 | 5082 | Distribution Circuit | Vegetation | Tree - branch fell on line | 33 | 167706 | 38.665 | -120.749 | MELLOADAM5304015814T54297loadof18797atmtr1007391579 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0019265 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1413224 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018257&numberofmonths=24&showchangehistorylog=1 | 19-0018257 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | RECLOSER | 26000 | 20190205 | 507 | 291626 | 6324 | Distribution Circuit | Environmental/External | Ice or snow | 655 | 3029661 | 38.7525 | -120.5549 | FLECKLINPAUL6235309063142HELICOPTERPATROLHASINFO | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018257 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1412496 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018370&numberofmonths=24&showchangehistorylog=1 | 19-0018370 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | RECLOSER | 6852 | 20190205 | 916 | 291952 | 2773 | Distribution Circuit | Vegetation | Tree - fell into line | 1442 | 1454949 | 38.7612 | -120.5582 | JESSEEBEN6209168268237MULTIPLELOCATIONS | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018370 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1412571 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018302&numberofmonths=24&showchangehistorylog=1 | 19-0018302 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2102 | 152762102 | OCB | 21022 | 20190205 | 731 | 291874 | 681 | Distribution Circuit | Vegetation | Tree - fell into line | 1649 | 512931 | 38.7934 | -120.6201 | GOLDRIDGERDONIXTRAIL | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018302 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1412526 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018387&numberofmonths=24&showchangehistorylog=1 | 19-0018387 | SIERRA | FIELD OPS NORTH | Tier 2 | PLACERVILLE-1111 | 153081111 | SWITCH | 52599 | 20190205 | 611 | 292222 | 899 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 45849 | 38.721 | -120.8019 | 3421BIGCUT | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018387 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1412586 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018473&numberofmonths=24&showchangehistorylog=1 | 19-0018473 | SIERRA | FIELD OPS NORTH | Tier 2 | PLACERVILLE-2106 | 153082106 | OTHER | WIREDOWNSOURCESIDEOF5833 | 20190205 | 855 | 292101 | 340 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2360 | 89237 | 38.8557 | -120.8433 | SSOF5833 | Overcast-Fog-Snow-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0018473 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1412647 | CSO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018646&numberofmonths=24&showchangehistorylog=1 | 19-0018646 | SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 12613 | 20190205 | 620 | 291730 | 1932 | Distribution Circuit | Vegetation | Tree - fell into line | 102 | 197064 | 38.7943 | -120.7332 | LDSIDEOF12613 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0018646 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1412737 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020403&numberofmonths=24&showchangehistorylog=1 | 19-0020403 | SIERRA | FIELD OPS NORTH | Tier 3 | ALLEGHANY-1102 | 152101102 | RECLOSER | 11022 | 20190209 | 1928 | 297365 | 5097 | Distribution Circuit | Vegetation | Tree - fell into line | 164 | 283891 | 39.4655 | -120.8443 | FLOATER10SPANSSO82927PSEOFSW824159TREEONWIRE15PSEOF1733MAINLINESOURCESIDEOFFUCO8003WIREDOWN | Overcast-Fog-Snow-Strong Winds-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020403 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1414079 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020394&numberofmonths=24&showchangehistorylog=1 | 19-0020394 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-1103 | 153661103 | OCB | 11032 | 20190209 | 1826 | 297302 | 2624 | Distribution Circuit | Vegetation | Tree - fell into line | 1824 | 194084 | 38.7393 | -120.6773 | SOURCESIDELOADSIDEOFFUCO18475 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020394 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Three Phase Fault | 1414071 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020476&numberofmonths=24&showchangehistorylog=1 | 19-0020476 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE | 18559 | 20190209 | 2144 | 297460 | 2327 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 41886 | 38.7535 | -120.6191 | 1SPSOCOUT18559 | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020476 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1414153 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020473&numberofmonths=24&showchangehistorylog=1 | 19-0020473 | SIERRA | FIELD OPS NORTH | Tier 3 | BONNIE NOOK-1101 | 152301101 | FUSE | 6377 | 20190209 | 2057 | 297424 | 1285 | Distribution Circuit | Vegetation | Tree - fell into line | 115 | 147775 | 39.2018 | -120.8362 | 2SPANSLOADSIDEOFFUCO6377 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020473 | OH | Sus | 31424320 | yes | 2019 | FEB | Yes | Three Phase Fault | 1414149 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020420&numberofmonths=24&showchangehistorylog=1 | 19-0020420 | SIERRA | FIELD OPS NORTH | Tier 3 | BONNIE NOOK-1102 | 152301102 | FUSE | 30711 | 20190209 | 2057 | 297419 | 2787 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 256404 | 39.2145 | -120.8088 | 1EO4181 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0020420 | OH | Sus | 31424320 | yes | 2019 | FEB | Yes | Line to Line | 1414096 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020807&numberofmonths=24&showchangehistorylog=1 | 19-0020807 | SIERRA | FIELD OPS NORTH | Tier 3 | BONNIE NOOK-1102 | 152301102 | FUSE | 5749 | 20190209 | 1830 | 299268 | 2657 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 5314 | 39.2167 | -120.7946 | TurneyRobert53020565633spansLSfuses5749 | Overcast-Fog-Snow-Below 32 F | Crossarm, Wood | Broken, wire on object | 19-0020807 | OH | Sus | 31424320 | yes | 2019 | FEB | Yes | Line to Ground | 1414507 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020434&numberofmonths=24&showchangehistorylog=1 | 19-0020434 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1106 | 152481106 | RECLOSER | 51486 | 20190209 | 2110 | 297435 | 959 | Distribution Circuit | Vegetation | Tree - fell into line | 1059 | 394653 | 39.1909 | -120.9967 | 2SPANSLOADSIDEOF2794 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020434 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Three Phase Fault | 1414110 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020544&numberofmonths=24&showchangehistorylog=1 | 19-0020544 | SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1103 | 152261103 | FUSE | 18619 | 20190209 | 2224 | 297491 | 1258 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 11322 | 38.7336 | -120.8452 | 2376LOARAJOHNWAY | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0020544 | OH | Sus | 43666953 | yes | 2019 | FEB | Yes | Line to Line | 1414222 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020560&numberofmonths=24&showchangehistorylog=1 | 19-0020560 | SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1107 | 152261107 | FUSE | 41463 | 20190209 | 2308 | 297566 | 966 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 42504 | 38.7171 | -120.825 | 1SPLDSIDEOF41463 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020560 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1414239 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020669&numberofmonths=24&showchangehistorylog=1 | 19-0020669 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 11791 | 20190209 | 2339 | 297587 | 2326 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 27912 | 38.7727 | -120.59 | 2078BLAIRRDPOLLOCKPINES | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020669 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1414368 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022378&numberofmonths=24&showchangehistorylog=1 | 19-0022378 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 20869 | 20190209 | 1522 | 305017 | 7228 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 36140 | 38.7605 | -120.5091 | NO20869 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0022378 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1415658 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022473&numberofmonths=24&showchangehistorylog=1 | 19-0022473 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 1385 | 20190209 | 1522 | 305286 | 7344 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 22032 | 38.7642 | -120.5488 | 1SPLDSIDEOF1385 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0022473 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1415727 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020499&numberofmonths=24&showchangehistorylog=1 | 19-0020499 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2102 | 152762102 | OCB | 21022 | 20190209 | 2249 | 297461 | 4141 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1097 | 3128800 | 38.7934 | -120.6201 | MIDWAYBETELDORADOPHSW6163 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020499 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1414173 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020748&numberofmonths=24&showchangehistorylog=1 | 19-0020748 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE | 18501 | 20190209 | 2148 | 299064 | 2740 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 87680 | 38.7533 | -120.5757 | 2POLESNWO18421 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020748 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1414452 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020958&numberofmonths=24&showchangehistorylog=1 | 19-0020958 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE | 18407 | 20190209 | 2115 | 299702 | 4235 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 38115 | 38.7679 | -120.5917 |  | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020958 | OH | Sus | 0 | yes | 2019 | FEB | Yes | None | 1414653 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021032&numberofmonths=24&showchangehistorylog=1 | 19-0021032 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE | 18401 | 20190209 | 2115 | 299860 | 4235 | Distribution Circuit | Vegetation | Tree - branch fell on line | 38 | 160930 | 38.7676 | -120.596 | 4LDSIDE | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021032 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1414705 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020450&numberofmonths=24&showchangehistorylog=1 | 19-0020450 | SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1101 | 152241101 | TRIP-SAVER | 5731 | 20190209 | 2040 | 297407 | 1050 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 97650 | 38.9857 | -121.0221 | 1175GRANGEROADMEADOWVISTA | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020450 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Three Phase Fault | 1414126 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020529&numberofmonths=24&showchangehistorylog=1 | 19-0020529 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-1103 | 153661103 | OTHER | WIREDOWN1WO223655138715 | 20190210 | 16 | 297828 | 2274 | Distribution Circuit | Vegetation | Tree - fell into line | 233 | 395822 | 38.7223 | -120.7208 | 1SPWOCGC223655138715 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020529 | OH | Sus | 43666953 | yes | 2019 | FEB | Yes | Open Circuit | 1414204 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020600&numberofmonths=24&showchangehistorylog=1 | 19-0020600 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-1104 | 153661104 | RECLOSER | 13512 | 20190210 | 804 | 297872 | 2154 | Distribution Circuit | Vegetation | Tree - fell into line | 640 | 326964 | 38.739 | -120.6678 | KNIFFINANDREW7075484583MULTIPLELOCATIONS | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020600 | OH | Sus | 31424310 | yes | 2019 | FEB | Yes | Multi-Fault | 1414289 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020799&numberofmonths=24&showchangehistorylog=1 | 19-0020799 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE | 18553 | 20190210 | 117 | 297773 | 3478 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 76516 | 38.7529 | -120.6145 | HESTEADNICKENDOFSHADOWLANE | Overcast-Fog-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0020799 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1414499 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020831&numberofmonths=24&showchangehistorylog=1 | 19-0020831 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE | 3369 | 20190210 | 352 | 298337 | 3548 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 24836 | 38.7521 | -120.6284 | LDSIDEOF3369 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020831 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1414530 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020834&numberofmonths=24&showchangehistorylog=1 | 19-0020834 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE | 7963 | 20190210 | 352 | 299366 | 3525 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 52875 | 38.7531 | -120.613 | 3NO7963 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020834 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1414535 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021142&numberofmonths=24&showchangehistorylog=1 | 19-0021142 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE | 7965 | 20190210 | 352 | 299195 | 3563 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 99764 | 38.7532 | -120.6117 | EACHSIDEOF12573COUT | Overcast-Fog-Snow-Below 32 F | Crossarm, Wood | Broken, wire on ground | 19-0021142 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1414760 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020572&numberofmonths=24&showchangehistorylog=1 | 19-0020572 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | RECLOSER | 186912 | 20190210 | 657 | 298148 | 615 | Distribution Circuit | Vegetation | Tree - fell into line | 1215 | 81335 | 38.641 | -120.7043 | SSOF80645 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020572 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1414254 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020887&numberofmonths=24&showchangehistorylog=1 | 19-0020887 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 21505 | 20190210 | 1446 | 299068 | 1461 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 100809 | 38.6392 | -120.5101 | 5043DEERWOODDRGRIZZLEYFLATS | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020887 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1414592 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021011&numberofmonths=24&showchangehistorylog=1 | 19-0021011 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 10987 | 20190210 | 1626 | 299177 | 2548 | Distribution Circuit | Vegetation | Tree - branch fell on line | 103 | 128114 | 38.7439 | -120.5658 | CGC224104839481 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0021011 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1414692 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021026&numberofmonths=24&showchangehistorylog=1 | 19-0021026 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 6123 | 20190210 | 1152 | 298880 | 3245 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 113575 | 38.6337 | -120.5369 | ATMET1009126223 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0021026 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1414703 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020521&numberofmonths=24&showchangehistorylog=1 | 19-0020521 | SIERRA | FIELD OPS NORTH | Tier 3 | BONNIE NOOK-1101 | 152301101 | RECLOSER | 11012 | 20190210 | 224 | 297571 | 946 | Distribution Circuit | Equipment Failure/Involved | Overhead | 399 | 273390 | 39.214 | -120.8098 | RENFREESAMlco6375and6377dutchflat | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0020521 | OH | Sus | 31424320 | yes | 2019 | FEB | Yes | Line to Ground | 1414196 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020643&numberofmonths=24&showchangehistorylog=1 | 19-0020643 | SIERRA | FIELD OPS NORTH | Tier 3 | BONNIE NOOK-1102 | 152301102 | OTHER | WIREDOWN1SPNO44675 | 20190210 | 343 | 297900 | 526 | Distribution Circuit | Vegetation | Tree - fell into line | 139 | 72376 | 39.2132 | -120.8093 | CramerChris1spanNO44675mainline | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020643 | OH | Sus | 31424320 | yes | 2019 | FEB | Yes | Line to Ground | 1414340 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020703&numberofmonths=24&showchangehistorylog=1 | 19-0020703 | SIERRA | FIELD OPS NORTH | Tier 3 | BONNIE NOOK-1102 | 152301102 | SWITCH | 6433 | 20190210 | 1238 | 298919 | 194 | Distribution Circuit | Environmental/External | Ice or snow | 127 | 24638 | 39.2054 | -120.8187 | 1SPANLDSIDE | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020703 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1414407 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020821&numberofmonths=24&showchangehistorylog=1 | 19-0020821 | SIERRA | FIELD OPS NORTH | Tier 3 | BONNIE NOOK-1102 | 152301102 | FUSE | 130441 | 20190210 | 1855 | 299288 | 1275 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 4979 | 39.2056 | -120.7994 | CramerChris1spanloadsideof130441 | Partly Cloudy-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020821 | OH | Sus | 31424320 | yes | 2019 | FEB | Yes | Line to Ground | 1414523 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020501&numberofmonths=24&showchangehistorylog=1 | 19-0020501 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | RECLOSER | 26000 | 20190210 | 114 | 297664 | 3680 | Distribution Circuit | Vegetation | Tree - fell into line | 655 | 99252 | 38.7525 | -120.5549 | 1SO1271WIREDOWN2SO20821 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020501 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1414175 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020598&numberofmonths=24&showchangehistorylog=1 | 19-0020598 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 6795 | 20190210 | 333 | 298342 | 2233 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 44660 | 38.7623 | -120.5744 | JESSEEBEN62091682682376588CENTERVIEWDR | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020598 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1414287 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020667&numberofmonths=24&showchangehistorylog=1 | 19-0020667 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 4741 | 20190210 | 125 | 298784 | 6625 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 72875 | 38.7613 | -120.5351 | EOL | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020667 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1414366 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020690&numberofmonths=24&showchangehistorylog=1 | 19-0020690 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 22391 | 20190210 | 333 | 298897 | 922 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 7376 | 38.7741 | -120.5923 | 3WO22391 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020690 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1414394 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020745&numberofmonths=24&showchangehistorylog=1 | 19-0020745 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 1273 | 20190210 | 213 | 299062 | 2059 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 12354 | 38.7197 | -120.5744 | 6EO1273 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020745 | OH | Sus | 0 | yes | 2019 | FEB | Yes | None | 1414450 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020496&numberofmonths=24&showchangehistorylog=1 | 19-0020496 | SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | RECLOSER | 1104 | 20190210 | 107 | 297594 | 2487 | Distribution Circuit | Vegetation | Tree - fell into line | 658 | 491996 | 38.9124 | -120.8201 | 2SWOF1131 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020496 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1414170 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020496&numberofmonths=24&showchangehistorylog=1 | 19-0020496 | SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | RECLOSER | 1104 | 20190210 | 428 | 297836 | 2276 | Distribution Circuit | Vegetation | Tree - fell into line | 479 | 389929 | 38.9124 | -120.8201 | FATORTRAVIS53021779619145WentworthSpringsRdGeorgetown | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020496 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1414212 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021897&numberofmonths=24&showchangehistorylog=1 | 19-0021897 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-1104 | 153661104 | FUSE | 20849 | 20190212 | 2325 | 301511 | 4050 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 48600 | 38.7514 | -120.6921 | MTR1007478099 | Overcast-Drizzle-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0021897 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1415337 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021637&numberofmonths=24&showchangehistorylog=1 | 19-0021637 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | OTHER | WIREDOWNNO80645 | 20190212 | 2154 | 301255 | 952 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1711 | 148676 | 38.605 | -120.7212 | 80645OVERPOND | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021637 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1415083 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021874&numberofmonths=24&showchangehistorylog=1 | 19-0021874 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 2661 | 20190212 | 2239 | 301383 | 1071 | Distribution Circuit | Vegetation | Tree - fell into line | 94 | 100674 | 38.6853 | -120.669 | 3940LEISURELN | Overcast-Drizzle-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0021874 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1415318 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021345&numberofmonths=24&showchangehistorylog=1 | 19-0021345 | SIERRA | FIELD OPS NORTH | Tier 3 | BONNIE NOOK-1102 | 152301102 | FUSE | 6411 | 20190212 | 758 | 300407 | 518 | Distribution Circuit | Vegetation | Tree - fell into line | 96 | 23752 | 39.2099 | -120.8013 | 2EASTOF6451FUCO6451 | Partly Cloudy-Below 32 F | Crossarm, Wood | Broken, wire on ground | 19-0021345 | OH | Sus | 31424320 | yes | 2019 | FEB | Yes | Line to Ground | 1414902 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021859&numberofmonths=24&showchangehistorylog=1 | 19-0021859 | SIERRA | FIELD OPS NORTH | Tier 3 | BONNIE NOOK-1102 | 152301102 | FUSE | 6407 | 20190212 | 2147 | 301343 | 922 | Distribution Circuit | Vegetation | Tree - fell into line | 133 | 117015 | 39.2088 | -120.8166 | MOODYRIDGERD1SPPASTAQUILALN | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021859 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1415307 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021653&numberofmonths=24&showchangehistorylog=1 | 19-0021653 | SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1104 | 152691104 | RECLOSER | 1006 | 20190212 | 2248 | 301407 | 735 | Distribution Circuit | Vegetation | Tree - fell into line | 1517 | 170849 | 39.0996 | -121.05 | 16521NORLENEWAY | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021653 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Multi-Fault | 1415100 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022266&numberofmonths=24&showchangehistorylog=1 | 19-0022266 | SIERRA | FIELD OPS NORTH | Tier 2 | PENRYN-1105 | 152561105 | FUSE | 5893 | 20190212 | 2258 | 301454 | 1023 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 11882 | 38.8973 | -121.1804 | 460GOLDHILLRD | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022266 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1415583 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021425&numberofmonths=24&showchangehistorylog=1 | 19-0021425 | SIERRA | FIELD OPS NORTH | Tier 3 | PIKE CITY-1102 | 152201102 | OTHER | WIREDOWN8SPANSSSOF8801 | 20190212 | 1213 | 300654 | 1712 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 46224 | 39.485 | -120.9937 | 8SPANSSSOF8801 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021425 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1414945 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021943&numberofmonths=24&showchangehistorylog=1 | 19-0021943 | SIERRA | FIELD OPS NORTH | Tier 3 | ALLEGHANY-1101 | 152101101 | RECLOSER | 808 | 20190213 | 854 | 303404 | 2913 | Distribution Circuit | Vegetation | Tree - fell into line | 387 | 414101 | 39.4879 | -120.8571 | SHADEBRIAN8pswolco32467 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021943 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1415376 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022505&numberofmonths=24&showchangehistorylog=1 | 19-0022505 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 10023 | 20190213 | 304 | 302351 | 989 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 3956 | 38.5469 | -120.6925 | 3LDSIDEOF10023 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022505 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1415747 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021637&numberofmonths=24&showchangehistorylog=1 | 19-0021637 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | OTHER | WIREDOWN2LDSIDE10463 | 20190213 | 1526 | 305256 | 140 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 3982 | 38.6131 | -120.7262 | 2POLESLDSIDEOF10463 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021637 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1415764 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022175&numberofmonths=24&showchangehistorylog=1 | 19-0022175 | SIERRA | FIELD OPS NORTH | Tier 2 | CLARKSVILLE-2103 | 153612103 | FUSE | 10979 | 20190213 | 848 | 303310 | 1727 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 6908 | 38.5972 | -121.0191 | 5SPANSSWOF10979 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022175 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1415521 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022544&numberofmonths=24&showchangehistorylog=1 | 19-0022544 | SIERRA | FIELD OPS NORTH | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 9313 | 20190213 | 1713 | 305363 | 1050 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 5250 | 38.8295 | -121.0466 | 3SPANSLDSIDE | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022544 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1415783 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021817&numberofmonths=24&showchangehistorylog=1 | 19-0021817 | SIERRA | FIELD OPS NORTH | Tier 2 | PLACERVILLE-2106 | 153082106 | FUSE | 32419 | 20190213 | 337 | 302511 | 648 | Distribution Circuit | Vegetation | Tree - fell into line | 928 | 68664 | 38.8686 | -120.8538 | LDSIDEOF32419 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021817 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1415267 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022910&numberofmonths=24&showchangehistorylog=1 | 19-0022910 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | RECLOSER | 8372 | 20190214 | 810 | 307642 | 494 | Distribution Circuit | Vegetation | Tree - fell into line | 712 | 136054 | 38.6092 | -120.7025 | BennettJeffrey7331PerryCreekRdMTR1007391920 | Overcast-Drizzle-32-90 F | Capacitor | Broken, wire on ground | 19-0022910 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Three Phase Fault | 1416144 | ECA | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023109&numberofmonths=24&showchangehistorylog=1 | 19-0023109 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 7959 | 20190214 | 819 | 307726 | 568 | Distribution Circuit | Vegetation | Tree - fell into line | 194 | 38182 | 38.6431 | -120.5261 | 6900TYLERRD | Overcast-Fog-Heavy Rain-Lightning-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023109 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1416305 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023669&numberofmonths=24&showchangehistorylog=1 | 19-0023669 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 21485 | 20190214 | 2000 | 310790 | 1162 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 4648 | 38.5824 | -120.5777 | MTR1009125447 | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0023669 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Multi-Fault | 1416820 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023299&numberofmonths=24&showchangehistorylog=1 | 19-0023299 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1102 | 152481102 | FUSE | 9063 | 20190214 | 820 | 307717 | 2161 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 30254 | 39.2184 | -120.9646 | 4PNO9063 | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023299 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416485 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022925&numberofmonths=24&showchangehistorylog=1 | 19-0022925 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1103 | 152481103 | RECLOSER | 2200 | 20190214 | 811 | 307702 | 2065 | Distribution Circuit | Vegetation | Tree - fell into line | 988 | 493014 | 39.275 | -121.0207 | WIREDOWNBUSHANDNBLOOMFIELDRDOJ2NO42931 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022925 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416158 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023817&numberofmonths=24&showchangehistorylog=1 | 19-0023817 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE | 8893 | 20190214 | 1630 | 310190 | 1630 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 22260 | 39.2612 | -120.9683 | 12876PASQUALERD | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | On Ground | 19-0023817 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1416964 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022843&numberofmonths=24&showchangehistorylog=1 | 19-0022843 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 3605 | 20190214 | 216 | 306358 | 2331 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 27972 | 39.1952 | -121.0238 | 2SPANSEO3605 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022843 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416088 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022976&numberofmonths=24&showchangehistorylog=1 | 19-0022976 | SIERRA | FIELD OPS NORTH | Tier 2 | BRUNSWICK-1106 | 152481106 | FUSE | 8677 | 20190214 | 322 | 306770 | 2353 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 91767 | 39.1559 | -120.9798 | CGC222897054333222890054268 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0022976 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416200 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023294&numberofmonths=24&showchangehistorylog=1 | 19-0023294 | SIERRA | FIELD OPS NORTH | Tier 3 | DIAMOND SPRINGS-1104 | 152261104 | FUSE | 18807 | 20190214 | 749 | 307494 | 1811 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 14488 | 38.6929 | -120.8459 | 4880ORIENTALST | Overcast-Drizzle-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0023294 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1416480 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023077&numberofmonths=24&showchangehistorylog=1 | 19-0023077 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 4595 | 20190214 | 846 | 307913 | 734 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 17765 | 38.6983 | -120.6037 | MTR1007365815 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0023077 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1416278 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022733&numberofmonths=24&showchangehistorylog=1 | 19-0022733 | SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1103 | 152691103 | RECLOSER | 32120 | 20190214 | 122 | 306138 | 1045 | Distribution Circuit | Vegetation | Tree - fell into line | 1660 | 501037 | 39.1048 | -121.0851 | 2079 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022733 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Multi-Fault | 1415970 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023576&numberofmonths=24&showchangehistorylog=1 | 19-0023576 | SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1103 | 152691103 | FUSE | 31299 | 20190214 | 329 | 306570 | 3541 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 21246 | 39.0936 | -121.0852 | SAPID100096141 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0023576 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1416722 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023744&numberofmonths=24&showchangehistorylog=1 | 19-0023744 | SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1104 | 152691104 | FUSE | 30377 | 20190214 | 1918 | 310859 | 1253 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 12530 | 39.1315 | -121.115 | 3PEO30377 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023744 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416894 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023580&numberofmonths=24&showchangehistorylog=1 | 19-0023580 | SIERRA | FIELD OPS NORTH | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 5869 | 20190214 | 633 | 307197 | 817 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 7353 | 38.9069 | -120.929 | 2NDTOLASTSPAN | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023580 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416727 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023516&numberofmonths=24&showchangehistorylog=1 | 19-0023516 | SIERRA | FIELD OPS NORTH | Tier 2 | PLACERVILLE-2106 | 153082106 | FUSE | 5833 | 20190214 | 721 | 307366 | 681 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 13626 | 38.8554 | -120.8435 | 5022HACKMILLERRDGREENWOOD | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023516 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1416663 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023200&numberofmonths=24&showchangehistorylog=1 | 19-0023200 | SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 1319 | 20190214 | 313 | 306513 | 967 | Distribution Circuit | Vegetation | Tree - fell into line | 211 | 137201 | 38.734 | -120.7991 | BennettJeffrey2864benson | Overcast-Drizzle-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0023200 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1416388 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023618&numberofmonths=24&showchangehistorylog=1 | 19-0023618 | SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 58241 | 20190214 | 246 | 306426 | 1086 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 17376 | 38.7507 | -120.7891 | 1SPWO58241 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023618 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1416766 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022782&numberofmonths=24&showchangehistorylog=1 | 19-0022782 | SIERRA | FIELD OPS NORTH | Tier 2 | WISE-1102 | 152271102 | FUSE | 5401 | 20190214 | 304 | 306487 | 450 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 13500 | 38.8988 | -121.096 | MTR1004426125 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022782 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416025 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024353&numberofmonths=24&showchangehistorylog=1 | 19-0024353 | SIERRA | FIELD OPS NORTH | Tier 2 | BRUNSWICK-1106 | 152481106 | OTHER | HOTWIREDOWN | 20190215 | 1859 | 313126 | 1011 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 35000 | 39.1525 | -120.9826 | TASSONELOUIS530682630218524CACTUSLN | Overcast-Fog-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 19-0024353 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1417437 | PW | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024355&numberofmonths=24&showchangehistorylog=1 | 19-0024355 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2102 | 152762102 | RECLOSER | 19562 | 20190215 | 2231 | 313131 | 917 | Distribution Circuit | Vegetation | Tree - fell into line | 504 | 80245 | 38.7604 | -120.5769 | 1PNOFUCO10343 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0024355 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1417439 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023772&numberofmonths=24&showchangehistorylog=1 | 19-0023772 | SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1101 | 152241101 | RECLOSER | 76178 | 20190215 | 138 | 311107 | 838 | Distribution Circuit | Vegetation | Tree - fell into line | 621 | 241224 | 39.0015 | -121.0224 | 1SPANNO1SPANSOFUCO5781 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023772 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1416923 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023780&numberofmonths=24&showchangehistorylog=1 | 19-0023780 | SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 3083 | 20190215 | 125 | 311100 | 743 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 31949 | 38.909 | -120.8362 | CORNEROFCHURCHANDORLEANESTREET | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023780 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Three Phase Fault | 1416934 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024509&numberofmonths=24&showchangehistorylog=1 | 19-0024509 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE | 7965 | 20190216 | 652 | 313518 | 4835 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 135380 | 38.7532 | -120.6117 | 1SPANSOUTHOF12573 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0024509 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1417592 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024386&numberofmonths=24&showchangehistorylog=1 | 19-0024386 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | RECLOSER | 97982 | 20190216 | 509 | 313269 | 5084 | Distribution Circuit | Vegetation | Tree - fell into line | 686 | 424731 | 38.6216 | -120.5867 | LDOF11511 | Overcast-Fog-Snow-Below 32 F | Crossarm, Wood | Broken, wire on ground | 19-0024386 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1417475 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024752&numberofmonths=24&showchangehistorylog=1 | 19-0024752 | SIERRA | FIELD OPS NORTH | Tier 3 | BONNIE NOOK-1101 | 152301101 | FUSE | 6389 | 20190216 | 1822 | 314938 | 2679 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 16074 | 39.1984 | -120.8337 | 6NO6389 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0024752 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1417825 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025018&numberofmonths=24&showchangehistorylog=1 | 19-0025018 | SIERRA | FIELD OPS NORTH | Tier 3 | BONNIE NOOK-1102 | 152301102 | FUSE | 62847 | 20190216 | 2312 | 315155 | 1239 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 6195 | 39.2069 | -120.8108 | 3SPANSLOADSIDEOFFUCO62847 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025018 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1418096 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024545&numberofmonths=24&showchangehistorylog=1 | 19-0024545 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 1309 | 20190216 | 1033 | 313872 | 226 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 4520 | 38.7857 | -120.6076 | 16SPANSLDSIDE1309 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024545 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1417625 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025143&numberofmonths=24&showchangehistorylog=1 | 19-0025143 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | SWITCH | 21275 | 20190216 | 1527 | 315874 | 3148 | Distribution Circuit | Vegetation | Tree - fell into line | 307 | 608094 | 38.724 | -120.5813 | 6202BUCKTAILLN | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025143 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1418221 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024444&numberofmonths=24&showchangehistorylog=1 | 19-0024444 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE | 7091 | 20190216 | 839 | 313702 | 341 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 5797 | 38.7603 | -120.5804 | LUNAMARCOS3185Easyst | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0024444 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1417530 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024518&numberofmonths=24&showchangehistorylog=1 | 19-0024518 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE | 18401 | 20190216 | 405 | 314041 | 3586 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 54053 | 38.7676 | -120.596 | 2200LUCKYMINERDAND2361BLAIRRD | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0024518 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1417601 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024393&numberofmonths=24&showchangehistorylog=1 | 19-0024393 | SIERRA | FIELD OPS NORTH | Tier 3 | FORESTHILL-1101 | 152181101 | OTHER | WIREDOWNMTR1008772529 | 20190216 | 359 | 313468 | 684 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 24884 | 39.0503 | -120.8008 | 6805BLACKHAWKLN | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0024393 | OH | Sus | 31424320 | yes | 2019 | FEB | Yes | Open Circuit | 1417482 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024463&numberofmonths=24&showchangehistorylog=1 | 19-0024463 | SIERRA | FIELD OPS NORTH | Tier 3 | FORESTHILL-1101 | 152181101 | OTHER | WIREDOWN6POLESSSO32001 | 20190216 | 130 | 313722 | 1473 | Distribution Circuit | Vegetation | Tree - branch fell on line | 50 | 115880 | 39.0542 | -120.7671 | 6POLESSSO32001 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0024463 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1417549 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024475&numberofmonths=24&showchangehistorylog=1 | 19-0024475 | SIERRA | FIELD OPS NORTH | Tier 3 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 30801 | 20190216 | 731 | 313538 | 2048 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 4096 | 38.9081 | -120.847 | CGC223285645496 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0024475 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1417560 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025115&numberofmonths=24&showchangehistorylog=1 | 19-0025115 | SIERRA | FIELD OPS NORTH | Tier 3 | PIKE CITY-1102 | 152201102 | FUSE | 8801 | 20190216 | 325 | 315723 | 2300 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 62097 | 39.4942 | -120.9979 | 2SPANSLDSIDEOF8801 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025115 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1418194 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024541&numberofmonths=24&showchangehistorylog=1 | 19-0024541 | SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | RECLOSER | 1104 | 20190216 | 1154 | 314164 | 3428 | Distribution Circuit | Vegetation | Tree - fell into line | 475 | 656583 | 38.9124 | -120.8201 | FATORTRAVIS53021779612058TiptonHillrdGeorgetown | Overcast-Fog-Snow-32-90 F | Pole-Wood | Broken, wire on ground | 19-0024541 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1417622 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024963&numberofmonths=24&showchangehistorylog=1 | 19-0024963 | SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 6903 | 20190216 | 937 | 315158 | 3565 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 28520 | 38.9407 | -120.7307 | EOCGC223620746608ALONGLAKEAVE | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0024963 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1418041 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025734&numberofmonths=24&showchangehistorylog=1 | 19-0025734 | SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | JUMPER | OJS3EO3440WOODPECKERCT | 20190216 | 422 | 318138 | 5096 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 20384 | 38.9672 | -120.7179 |  | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025734 | OH | Sus | 0 | yes | 2019 | FEB | Yes | None | 1418779 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025299&numberofmonths=24&showchangehistorylog=1 | 19-0025299 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-1104 | 153661104 | OTHER | WIREDOWNSSOF12221 | 20190217 | 1630 | 316643 | 1227 | Distribution Circuit | Vegetation | Tree - fell into line | 2378 | 76952 | 38.7477 | -120.6412 | 12221 | Partly Cloudy-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025299 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1418350 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025044&numberofmonths=24&showchangehistorylog=1 | 19-0025044 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 21145 | 20190217 | 328 | 315218 | 504 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 6552 | 38.6341 | -120.5322 | 1SPANLDSIDEOF21145 | Overcast-Fog-Snow-Below 32 F | Crossarm, Wood | Broken, wire on ground | 19-0025044 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1418121 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025117&numberofmonths=24&showchangehistorylog=1 | 19-0025117 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 2825 | 20190217 | 1027 | 315576 | 103 | Distribution Circuit | Vegetation | Tree - fell into line | 98 | 10094 | 38.6327 | -120.5458 | 5368WILDBERRYCOURT | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025117 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1418196 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025120&numberofmonths=24&showchangehistorylog=1 | 19-0025120 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 21495 | 20190217 | 1024 | 315786 | 198 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 5544 | 38.6266 | -120.5517 | 5368WILDBERRYCOURT | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025120 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1418199 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025178&numberofmonths=24&showchangehistorylog=1 | 19-0025178 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 7959 | 20190217 | 1038 | 315614 | 1597 | Distribution Circuit | Vegetation | Tree - fell into line | 125 | 88903 | 38.6431 | -120.5261 | SOUTHOFCGC224236935778 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0025178 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1418255 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025179&numberofmonths=24&showchangehistorylog=1 | 19-0025179 | SIERRA | FIELD OPS NORTH | Tier 3 | BONNIE NOOK-1101 | 152301101 | FUSE | 7353 | 20190217 | 810 | 316019 | 1750 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 21000 | 39.2126 | -120.8168 | 695ALTARAVINERD | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025179 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1418256 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025180&numberofmonths=24&showchangehistorylog=1 | 19-0025180 | SIERRA | FIELD OPS NORTH | Tier 3 | BONNIE NOOK-1101 | 152301101 | FUSE | 6391 | 20190217 | 810 | 316026 | 3305 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 128895 | 39.2094 | -120.8269 | RENFREESAMlco6391 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025180 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1418257 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025239&numberofmonths=24&showchangehistorylog=1 | 19-0025239 | SIERRA | FIELD OPS NORTH | Tier 3 | BONNIE NOOK-1102 | 152301102 | FUSE | 6421 | 20190217 | 1031 | 316476 | 2060 | Distribution Circuit | Vegetation | Tree - grew into line | 7 | 14420 | 39.2154 | -120.8009 | 12SPANSLDSIDEWIREDOWN | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025239 | OH | Sus | 31424320 | yes | 2019 | FEB | Yes | Line to Line | 1418313 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025165&numberofmonths=24&showchangehistorylog=1 | 19-0025165 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1105 | 152481105 | OTHER | WIREDOWN3619 | 20190217 | 1115 | 315675 | 3169 | Distribution Circuit | Vegetation | Tree - fell into line | 201 | 123681 | 39.2668 | -120.9046 | JIMENEZAL530913796312751SUMMITRIDGEDR | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0025165 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1418242 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025087&numberofmonths=24&showchangehistorylog=1 | 19-0025087 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 68757 | 20190217 | 935 | 315499 | 658 | Distribution Circuit | Vegetation | Tree - fell into line | 562 | 351561 | 38.7058 | -120.5996 | 5866SIERRASPRINGSDR | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025087 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1418163 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025157&numberofmonths=24&showchangehistorylog=1 | 19-0025157 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 18411 | 20190217 | 1259 | 315892 | 467 | Distribution Circuit | Vegetation | Tree - fell into line | 73 | 34091 | 38.7722 | -120.5821 | 6180ELCAMINODR | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025157 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1418234 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025163&numberofmonths=24&showchangehistorylog=1 | 19-0025163 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | RECLOSER | 6852 | 20190217 | 1334 | 315960 | 1651 | Distribution Circuit | Vegetation | Tree - fell into line | 1166 | 602490 | 38.7612 | -120.5582 | WIREDOWNNOSW7575 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025163 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1418240 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025171&numberofmonths=24&showchangehistorylog=1 | 19-0025171 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 20867 | 20190217 | 939 | 315988 | 1504 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 91744 | 38.7197 | -120.5828 | 5189LOCHLEVENDR | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025171 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1418248 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025200&numberofmonths=24&showchangehistorylog=1 | 19-0025200 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | RECLOSER | 19612 | 20190217 | 1303 | 315909 | 3319 | Distribution Circuit | Vegetation | Tree - fell into line | 170 | 564230 | 38.7621 | -120.5586 | 3SPANSEOFREGSH486 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025200 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1418278 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025227&numberofmonths=24&showchangehistorylog=1 | 19-0025227 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 18949 | 20190217 | 939 | 316434 | 768 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 15360 | 38.7164 | -120.58 | 5163FAWNDR | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025227 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1418303 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025261&numberofmonths=24&showchangehistorylog=1 | 19-0025261 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 1081 | 20190217 | 1216 | 315826 | 2872 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 48824 | 38.7848 | -120.603 | BennettJeffrey1941kingofthemountain | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025261 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1418323 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025534&numberofmonths=24&showchangehistorylog=1 | 19-0025534 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 4741 | 20190217 | 1303 | 317233 | 3319 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 36509 | 38.7613 | -120.5351 | 3094FORESTRD | Overcast-Snow-Below 32 F | Crossarm, Wood | Broken, wire on ground | 19-0025534 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1418590 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025057&numberofmonths=24&showchangehistorylog=1 | 19-0025057 | SIERRA | FIELD OPS NORTH | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 1180 | 20190217 | 900 | 315453 | 560 | Distribution Circuit | Vegetation | Tree - fell into line | 235 | 73936 | 38.8952 | -120.9116 | 4510GREENWOOD2NOFUCO31113 | Overcast-Fog-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0025057 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1418133 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025085&numberofmonths=24&showchangehistorylog=1 | 19-0025085 | SIERRA | FIELD OPS NORTH | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 95773 | 20190217 | 941 | 315504 | 303 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 9999 | 38.897 | -120.8933 | 4530HWY193 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025085 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1418161 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025168&numberofmonths=24&showchangehistorylog=1 | 19-0025168 | SIERRA | FIELD OPS NORTH | Tier 2 | PLACERVILLE-1110 | 153081110 | FUSE | 21759 | 20190217 | 956 | 315526 | 377 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 6786 | 38.7784 | -120.8967 | 10SPANSLOADSIDE | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025168 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1418245 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025572&numberofmonths=24&showchangehistorylog=1 | 19-0025572 | SIERRA | FIELD OPS NORTH | Tier 2 | PLACERVILLE-2106 | 153082106 | JUMPER | WIREDOWN1SOF5845 | 20190217 | 1440 | 317409 | 1653 | Distribution Circuit | Equipment Failure/Involved | Overhead | 33 | 21286 | 38.8422 | -120.8379 | 1SO5845 | Partly Cloudy-Fog-Below 32 F | Connector or Splice (OH) | Broken, wire on ground | 19-0025572 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1418621 | CSO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028071&numberofmonths=24&showchangehistorylog=1 | 19-0028071 | SIERRA | FIELD OPS NORTH | Tier 3 | ALLEGHANY-1101 | 152101101 | RECLOSER | 11012 | 20190226 | 13 | 323739 | 10688 | Distribution Circuit | Vegetation | Tree - fell into line | 1075 | 3063636 | 39.4655 | -120.8444 | 7939 | Overcast-Fog-Snow-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0028071 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1420182 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028630&numberofmonths=24&showchangehistorylog=1 | 19-0028630 | SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1101 | 152241101 | FUSE | 34911 | 20190226 | 2231 | 325497 | 696 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 6960 | 39.0046 | -121.0306 | 34911 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028630 | OH | Sus | 31426710 | yes | 2019 | FEB | Yes | Line to Ground | 1420536 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028627&numberofmonths=24&showchangehistorylog=1 | 19-0028627 | SIERRA | FIELD OPS NORTH | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 21012 | 20190226 | 2312 | 325667 | 201 | Distribution Circuit | Vegetation | Tree - fell into line | 3664 | 483938 | 38.9144 | -121.0197 | HWY49GILLESPIERD | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028627 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1420533 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028294&numberofmonths=24&showchangehistorylog=1 | 19-0028294 | SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2102 | 153132102 | FUSE | 32973 | 20190226 | 702 | 323901 | 703 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 6596 | 39.2758 | -121.2064 | 18314FINLEY | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028294 | OH | Sus | 31426712 | yes | 2019 | FEB | Yes | Line to Ground | 1420307 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028825&numberofmonths=24&showchangehistorylog=1 | 19-0028825 | SIERRA | FIELD OPS NORTH | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 11479 | 20190226 | 2334 | 326648 | 726 | Distribution Circuit | Vegetation | Tree - fell into line | 130 | 94380 | 38.8062 | -120.9254 | 1988LULLABYLN | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028825 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1420706 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028268&numberofmonths=24&showchangehistorylog=1 | 19-0028268 | SIERRA | FIELD OPS NORTH | Tier 2 | SPAULDING-1101 | 152251101 | FUSE | 91077 | 20190226 | 1145 | 324380 | 1319 | Distribution Circuit | Vegetation | Tree - fell into line | 325 | 20759 | 39.3117 | -120.6594 | LDSIDE91077 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028268 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1420296 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028532&numberofmonths=24&showchangehistorylog=1 | 19-0028532 | SIERRA | FIELD OPS NORTH | Tier 3 | SPAULDING-1101 | 152251101 | SWITCH | 34807 | 20190226 | 1610 | 325163 | 8792 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 26376 | 39.2496 | -120.7557 | 15SPANSEASTOF1611 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028532 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1420440 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028556&numberofmonths=24&showchangehistorylog=1 | 19-0028556 | SIERRA | FIELD OPS NORTH | Tier 3 | SPAULDING-1101 | 152251101 | RECLOSER | 75874 | 20190226 | 2029 | 325256 | 8434 | Distribution Circuit | Vegetation | Tree - fell into line | 319 | 753746 | 39.2911 | -120.6782 | MANYMANYLOCATIONS | Overcast-Fog-Snow-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028556 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1420461 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028978&numberofmonths=24&showchangehistorylog=1 | 19-0028978 | SIERRA | FIELD OPS NORTH | Tier 2 | WEIMAR-1102 | 152491102 | JUMPER | OJ1EOCGC222835549678 | 20190226 | 2237 | 325506 | 1120 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2240 | 39.0267 | -121.0025 | CGC222835549678 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028978 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1420807 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0029117&numberofmonths=24&showchangehistorylog=1 | 19-0029117 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1103 | 152481103 | FUSE | 8739 | 20190227 | 21 | 326443 | 2355 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 15741 | 39.3134 | -121.0347 | 19215RANCHRD | Partly Cloudy-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0029117 | OH | Sus | 31426712 | yes | 2019 | FEB | Yes | Line to Line | 1420877 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028802&numberofmonths=24&showchangehistorylog=1 | 19-0028802 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE | 7349 | 20190227 | 220 | 326150 | 2081 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 13536 | 39.24 | -120.9875 | SHADEBRIAN2polesnoeol | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028802 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1420689 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028884&numberofmonths=24&showchangehistorylog=1 | 19-0028884 | SIERRA | FIELD OPS NORTH | Tier 2 | COLUMBIA HILL-1101 | 152471101 | FUSE | 8115 | 20190227 | 307 | 326222 | 996 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 36852 | 39.3255 | -121.1124 | ESIDEOFMTR1007572734 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028884 | OH | Sus | 31426712 | yes | 2019 | FEB | Yes | Multi-Fault | 1420759 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028926&numberofmonths=24&showchangehistorylog=1 | 19-0028926 | SIERRA | FIELD OPS NORTH | Tier 2 | GRASS VALLEY-1103 | 152031103 | FUSE | 86845 | 20190227 | 343 | 326257 | 1866 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3732 | 39.1521 | -121.0773 | 2SPANSLDSIDEOF86845 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028926 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1420782 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028697&numberofmonths=24&showchangehistorylog=1 | 19-0028697 | SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1102 | 152241102 | RECLOSER | 39104 | 20190227 | 324 | 326235 | 850 | Distribution Circuit | Vegetation | Tree - fell into line | 892 | 503360 | 38.9734 | -121.014 | HARTEMMETT1506530906203118497SDunveganDr | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028697 | OH | Sus | 31426710 | yes | 2019 | FEB | Yes | Line to Line | 1420608 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028781&numberofmonths=24&showchangehistorylog=1 | 19-0028781 | SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1109 | 152691109 | OTHER | WIREDOWN22365CHERYL | 20190227 | 701 | 326563 | 584 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 2684 | 39.0503 | -121.0975 | 22365CHERYL | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028781 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1420672 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028877&numberofmonths=24&showchangehistorylog=1 | 19-0028877 | SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1110 | 152691110 | FUSE | 3651 | 20190227 | 141 | 326086 | 765 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 14535 | 39.0499 | -121.0455 | 22204KNOWLESDR | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028877 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1420749 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028907&numberofmonths=24&showchangehistorylog=1 | 19-0028907 | SIERRA | FIELD OPS NORTH | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 32425 | 20190227 | 955 | 326830 | 611 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 611 | 38.9054 | -120.8688 | BROKENPOLE2POLESSSOFRISER34021 | Overcast-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0028907 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1420771 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028627&numberofmonths=24&showchangehistorylog=1 | 19-0028627 | SIERRA | FIELD OPS NORTH | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | RECLOSER | 30779 | 20190227 | 1923 | 327564 | 92 | Distribution Circuit | Vegetation | Tree - fell into line | 90 | 3470 | 38.8698 | -121.0202 | HWY49CAVEVALLEYRDCOOL | Strong Winds-Rain-Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028627 | OH | Sus | 0 | yes | 2019 | FEB | Yes | None | 1420923 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0029148&numberofmonths=24&showchangehistorylog=1 | 19-0029148 | SIERRA | FIELD OPS NORTH | Tier 2 | TAMARACK-1101 | 152291101 | FUSE | 6613 | 20190227 | 716 | 327317 | 1829 | Distribution Circuit | Vegetation | Tree - branch fell on line | 64 | 104929 | 39.3178 | -120.4494 | 3SPANSSO6633ONMAINLINE | Strong Winds-Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0029148 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1420894 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0065574&numberofmonths=24&showchangehistorylog=1 | 19-0065574 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE | 12633 | 20190610 | 1854 | 404516 | 1013 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 16 | 16208 | 38.8037 | -120.699 | 6370WILDFLOWERCT | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0065574 | OH | Sus | 43837871 | yes | 2019 | JUN | Yes | Line to Ground | 1447723 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0065481&numberofmonths=24&showchangehistorylog=1 | 19-0065481 | SIERRA | FIELD OPS NORTH | Tier 2 | PLACERVILLE-2106 | 153082106 | FUSE | 5987 | 20190610 | 1627 | 404148 | 768 | Distribution Circuit | Vegetation | Tree - fell into line | 73 | 14169 | 38.82 | -120.8494 | 6181SHASTA | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0065481 | OH | Sus | 31452985 | yes | 2019 | JUN | Yes | Line to Ground | 1447649 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0118081&numberofmonths=24&showchangehistorylog=1 | 19-0118081 | SIERRA | FIELD OPS NORTH | Tier 2 | COLUMBIA HILL-1101 | 152471101 | FUSE | 7355 | 20191026 | 1824 | 692399 | 5741 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 86115 | 39.3257 | -121.1127 | TRANSMISSIONPOLE388 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0118081 | OH | Sus | 0 | yes | 2019 | OCT | Yes | Line to Line | 1487123 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0115927&numberofmonths=24&showchangehistorylog=1 | 19-0115927 | SIERRA | FIELD OPS NORTH | Tier 3 | FORESTHILL-1101 | 152181101 | JUMPER | OJS1EO3585 | 20191026 | 1855 | 691431 | 2737 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 13685 | 39.0222 | -120.8075 | 3585 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0115927 | OH | Sus | 0 | yes | 2019 | OCT | Yes | Line to Ground | 1486822 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0117871&numberofmonths=24&showchangehistorylog=1 | 19-0117871 | SIERRA | FIELD OPS NORTH | Tier 2 | GRASS VALLEY-1101 | 152031101 | FUSE | 32729 | 20191026 | 1841 | 691709 | 5430 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 108600 | 39.16 | -121.058 | FIRSTSPANLOADSIDEOF32729 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0117871 | OH | Sus | 0 | yes | 2019 | OCT | Yes | Open Circuit | 1486892 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0115965&numberofmonths=24&showchangehistorylog=1 | 19-0115965 | SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1104 | 152691104 | JUMPER | OJSEOF222683551520 | 20191026 | 1705 | 691899 | 5312 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 5312 | 39.0775 | -121.0552 | EOF222683551520 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0115965 | OH | Sus | 0 | yes | 2019 | OCT | Yes | Open Circuit | 1486942 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0115965&numberofmonths=24&showchangehistorylog=1 | 19-0115965 | SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1104 | 152691104 | JUMPER | OJS4NOF222702153142 | 20191026 | 1705 | 691977 | 5418 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 5418 | 39.1238 | -121.05 | 222702153142 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0115965 | OH | Sus | 0 | yes | 2019 | OCT | Yes | Line to Ground | 1486974 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0117572&numberofmonths=24&showchangehistorylog=1 | 19-0117572 | SIERRA | FIELD OPS NORTH | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 18229 | 20191026 | 1811 | 690417 | 2924 | Distribution Circuit | Vegetation | Tree - branch fell on line | 28 | 81872 | 38.785 | -120.9558 | 1087SPRINGCRESTCT | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0117572 | OH | Sus | 0 | yes | 2019 | OCT | Yes | Force Out | 1486357 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0117452&numberofmonths=24&showchangehistorylog=1 | 19-0117452 | SIERRA | FIELD OPS NORTH | Tier 2 | WEIMAR-1101 | 152491101 | FUSE | 33905 | 20191026 | 1858 | 688974 | 2688 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 34944 | 39.0423 | -120.9686 | 20870SUNSETWAY | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0117452 | OH | Sus | 0 | yes | 2019 | OCT | Yes | Force Out | 1486019 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0118709&numberofmonths=24&showchangehistorylog=1 | 19-0118709 | SIERRA | FIELD OPS NORTH | Tier 2 | LINCOLN-1101 | 153701101 | FUSE | 9195 | 20191029 | 1513 | 694256 | 1213 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 14556 | 38.9023 | -121.1934 | FATORTRAVIS5302177961780StonewoodRdNewcastle | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0118709 | OH | Sus | 0 | yes | 2019 | OCT | Yes | Line to Ground | 1487767 | CSO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0130005&numberofmonths=24&showchangehistorylog=1 | 19-0130005 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-1104 | 153661104 | TRIP-SAVER | 12625 | 20191127 | 405 | 719839 | 687 | Distribution Circuit | Vegetation | Tree - fell into line | 149 | 84135 | 38.7913 | -120.7022 | 6497LOGCABIN | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0130005 | OH | Sus | 0 | yes | 2019 | NOV | Yes | Three Phase Fault | 1494954 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0129944&numberofmonths=24&showchangehistorylog=1 | 19-0129944 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1103 | 152481103 | RECLOSER | 2200 | 20191127 | 654 | 720344 | 642 | Distribution Circuit | Vegetation | Tree - fell into line | 114 | 51186 | 39.275 | -121.0207 | MET1007523072 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0129944 | OH | Sus | 0 | yes | 2019 | NOV | Yes | Line to Ground | 1494908 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0130790&numberofmonths=24&showchangehistorylog=1 | 19-0130790 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 68757 | 20191127 | 2355 | 722494 | 1276 | Distribution Circuit | Vegetation | Tree - fell into line | 521 | 602844 | 38.7058 | -120.5996 | MELLOADAM53040158145215sierrasprings | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0130790 | OH | Sus | 0 | yes | 2019 | NOV | Yes | Three Phase Fault | 1495473 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0009767&numberofmonths=24&showchangehistorylog=1 | 20-0009767 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 13253 | 20200116 | 946 | 762549 | 234 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 1404 | 38.6762 | -120.6611 | 5001DOLLHOUSERD | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0009767 | OH | Sus | 31486518 | yes | 2020 | JAN | Yes | Line to Ground | 1506820 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0010264&numberofmonths=24&showchangehistorylog=1 | 20-0010264 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | JUMPER | WIREDOWN5151CLEARCREEK | 20200116 | 1641 | 763348 | 269 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 2402 | 38.6942 | -120.6345 | MTR1007651005 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0010264 | OH | Sus | 0 | yes | 2020 | JAN | Yes | Line to Ground | 1506986 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0010227&numberofmonths=24&showchangehistorylog=1 | 20-0010227 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 7043 | 20200116 | 1426 | 763096 | 1258 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 42772 | 39.1984 | -121.0256 | 11757LOWERCOLFAXRD | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0010227 | OH | Sus | 0 | yes | 2020 | JAN | Yes | Line to Line | 1506961 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0010296&numberofmonths=24&showchangehistorylog=1 | 20-0010296 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 7067 | 20200116 | 1625 | 763329 | 1122 | Distribution Circuit | Equipment Failure/Involved | Overhead | 57 | 63954 | 39.1732 | -120.9739 | TOMASIMIKE916747024214221BERTINORD | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0010296 | OH | Sus | 0 | yes | 2020 | JAN | Yes | Line to Ground | 1507012 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0010333&numberofmonths=24&showchangehistorylog=1 | 20-0010333 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 6757 | 20200116 | 1819 | 763551 | 1106 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 18802 | 39.1882 | -120.9618 | 3SPANSSOF67575SPANSSOF67577SPANSSOF6757 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0010333 | OH | Sus | 0 | yes | 2020 | JAN | Yes | Line to Ground | 1507050 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0010339&numberofmonths=24&showchangehistorylog=1 | 20-0010339 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1106 | 152481106 | OTHER | WIREDOWNAT13630FORESTPARKLN | 20200116 | 1815 | 763673 | 1430 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 18479 | 39.1917 | -121.0025 | IFO13630FORESTPARKLN | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0010339 | OH | Sus | 0 | yes | 2020 | JAN | Yes | Open Circuit | 1507056 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0009717&numberofmonths=24&showchangehistorylog=1 | 20-0009717 | SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2102 | 153132102 | JUMPER | 6PLDSIDEOF32993 | 20200116 | 929 | 762623 | 258 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 21930 | 39.2526 | -121.1126 | 6PLDSIDEOF32993 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0009717 | OH | Sus | 31486515 | yes | 2020 | JAN | Yes | Line to Ground | 1506805 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0010254&numberofmonths=24&showchangehistorylog=1 | 20-0010254 | SIERRA | FIELD OPS NORTH | Tier 3 | PIKE CITY-1101 | 152201101 | FUSE | 8213 | 20200116 | 1555 | 765314 | 4105 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 111642 | 39.4687 | -121.0856 | 2SPANSNEOCGC222559766576SAPID100092003 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0010254 | OH | Sus | 0 | yes | 2020 | JAN | Yes | Line to Ground | 1507477 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0010891&numberofmonths=24&showchangehistorylog=1 | 20-0010891 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE | 7853 | 20200117 | 49 | 763778 | 2022 | Distribution Circuit | Vegetation | Tree - branch fell on line | 34 | 55692 | 39.242 | -120.9626 | 1POLESOFMTR1007521074 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0010891 | OH | Sus | 0 | yes | 2020 | JAN | Yes | Line to Line | 1507410 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0010528&numberofmonths=24&showchangehistorylog=1 | 20-0010528 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 4543 | 20200117 | 654 | 764495 | 489 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1956 | 39.1805 | -120.9376 | 14463ARROWHEADMINERDGRASSVALLEY | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0010528 | OH | Sus | 0 | yes | 2020 | JAN | Yes | Line to Ground | 1507237 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0010564&numberofmonths=24&showchangehistorylog=1 | 20-0010564 | SIERRA | FIELD OPS NORTH | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE | 5907 | 20200117 | 1007 | 764712 | 167 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 9352 | 39.0543 | -120.7586 | CGC223539750580 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0010564 | OH | Sus | 0 | yes | 2020 | JAN | Yes | Line to Ground | 1507279 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0010985&numberofmonths=24&showchangehistorylog=1 | 20-0010985 | SIERRA | FIELD OPS NORTH | Tier 2 | PLACERVILLE-2106 | 153082106 | FUSE | 5831 | 20200117 | 1825 | 765201 | 135 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 53 | 7155 | 38.8494 | -120.8687 | 2SPNO5831 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0010985 | OH | Sus | 0 | yes | 2020 | JAN | Yes | Line to Ground | 1507452 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0019493&numberofmonths=24&showchangehistorylog=1 | 20-0019493 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | SWITCH | 87861 | 20200209 | 1725 | 785891 | 260 | Distribution Circuit | Vegetation | Tree - branch fell on line | 660 | 24811 | 38.6701 | -120.5331 | EOF39544 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0019493 | OH | Sus | 0 | yes | 2020 | FEB | Yes | Force Out | 1513520 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0019060&numberofmonths=24&showchangehistorylog=1 | 20-0019060 | SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2102 | 153132102 | FUSE | 31481 | 20200209 | 904 | 781421 | 503 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 12584 | 39.2531 | -121.1029 | LDSIDEOFMTR1007605641 | Clear- | Pole-Wood | Broken, wire on ground | 20-0019060 | OH | Sus | 0 | yes | 2020 | FEB | Yes | Line to Ground | 1513076 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0019161&numberofmonths=24&showchangehistorylog=1 | 20-0019161 | SIERRA | FIELD OPS NORTH | Tier 2 | PLACERVILLE-1112 | 153081112 | RECLOSER | 19742 | 20200209 | 1100 | 782689 | 670 | Distribution Circuit | Vegetation | Tree - branch fell on line | 758 | 71411 | 38.731 | -120.8097 | CURTISMARK2861HILLTOPDR | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0019161 | OH | Sus | 0 | yes | 2020 | FEB | Yes | Line to Ground | 1513184 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0018955&numberofmonths=24&showchangehistorylog=1 | 20-0018955 | SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 82493 | 20200209 | 714 | 781231 | 426 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 2556 | 38.7461 | -120.7917 | IFO2431MORRENEDR | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0018955 | OH | Sus | 0 | yes | 2020 | FEB | Yes | Line to Ground | 1512967 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0019238&numberofmonths=24&showchangehistorylog=1 | 20-0019238 | SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 65865 | 20200209 | 1129 | 783029 | 305 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 26535 | 38.7482 | -120.7944 | 2SPANSSSOF96233 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0019238 | OH | Sus | 0 | yes | 2020 | FEB | Yes | Line to Ground | 1513264 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0019082&numberofmonths=24&showchangehistorylog=1 | 20-0019082 | SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2110 | 153652110 | FUSE | 22341 | 20200209 | 742 | 781243 | 476 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 32844 | 38.6529 | -120.9104 | 4PEOF22341 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0019082 | OH | Sus | 0 | yes | 2020 | FEB | Yes | Line to Ground | 1513100 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0019137&numberofmonths=24&showchangehistorylog=1 | 20-0019137 | SIERRA | FIELD OPS NORTH | Tier 2 | TAMARACK-1101 | 152291101 | FUSE | 6655 | 20200209 | 933 | 781707 | 374 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 20944 | 39.322 | -120.4385 | 5SPANSLDSIDEOF6655 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0019137 | OH | Sus | 0 | yes | 2020 | FEB | Yes | Line to Line | 1513158 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0032190&numberofmonths=24&showchangehistorylog=1 | 20-0032190 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1105 | 152481105 | RECLOSER | 2130 | 20200315 | 303 | 851720 | 719 | Distribution Circuit | Vegetation | Tree - branch fell on line | 201 | 116997 | 39.2741 | -120.9695 | SSOFSECT2108BETWEEN9891619 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0032190 | OH | Sus | 0 | yes | 2020 | MAR | Yes | Line to Line | 1521523 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0032186&numberofmonths=24&showchangehistorylog=1 | 20-0032186 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2102 | 152762102 | OCB | 21022 | 20200315 | 418 | 851598 | 865 | Distribution Circuit | Vegetation | Tree - fell into line | 773 | 409373 | 38.7934 | -120.6201 | 1WOFH471SPANNOF2413 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0032186 | OH | Sus | 0 | yes | 2020 | MAR | Yes | Line to Line | 1521519 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0032482&numberofmonths=24&showchangehistorylog=1 | 20-0032482 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1103 | 152481103 | RECLOSER | 2200 | 20200316 | 259 | 853310 | 933 | Distribution Circuit | Vegetation | Tree - branch fell on line | 114 | 86474 | 39.275 | -121.0207 | 3SPEOFFUCO31863 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0032482 | OH | Sus | 0 | yes | 2020 | MAR | Yes | Line to Ground | 1521814 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0032861&numberofmonths=24&showchangehistorylog=1 | 20-0032861 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 7039 | 20200316 | 637 | 853567 | 533 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 27183 | 39.1992 | -121.0201 | 8SPANSLDSIDEOF7039 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 20-0032861 | OH | Sus | 0 | yes | 2020 | MAR | Yes | Line to Ground | 1522067 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0084057&numberofmonths=24&showchangehistorylog=1 | 20-0084057 | SIERRA | FIELD OPS NORTH | Tier 2 | WISE-1102 | 152271102 | RECLOSER | 2230 | 20200815 | 316 | 1003656 | 468 | Distribution Circuit | 3rd Party | Vehicle | 849 | 297015 | 38.8961 | -121.1374 | SSSPANOFLR307494 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0084057 | OH | Sus | 0 | yes | 2020 | AUG | Yes | Line to Line | 1554595 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0085010&numberofmonths=24&showchangehistorylog=1 | 20-0085010 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 10267 | 20200816 | 1235 | 1012726 | 515 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2060 | 38.5673 | -120.7036 | 6SPLDSIDEOF10267 | Partly Cloudy-Heat Wave-Above 90 | Pole-Wood | Broken, wire on ground | 20-0085010 | OH | Sus | 0 | yes | 2020 | AUG | Yes | Line to Line | 1555457 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0085084&numberofmonths=24&showchangehistorylog=1 | 20-0085084 | SIERRA | FIELD OPS NORTH | Tier 2 | BRUNSWICK-1106 | 152481106 | FUSE | 30717 | 20200816 | 1517 | 1013150 | 381 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 1799 | 39.1174 | -120.9931 | 21411OXNARDCT | Clear-Heat Wave-Above 90 | Conductor, Overhead | Broken, wire on ground | 20-0085084 | OH | Sus | 0 | yes | 2020 | AUG | Yes | Line to Line | 1555528 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0010382&numberofmonths=24&showchangehistorylog=1 | 21-0010382 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 1361 | 20210119 | 115 | 1213909 | 601 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 13823 | 38.5813 | -120.5699 | 6620OMORANCHRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0010382 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1594352 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0010618&numberofmonths=24&showchangehistorylog=1 | 21-0010618 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | RECLOSER | 97982 | 20210119 | 1035 | 1216483 | 163 | Distribution Circuit | Vegetation | Tree - fell into line | 105 | 17115 | 38.6217 | -120.5868 | 10405GRIZZLYFLATRDLat386351307Lon1205236512 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0010618 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1594523 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0010524&numberofmonths=24&showchangehistorylog=1 | 21-0010524 | SIERRA | FIELD OPS NORTH | Tier 3 | BONNIE NOOK-1101 | 152301101 | FUSE | 6391 | 20210119 | 548 | 1214912 | 600 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 6803 | 39.2095 | -120.827 | JUSTWO33100MAINST | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0010524 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1594464 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0010110&numberofmonths=24&showchangehistorylog=1 | 21-0010110 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1103 | 152481103 | FUSE | 33617 | 20210119 | 140 | 1213869 | 924 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 27720 | 39.2929 | -121.0153 | 1SPANLDSIDEOF33617 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0010110 | OH | Sus | 0 | No | 2021 | JAN | Yes | Force Out | 1594077 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0010111&numberofmonths=24&showchangehistorylog=1 | 21-0010111 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1103 | 152481103 | FUSE | 34225 | 20210119 | 48 | 1214339 | 971 | Distribution Circuit | Equipment Failure/Involved | Overhead | 28 | 27188 | 39.2929 | -121.0155 | 1SPANLDSIDEOF34225 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0010111 | OH | Sus | 44629093 | No | 2021 | JAN | Yes | Force Out | 1594078 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0010477&numberofmonths=24&showchangehistorylog=1 | 21-0010477 | SIERRA | FIELD OPS NORTH | Tier 2 | BRUNSWICK-1104 | 152481104 | FUSE | 4183 | 20210119 | 4 | 1213435 | 815 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 13285 | 39.2689 | -121.0566 | EOLPOLEALLTHEWAYTOTHENORTHOFTHEHARDTAP | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0010477 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Line | 1594425 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0010727&numberofmonths=24&showchangehistorylog=1 | 21-0010727 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE | 9819 | 20210119 | 911 | 1216050 | 377 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 3393 | 39.3217 | -120.8643 | 1SPANSSOF31911 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0010727 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1594615 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0010494&numberofmonths=24&showchangehistorylog=1 | 21-0010494 | SIERRA | FIELD OPS NORTH | Tier 3 | DRUM-1101 | 152321101 | JUMPER | 1602 | 20210119 | 829 | 1216130 | 258 | Distribution Circuit | Vegetation | Tree - fell into line | 194 | 16128 | 39.2889 | -120.6907 | 2SPANSLDSIDEOF30691 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0010494 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1594440 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0010869&numberofmonths=24&showchangehistorylog=1 | 21-0010869 | SIERRA | FIELD OPS NORTH | Tier 2 | ECHO SUMMIT-1101 | 158031101 | RECLOSER | 481660 | 20210119 | 1403 | 1217323 | 266 | Distribution Circuit | Equipment Failure/Involved | Overhead | 78 | 8214 | 38.8107 | -120.0319 | 1PHASEOFWIREDOWNCGC225420041920 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0010869 | OH | Sus | 0 | No | 2021 | JAN | Yes | Three Phase Fault | 1594708 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0010975&numberofmonths=24&showchangehistorylog=1 | 21-0010975 | SIERRA | FIELD OPS NORTH | Tier 2 | PENRYN-1105 | 152561105 | FUSE | 9143 | 20210119 | 1319 | 1217221 | 339 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 4407 | 38.9014 | -121.1876 | BETSAPID103936943and100043279 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0010975 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Line | 1594770 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0010790&numberofmonths=24&showchangehistorylog=1 | 21-0010790 | SIERRA | FIELD OPS NORTH | Tier 2 | PLACERVILLE-2106 | 153082106 | OTHER | HOTWIREDOWN5837 | 20210119 | 1011 | 1216521 | 582 | Distribution Circuit | Vegetation | Tree - fell into line | 669 | 74519 | 38.8576 | -120.8379 | 1SOF5837 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0010790 | OH | Sus | 0 | No | 2021 | JAN | Yes | Open Circuit | 1594654 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0010573&numberofmonths=24&showchangehistorylog=1 | 21-0010573 | SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 2197 | 20210119 | 407 | 1214541 | 728 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 12376 | 38.8265 | -120.812 | HYLANDTRAVIS6931kashaln | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0010573 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1594493 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0010453&numberofmonths=24&showchangehistorylog=1 | 21-0010453 | SIERRA | FIELD OPS NORTH | Tier 2 | TAMARACK-1101 | 152291101 | FUSE | 6617 | 20210119 | 840 | 1214938 | 445 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 24920 | 39.3203 | -120.4331 | 51519DONNERPASSRD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0010453 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1594405 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0013871&numberofmonths=24&showchangehistorylog=1 | 21-0013871 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-1104 | 153661104 | FUSE | 18545 | 20210125 | 554 | 1223453 | 684 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 15048 | 38.7535 | -120.6976 | 4PLDSIDEOF18545 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0013871 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Line | 1596773 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0013624&numberofmonths=24&showchangehistorylog=1 | 21-0013624 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 13247 | 20210125 | 508 | 1223369 | 722 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 12274 | 38.698 | -120.6707 | SAPID101408678 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 21-0013624 | OH | Sus | 0 | No | 2021 | JAN | Yes | Multi-Fault | 1596608 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0013682&numberofmonths=24&showchangehistorylog=1 | 21-0013682 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | OTHER | WIREDOWN6POLESLDSIDEOF2025 | 20210125 | 126 | 1223043 | 881 | Distribution Circuit | Vegetation | Tree - fell into line | 369 | 20015 | 38.64 | -120.6436 | 2025ONMAINLINE6POLESLDSIDEOF2025 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0013682 | OH | Sus | 0 | No | 2021 | JAN | Yes | Open Circuit | 1596636 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0013927&numberofmonths=24&showchangehistorylog=1 | 21-0013927 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 2029 | 20210125 | 1141 | 1224340 | 184 | Distribution Circuit | Vegetation | Tree - branch fell on line | 56 | 10304 | 38.6204 | -120.6018 | 6134SWEENEYRD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0013927 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1596814 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0013999&numberofmonths=24&showchangehistorylog=1 | 21-0013999 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | JUMPER | WIREDOWN6760DIABLOVIEWCT | 20210125 | 1420 | 1224725 | 94 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 2250 | 38.6906 | -120.6273 | WIREDOWN6760DIABLOVIEWCT | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0013999 | OH | Sus | 0 | No | 2021 | JAN | Yes | Open Circuit | 1596861 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0013869&numberofmonths=24&showchangehistorylog=1 | 21-0013869 | SIERRA | FIELD OPS NORTH | Tier 3 | FORESTHILL-1102 | 152181102 | FUSE | 6007 | 20210125 | 547 | 1223441 | 811 | Distribution Circuit | Vegetation | Tree - branch fell on line | 117 | 94887 | 39.0001 | -120.9071 | 1NOF30261 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0013869 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Line | 1596771 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0013786&numberofmonths=24&showchangehistorylog=1 | 21-0013786 | SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1102 | 152241102 | OTHER | WIREDOWN2SPANSLDSIDEOF6149 | 20210125 | 900 | 1224119 | 260 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 520 | 39.0001 | -120.9797 | 2SPANLSSIDEOF6149 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0013786 | OH | Sus | 0 | No | 2021 | JAN | Yes | Open Circuit | 1596721 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0013636&numberofmonths=24&showchangehistorylog=1 | 21-0013636 | SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1104 | 152691104 | FUSE | 6955 | 20210125 | 540 | 1223404 | 767 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 25194 | 39.1192 | -121.058 | CGC222672752784 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 21-0013636 | OH | Sus | 35227541 | No | 2021 | JAN | Yes | Line to Line | 1596610 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0013770&numberofmonths=24&showchangehistorylog=1 | 21-0013770 | SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1104 | 152691104 | FUSE | 8439 | 20210125 | 349 | 1224083 | 847 | Distribution Circuit | Vegetation | Tree - branch fell on line | 96 | 54612 | 39.1067 | -121.0093 | SAPID100097770CGC222793852470 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 21-0013770 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1596708 | PW | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0013797&numberofmonths=24&showchangehistorylog=1 | 21-0013797 | SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1110 | 152691110 | FUSE | 31279 | 20210125 | 650 | 1223557 | 781 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 15620 | 39.0832 | -121.0017 | 6LDSIDEOF31279 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 21-0013797 | OH | Sus | 0 | No | 2021 | JAN | Yes | Force Out | 1596727 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0013970&numberofmonths=24&showchangehistorylog=1 | 21-0013970 | SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1110 | 152691110 | FUSE | 7489 | 20210125 | 634 | 1223521 | 798 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 24738 | 39.0799 | -121.0125 | SHADEBRIAN5303622052multiplelocations | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0013970 | OH | Sus | 0 | No | 2021 | JAN | Yes | Force Out | 1596841 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0014492&numberofmonths=24&showchangehistorylog=1 | 21-0014492 | SIERRA | FIELD OPS NORTH | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 8569 | 20210125 | 2155 | 1225369 | 1143 | Distribution Circuit | Vegetation | Tree - branch fell on line | 27 | 23973 | 38.9047 | -120.8732 | MTR1004193550 | Clear-32-90F | Cutout, fuse holder | Broken, wire on ground | 21-0014492 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1597163 | CFH | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0014073&numberofmonths=24&showchangehistorylog=1 | 21-0014073 | SIERRA | FIELD OPS NORTH | Tier 2 | SHADY GLEN-1101 | 152431101 | FUSE | 64017 | 20210125 | 337 | 1224107 | 990 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 11076 | 39.0993 | -120.9487 | 2SPANSSSOFMTR1004688499 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0014073 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1596907 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0013546&numberofmonths=24&showchangehistorylog=1 | 21-0013546 | SIERRA | FIELD OPS NORTH | Tier 2 | WEIMAR-1101 | 152491101 | RECLOSER | 2740 | 20210125 | 28 | 1222999 | 989 | Distribution Circuit | Vegetation | Tree - fell into line | 547 | 517834 | 39.0343 | -120.9746 | 2SPANSLDSIDE2740 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0013546 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1596530 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0014549&numberofmonths=24&showchangehistorylog=1 | 21-0014549 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 21143 | 20210126 | 1106 | 1226025 | 448 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 448 | 38.6344 | -120.6373 | 1SPANLDSIDEOF21143 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0014549 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Line | 1597189 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0016028&numberofmonths=24&showchangehistorylog=1 | 21-0016028 | SIERRA | FIELD OPS NORTH | Tier 3 | COLUMBIA HILL-1101 | 152471101 | FUSE | 4373 | 20210126 | 2340 | 1230775 | 759 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 27324 | 39.3823 | -121.0478 | 19177SAGESRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0016028 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Line | 1598513 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0016180&numberofmonths=24&showchangehistorylog=1 | 21-0016180 | SIERRA | FIELD OPS NORTH | Tier 3 | PIKE CITY-1101 | 152201101 | FUSE | 8203 | 20210126 | 2340 | 1230882 | 1030 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 89610 | 39.4387 | -120.9996 | SAPID100096405 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0016180 | OH | Sus | 0 | No | 2021 | JAN | Yes | Three Phase Fault | 1598635 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0015917&numberofmonths=24&showchangehistorylog=1 | 21-0015917 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 21315 | 20210127 | 928 | 1234435 | 332 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 9494 | 38.6196 | -120.7647 | 2SPANSSOF13267 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0015917 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1598429 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0015947&numberofmonths=24&showchangehistorylog=1 | 21-0015947 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 21457 | 20210127 | 915 | 1234584 | 487 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 36259 | 38.5732 | -120.7145 | FU21457 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0015947 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1598452 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0016139&numberofmonths=24&showchangehistorylog=1 | 21-0016139 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 12319 | 20210127 | 1044 | 1235118 | 426 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 6816 | 38.6221 | -120.7394 | 4290RANCHOMANTES | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0016139 | OH | Sus | 0 | No | 2021 | JAN | Yes | Force Out | 1598604 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0015601&numberofmonths=24&showchangehistorylog=1 | 21-0015601 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2102 | 152762102 | RECLOSER | 19542 | 20210127 | 331 | 1232541 | 633 | Distribution Circuit | Vegetation | Tree - fell into line | 618 | 225024 | 38.7617 | -120.5776 | 3WESTOF19542 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0015601 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1598152 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0015807&numberofmonths=24&showchangehistorylog=1 | 21-0015807 | SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE | 477265 | 20210127 | 331 | 1232550 | 917 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 14672 | 38.7406 | -120.5821 | CGC224060539450 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0015807 | OH | Sus | 0 | No | 2021 | JAN | Yes | Force Out | 1598341 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0016007&numberofmonths=24&showchangehistorylog=1 | 21-0016007 | SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1107 | 152691107 | FUSE | 3533 | 20210127 | 819 | 1233887 | 341 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 1991 | 39.0175 | -121.0603 | 27631TABLEMEADOWRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0016007 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1598497 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0015704&numberofmonths=24&showchangehistorylog=1 | 21-0015704 | SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2105 | 153132105 | FUSE | 4717 | 20210127 | 157 | 1232043 | 629 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 33337 | 39.1675 | -121.1419 | 3SPANSNO4717 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0015704 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1598254 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0016189&numberofmonths=24&showchangehistorylog=1 | 21-0016189 | SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 6679 | 20210127 | 649 | 1233327 | 546 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 15352 | 38.7109 | -120.9446 | 2580PONDOROSAWAY | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0016189 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1598644 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0018068&numberofmonths=24&showchangehistorylog=1 | 21-0018068 | SIERRA | FIELD OPS NORTH | Tier 3 | BONNIE NOOK-1102 | 152301102 | RECLOSER | 11022 | 20210128 | 2244 | 1240766 | 1052 | Distribution Circuit | Vegetation | Tree - fell into line | 362 | 363083 | 39.214 | -120.8098 | MTR1004588260 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0018068 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1600089 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0017673&numberofmonths=24&showchangehistorylog=1 | 21-0017673 | SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 31233 | 20210128 | 1000 | 1239227 | 685 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 3425 | 38.9501 | -120.7165 | SAPID100038691 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0017673 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Line | 1599760 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0018317&numberofmonths=24&showchangehistorylog=1 | 21-0018317 | SIERRA | FIELD OPS NORTH | Tier 2 | SPAULDING-1101 | 152251101 | OTHER | WIREDOWN35859 | 20210128 | 1730 | 1241215 | 2766 | Distribution Circuit | Equipment Failure/Involved | Overhead | 85 | 116422 | 39.3133 | -120.6535 | 35859 | Snow-Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0018317 | OH | Sus | 0 | No | 2021 | JAN | Yes | Open Circuit | 1600277 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0115798&numberofmonths=24&showchangehistorylog=1 | 21-0115798 | SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2110 | 153652110 | RECLOSER | 51800 | 20210910 | 813 | 1467728 | 633 | Distribution Circuit | 3rd Party | Vehicle | 1005 | 313378 | 38.6635 | -120.9306 | 4SPANSSOF20199 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0115798 | OH | Sus | 0 | No | 2021 | SEP | Yes | Line to Line | 1664706 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0128898&numberofmonths=24&showchangehistorylog=1 | 21-0128898 | SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2110 | 153652110 | RECLOSER | 51800 | 20211011 | 1247 | 1493339 | 449 | Distribution Circuit | Vegetation | Tree - fell into line | 1005 | 214783 | 38.6635 | -120.9306 | FULTONERIC2eo4390MonarchLnShinglesprings | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 21-0128898 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Ground | 1672974 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0135853&numberofmonths=24&showchangehistorylog=1 | 21-0135853 | SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1101 | 152241101 | RECLOSER | 1704 | 20211024 | 934 | 1508700 | 477 | Distribution Circuit | Vegetation | Tree - fell into line | 452 | 125384 | 38.9945 | -121.026 | MTR1004688571 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0135853 | OH | Sus | 0 | No | 2021 | OCT | Yes | Three Phase Fault | 1677325 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0135774&numberofmonths=24&showchangehistorylog=1 | 21-0135774 | SIERRA | FIELD OPS NORTH | Tier 2 | WEIMAR-1101 | 152491101 | RECLOSER | 2058 | 20211024 | 840 | 1508811 | 85 | Distribution Circuit | Vegetation | Tree - fell into line | 317 | 26945 | 39.0443 | -120.9859 | 2EOF15491 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0135774 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Line | 1677251 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0137022&numberofmonths=24&showchangehistorylog=1 | 21-0137022 | SIERRA | FIELD OPS NORTH | Tier 2 | SHINGLE SPRINGS-2110 | 153652110 | RECLOSER | 7742 | 20211025 | 853 | 1517847 | 1544 | Distribution Circuit | Vegetation | Tree - fell into line | 1004 | 287188 | 38.6615 | -120.9109 | TROTTERLNBRAMBLEWOODLN | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0137022 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Ground | 1678479 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0157144&numberofmonths=24&showchangehistorylog=1 | 21-0157144 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | RECLOSER | 8372 | 20211213 | 1120 | 1566809 | 457 | Distribution Circuit | Equipment Failure/Involved | Overhead | 718 | 183289 | 38.6091 | -120.7023 | 5SPANSLDSIDEOFSB18043 | Strong Winds-Clear-32-90F | Pole-Wood | Broken, wire on ground | 21-0157144 | OH | Sus | 0 | No | 2021 | DEC | Yes | Three Phase Fault | 1694044 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0157378&numberofmonths=24&showchangehistorylog=1 | 21-0157378 | SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1101 | 152241101 | FUSE | 35281 | 20211213 | 1415 | 1567530 | 240 | Distribution Circuit | Vegetation | Tree - branch fell on line | 120 | 28800 | 39.0047 | -121.034 | 1SPLDSIDEOFCOUT35281 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0157378 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1694281 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0156929&numberofmonths=24&showchangehistorylog=1 | 21-0156929 | SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1104 | 152691104 | OTHER | WIREDOWN17197NORLENEWAY | 20211213 | 454 | 1565722 | 310 | Distribution Circuit | Vegetation | Tree - branch fell on line | 967 | 137701 | 39.1272 | -121.0561 | FEDERMEYERROBERT91664232617197NorleneWay | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0156929 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1693819 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0157672&numberofmonths=24&showchangehistorylog=1 | 21-0157672 | SIERRA | FIELD OPS NORTH | Tier 2 | PLACERVILLE-2106 | 153082106 | RECLOSER | 23190 | 20211213 | 2348 | 1569127 | 1296 | Distribution Circuit | Vegetation | Tree - fell into line | 1994 | 1735810 | 38.7384 | -120.7798 | MYERSSTEVEN7074385171MULTIPLELOCATIONS | Clear-32-90F | Crossarm, Wood | Broken, wire on ground | 21-0157672 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1694568 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0157855&numberofmonths=24&showchangehistorylog=1 | 21-0157855 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-1104 | 153661104 | OTHER | WIREDOWNCAUSING18473TOBLOW | 20211214 | 417 | 1570166 | 575 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 8061 | 38.7183 | -120.7082 | 3170PIONEERHILLROAD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0157855 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1694759 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0157812&numberofmonths=24&showchangehistorylog=1 | 21-0157812 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 7097 | 20211214 | 136 | 1569234 | 862 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 12068 | 39.1728 | -120.9911 | 14744MEADOWDR | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0157812 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1694713 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0157773&numberofmonths=24&showchangehistorylog=1 | 21-0157773 | SIERRA | FIELD OPS NORTH | Tier 3 | COLUMBIA HILL-1101 | 152471101 | OCB | 11012 | 20211214 | 450 | 1569628 | 721 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 66859 | 39.3313 | -121.1015 | RAGGIOJAMES22607pleasantvalleyrd | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0157773 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1694673 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0158005&numberofmonths=24&showchangehistorylog=1 | 21-0158005 | SIERRA | FIELD OPS NORTH | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 9387 | 20211214 | 353 | 1569500 | 1024 | Distribution Circuit | Vegetation | Tree - branch fell on line | 87 | 78316 | 38.9239 | -120.9071 | IRENEANDSYD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0158005 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Line | 1694927 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0157844&numberofmonths=24&showchangehistorylog=1 | 21-0157844 | SIERRA | FIELD OPS NORTH | Tier 2 | WEIMAR-1101 | 152491101 | FUSE | 6109 | 20211214 | 333 | 1569465 | 551 | Distribution Circuit | Vegetation | Tree - fell into line | 123 | 67773 | 39.0425 | -120.9722 | LINEBETWEEN33905AND33907 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0157844 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1694743 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0157901&numberofmonths=24&showchangehistorylog=1 | 21-0157901 | SIERRA | FIELD OPS NORTH | Tier 2 | WEIMAR-1101 | 152491101 | FUSE | 6193 | 20211214 | 441 | 1569610 | 688 | Distribution Circuit | Vegetation | Tree - fell into line | 97 | 54751 | 39.0715 | -120.9763 | 1SSOF33997 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0157901 | OH | Sus | 0 | No | 2021 | DEC | Yes | Three Phase Fault | 1694820 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0158094&numberofmonths=24&showchangehistorylog=1 | 21-0158094 | SIERRA | FIELD OPS NORTH | Tier 2 | WEIMAR-1101 | 152491101 | FUSE | 6125 | 20211214 | 550 | 1569764 | 622 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 32344 | 39.0506 | -120.9622 | 1EOF36513 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0158094 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Line | 1695014 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0158146&numberofmonths=24&showchangehistorylog=1 | 21-0158146 | SIERRA | FIELD OPS NORTH | Tier 2 | WEIMAR-1102 | 152491102 | FUSE | 6103 | 20211214 | 429 | 1569587 | 791 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 25312 | 39.0467 | -120.9968 | 1370SAGERD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0158146 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Line | 1695064 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0160544&numberofmonths=24&showchangehistorylog=1 | 21-0160544 | SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1101 | 152241101 | RECLOSER | 76178 | 20211225 | 920 | 1581205 | 445 | Distribution Circuit | Vegetation | Tree - fell into line | 629 | 48530 | 39.0014 | -121.0224 | 1POLEWOF7021 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0160544 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1698017 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0160561&numberofmonths=24&showchangehistorylog=1 | 21-0160561 | SIERRA | FIELD OPS NORTH | Tier 3 | PIKE CITY-1101 | 152201101 | OTHER | WIREDOWN1NOFCGC222615464625 | 20211225 | 1055 | 1581301 | 297 | Distribution Circuit | Vegetation | Tree - branch fell on line | 139 | 38338 | 39.4373 | -121.0747 | 1SPANNOFCGC222615464625 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0160561 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1698033 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0161237&numberofmonths=24&showchangehistorylog=1 | 21-0161237 | SIERRA | FIELD OPS NORTH | Tier 2 | PLACERVILLE-1112 | 153081112 | JUMPER | OJ2SPANSSOURCESIDEOF12913 | 20211227 | 1905 | 1587223 | 1501 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 15010 | 38.7187 | -120.7815 | 12913 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0161237 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1699052 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0161622&numberofmonths=24&showchangehistorylog=1 | 21-0161622 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 6693 | 20211229 | 1125 | 1588393 | 480 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 11040 | 39.2001 | -121.0107 | ldsideoffusesmultiplelocations | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0161622 | OH | Sus | 0 | No | 2021 | DEC | Yes | None | 1699441 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0107108&numberofmonths=24&showchangehistorylog=1 | 22-0107108 | SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | RECLOSER | 12392 | 20220907 | 151 | 1803884 | 726 | Distribution Circuit | Equipment Failure/Involved | Overhead | 870 | 450048 | 38.7121 | -120.9501 | COLLINSJEFF2357SkinnerRd | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0107108 | OH | Sus | 0 | No | 2022 | SEP | Yes | Line to Ground | 1766601 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0138129&numberofmonths=24&showchangehistorylog=1 | 22-0138129 | SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | JUMPER | WIREDOWNATMTR1009711651 | 20221210 | 721 | 1880431 | 432 | Distribution Circuit | Vegetation | Tree - fell into line | 1224 | 41105 | 38.6238 | -120.7529 | MTR1009711651 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 22-0138129 | OH | Sus | 0 | No | 2022 | DEC | Yes | Open Circuit | 1788961 | PW | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0138498&numberofmonths=24&showchangehistorylog=1 | 22-0138498 | SIERRA | FIELD OPS NORTH | Tier 2 | WEIMAR-1101 | 152491101 | FUSE | 8463 | 20221210 | 1246 | 1882399 | 355 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 18105 | 39.0463 | -120.9816 | 21415SNOOKSRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0138498 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Line | 1789327 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0142451&numberofmonths=24&showchangehistorylog=1 | 22-0142451 | SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 22399 | 20221231 | 1 | 1902894 | 656 | Distribution Circuit | Vegetation | Tree - fell into line | 293 | 100678 | 38.686 | -120.6419 | 1SPSSOF6623 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0142451 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1794249 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0004228&numberofmonths=24&showchangehistorylog=1 | 23-0004228 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1103 | 152481103 | FUSE | 4693 | 20221231 | 2253 | 1907455 | 1003 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 6018 | 39.2859 | -121.0059 | SHADEBRIAN530362205211846honeysuckleway | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0004228 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Line | 1794820 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0007275&numberofmonths=24&showchangehistorylog=1 | 23-0007275 | SIERRA | FIELD OPS NORTH | Tier 2 | BRUNSWICK-1106 | 152481106 | JUMPER | WIREDOWNCGC222859652943 | 20230105 | 1000 | 1921585 | 280 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1073 | 39.1158 | -120.9939 | CGC222859652943 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0007275 | OH | Sus | 0 | No | 2023 | JAN | Yes | Open Circuit | 1797541 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0010209&numberofmonths=24&showchangehistorylog=1 | 23-0010209 | SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1107 | 152691107 | FUSE | 9901 | 20230108 | 115 | 1931567 | 1133 | Distribution Circuit | Vegetation | Tree - fell into line | 107 | 101833 | 39.0041 | -121.055 | 15797MCELROYRD | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0010209 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Line | 1800060 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0009910&numberofmonths=24&showchangehistorylog=1 | 23-0009910 | SIERRA | FIELD OPS NORTH | Tier 2 | HORSESHOE-1101 | 152571101 | FUSE | 3861 | 20230108 | 27 | 1930945 | 938 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 46900 | 38.7827 | -121.1456 | 5500MOSSLNGRANITEBAY | Clear-32-90F | Pole-Wood | Broken, wire on ground | 23-0009910 | OH | Sus | 0 | No | 2023 | JAN | Yes | Three Phase Fault | 1799761 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0010014&numberofmonths=24&showchangehistorylog=1 | 23-0010014 | SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2105 | 153132105 | FUSE | 7227 | 20230108 | 724 | 1932516 | 616 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 8624 | 39.2305 | -121.1361 | CGC222444056970 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0010014 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1799859 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0010224&numberofmonths=24&showchangehistorylog=1 | 23-0010224 | SIERRA | FIELD OPS NORTH | Tier 2 | PENRYN-1105 | 152561105 | FUSE | 69443 | 20230108 | 102 | 1931466 | 1186 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 41510 | 38.8649 | -121.1526 | CGC222421943610TOEOL | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0010224 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Line | 1800074 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0010749&numberofmonths=24&showchangehistorylog=1 | 23-0010749 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1103 | 152481103 | RECLOSER | 173934 | 20230109 | 338 | 1935489 | 857 | Distribution Circuit | Vegetation | Tree - fell into line | 471 | 142317 | 39.2841 | -121.0236 | FUCO33619 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0010749 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1800615 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0011137&numberofmonths=24&showchangehistorylog=1 | 23-0011137 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 7055 | 20230109 | 646 | 1936288 | 664 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 14608 | 39.1909 | -120.9915 | 1SPANLDSIDEOFCGC222864055725 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0011137 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1800945 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0011369&numberofmonths=24&showchangehistorylog=1 | 23-0011369 | SIERRA | FIELD OPS NORTH | Tier 3 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 5891 | 20230109 | 1427 | 1938448 | 211 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 3413 | 38.8911 | -120.8621 | 1SPLDSD5891 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0011369 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1801138 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0011078&numberofmonths=24&showchangehistorylog=1 | 23-0011078 | SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-1110 | 153081110 | OTHER | WIREDOWNLSOFCGC223397939251 | 20230109 | 332 | 1937719 | 934 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 28190 | 38.739 | -120.8097 | 864OAKTERRACERD | Overcast-Fog-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0011078 | OH | Sus | 0 | No | 2023 | JAN | Yes | Open Circuit | 1800893 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0012259&numberofmonths=24&showchangehistorylog=1 | 23-0012259 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE | 7371 | 20230110 | 430 | 1942234 | 854 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 15242 | 39.2788 | -120.9795 | 1LDSIDECGC222852258728 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0012259 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Line | 1802016 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0012039&numberofmonths=24&showchangehistorylog=1 | 23-0012039 | SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 2167 | 20230110 | 421 | 1941946 | 577 | Distribution Circuit | Vegetation | Tree - fell into line | 123 | 70971 | 38.6701 | -120.7775 | 20433 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0012039 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Line | 1801821 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0012871&numberofmonths=24&showchangehistorylog=1 | 23-0012871 | SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | OTHER | WIREDOWNLDSIDE583890TWD223579337115 | 20230110 | 513 | 1942622 | 2063 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 3024 | 38.6782 | -120.7459 | WIREDOWN2LDSIDEOF583890TWDCGC223579337115 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 23-0012871 | OH | Sus | 0 | No | 2023 | JAN | Yes | Open Circuit | 1802447 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0012209&numberofmonths=24&showchangehistorylog=1 | 23-0012209 | SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1107 | 152261107 | OTHER | WIREDOWNCGC223188638303 | 20230110 | 413 | 1941636 | 502 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 4729 | 38.7129 | -120.8831 | CGC223188638303 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0012209 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1801971 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0012056&numberofmonths=24&showchangehistorylog=1 | 23-0012056 | SIERRA | FIELD OPS NORTH | Tier 2 | GRASS VALLEY-1103 | 152031103 | FUSE | 7847 | 20230110 | 422 | 1943827 | 634 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 15216 | 39.1984 | -121.0934 | 1SPANLDSIDE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0012056 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1801836 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0012101&numberofmonths=24&showchangehistorylog=1 | 23-0012101 | SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1104 | 152691104 | TRIP-SAVER | 4281 | 20230110 | 423 | 1942026 | 806 | Distribution Circuit | Vegetation | Tree - fell into line | 134 | 29294 | 39.0914 | -121.0565 | CGC222752552365 | Partly Cloudy-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0012101 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1801874 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0011872&numberofmonths=24&showchangehistorylog=1 | 23-0011872 | SIERRA | FIELD OPS NORTH | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 1130 | 20230110 | 421 | 1941932 | 609 | Distribution Circuit | Vegetation | Tree - fell into line | 291 | 177219 | 38.9127 | -120.9157 | SAPID100087421 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0011872 | OH | Sus | 0 | No | 2023 | JAN | Yes | Three Phase Fault | 1801639 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0011894&numberofmonths=24&showchangehistorylog=1 | 23-0011894 | SIERRA | FIELD OPS NORTH | Tier 2 | PENRYN-1103 | 152561103 | RECLOSER | 604 | 20230110 | 407 | 1941623 | 786 | Distribution Circuit | Vegetation | Tree - fell into line | 782 | 119325 | 38.8544 | -121.1507 | CGC222474743381 | Partly Cloudy-Drizzle-32-90 F | Transformer (OH) | Broken, wire on ground | 23-0011894 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1801662 | TXO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0011997&numberofmonths=24&showchangehistorylog=1 | 23-0011997 | SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 11707 | 20230110 | 659 | 1941600 | 364 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 7644 | 38.6924 | -120.9238 | 1SPANLDSIDE223081337566 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0011997 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1801773 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0012045&numberofmonths=24&showchangehistorylog=1 | 23-0012045 | SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2110 | 153652110 | FUSE | 22355 | 20230110 | 518 | 1942642 | 585 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 10530 | 38.6321 | -120.9241 | CGC223079735461 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0012045 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1801828 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0016026&numberofmonths=24&showchangehistorylog=1 | 23-0016026 | SIERRA | FIELD OPS NORTH | Tier 2 | WISE-1102 | 152271102 | RECLOSER | 2054 | 20230114 | 955 | 1953769 | 663 | Distribution Circuit | Vegetation | Tree - fell into line | 315 | 24801 | 38.8964 | -121.1202 | 2WO5553TWDCGC222432445449 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0016026 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Line | 1804842 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0031476&numberofmonths=24&showchangehistorylog=1 | 23-0031476 | SIERRA | FIELD OPS NORTH | Tier 3 | DIAMOND SPRINGS-1107 | 152261107 | FUSE | 20791 | 20230221 | 1453 | 1991982 | 643 | Distribution Circuit | 3rd Party | Vehicle | 44 | 28292 | 38.7304 | -120.9223 | 1EOFCGC223096838778 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 23-0031476 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Line | 1815109 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0033780&numberofmonths=24&showchangehistorylog=1 | 23-0033780 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE | 7371 | 20230224 | 519 | 2003069 | 499 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 15469 | 39.2788 | -120.9795 | 2SPANSLDSIDEOF7371 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 23-0033780 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Ground | 1816800 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0034000&numberofmonths=24&showchangehistorylog=1 | 23-0034000 | SIERRA | FIELD OPS NORTH | Tier 2 | BRUNSWICK-1106 | 152481106 | FUSE | 7669 | 20230224 | 943 | 2004823 | 306 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 6263 | 39.1527 | -121.0381 | SHADEBRIAN530362205211698Myrnadr | Clear-32-90F | Transformer (OH) | Broken, wire on ground | 23-0034000 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Ground | 1816972 | TXO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0034159&numberofmonths=24&showchangehistorylog=1 | 23-0034159 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 9483 | 20230224 | 1217 | 2005329 | 350 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2100 | 39.1902 | -120.9675 | 4SPANSLDSIDE9483 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0034159 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Line | 1817080 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0033760&numberofmonths=24&showchangehistorylog=1 | 23-0033760 | SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1103 | 152691103 | RECLOSER | 995672 | 20230224 | 727 | 2003780 | 290 | Distribution Circuit | Equipment Failure/Involved | Overhead | 337 | 63124 | 39.1336 | -121.0717 | 10348quailcreekrd | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 23-0033760 | OH | Sus | 0 | No | 2023 | FEB | Yes | Multi-Fault | 1816786 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0034037&numberofmonths=24&showchangehistorylog=1 | 23-0034037 | SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1104 | 152691104 | FUSE | 35323 | 20230224 | 1054 | 2004949 | 383 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 766 | 39.096 | -121.0531 | LASTSPANLDSIDEOFFU35323 | Clear-32-90F | Transformer (OH) | Broken, wire on ground | 23-0034037 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Ground | 1816998 | TXO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0034322&numberofmonths=24&showchangehistorylog=1 | 23-0034322 | SIERRA | FIELD OPS NORTH | Tier 3 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 8571 | 20230224 | 1336 | 2005689 | 211 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 1477 | 38.9018 | -120.8612 | 1SSOFCGC223239545155 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0034322 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Line | 1817197 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0033884&numberofmonths=24&showchangehistorylog=1 | 23-0033884 | SIERRA | FIELD OPS NORTH | Tier 2 | PENRYN-1107 | 152561107 | FUSE | 38443 | 20230224 | 407 | 2002443 | 548 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1644 | 38.7963 | -121.1342 | CGC222471641227 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0033884 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Line | 1816884 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0034492&numberofmonths=24&showchangehistorylog=1 | 23-0034492 | SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 1445 | 20230224 | 1534 | 2006036 | 331 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 4634 | 38.8109 | -120.8052 | SAP101416835 | Clear-32-90 F | Conductor, Overhead | On Ground | 23-0034492 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Line | 1817341 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0036049&numberofmonths=24&showchangehistorylog=1 | 23-0036049 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1103 | 152481103 | RECLOSER | 2200 | 20230226 | 2342 | 2011101 | 752 | Distribution Circuit | Vegetation | Tree - fell into line | 114 | 56772 | 39.275 | -121.021 | SHADEBRIAN530362205212463northBloomfieldrd | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0036049 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Ground | 1818854 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0035924&numberofmonths=24&showchangehistorylog=1 | 23-0035924 | SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1103 | 152691103 | FUSE | 8175 | 20230226 | 1711 | 2010410 | 307 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 3684 | 39.1125 | -121.1435 | 2NDSPANLDSIDEOF8175 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0035924 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Line | 1818737 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0036136&numberofmonths=24&showchangehistorylog=1 | 23-0036136 | SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 33795 | 20230227 | 10 | 2011109 | 836 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2508 | 39.1997 | -121.0106 | LASTSPANOFTAP | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0036136 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Line | 1818897 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0036534&numberofmonths=24&showchangehistorylog=1 | 23-0036534 | SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1103 | 152691103 | FUSE | 9741 | 20230227 | 1306 | 2012384 | 251 | Distribution Circuit | Vegetation | Tree - fell into line | 129 | 32379 | 39.1038 | -121.0843 | SHADEBRIAN530362205210369oakdr | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0036534 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Line | 1819124 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0036485&numberofmonths=24&showchangehistorylog=1 | 23-0036485 | SIERRA | FIELD OPS NORTH | Tier 2 | PLACERVILLE-1112 | 153081112 | SWITCH | 774186 | 20230227 | 1348 | 2012573 | 375 | Distribution Circuit | Vegetation | Tree - fell into line | 1238 | 175580 | 38.7259 | -120.7943 | ATMTR1007048567 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0036485 | OH | Sus | 0 | No | 2023 | FEB | Yes | Three Phase Fault | 1819094 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0045246&numberofmonths=24&showchangehistorylog=1 | 23-0045246 | SIERRA | FIELD OPS NORTH | Tier 2 | PLACERVILLE-2106 | 153082106 | FUSE | 5837 | 20230314 | 1208 | 2038155 | 276 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2208 | 38.8578 | -120.8381 | CGC223311043736 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0045246 | OH | Sus | 0 | No | 2023 | MAR | Yes | Three Phase Fault | 1825271 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0044842&numberofmonths=24&showchangehistorylog=1 | 23-0044842 | SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | RECLOSER | 61892 | 20230314 | 1132 | 2037179 | 469 | Distribution Circuit | Vegetation | Tree - fell into line | 409 | 108741 | 38.7121 | -120.9501 | 2SPANSWESTEASTOF20463 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0044842 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Line | 1824952 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0045110&numberofmonths=24&showchangehistorylog=1 | 23-0045110 | SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 8145 | 20230314 | 1129 | 2037159 | 209 | Distribution Circuit | Vegetation | Tree - fell into line | 190 | 39710 | 38.6977 | -120.9365 | 2NOFCGC223055037560 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0045110 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1825166 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0022201&numberofmonths=24&showchangehistorylog=1 | 13-0022201 | SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 779 | 20130408 | 453 | 768788 | 2509 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 110396 | 38.5969 | -122.9891 | 4SPANSLOADSIDEOF779 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0022201 | OH | Sus | 0 | yes | 2013 | APR | Yes | Line to Line | 99291792 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0022686&numberofmonths=24&showchangehistorylog=1 | 13-0022686 | SONOMA | FIELD OPS NORTH | Tier 3 | FORT ROSS-1121 | 42851121 | OTHER |  | 20130408 | 1611 | 770677 | 399 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 399 | 38.5255 | -123.1189 | BEYONDMTR1007687472 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0022686 | OH | Sus | 0 | yes | 2013 | APR | Yes | None | 99291952 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0022819&numberofmonths=24&showchangehistorylog=1 | 13-0022819 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1101 | 42091101 | SWITCH | 90299 | 20130408 | 2218 | 771228 | 282 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 17484 | 38.4803 | -122.9089 | 1SPANSSOF80157777MARTINELLIRD | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on object | 13-0022819 | OH | Sus | 0 | yes | 2013 | APR | Yes | None | 99291845 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0022175&numberofmonths=24&showchangehistorylog=1 | 13-0022175 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 7401 | 20130408 | 136 | 768287 | 619 | Distribution Circuit | Vegetation | Tree - fell into line | 66 | 40854 | 38.5037 | -122.9486 | 2PSSOFFUCOS12997 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0022175 | OH | Sus | 0 | yes | 2013 | APR | Yes |  | 99292329 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078169&numberofmonths=24&showchangehistorylog=1 | 13-0078169 | SONOMA | FIELD OPS NORTH | Tier 2 | GEYSERVILLE-1102 | 42891102 | SWITCH | 12751 | 20131121 | 2045 | 909300 | 420 | Distribution Circuit | Equipment Failure/Involved | Other | 6 | 2520 | 38.6952 | -122.8568 | ATLR756 | Clear-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 13-0078169 | OH | Sus | 0 | yes | 2013 | NOV | Yes |  | 99251941 | CSO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078591&numberofmonths=24&showchangehistorylog=1 | 13-0078591 | SONOMA | FIELD OPS NORTH | Tier 3 | GEYSERVILLE-1102 | 42891102 | FUSE | 735 | 20131121 | 1940 | 907687 | 3995 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 35955 | 38.8024 | -122.8325 |  | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078591 | OH | Sus | 0 | yes | 2013 | NOV | Yes | None | 99250915 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078339&numberofmonths=24&showchangehistorylog=1 | 13-0078339 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 2379 | 20131121 | 1816 | 909415 | 2519 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 103279 | 38.5016 | -122.9308 | BEYONDFUCOS2379 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078339 | OH | Sus | 0 | yes | 2013 | NOV | Yes | Line to Ground | 99251240 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078018&numberofmonths=24&showchangehistorylog=1 | 13-0078018 | SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | FUSE | 2225 | 20131121 | 1624 | 907529 | 424 | Distribution Circuit | Equipment Failure/Involved | Other | 90 | 38160 | 38.524 | -122.6538 | WIREDOWNAT3174CALISTOGARD | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078018 | OH | Sus | 0 | yes | 2013 | NOV | Yes | Line to Line | 99252032 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078555&numberofmonths=24&showchangehistorylog=1 | 13-0078555 | SONOMA | FIELD OPS NORTH | Tier 2 | CLOVERDALE-1101 | 42821101 | FUSE | 7373 | 20131122 | 943 | 911852 | 1518 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 36432 | 38.7941 | -123.0286 | SAME | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078555 | OH | Sus | 0 | yes | 2013 | NOV | Yes | Line to Ground | 99251221 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078403&numberofmonths=24&showchangehistorylog=1 | 13-0078403 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1101 | 42091101 | OTHER |  | 20131122 | 812 | 911278 | 543 | Distribution Circuit | Equipment Failure/Involved | Other | 1 | 543 | 38.475 | -122.9487 |  | Clear-32 - 90 F | Other | Broken, wire on object | 13-0078403 | OH | Sus | 0 | yes | 2013 | NOV | Yes | None | 99251639 | NON | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078767&numberofmonths=24&showchangehistorylog=1 | 13-0078767 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 841 | 20131122 | 1659 | 912782 | 1278 | Distribution Circuit | Vegetation | Tree - branch fell on line | 134 | 169952 | 38.5086 | -122.9263 | Galea3472MULTIPLELOCLOADSIDEOFCO841 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078767 | OH | Sus | 0 | yes | 2013 | NOV | Yes |  | 99251197 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078815&numberofmonths=24&showchangehistorylog=1 | 13-0078815 | SONOMA | FIELD OPS NORTH | Tier 2 | PENNGROVE-1101 | 43471101 | FUSE | 9875 | 20131122 | 1947 | 913093 | 583 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 5247 | 38.3288 | -122.6284 | 2SPFROMEOLLDSIDEOFFUSE9875 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078815 | OH | Sus | 0 | yes | 2013 | NOV | Yes | Line to Ground | 99251415 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0073417&numberofmonths=24&showchangehistorylog=1 | 14-0073417 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | FUSE | 2883 | 20141203 | 1208 | 1122972 | 252 | Distribution Circuit | Vegetation | Tree - branch fell on line | 39 | 9828 | 38.275 | -122.7158 | 2SPANSLDSIDEOF2883GOINGWEST | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073417 | OH | Sus | 0 | yes | 2014 | DEC | Yes | None | 99196815 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0073428&numberofmonths=24&showchangehistorylog=1 | 14-0073428 | SONOMA | FIELD OPS NORTH | Tier 3 | DUNBAR-1103 | 43071103 | FUSE | 3075 | 20141203 | 1050 | 1122427 | 406 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 6496 | 38.3867 | -122.4877 | 12359MANZANITA | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073428 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99196808 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0073573&numberofmonths=24&showchangehistorylog=1 | 14-0073573 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 1045 | 20141203 | 1503 | 1123301 | 587 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 39329 | 38.5008 | -122.9053 | 9470WESTSIDERD | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073573 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99196697 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0073321&numberofmonths=24&showchangehistorylog=1 | 14-0073321 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | OTHER |  | 20141203 | 1009 | 1122245 | 324 | Distribution Circuit | Vegetation | Tree - branch fell on line | 687 | 109791 | 38.4856 | -123.0583 | MAINLINEBETFUCO2197CAPBK978 | Heavy rain-32 - 90 F | Conductor, Overhead | On Ground | 14-0073321 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99196872 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0074824&numberofmonths=24&showchangehistorylog=1 | 14-0074824 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1105 | 42271105 | SECTIONALIZER | 244 | 20141211 | 46 | 1128815 | 276 | Distribution Circuit | Equipment Failure/Involved | Other | 360 | 89341 | 38.3456 | -122.7783 | 1SPANSSOF244 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074824 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194414 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075304&numberofmonths=24&showchangehistorylog=1 | 14-0075304 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1105 | 42271105 | OTHER |  | 20141211 | 534 | 1132514 | 926 | Distribution Circuit | Equipment Failure/Involved | Other | 489 | 384387 | 38.321 | -122.7787 | 5170ROBLARRD | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075304 | OH | Sus | 0 | yes | 2014 | DEC | Yes | None | 99194362 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0074797&numberofmonths=24&showchangehistorylog=1 | 14-0074797 | SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER | 124 | 20141211 | 28 | 1128777 | 2252 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 18310 | 38.5656 | -123.2726 | INGRAMJEFF431404SEAVIEWRD | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074797 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99193590 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0074867&numberofmonths=24&showchangehistorylog=1 | 14-0074867 | SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | OCB | OCB | 20141211 | 303 | 1128916 | 1115 | Distribution Circuit | Vegetation | Tree - fell into line | 462 | 461704 | 38.5398 | -123.2236 | INGRAMJEFF4350DANOHARD | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074867 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99194404 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075623&numberofmonths=24&showchangehistorylog=1 | 14-0075623 | SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE | 2699 | 20141211 | 1008 | 1134366 | 1827 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 60291 | 38.543 | -123.2894 | HWY1 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075623 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99194315 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075869&numberofmonths=24&showchangehistorylog=1 | 14-0075869 | SONOMA | FIELD OPS NORTH | Tier 3 | FORT ROSS-1121 | 42851121 | FUSE | 2989 | 20141211 | 2051 | 1136039 | 1299 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 5196 | 38.5328 | -123.1349 | BEYONDFUCOS2989 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075869 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99194248 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075482&numberofmonths=24&showchangehistorylog=1 | 14-0075482 | SONOMA | FIELD OPS NORTH | Tier 2 | GEYSERVILLE-1101 | 42891101 | OTHER |  | 20141211 | 840 | 1131721 | 1595 | Distribution Circuit | Equipment Failure/Involved | Other | 1 | 1595 | 38.72 | -122.926 | 1SPANDOWNSSD13015 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 14-0075482 | OH | Sus | 0 | yes | 2014 | DEC | Yes |  | 99194339 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0074821&numberofmonths=24&showchangehistorylog=1 | 14-0074821 | SONOMA | FIELD OPS NORTH | Tier 2 | MIRABEL-1101 | 42091101 | FUSE | 1003 | 20141211 | 47 | 1128802 | 2373 | Distribution Circuit | Vegetation | Tree - fell into line | 76 | 152658 | 38.4762 | -122.9068 | HWY116 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074821 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99194415 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075419&numberofmonths=24&showchangehistorylog=1 | 14-0075419 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1101 | 42091101 | FUSE | 4859 | 20141211 | 632 | 1131265 | 1423 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 65458 | 38.4755 | -122.9524 | 10SPANSLOADSIDEOF4859 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075419 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99194350 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0074817&numberofmonths=24&showchangehistorylog=1 | 14-0074817 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 1499 | 20141211 | 108 | 1128864 | 430 | Distribution Circuit | Vegetation | Tree - branch fell on line | 132 | 56760 | 38.5088 | -122.9292 | 11091SEQUOIA | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074817 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99193588 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075269&numberofmonths=24&showchangehistorylog=1 | 14-0075269 | SONOMA | FIELD OPS NORTH | Tier 2 | MIRABEL-1102 | 42091102 | FUSE | 13669 | 20141211 | 503 | 1132545 | 1657 | Distribution Circuit | Equipment Failure/Involved | Other | 9 | 14913 | 38.5089 | -122.887 | 5SPLDSIDEOF13669TWD4551 | Heavy rain-32 - 90 F | Conductor, Overhead | On Ground | 14-0075269 | OH | Sus | 0 | yes | 2014 | DEC | Yes | None | 99194363 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0074858&numberofmonths=24&showchangehistorylog=1 | 14-0074858 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 12003 | 20141211 | 52 | 1129030 | 930 | Distribution Circuit | Equipment Failure/Involved | Other | 1317 | 445904 | 38.4107 | -122.9539 | Fechter3471SSLR3184595COLEMANVLYRD | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074858 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Multi-Fault | 99193586 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075353&numberofmonths=24&showchangehistorylog=1 | 14-0075353 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 3053 | 20141211 | 546 | 1133068 | 1483 | Distribution Circuit | Equipment Failure/Involved | Other | 105 | 155715 | 38.4191 | -122.93 | 13393DUPONT | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 14-0075353 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99193569 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075664&numberofmonths=24&showchangehistorylog=1 | 14-0075664 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 18387 | 20141211 | 1602 | 1134777 | 2540 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 5080 | 38.4014 | -122.974 | Fechter34714110JOYRD | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075664 | OH | Sus | 0 | yes | 2014 | DEC | Yes |  | 99193558 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075729&numberofmonths=24&showchangehistorylog=1 | 14-0075729 | SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1102 | 42571102 | FUSE | 525 | 20141211 | 308 | 1131740 | 1338 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 49506 | 38.4048 | -122.8963 | 1380FURLONGRD | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075729 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194660 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075998&numberofmonths=24&showchangehistorylog=1 | 14-0075998 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | RECLOSER | 396 | 20141211 | 604 | 1129964 | 1465 | Distribution Circuit | Equipment Failure/Involved | Other | 227 | 332555 | 38.4097 | -122.9357 | 3SPANSLDSIDEOFLR3962118FACENDINILN | Heavy rain-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0075998 | OH | Sus | 0 | yes | 2014 | DEC | Yes |  | 99193533 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075540&numberofmonths=24&showchangehistorylog=1 | 14-0075540 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | SWITCH | 4477 | 20141211 | 1115 | 1133331 | 502 | Distribution Circuit | Vegetation | Tree - branch fell on line | 210 | 105420 | 38.5262 | -123.0893 | Arvig39705970austincreekrdcazadero | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075540 | OH | Sus | 0 | yes | 2014 | DEC | Yes | None | 99194795 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075605&numberofmonths=24&showchangehistorylog=1 | 14-0075605 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 53477 | 20141211 | 951 | 1132494 | 842 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 47994 | 38.496 | -123.0693 | 11KIDCREEKRDINCAZADERO | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075605 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99194321 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076101&numberofmonths=24&showchangehistorylog=1 | 14-0076101 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 74315 | 20141211 | 6 | 1128755 | 2699 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 53980 | 38.4909 | -123.0602 | 2000CAZADEROHWYMONTERIO | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076101 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99194173 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0074894&numberofmonths=24&showchangehistorylog=1 | 14-0074894 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | OCB | OCB | 20141211 | 405 | 1129219 | 655 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1151 | 583570 | 38.4712 | -123.0121 | Kikuchi151220355FoothillDrMonteRio | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074894 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99194399 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0074859&numberofmonths=24&showchangehistorylog=1 | 14-0074859 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | RECLOSER | 346 | 20141211 | 341 | 1129058 | 852 | Distribution Circuit | Vegetation | Tree - branch fell on line | 468 | 218171 | 38.5042 | -122.9976 | 1137 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074859 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99194408 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0074877&numberofmonths=24&showchangehistorylog=1 | 14-0074877 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 8227 | 20141211 | 334 | 1128950 | 580 | Distribution Circuit | Equipment Failure/Involved | Other | 17 | 9860 | 38.5037 | -123.0301 | 9SPANSLDSIDEOF8227 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074877 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99195297 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075114&numberofmonths=24&showchangehistorylog=1 | 14-0075114 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | RECLOSER | 5026 | 20141211 | 608 | 1130871 | 593 | Distribution Circuit | Vegetation | Tree - fell into line | 288 | 170784 | 38.5 | -122.9924 | Arvig397015095DrakerdGuerneville | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075114 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Three Phase Fault | 99194377 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075014&numberofmonths=24&showchangehistorylog=1 | 14-0075014 | SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1108 | 42631108 | RECLOSER | 296 | 20141211 | 445 | 1129291 | 319 | Distribution Circuit | Vegetation | Tree - fell into line | 119 | 34066 | 38.2073 | -122.6761 | 2SPANSLDSIDEOF62841 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075014 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194386 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075806&numberofmonths=24&showchangehistorylog=1 | 14-0075806 | SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1108 | 42631108 | RECLOSER | 632 | 20141211 | 1219 | 1133696 | 1846 | Distribution Circuit | Equipment Failure/Involved | Other | 80 | 36527 | 38.2724 | -122.8142 | 4680CHILENOVLYRD | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 14-0075806 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Multi-Fault | 99193547 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075375&numberofmonths=24&showchangehistorylog=1 | 14-0075375 | SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | FUSE | 2225 | 20141211 | 519 | 1130725 | 779 | Distribution Circuit | Vegetation | Tree - branch fell on line | 90 | 70110 | 38.524 | -122.6538 | PAGANVICTOR707689344113PLSO22253166CALISTOGARD | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075375 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194917 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076607&numberofmonths=24&showchangehistorylog=1 | 14-0076607 | SONOMA | FIELD OPS NORTH | Tier 2 | SALMON CREEK-1101 | 43161101 | FUSE | 2331 | 20141211 | 707 | 1139324 | 3084 | Distribution Circuit | Vegetation | Tree - bark fell into line | 13 | 40092 | 38.3652 | -123.0707 | 20002COLEMANVALLEYRD | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076607 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99193437 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076165&numberofmonths=24&showchangehistorylog=1 | 14-0076165 | SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1101 | 43071101 | FUSE | 65797 | 20141212 | 430 | 1137036 | 608 | Distribution Circuit | Vegetation | Tree - fell into line | 151 | 91808 | 38.398 | -122.5496 | MTR1007760555 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076165 | OH | Sus | 0 | yes | 2014 | DEC | Yes | None | 99194138 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076514&numberofmonths=24&showchangehistorylog=1 | 14-0076514 | SONOMA | FIELD OPS NORTH | Tier 3 | FORT ROSS-1121 | 42851121 | FUSE | 4523 | 20141212 | 1742 | 1139001 | 448 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 7168 | 38.5363 | -123.14 | 12BLUEJAYRIDGEROADCAZADERO | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076514 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Three Phase Fault | 99193873 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076248&numberofmonths=24&showchangehistorylog=1 | 14-0076248 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 1789 | 20141212 | 753 | 1137435 | 962 | Distribution Circuit | Vegetation | Tree - branch fell on line | 40 | 38480 | 38.4154 | -122.9408 | HUNTDANIELLEOAKTREEFELLONPRIMARYWIRESFUSESBURNEDOUT | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0076248 | OH | Sus | 0 | yes | 2014 | DEC | Yes |  | 99194064 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076336&numberofmonths=24&showchangehistorylog=1 | 14-0076336 | SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1102 | 42571102 | FUSE | 1793 | 20141212 | 838 | 1137618 | 2032 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 25648 | 38.421 | -122.8996 | Deignan357111366 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076336 | OH | Sus | 0 | yes | 2014 | DEC | Yes |  | 99193484 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076360&numberofmonths=24&showchangehistorylog=1 | 14-0076360 | SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1102 | 42571102 | FUSE | 9797 | 20141212 | 827 | 1137572 | 1684 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 35364 | 38.4156 | -122.9003 | MTR1003141999 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076360 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Multi-Fault | 99193479 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076369&numberofmonths=24&showchangehistorylog=1 | 14-0076369 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 883 | 20141212 | 1150 | 1138263 | 555 | Distribution Circuit | Vegetation | Tree - branch fell on line | 92 | 19006 | 38.4075 | -122.9481 | 3SPANSSOURCESIDEOF4895TWD7547 | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076369 | OH | Sus | 0 | yes | 2014 | DEC | Yes | None | 99193972 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076400&numberofmonths=24&showchangehistorylog=1 | 14-0076400 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 12683 | 20141212 | 1022 | 1137969 | 1398 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 1398 | 38.4978 | -122.9696 | 12245HWY116 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076400 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99193472 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076454&numberofmonths=24&showchangehistorylog=1 | 14-0076454 | SONOMA | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | RECLOSER | 87402 | 20141212 | 1235 | 1138438 | 1549 | Distribution Circuit | Equipment Failure/Involved | Other | 36 | 10649 | 38.1635 | -122.8912 | Kikuchi15121700MarshallPetalumaRd | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076454 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99193461 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079356&numberofmonths=24&showchangehistorylog=1 | 14-0079356 | SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1101 | 43071101 | FUSE | 9373 | 20141230 | 1601 | 1153721 | 854 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 11956 | 38.394 | -122.5502 | 1SPANLDSIDEOF9373 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079356 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99190154 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079501&numberofmonths=24&showchangehistorylog=1 | 14-0079501 | SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | FUSE | 17875 | 20141230 | 1530 | 1153449 | 780 | Distribution Circuit | Equipment Failure/Involved | Other | 4 | 3120 | 38.3689 | -122.5397 | LEMYREDEREKUN | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 14-0079501 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99190301 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079275&numberofmonths=24&showchangehistorylog=1 | 14-0079275 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 11985 | 20141230 | 1434 | 1152843 | 690 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 4830 | 38.43 | -122.9307 | 4SPANSLDSIDEOFFUCO11985 | Strong winds-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 14-0079275 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99190461 | CAW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079069&numberofmonths=24&showchangehistorylog=1 | 14-0079069 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | RECLOSER | 202 | 20141230 | 1149 | 1151733 | 499 | Distribution Circuit | Vegetation | Tree - branch fell on line | 113 | 51971 | 38.4983 | -122.9912 | 11860HWY116 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 14-0079069 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Multi-Fault | 99190615 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079106&numberofmonths=24&showchangehistorylog=1 | 14-0079106 | SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1108 | 42631108 | SWITCH | 17557 | 20141230 | 1201 | 1152477 | 616 | Distribution Circuit | Vegetation | Tree - fell into line | 100 | 48667 | 38.264 | -122.7281 | Horner38885570BODEGAAVE | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079106 | OH | Sus | 0 | yes | 2014 | DEC | Yes | None | 99190586 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079131&numberofmonths=24&showchangehistorylog=1 | 14-0079131 | SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | FUSE | 2269 | 20141230 | 1305 | 1152111 | 258 | Distribution Circuit | Vegetation | Tree - branch fell on line | 25 | 6450 | 38.518 | -122.6016 | MTR1004791147 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079131 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99190564 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010115&numberofmonths=24&showchangehistorylog=1 | 15-0010115 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | FUSE | 4125 | 20150206 | 1227 | 1174830 | 368 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 2944 | 38.1881 | -122.9128 | 2SPANSLDSIDEOFFUSE4125 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010115 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99185155 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010559&numberofmonths=24&showchangehistorylog=1 | 15-0010559 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1105 | 42271105 | FUSE | 6563 | 20150206 | 1601 | 1176374 | 485 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 5820 | 38.3217 | -122.7873 | 2SPANSLDSIDE | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010559 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99184889 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010497&numberofmonths=24&showchangehistorylog=1 | 15-0010497 | SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE | 13153 | 20150206 | 1725 | 1176885 | 99 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 297 | 38.5561 | -123.2668 | 1SPANLDSIDEOF13153 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010497 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99184931 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010736&numberofmonths=24&showchangehistorylog=1 | 15-0010736 | SONOMA | FIELD OPS NORTH | Tier 3 | FORT ROSS-1121 | 42851121 | FUSE | 13983 | 20150206 | 1601 | 1176715 | 1684 | Distribution Circuit | Vegetation | Tree - fell into line | 105 | 69900 | 38.5336 | -123.1304 | WIREDOWNNEARFUCO6873AND10179 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010736 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Multi-Fault | 99184555 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010611&numberofmonths=24&showchangehistorylog=1 | 15-0010611 | SONOMA | FIELD OPS NORTH | Tier 3 | FULTON-1107 | 42561107 | FUSE | 3655 | 20150206 | 1618 | 1176570 | 2903 | Distribution Circuit | Equipment Failure/Involved | Other | 33 | 16869 | 38.5595 | -122.691 | 3209FRANZVALLEYRD | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010611 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99183940 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010861&numberofmonths=24&showchangehistorylog=1 | 15-0010861 | SONOMA | FIELD OPS NORTH | Tier 2 | GEYSERVILLE-1101 | 42891101 | FUSE | 5183 | 20150206 | 1742 | 1177023 | 2609 | Distribution Circuit | Vegetation | Tree - fell into line | 72 | 82103 | 38.7113 | -123.0003 | 3SPLDSIDEOFSBCO12427 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010861 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183396 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010966&numberofmonths=24&showchangehistorylog=1 | 15-0010966 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1101 | 42091101 | FUSE | 1027 | 20150206 | 2107 | 1178547 | 1742 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 20904 | 38.4853 | -122.9766 | 5SPANSLDSIDEOFFUCO1027 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 15-0010966 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99184481 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010550&numberofmonths=24&showchangehistorylog=1 | 15-0010550 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 1499 | 20150206 | 1607 | 1176448 | 675 | Distribution Circuit | Vegetation | Tree - branch fell on line | 132 | 89100 | 38.5088 | -122.9292 | 11400MCPEAKRD | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 15-0010550 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99184895 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010595&numberofmonths=24&showchangehistorylog=1 | 15-0010595 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 841 | 20150206 | 1700 | 1176792 | 514 | Distribution Circuit | Equipment Failure/Involved | Other | 133 | 41682 | 38.5086 | -122.9263 | 11086HILLSIDELN | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010595 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99184864 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010694&numberofmonths=24&showchangehistorylog=1 | 15-0010694 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 3041 | 20150206 | 1539 | 1176244 | 2886 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 37518 | 38.3805 | -122.9883 | 2000FITZPATRICKLANE | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010694 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183931 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010802&numberofmonths=24&showchangehistorylog=1 | 15-0010802 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 1525 | 20150206 | 2350 | 1178988 | 1007 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 55385 | 38.4105 | -122.9827 | 17650WILLOWCRKRD18099WILLOWCRKRD | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on object | 15-0010802 | OH | Sus | 0 | yes | 2015 | FEB | Yes | None | 99184538 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010818&numberofmonths=24&showchangehistorylog=1 | 15-0010818 | SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1102 | 42571102 | FUSE | 3437 | 20150206 | 2131 | 1178755 | 1457 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 28193 | 38.4431 | -122.9171 | 11811GREENVLYRD | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 15-0010818 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99184536 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011359&numberofmonths=24&showchangehistorylog=1 | 15-0011359 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 5687 | 20150206 | 2244 | 1181667 | 2358 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 14148 | 38.4076 | -122.9316 | 1SPANLDSIDEOF5687 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011359 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183838 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010163&numberofmonths=24&showchangehistorylog=1 | 15-0010163 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | OTHER |  | 20150206 | 1250 | 1175208 | 377 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 1885 | 38.5104 | -123.07 | 2SPANSLDSIDEOF3889 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010163 | OH | Sus | 0 | yes | 2015 | FEB | Yes | None | 99184643 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010448&numberofmonths=24&showchangehistorylog=1 | 15-0010448 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 3891 | 20150206 | 1440 | 1175912 | 2920 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 90520 | 38.5159 | -123.0644 | 15980EAUSTINCREEKRD4200NAUSTINCRRD | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010448 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99183948 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010655&numberofmonths=24&showchangehistorylog=1 | 15-0010655 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 74315 | 20150206 | 1659 | 1176717 | 761 | Distribution Circuit | Vegetation | Tree - branch fell on line | 20 | 15220 | 38.4909 | -123.0602 | 2SPANLDSIDEOF74315 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010655 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99184836 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010757&numberofmonths=24&showchangehistorylog=1 | 15-0010757 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 2579 | 20150206 | 1704 | 1176749 | 2685 | Distribution Circuit | Equipment Failure/Involved | Other | 11 | 29535 | 38.4982 | -123.0732 | 2SPANSLDSIDEOF2579 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010757 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99183925 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010357&numberofmonths=24&showchangehistorylog=1 | 15-0010357 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | RECLOSER | 652 | 20150206 | 1214 | 1176051 | 1615 | Distribution Circuit | Vegetation | Tree - branch fell on line | 314 | 411978 | 38.5198 | -122.9784 | 14770WILLOWRD | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010357 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99184629 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010626&numberofmonths=24&showchangehistorylog=1 | 15-0010626 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 2055 | 20150206 | 1717 | 1176832 | 630 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 21420 | 38.4939 | -122.9611 | TUNSTALLMONDOST | Strong winds-32 - 90 F | Conductor, Underground | Broken, wire on ground | 15-0010626 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99184851 | CU | UG | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010647&numberofmonths=24&showchangehistorylog=1 | 15-0010647 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 879 | 20150206 | 1600 | 1176515 | 2280 | Distribution Circuit | Vegetation | Tree - branch fell on line | 24 | 54720 | 38.5019 | -123.0041 | RPTSWIREDOWN2SPANSLDSIDEOF879 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010647 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99183936 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010852&numberofmonths=24&showchangehistorylog=1 | 15-0010852 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 8163 | 20150206 | 2214 | 1179148 | 587 | Distribution Circuit | Vegetation | Tree - fell into line | 73 | 42851 | 38.4985 | -123.021 | 4SPANSLDSIDEOF8163 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010852 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99184527 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010414&numberofmonths=24&showchangehistorylog=1 | 15-0010414 | SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1108 | 42631108 | FUSE | 3331 | 20150206 | 1245 | 1175033 | 1030 | Distribution Circuit | Vegetation | Tree - branch fell on line | 20 | 18221 | 38.194 | -122.7091 | Deignan3571286WETMORELN | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010414 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99184620 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010439&numberofmonths=24&showchangehistorylog=1 | 15-0010439 | SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1108 | 42631108 | OTHER |  | 20150206 | 1632 | 1176571 | 48 | Distribution Circuit | Equipment Failure/Involved | Other | 1 | 48 | 38.2517 | -122.7321 | 3770MIDDLETWOROCKRD | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on object | 15-0010439 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99184968 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010464&numberofmonths=24&showchangehistorylog=1 | 15-0010464 | SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1108 | 42631108 | FUSE | 2771 | 20150206 | 1544 | 1176277 | 1452 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 15972 | 38.2428 | -122.7524 | 11SPANSLDSIDEOFFUCO2771 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010464 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99184609 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010779&numberofmonths=24&showchangehistorylog=1 | 15-0010779 | SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | FUSE | 5797 | 20150206 | 1844 | 1177691 | 766 | Distribution Circuit | Vegetation | Tree - fell into line | 120 | 91920 | 38.52 | -122.6222 | HIGHSIDEOFFUCO5799 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010779 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99184545 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010970&numberofmonths=24&showchangehistorylog=1 | 15-0010970 | SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | FUSE | 2225 | 20150206 | 2154 | 1179103 | 933 | Distribution Circuit | Vegetation | Tree - fell into line | 90 | 83970 | 38.524 | -122.6538 | 3100CALISTOGARD8SPANSLDSIDEOFFUCO2225 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 15-0010970 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99184479 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010264&numberofmonths=24&showchangehistorylog=1 | 15-0010264 | SONOMA | FIELD OPS NORTH | Tier 3 | SALMON CREEK-1101 | 43161101 | FUSE | 615 | 20150206 | 1321 | 1175364 | 399 | Distribution Circuit | Equipment Failure/Involved | Other | 16 | 3121 | 38.3642 | -122.9802 | 1SPANFROM615 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on object | 15-0010264 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99185074 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010472&numberofmonths=24&showchangehistorylog=1 | 15-0010472 | SONOMA | FIELD OPS NORTH | Tier 2 | SALMON CREEK-1101 | 43161101 | FUSE | 2331 | 20150206 | 1259 | 1175978 | 1988 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 25844 | 38.3652 | -123.0707 | 7SPLDSIDEOF2331 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010472 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99184608 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011266&numberofmonths=24&showchangehistorylog=1 | 15-0011266 | SONOMA | FIELD OPS NORTH | Tier 3 | DUNBAR-1102 | 43071102 | FUSE | 4897 | 20150207 | 124 | 1179757 | 2093 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 23023 | 38.368 | -122.5889 | 225MTNMEADOWLIN | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 15-0011266 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183860 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011246&numberofmonths=24&showchangehistorylog=1 | 15-0011246 | SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 46763 | 20150207 | 1403 | 1181312 | 1663 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3326 | 38.5932 | -122.9179 | LDSIDEOFFUCO46763 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011246 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99183864 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011265&numberofmonths=24&showchangehistorylog=1 | 15-0011265 | SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 3031 | 20150207 | 1056 | 1181025 | 1804 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 30668 | 38.6045 | -122.9771 | 3Psourceside2629 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011265 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183861 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011393&numberofmonths=24&showchangehistorylog=1 | 15-0011393 | SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 769 | 20150207 | 1859 | 1181810 | 1081 | Distribution Circuit | Vegetation | Tree - branch fell on line | 31 | 33511 | 38.5963 | -122.9143 | 4901WALLACECREEKRD | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011393 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99183829 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011245&numberofmonths=24&showchangehistorylog=1 | 15-0011245 | SONOMA | FIELD OPS NORTH | Tier 3 | FORT ROSS-1121 | 42851121 | FUSE | 4523 | 20150207 | 1038 | 1180965 | 1782 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 28512 | 38.5363 | -123.14 | 13SPANSONTAPTHATGOESNORTHOFFUCO8971 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011245 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183865 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010948&numberofmonths=24&showchangehistorylog=1 | 15-0010948 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 15445 | 20150207 | 415 | 1180005 | 748 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 10472 | 38.463 | -122.9406 | ATMTR781J38 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 15-0010948 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99184491 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011400&numberofmonths=24&showchangehistorylog=1 | 15-0011400 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 15479 | 20150207 | 2202 | 1181943 | 143 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 1859 | 38.4387 | -122.9183 | 2SPANSLDSIDEOF15479 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on object | 15-0011400 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99184231 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011300&numberofmonths=24&showchangehistorylog=1 | 15-0011300 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE | 4573 | 20150207 | 1600 | 1181494 | 1452 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 15972 | 38.4341 | -122.9724 | 1SPANLDSIDEOFFUCO4573 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011300 | OH | Sus | 0 | yes | 2015 | FEB | Yes | None | 99183855 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0012112&numberofmonths=24&showchangehistorylog=1 | 15-0012112 | SONOMA | FIELD OPS NORTH | Tier 2 | CLOVERDALE-1102 | 42821102 | FUSE | 809 | 20150208 | 2124 | 1186201 | 802 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 17981 | 38.883 | -123.0464 | 217148544748 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012112 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183167 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011744&numberofmonths=24&showchangehistorylog=1 | 15-0011744 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1101 | 42091101 | FUSE | 485 | 20150208 | 1656 | 1183291 | 279 | Distribution Circuit | Equipment Failure/Involved | Other | 1 | 279 | 38.483 | -123.0002 | 1spanloadside485 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011744 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183598 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011921&numberofmonths=24&showchangehistorylog=1 | 15-0011921 | SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1101 | 42571101 | FUSE | 1709 | 20150208 | 2115 | 1184510 | 1224 | Distribution Circuit | Vegetation | Tree - fell into line | 166 | 176994 | 38.3736 | -122.8692 | 217501625727 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 15-0011921 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Three Phase Fault | 99182801 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011867&numberofmonths=24&showchangehistorylog=1 | 15-0011867 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 74315 | 20150208 | 2054 | 1184128 | 1056 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 21120 | 38.4909 | -123.0602 | 2CAMPTHAYERRDCAZADERO | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011867 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183288 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011976&numberofmonths=24&showchangehistorylog=1 | 15-0011976 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 3891 | 20150208 | 2348 | 1185265 | 737 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 22847 | 38.5159 | -123.0644 | 15980EAUSTINCREEKRD4200NAUSTINCRRD | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011976 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183248 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011835&numberofmonths=24&showchangehistorylog=1 | 15-0011835 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE | 15417 | 20150208 | 2059 | 1184157 | 893 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 14288 | 38.4215 | -122.9569 | NOONANTODD26GILSONAVECAMPMEEKER | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011835 | OH | Sus | 0 | yes | 2015 | FEB | Yes | None | 99183297 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0012083&numberofmonths=24&showchangehistorylog=1 | 15-0012083 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE | 4573 | 20150208 | 2206 | 1184985 | 1106 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 12166 | 38.4341 | -122.9724 | 2SPANSLDSIDEOF4573 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012083 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99183189 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011971&numberofmonths=24&showchangehistorylog=1 | 15-0011971 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 1031 | 20150208 | 2128 | 1185394 | 802 | Distribution Circuit | Vegetation | Tree - branch fell on line | 24 | 17395 | 38.4926 | -122.9614 | 8SPANSEOFCUTOUTSAND12spansourceside1031 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011971 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183251 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011887&numberofmonths=24&showchangehistorylog=1 | 15-0011887 | SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1108 | 42631108 | SWITCH | 62841 | 20150208 | 2127 | 1184674 | 875 | Distribution Circuit | Vegetation | Tree - branch fell on line | 78 | 36996 | 38.196 | -122.7074 | 2SPANSFROMSW62841TWDFUCO3331 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011887 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183282 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011952&numberofmonths=24&showchangehistorylog=1 | 15-0011952 | SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | FUSE | 2269 | 20150208 | 2354 | 1185274 | 1221 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 30525 | 38.518 | -122.6016 | 218312530757 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011952 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99183261 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0039527&numberofmonths=24&showchangehistorylog=1 | 15-0039527 | SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 779 | 20150608 | 2017 | 1246807 | 895 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 40275 | 38.5969 | -122.9891 | 5SPANSLDSIDEOFFUCO779 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0039527 | OH | Sus | 0 | yes | 2015 | JUN | Yes | Line to Ground | 99164774 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0084863&numberofmonths=24&showchangehistorylog=1 | 15-0084863 | SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 3069 | 20151213 | 757 | 1362231 | 597 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2985 | 38.6052 | -122.9829 | LOADSIDE3069METER1007731300 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084863 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1174530 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0084968&numberofmonths=24&showchangehistorylog=1 | 15-0084968 | SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 13053 | 20151213 | 932 | 1360868 | 763 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1910 | 38.5848 | -122.9494 | Nott35695050MILLCREEKRD | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084968 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Force Out | 1174641 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0084603&numberofmonths=24&showchangehistorylog=1 | 15-0084603 | SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER | 134 | 20151213 | 715 | 1360165 | 1045 | Distribution Circuit | Vegetation | Tree - fell into line | 229 | 147116 | 38.5588 | -123.2702 | SSOFFUCO1030MAINLINELDSIDEOFFUCO8493 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084603 | OH | Sus | 42588659 | yes | 2015 | DEC | Yes | Multi-Fault | 1174268 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0084637&numberofmonths=24&showchangehistorylog=1 | 15-0084637 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 7401 | 20151213 | 822 | 1360429 | 329 | Distribution Circuit | Vegetation | Tree - branch fell on line | 66 | 21714 | 38.5037 | -122.9487 | Galea3472CO12997RIVERSIDEDR | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084637 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1174301 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0084615&numberofmonths=24&showchangehistorylog=1 | 15-0084615 | SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1101 | 42571101 | OTHER | WIREDOWN501SANDRETTO | 20151213 | 750 | 1360617 | 520 | Distribution Circuit | Equipment Failure/Involved | Overhead | 94 | 14215 | 38.3964 | -122.8894 | 501SANDRETODR | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084615 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1174279 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0084773&numberofmonths=24&showchangehistorylog=1 | 15-0084773 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 4913 | 20151213 | 824 | 1360443 | 546 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 2730 | 38.4019 | -122.9436 | 3110BOHEMIANHWY | Strong Winds-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084773 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1174441 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0084775&numberofmonths=24&showchangehistorylog=1 | 15-0084775 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 429 | 20151213 | 813 | 1360357 | 749 | Distribution Circuit | Equipment Failure/Involved | Overhead | 116 | 72844 | 38.4734 | -123.0226 | 21849EASTAVE | Strong Winds-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084775 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Force Out | 1174443 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0084555&numberofmonths=24&showchangehistorylog=1 | 15-0084555 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | OCB | 11122 | 20151213 | 803 | 1360333 | 984 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1122 | 251687 | 38.4714 | -123.0115 | 20795BOHEMIANAVE | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084555 | OH | Sus | 42588659 | yes | 2015 | DEC | Yes | Line to Ground | 1174217 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0087141&numberofmonths=24&showchangehistorylog=1 | 15-0087141 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | RECLOSER | 334 | 20151224 | 1543 | 1371213 | 515 | Distribution Circuit | Equipment Failure/Involved | Overhead | 92 | 16100 | 38.5009 | -122.9052 | WIREDOWNPASTUNMARKEDSOLIDBLADES10971WESTSIDERD | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0087141 | OH | Sus | 31208799 | yes | 2015 | DEC | Yes | Line to Ground | 1177217 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017975&numberofmonths=24&showchangehistorylog=1 | 16-0017975 | SONOMA | FIELD OPS NORTH | Tier 2 | CLOVERDALE-1102 | 42821102 | RECLOSER | 156 | 20160305 | 2214 | 1420157 | 447 | Distribution Circuit | Vegetation | Tree - fell into line | 590 | 83569 | 38.7991 | -122.9913 | 240GEYSERSROADCLOVERDALE | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017975 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1189846 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017578&numberofmonths=24&showchangehistorylog=1 | 16-0017578 | SONOMA | FIELD OPS NORTH | Tier 3 | FORT ROSS-1121 | 42851121 | FUSE | 2987 | 20160305 | 1557 | 1417038 | 1419 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 82053 | 38.5419 | -123.09 | 21090KINGRIDGERDCAZADERO | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017578 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1189433 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017625&numberofmonths=24&showchangehistorylog=1 | 16-0017625 | SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER | 134 | 20160305 | 1618 | 1417447 | 621 | Distribution Circuit | Equipment Failure/Involved | Overhead | 229 | 135141 | 38.5588 | -123.2702 | 2SPANSLOADSIDEOFMTR29P542 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017625 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1189479 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017842&numberofmonths=24&showchangehistorylog=1 | 16-0017842 | SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1102 | 42571102 | FUSE | 3437 | 20160305 | 1841 | 1418200 | 291 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 4901 | 38.4438 | -122.9179 | SSOF15479 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017842 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1189696 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017743&numberofmonths=24&showchangehistorylog=1 | 16-0017743 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 8139 | 20160305 | 1704 | 1417545 | 525 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 18900 | 38.4981 | -123.073 | 13SUNRISEMOUNTAINRDCAZADERO | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017743 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1189597 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017810&numberofmonths=24&showchangehistorylog=1 | 16-0017810 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 1581 | 20160305 | 1909 | 1418337 | 1393 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 11144 | 38.4926 | -123.0609 | 2SPLDSIDEOFFUSE1581 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017810 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1189663 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017683&numberofmonths=24&showchangehistorylog=1 | 16-0017683 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | RECLOSER | 346 | 20160305 | 1823 | 1418145 | 314 | Distribution Circuit | Vegetation | Tree - branch fell on line | 515 | 100456 | 38.5044 | -122.9975 | CORNEROFARMSTRONGWOODSRDSWEETWATERSPRINGS | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017683 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1189539 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017746&numberofmonths=24&showchangehistorylog=1 | 16-0017746 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 1997 | 20160305 | 1759 | 1417948 | 632 | Distribution Circuit | Vegetation | Tree - fell into line | 110 | 69520 | 38.502 | -123.0239 | Kikuchi151215521OldCazaderoRdGuerneville | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017746 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1189600 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0003336&numberofmonths=24&showchangehistorylog=1 | 17-0003336 | SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 781 | 20170103 | 2055 | 1616778 | 502 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 7530 | 38.6024 | -123.0033 | LDSIDEOF78110905 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003336 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1243509 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0003174&numberofmonths=24&showchangehistorylog=1 | 17-0003174 | SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1101 | 42571101 | RECLOSER | 322 | 20170103 | 1657 | 1616109 | 659 | Distribution Circuit | Vegetation | Tree - fell into line | 376 | 31670 | 38.3868 | -122.8901 | 300FTLD1380BODEGAHWY | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003174 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1243343 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0003218&numberofmonths=24&showchangehistorylog=1 | 17-0003218 | SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1101 | 42571101 | JUMPER | LINE830MONTGOMERY | 20170103 | 1638 | 1616642 | 502 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 9090 | 38.4027 | -122.8781 | KOTULAJON4343830MONTGOMERYRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003218 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1243387 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0003158&numberofmonths=24&showchangehistorylog=1 | 17-0003158 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 6899 | 20170103 | 1626 | 1616007 | 358 | Distribution Circuit | Vegetation | Tree - branch fell on line | 81 | 21198 | 38.3934 | -122.974 | Galea34723500JOYRD | Overcast-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003158 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1243328 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005878&numberofmonths=24&showchangehistorylog=1 | 17-0005878 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | FUSE | 59789 | 20170108 | 522 | 1630212 | 5333 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 10666 | 38.2666 | -122.808 | 2SPANSLDSIDEOF59789 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005878 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245662 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005343&numberofmonths=24&showchangehistorylog=1 | 17-0005343 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1105 | 42271105 | RECLOSER | 36536 | 20170108 | 1321 | 1626893 | 454 | Distribution Circuit | Vegetation | Tree - branch fell on line | 662 | 219114 | 38.3142 | -122.7365 | BYMTR1009762419 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005343 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245133 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007499&numberofmonths=24&showchangehistorylog=1 | 17-0007499 | SONOMA | FIELD OPS NORTH | Tier 3 | DUNBAR-1101 | 43071101 | FUSE | 4829 | 20170108 | 1854 | 1628711 | 3901 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 15604 | 38.3965 | -122.5754 | 2601BRISTOLRDKENWOOD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007499 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1247049 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005754&numberofmonths=24&showchangehistorylog=1 | 17-0005754 | SONOMA | FIELD OPS NORTH | Tier 3 | DUNBAR-1103 | 43071103 | OTHER | WIREDOWNMTR1007382525 | 20170108 | 1745 | 1628450 | 1013 | Distribution Circuit | Vegetation | Tree - fell into line | 118 | 89606 | 38.3905 | -122.4923 | MTR1007382525 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005754 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Force Out | 1245538 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005443&numberofmonths=24&showchangehistorylog=1 | 17-0005443 | SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | JUMPER | OJATLB2SPANSLDSIDEOF4367 | 20170108 | 1448 | 1627674 | 1497 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 20958 | 38.5481 | -123.2445 | MTR1007683713 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005443 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Open Circuit | 1245227 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005412&numberofmonths=24&showchangehistorylog=1 | 17-0005412 | SONOMA | FIELD OPS NORTH | Tier 3 | FULTON-1107 | 42561107 | OTHER | WIREDOWNBTWN4265LR604 | 20170108 | 1216 | 1626173 | 1646 | Distribution Circuit | Vegetation | Tree - fell into line | 222 | 77180 | 38.5476 | -122.7204 | Rendon4754BETWEENSW4265ANDLR604 | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005412 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Force Out | 1245195 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005449&numberofmonths=24&showchangehistorylog=1 | 17-0005449 | SONOMA | FIELD OPS NORTH | Tier 2 | GEYSERVILLE-1101 | 42891101 | JUMPER | WIREDOWN3LDSIDEOF12427 | 20170108 | 1528 | 1627707 | 2646 | Distribution Circuit | Vegetation | Tree - branch fell on line | 72 | 21360 | 38.6673 | -123.2054 | 3SPANSLDSIDEOF14247 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005449 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245233 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005608&numberofmonths=24&showchangehistorylog=1 | 17-0005608 | SONOMA | FIELD OPS NORTH | Tier 2 | GEYSERVILLE-1101 | 42891101 | FUSE | 2913 | 20170108 | 1504 | 1627577 | 2951 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 17706 | 38.7033 | -122.9202 | 6PLD1303 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005608 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1245386 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005677&numberofmonths=24&showchangehistorylog=1 | 17-0005677 | SONOMA | FIELD OPS NORTH | Tier 2 | GEYSERVILLE-1101 | 42891101 | FUSE | 5183 | 20170108 | 1753 | 1628472 | 1132 | Distribution Circuit | Equipment Failure/Involved | Overhead | 64 | 64240 | 38.7113 | -123.0002 | 11SPANSSOURCESIDEOFMETER1008560846 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005677 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1245458 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005472&numberofmonths=24&showchangehistorylog=1 | 17-0005472 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 1139 | 20170108 | 636 | 1625477 | 2083 | Distribution Circuit | Vegetation | Tree - fell into line | 143 | 209900 | 38.5091 | -122.9195 | MooreDave361210549WOODSIDERD | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0005472 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245256 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006024&numberofmonths=24&showchangehistorylog=1 | 17-0006024 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 8457 | 20170108 | 1132 | 1625565 | 1364 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 17732 | 38.5137 | -122.9329 | MooreShon4250NEAR11719SKYLINERDMETER1008376009 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006024 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245769 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005594&numberofmonths=24&showchangehistorylog=1 | 17-0005594 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1101 | 42571101 | OTHER | WIREDOWN4SLS4417 | 20170108 | 1115 | 1625342 | 4515 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 61454 | 38.3837 | -122.906 | 4SPANSLOADSIDEOF4417 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005594 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245373 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006196&numberofmonths=24&showchangehistorylog=1 | 17-0006196 | SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1101 | 42571101 | FUSE | 1761 | 20170108 | 1338 | 1626975 | 1775 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 60350 | 38.3789 | -122.8977 | LDSIDEOF1761FUCO | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006196 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245892 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0004973&numberofmonths=24&showchangehistorylog=1 | 17-0004973 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 1525 | 20170108 | 547 | 1622733 | 2049 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 114744 | 38.4106 | -122.9827 | 18450WILLOWCREEKRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004973 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1244774 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0004977&numberofmonths=24&showchangehistorylog=1 | 17-0004977 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | RECLOSER | 104 | 20170108 | 738 | 1623186 | 845 | Distribution Circuit | Vegetation | Tree - fell into line | 1242 | 1038565 | 38.403 | -122.9214 | MCNAMEELEE318375willowcreekroad | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004977 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1244778 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005148&numberofmonths=24&showchangehistorylog=1 | 17-0005148 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 6917 | 20170108 | 738 | 1625138 | 1614 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 124278 | 38.3873 | -122.9728 | MCNAMEELEE316969taylorlane | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005148 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1244944 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005527&numberofmonths=24&showchangehistorylog=1 | 17-0005527 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 1181 | 20170108 | 1117 | 1625928 | 3360 | Distribution Circuit | Vegetation | Tree - fell into line | 110 | 54271 | 38.4027 | -122.9163 | CRAMERCHRIS1650Jonive | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005527 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245310 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005528&numberofmonths=24&showchangehistorylog=1 | 17-0005528 | SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1102 | 42571102 | FUSE | 525 | 20170108 | 1243 | 1626420 | 1518 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 54648 | 38.4049 | -122.8963 | 1438FURLONGRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005528 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245311 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005627&numberofmonths=24&showchangehistorylog=1 | 17-0005627 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 3053 | 20170108 | 738 | 1628823 | 1756 | Distribution Circuit | Vegetation | Tree - fell into line | 105 | 159870 | 38.4189 | -122.9304 | 12309DUPONTRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005627 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245409 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005725&numberofmonths=24&showchangehistorylog=1 | 17-0005725 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 12019 | 20170108 | 1704 | 1629175 | 4325 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 56225 | 38.4002 | -122.9571 | 1SPANLDSIDEOFFU12019 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005725 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245509 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005105&numberofmonths=24&showchangehistorylog=1 | 17-0005105 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 8139 | 20170108 | 734 | 1623134 | 4948 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 178128 | 38.4981 | -123.073 | CAZANOMALODGERD1500WOCAZADERORD | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0005105 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1244903 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005648&numberofmonths=24&showchangehistorylog=1 | 17-0005648 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 2659 | 20170108 | 1050 | 1625102 | 2998 | Distribution Circuit | Vegetation | Tree - branch fell on line | 37 | 110926 | 38.5068 | -123.0701 | 3420CAZHIGHWAY | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005648 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245428 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006214&numberofmonths=24&showchangehistorylog=1 | 17-0006214 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 2301 | 20170108 | 1951 | 1631579 | 1524 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 27432 | 38.5285 | -123.0957 | 550KRAMERRD | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006214 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1245908 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006173&numberofmonths=24&showchangehistorylog=1 | 17-0006173 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE | 17177 | 20170108 | 945 | 1624342 | 3122 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 6244 | 38.4429 | -122.9912 | LDSIDEFU17177 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006173 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245878 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0004983&numberofmonths=24&showchangehistorylog=1 | 17-0004983 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 1053 | 20170108 | 626 | 1622748 | 371 | Distribution Circuit | Vegetation | Tree - fell into line | 114 | 42294 | 38.4952 | -123.0101 | MooreShon425017315PARKAVE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004983 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Three Phase Fault | 1244784 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0004990&numberofmonths=24&showchangehistorylog=1 | 17-0004990 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 4597 | 20170108 | 651 | 1622833 | 304 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 3952 | 38.4977 | -122.9909 | 13560MAYSCANYONRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004990 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1244790 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005113&numberofmonths=24&showchangehistorylog=1 | 17-0005113 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 1313 | 20170108 | 816 | 1623555 | 1785 | Distribution Circuit | Vegetation | Tree - fell into line | 110 | 168231 | 38.504 | -122.9884 | KOTULAJON434314996MERRYLN | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005113 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1244911 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005190&numberofmonths=24&showchangehistorylog=1 | 17-0005190 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | OTHER | HOTWIREDOWN | 20170108 | 849 | 1625486 | 2025 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 161839 | 38.4989 | -122.9795 | BETSW107312683 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005190 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1244982 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005257&numberofmonths=24&showchangehistorylog=1 | 17-0005257 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 2787 | 20170108 | 1048 | 1625076 | 421 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 10104 | 38.5208 | -122.9793 | MTR1007800542 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005257 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245047 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006208&numberofmonths=24&showchangehistorylog=1 | 17-0006208 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | FUSE | 18477 | 20170109 | 1325 | 1631365 | 1278 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 5112 | 38.2844 | -122.7225 | Deignan3571931PEPPER | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006208 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245899 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006220&numberofmonths=24&showchangehistorylog=1 | 17-0006220 | SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | JUMPER | OJSS14895 | 20170109 | 1511 | 1631695 | 4204 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 12612 | 38.3377 | -122.5277 | GOLLANSEAN3473100OSOTRAIL | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006220 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245924 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006309&numberofmonths=24&showchangehistorylog=1 | 17-0006309 | SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | RECLOSER | 24918 | 20170109 | 1213 | 1632095 | 3104 | Distribution Circuit | Vegetation | Tree - fell into line | 171 | 433710 | 38.5914 | -122.92 | BYMTR1008942983 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006309 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246010 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006337&numberofmonths=24&showchangehistorylog=1 | 17-0006337 | SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1102 | 42571102 | JUMPER | OJS1SSOFMTR500013313TOEOL | 20170109 | 1815 | 1632044 | 2940 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2940 | 38.4147 | -122.8992 | MTR500013313 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006337 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Force Out | 1246042 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006212&numberofmonths=24&showchangehistorylog=1 | 17-0006212 | SONOMA | FIELD OPS NORTH | Tier 2 | SALMON CREEK-1101 | 43161101 | FUSE | 8859 | 20170109 | 941 | 1631664 | 4451 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 8902 | 38.3452 | -123.0086 | 6SPANSLOADSIDE8859 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006212 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245906 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006689&numberofmonths=24&showchangehistorylog=1 | 17-0006689 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1105 | 42271105 | FUSE | 2417 | 20170110 | 1244 | 1633282 | 2851 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 4255 | 38.2879 | -122.8003 | Deignan35711400WALKERRD | Partly Cloudy-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0006689 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246308 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006875&numberofmonths=24&showchangehistorylog=1 | 17-0006875 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1105 | 42271105 | RECLOSER | 36536 | 20170110 | 1739 | 1635033 | 1285 | Distribution Circuit | Equipment Failure/Involved | Overhead | 660 | 556009 | 38.3142 | -122.7365 | MCDONALDCHADTMANFUSES69405FUCO6563 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006875 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246454 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007038&numberofmonths=24&showchangehistorylog=1 | 17-0007038 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1105 | 42271105 | FUSE | 3287 | 20170110 | 1442 | 1633837 | 1324 | Distribution Circuit | Vegetation | Tree - fell into line | 168 | 65442 | 38.3381 | -122.7858 | MooreShon42504SPANSLDSIDEOF4104CANNFIELDRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007038 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246623 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007663&numberofmonths=24&showchangehistorylog=1 | 17-0007663 | SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | FUSE | 16739 | 20170110 | 1754 | 1635461 | 4071 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 77349 | 38.3724 | -122.5663 | 5320ENTERPRISE | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007663 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Multi-Fault | 1247168 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007408&numberofmonths=24&showchangehistorylog=1 | 17-0007408 | SONOMA | FIELD OPS NORTH | Tier 2 | LAKEVILLE-1102 | 43371102 | JUMPER | OJS7SPANSFROM3793 | 20170110 | 2228 | 1638128 | 1272 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 1272 | 38.3333 | -122.5871 | 4SPANSFROM3793TWD5721 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007408 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246995 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006383&numberofmonths=24&showchangehistorylog=1 | 17-0006383 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1101 | 42091101 | FUSE | 1595 | 20170110 | 251 | 1632464 | 3605 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 18025 | 38.477 | -122.9333 | 9045HWY116 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006383 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1246091 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006661&numberofmonths=24&showchangehistorylog=1 | 17-0006661 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1101 | 42091101 | FUSE | 1939 | 20170110 | 1323 | 1633371 | 2647 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 23823 | 38.4782 | -122.9384 | 1SANLOADSIDE1939 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006661 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1246289 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006575&numberofmonths=24&showchangehistorylog=1 | 17-0006575 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 13491 | 20170110 | 1114 | 1633020 | 3407 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 59560 | 38.4969 | -122.9027 | 1SPANLOADSIDEOF13491 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006575 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1246225 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006855&numberofmonths=24&showchangehistorylog=1 | 17-0006855 | SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1101 | 42571101 | FUSE | 11721 | 20170110 | 1337 | 1634698 | 1843 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 18430 | 38.3876 | -122.8898 | 2SPANSINFROMFUCOUT11721 | Clear-32-90 F | Conductor, Overhead | On Ground | 17-0006855 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246436 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006988&numberofmonths=24&showchangehistorylog=1 | 17-0006988 | SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1101 | 42571101 | JUMPER | OJ1SSOFMTRG38872 | 20170110 | 1834 | 1636505 | 2906 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 5812 | 38.398 | -122.8912 | MTRG38872 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006988 | OH | Sus | 0 | yes | 2017 | JAN | Yes | None | 1246570 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007321&numberofmonths=24&showchangehistorylog=1 | 17-0007321 | SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1102 | 42571102 | FUSE | 3437 | 20170110 | 1752 | 1634972 | 1617 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 21221 | 38.4438 | -122.9179 | 11819GREENVALLEYRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007321 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246902 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006657&numberofmonths=24&showchangehistorylog=1 | 17-0006657 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER | 64758 | 20170110 | 1238 | 1633280 | 3062 | Distribution Circuit | Vegetation | Tree - fell into line | 282 | 455556 | 38.5089 | -123.0696 | MTR1007822294 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0006657 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Three Phase Fault | 1246286 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006897&numberofmonths=24&showchangehistorylog=1 | 17-0006897 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER | 240 | 20170110 | 1515 | 1634000 | 1609 | Distribution Circuit | Vegetation | Tree - fell into line | 620 | 670768 | 38.4715 | -123.0471 | NoonanTodd3469ATCOPOLE2595AUSTINCRKRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006897 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246476 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0008420&numberofmonths=24&showchangehistorylog=1 | 17-0008420 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 10183 | 20170110 | 1342 | 1640661 | 3260 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 22820 | 38.5231 | -123.0438 | LDSIDEOFMTR1007685682 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0008420 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247808 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006503&numberofmonths=24&showchangehistorylog=1 | 17-0006503 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE | 439 | 20170110 | 918 | 1632783 | 1778 | Distribution Circuit | Environmental/External | Water | 15 | 26670 | 38.4631 | -123.0122 | KOTULAJON43439045MIDDLETERRACEMONTERIO | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0006503 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Force Out | 1246170 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006513&numberofmonths=24&showchangehistorylog=1 | 17-0006513 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | JUMPER | WIREDOWN1SPANSOURCESIDEOF11757HWY116 | 20170110 | 836 | 1632922 | 1980 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 63888 | 38.497 | -122.9554 | Kikuchi151211757Hwy116Guerneville | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006513 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Open Circuit | 1246174 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006680&numberofmonths=24&showchangehistorylog=1 | 17-0006680 | SONOMA | FIELD OPS NORTH | Tier 2 | RINCON-1103 | 43321103 | OCB | 11032 | 20170110 | 1414 | 1633660 | 579 | Distribution Circuit | Vegetation | Tree - fell into line | 2228 | 285114 | 38.4901 | -122.6661 | WASSONPHILLIP3spansnorthoflr568 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006680 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246301 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006993&numberofmonths=24&showchangehistorylog=1 | 17-0006993 | SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | FUSE | 3447 | 20170110 | 1600 | 1634189 | 2851 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 45616 | 38.5157 | -122.6297 | 8SPANSSSOF3447 | Overcast-Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0006993 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246575 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007304&numberofmonths=24&showchangehistorylog=1 | 17-0007304 | SONOMA | FIELD OPS NORTH | Tier 3 | SANTA ROSA A-1107 | 42151107 | OTHER | WIREDOWNATMTR1007528387 | 20170110 | 1752 | 1635207 | 2431 | Distribution Circuit | Vegetation | Tree - fell into line | 203 | 21678 | 38.4522 | -122.6856 | MTR1007528387 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007304 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246885 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007880&numberofmonths=24&showchangehistorylog=1 | 17-0007880 | SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 779 | 20170111 | 1643 | 1640336 | 4042 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 74140 | 38.5971 | -122.9894 | LDSIDEOFSB3033 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007880 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247337 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007472&numberofmonths=24&showchangehistorylog=1 | 17-0007472 | SONOMA | FIELD OPS NORTH | Tier 3 | SONOMA-1103 | 42721103 | FUSE | 5543 | 20170111 | 540 | 1639122 | 2145 | Distribution Circuit | Vegetation | Tree - fell into line | 75 | 155705 | 38.303 | -122.4409 | 1844GEHRICKERDSONOMA | Partly Cloudy-Fog-Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0007472 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247034 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0010035&numberofmonths=24&showchangehistorylog=1 | 17-0010035 | SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER | 134 | 20170118 | 1315 | 1646247 | 1591 | Distribution Circuit | Vegetation | Tree - fell into line | 640 | 197059 | 38.5588 | -123.2702 | COS2935MM3989HWY1WIREDOWN59153tapwiredown2SLS2699WIREDOWNTREELEANINGONLINES15000MEYERSGRADE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010035 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1249074 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0010587&numberofmonths=24&showchangehistorylog=1 | 17-0010587 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 6229 | 20170118 | 2257 | 1649303 | 774 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 27090 | 38.4585 | -122.9351 | BETWEENGREENWOODANDBUNDY | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010587 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1249604 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0010685&numberofmonths=24&showchangehistorylog=1 | 17-0010685 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 669275 | 20170119 | 457 | 1649900 | 428 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 3573 | 38.4105 | -122.9493 | MTR94E410 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010685 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1249697 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0010643&numberofmonths=24&showchangehistorylog=1 | 17-0010643 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 1997 | 20170119 | 242 | 1649766 | 469 | Distribution Circuit | Vegetation | Tree - branch fell on line | 110 | 51590 | 38.502 | -123.0239 | 15561OLDCAZADERORD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010643 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1249658 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011112&numberofmonths=24&showchangehistorylog=1 | 17-0011112 | SONOMA | FIELD OPS NORTH | Tier 2 | SALMON CREEK-1101 | 43161101 | OTHER | 8859 | 20170119 | 1933 | 1651846 | 382 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 764 | 38.3452 | -123.0086 | 4SPANSLSO8859 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011112 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1250021 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011202&numberofmonths=24&showchangehistorylog=1 | 17-0011202 | SONOMA | FIELD OPS NORTH | Tier 2 | MIRABEL-1102 | 42091102 | FUSE | 13669 | 20170120 | 338 | 1652166 | 464 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 4176 | 38.509 | -122.8869 | 9294WESTSIDERD | Partly Cloudy-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011202 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Three Phase Fault | 1250115 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011215&numberofmonths=24&showchangehistorylog=1 | 17-0011215 | SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1102 | 42571102 | FUSE | 9797 | 20170120 | 319 | 1652107 | 958 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 20118 | 38.4152 | -122.9003 | Galea34722156 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011215 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Three Phase Fault | 1250128 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011535&numberofmonths=24&showchangehistorylog=1 | 17-0011535 | SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1108 | 42631108 | FUSE | 12221 | 20170120 | 1203 | 1653404 | 230 | Distribution Circuit | Vegetation | Tree - branch fell on line | 10 | 2300 | 38.2197 | -122.6836 | 3SPANSLDSIDEOFFUCO12221 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0011535 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Force Out | 1250401 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011361&numberofmonths=24&showchangehistorylog=1 | 17-0011361 | SONOMA | FIELD OPS NORTH | Tier 2 | SALMON CREEK-1101 | 43161101 | FUSE | 8859 | 20170120 | 852 | 1653353 | 174 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 348 | 38.3452 | -123.0086 | 4SSSOF8859 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011361 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Three Phase Fault | 1250254 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012557&numberofmonths=24&showchangehistorylog=1 | 17-0012557 | SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 6751 | 20170121 | 2159 | 1657436 | 811 | Distribution Circuit | Vegetation | Tree - fell into line | 134 | 108674 | 38.592 | -122.9622 | 4SPANSLDSIDEOF6751 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012557 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1251379 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012165&numberofmonths=24&showchangehistorylog=1 | 17-0012165 | SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER | 134 | 20170121 | 1829 | 1657113 | 1519 | Distribution Circuit | Vegetation | Tree - fell into line | 232 | 289669 | 38.5588 | -123.2702 | LDSIDEOFLR56023350HWY122325TIMBERCOVERD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0012165 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1250982 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012037&numberofmonths=24&showchangehistorylog=1 | 17-0012037 | SONOMA | FIELD OPS NORTH | Tier 2 | MIRABEL-1102 | 42091102 | FUSE | 913 | 20170121 | 1028 | 1656267 | 1577 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 5303 | 38.517 | -122.8908 | FUCO913 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012037 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1250853 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012991&numberofmonths=24&showchangehistorylog=1 | 17-0012991 | SONOMA | FIELD OPS NORTH | Tier 3 | DUNBAR-1103 | 43071103 | OTHER | WIREDOWN | 20170122 | 528 | 1659020 | 588 | Distribution Circuit | Vegetation | Tree - branch fell on line | 118 | 14224 | 38.3863 | -122.4835 | MCNAMEELEE312665mapleglenroad | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012991 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1251812 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012894&numberofmonths=24&showchangehistorylog=1 | 17-0012894 | SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | RECLOSER | 24918 | 20170122 | 609 | 1659460 | 425 | Distribution Circuit | Environmental/External | Flood/Erosion | 53 | 22525 | 38.5914 | -122.92 | 2SPANSLDSIDE6263 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012894 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Three Phase Fault | 1251715 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012984&numberofmonths=24&showchangehistorylog=1 | 17-0012984 | SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1101 | 42571101 | FUSE | 18133 | 20170122 | 940 | 1660164 | 332 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 1992 | 38.3804 | -122.8853 | Galea34721009TILTONRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012984 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1251805 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012820&numberofmonths=24&showchangehistorylog=1 | 17-0012820 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | RECLOSER | 5040 | 20170122 | 449 | 1659021 | 755 | Distribution Circuit | Vegetation | Tree - fell into line | 386 | 291430 | 38.4322 | -122.967 | 5665BOHEMIANHWY | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0012820 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1251642 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018514&numberofmonths=24&showchangehistorylog=1 | 17-0018514 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1104 | 42271104 | FUSE | 14645 | 20170207 | 804 | 1678601 | 506 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 4048 | 38.312 | -122.7091 | FIRST2SPANSLOADSIDEOF14645 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018514 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1256315 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018291&numberofmonths=24&showchangehistorylog=1 | 17-0018291 | SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | FUSE | 4877 | 20170207 | 303 | 1677772 | 861 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 18942 | 38.382 | -122.5549 | 9001BENNETTVALLEYRD | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018291 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1256131 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018486&numberofmonths=24&showchangehistorylog=1 | 17-0018486 | SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 6751 | 20170207 | 445 | 1679879 | 2090 | Distribution Circuit | Vegetation | Tree - fell into line | 134 | 280060 | 38.592 | -122.9622 | 2POLESLDSIDEOF6751 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0018486 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Three Phase Fault | 1256297 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018190&numberofmonths=24&showchangehistorylog=1 | 17-0018190 | SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE | 4271 | 20170207 | 112 | 1677190 | 803 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 11242 | 38.5391 | -123.2764 | 22038DAVISWAY | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018190 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1256052 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018642&numberofmonths=24&showchangehistorylog=1 | 17-0018642 | SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE | 4947 | 20170207 | 315 | 1678975 | 2156 | Distribution Circuit | Equipment Failure/Involved | Overhead | 55 | 118580 | 38.5577 | -123.0969 | MooreDave3612BETWEEN11349AND23250KINGRIDGERD | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018642 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1256412 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018723&numberofmonths=24&showchangehistorylog=1 | 17-0018723 | SONOMA | FIELD OPS NORTH | Tier 3 | FULTON-1107 | 42561107 | OTHER | WIREDOWNIRO9108LOCHHAVEN | 20170207 | 1417 | 1680804 | 1310 | Distribution Circuit | Vegetation | Tree - branch fell on line | 149 | 114666 | 38.5509 | -122.7111 | MooreShon4250IRO9108LOCHHAVEN | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0018723 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1256472 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018519&numberofmonths=24&showchangehistorylog=1 | 17-0018519 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1101 | 42091101 | FUSE | 1071 | 20170207 | 907 | 1679369 | 4863 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 27917 | 38.474 | -122.9175 | 8575HWY116 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018519 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1256319 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018236&numberofmonths=24&showchangehistorylog=1 | 17-0018236 | SONOMA | FIELD OPS NORTH | Tier 2 | MIRABEL-1102 | 42091102 | FUSE | 13669 | 20170207 | 632 | 1678158 | 1796 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 19068 | 38.509 | -122.8869 | 10SPANSLOADSIDEOF13669 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018236 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Three Phase Fault | 1256089 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018582&numberofmonths=24&showchangehistorylog=1 | 17-0018582 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 7951 | 20170207 | 629 | 1680184 | 950 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 16150 | 38.4566 | -122.9364 | 2SPANSLOADSIDEOF7951 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018582 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Three Phase Fault | 1256355 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018586&numberofmonths=24&showchangehistorylog=1 | 17-0018586 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 6229 | 20170207 | 822 | 1680191 | 733 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 25655 | 38.4585 | -122.9351 | BET1544515477 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018586 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1256358 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018720&numberofmonths=24&showchangehistorylog=1 | 17-0018720 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 12035 | 20170207 | 1218 | 1680588 | 2395 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 84538 | 38.4041 | -123.0038 | 2SPANSSSOFMTR1007734719 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018720 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1256469 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018737&numberofmonths=24&showchangehistorylog=1 | 17-0018737 | SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1102 | 42571102 | OTHER | WIREDOWN3SSOFMTR1009647024 | 20170207 | 1507 | 1680503 | 1453 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 4359 | 38.3584 | -122.9019 | 4SSSIDEOFMTR1009647024 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018737 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1256485 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0019031&numberofmonths=24&showchangehistorylog=1 | 17-0019031 | SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1102 | 42571102 | JUMPER | WIREDOWN | 20170207 | 1025 | 1681962 | 1925 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 38500 | 38.4434 | -122.9179 | 1STSPANLDSIDEOFFUCO3437 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019031 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1256689 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018556&numberofmonths=24&showchangehistorylog=1 | 17-0018556 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | OTHER | 1995 | 20170207 | 904 | 1679352 | 1619 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 17809 | 38.532 | -123.0037 | 1315SPANSLDSIDEOF1995 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018556 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1256341 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018630&numberofmonths=24&showchangehistorylog=1 | 17-0018630 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | JUMPER | 11SPANSLDSIDEOF2055 | 20170207 | 817 | 1678885 | 708 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 4248 | 38.494 | -122.9578 | 8155MONDOLNGERNVILLE | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018630 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1256400 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018057&numberofmonths=24&showchangehistorylog=1 | 17-0018057 | SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1108 | 42631108 | RECLOSER | 208 | 20170207 | 224 | 1677412 | 721 | Distribution Circuit | Vegetation | Tree - fell into line | 182 | 81498 | 38.2261 | -122.7213 | ONMAINLINE1SSOFCOUT2405 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018057 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Multi-Fault | 1255911 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018332&numberofmonths=24&showchangehistorylog=1 | 17-0018332 | SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | FUSE | 6119 | 20170207 | 309 | 1679273 | 2485 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 19172 | 38.5397 | -122.6404 | 5455GATESRD | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0018332 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1256168 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018420&numberofmonths=24&showchangehistorylog=1 | 17-0018420 | SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | FUSE | 15035 | 20170207 | 902 | 1679630 | 786 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 5502 | 38.5466 | -122.6442 | 6LDSIDEOFFUSES | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018420 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Force Out | 1256244 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018374&numberofmonths=24&showchangehistorylog=1 | 17-0018374 | SONOMA | FIELD OPS NORTH | Tier 2 | SALMON CREEK-1101 | 43161101 | FUSE | 15553 | 20170207 | 456 | 1677976 | 1982 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3964 | 38.3917 | -123.0855 | 1SPANLDSIDEOF15553 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018374 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1256207 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0019307&numberofmonths=24&showchangehistorylog=1 | 17-0019307 | SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER | 560 | 20170209 | 643 | 1682791 | 715 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 22165 | 38.5562 | -123.3034 | FISCKMILLCOVE4SSOFMTR1008863028 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019307 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1256895 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0019471&numberofmonths=24&showchangehistorylog=1 | 17-0019471 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | RECLOSER | 79306 | 20170209 | 1216 | 1683342 | 469 | Distribution Circuit | Vegetation | Tree - fell into line | 76 | 26003 | 38.3722 | -122.9117 | 3EOFSW32291SO10133 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019471 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1256988 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0019448&numberofmonths=24&showchangehistorylog=1 | 17-0019448 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | RECLOSER | 652 | 20170209 | 1243 | 1683406 | 497 | Distribution Circuit | Vegetation | Tree - fell into line | 312 | 125756 | 38.52 | -122.9783 | COUTPOLE2333 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019448 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1256972 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0019503&numberofmonths=24&showchangehistorylog=1 | 17-0019503 | SONOMA | FIELD OPS NORTH | Tier 2 | RINCON-1103 | 43321103 | OCB | 11032 | 20170209 | 1423 | 1683627 | 1100 | Distribution Circuit | Vegetation | Tree - fell into line | 458 | 419106 | 38.4901 | -122.6661 | MAINLINE1POLENOFTRANSFCGC21812553015 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0019503 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1257008 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0022769&numberofmonths=24&showchangehistorylog=1 | 17-0022769 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 6233 | 20170217 | 2125 | 1698484 | 710 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 9230 | 38.4471 | -122.9241 | 2PLDOF6233 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022769 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1259785 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0022844&numberofmonths=24&showchangehistorylog=1 | 17-0022844 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER | 23916 | 20170218 | 135 | 1698749 | 687 | Distribution Circuit | Environmental/External | Flood/Erosion | 689 | 258198 | 38.49 | -123.06 | INGRAMJEFF41880AUSTINCREEKRD | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0022844 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1259860 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023734&numberofmonths=24&showchangehistorylog=1 | 17-0023734 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | FUSE | 4219 | 20170220 | 857 | 1702782 | 483 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 1449 | 38.2318 | -122.9124 | 2ND3RDSPANSLDSIDEOF4219 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023734 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Force Out | 1260725 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024531&numberofmonths=24&showchangehistorylog=1 | 17-0024531 | SONOMA | FIELD OPS NORTH | Tier 2 | GEYSERVILLE-1101 | 42891101 | FUSE | 5531 | 20170220 | 2047 | 1705953 | 2393 | Distribution Circuit | Vegetation | Tree - branch fell on line | 25 | 39159 | 38.6773 | -123.0625 | 2SPANSBEYONDSBCO12427 | Clear-32-90 F | Conductor, Overhead | On Ground | 17-0024531 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1261496 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024771&numberofmonths=24&showchangehistorylog=1 | 17-0024771 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 6917 | 20170220 | 2154 | 1706261 | 1004 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 16406 | 38.3873 | -122.9728 | ALVAREZR388517402TAYLORLN | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024771 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1261742 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024718&numberofmonths=24&showchangehistorylog=1 | 17-0024718 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 8139 | 20170220 | 2102 | 1706068 | 950 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 34200 | 38.4981 | -123.073 | 68SUNRISEMTNRD | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024718 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1261686 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023876&numberofmonths=24&showchangehistorylog=1 | 17-0023876 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | JUMPER | WIREDOWN15383 | 20170220 | 1441 | 1703543 | 371 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 9897 | 38.4481 | -123.0004 | FUCO15383AND4SPANSLDSIDE8231TYRONRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023876 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1260853 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024348&numberofmonths=24&showchangehistorylog=1 | 17-0024348 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE | 4737 | 20170220 | 2049 | 1705997 | 978 | Distribution Circuit | Vegetation | Tree - branch fell on line | 53 | 51834 | 38.4721 | -123.0032 | ALVAREZR388520240ALDERRD | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0024348 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1261312 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024996&numberofmonths=24&showchangehistorylog=1 | 17-0024996 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 15593 | 20170220 | 2230 | 1706267 | 731 | Distribution Circuit | Vegetation | Tree - fell into line | 100 | 73100 | 38.5184 | -122.9749 | EOLPOLE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024996 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1261953 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024829&numberofmonths=24&showchangehistorylog=1 | 17-0024829 | SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1108 | 42631108 | FUSE | 1621 | 20170220 | 2247 | 1706489 | 833 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 35819 | 38.2569 | -122.7072 | 311MONTEVISTA | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024829 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1261798 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025246&numberofmonths=24&showchangehistorylog=1 | 17-0025246 | SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | FUSE | 3085 | 20170221 | 1410 | 1708756 | 411 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 8030 | 38.3692 | -122.5392 | MTR1007902549 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025246 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1262145 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024937&numberofmonths=24&showchangehistorylog=1 | 17-0024937 | SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | OTHER | WIREDOWN2SPANSLDSIDEOF9599 | 20170221 | 116 | 1707172 | 1090 | Distribution Circuit | Vegetation | Tree - fell into line | 171 | 137031 | 38.5362 | -123.2757 | 2SPANSLDSIDEOF9599 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024937 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1261911 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025268&numberofmonths=24&showchangehistorylog=1 | 17-0025268 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1101 | 42091101 | FUSE | 8347 | 20170221 | 1724 | 1709163 | 1251 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2502 | 38.4847 | -122.9777 | MTR100971862411945MAYSCANYONRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025268 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1262170 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024846&numberofmonths=24&showchangehistorylog=1 | 17-0024846 | SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | FUSE | 15707 | 20170221 | 140 | 1707245 | 729 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 19683 | 38.5448 | -122.6488 | 2SNOF15035 | Overcast-Drizzle-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0024846 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1261816 | CSO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037479&numberofmonths=24&showchangehistorylog=1 | 17-0037479 | SONOMA | FIELD OPS NORTH | Tier 2 | BELLEVUE-2103 | 43182103 | FUSE | 3789 | 20170406 | 2154 | 1748032 | 2290 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 84730 | 38.3913 | -122.6054 | 3400MATANCASCRLN | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037479 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1271695 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037238&numberofmonths=24&showchangehistorylog=1 | 17-0037238 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | RECLOSER | 132 | 20170406 | 1907 | 1746115 | 883 | Distribution Circuit | Vegetation | Tree - fell into line | 1017 | 145509 | 38.2647 | -122.8057 | FEEDINGMTR1009704835 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037238 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Line | 1271457 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037273&numberofmonths=24&showchangehistorylog=1 | 17-0037273 | SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | OCB | 11212 | 20170406 | 2009 | 1746631 | 2878 | Distribution Circuit | Vegetation | Tree - fell into line | 523 | 818800 | 38.5408 | -123.2237 | ALVAREZR3885ATCO9665 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0037273 | OH | Sus | 0 | yes | 2017 | APR | Yes | Multi-Fault | 1271493 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037736&numberofmonths=24&showchangehistorylog=1 | 17-0037736 | SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER | 560 | 20170406 | 2002 | 1750400 | 2893 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 89683 | 38.5562 | -123.3034 | FISKMILLCOVE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037736 | OH | Sus | 0 | yes | 2017 | APR | Yes | Multi-Fault | 1271931 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037737&numberofmonths=24&showchangehistorylog=1 | 17-0037737 | SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE | 11011 | 20170406 | 2009 | 1750403 | 2878 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 20146 | 38.5448 | -123.2926 | LDSIDEFU11011 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037737 | OH | Sus | 0 | yes | 2017 | APR | Yes | Open Circuit | 1271932 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037250&numberofmonths=24&showchangehistorylog=1 | 17-0037250 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 2027 | 20170406 | 1810 | 1745918 | 412 | Distribution Circuit | Vegetation | Tree - branch fell on line | 28 | 11536 | 38.5191 | -122.98 | MTR1008020358 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037250 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Line | 1271469 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037460&numberofmonths=24&showchangehistorylog=1 | 17-0037460 | SONOMA | FIELD OPS NORTH | Tier 3 | SANTA ROSA A-1104 | 42151104 | FUSE | 4891 | 20170406 | 2125 | 1747741 | 1363 | Distribution Circuit | Equipment Failure/Involved | Overhead | 126 | 135174 | 38.5114 | -122.7173 | MTR1007566100 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037460 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Line | 1271674 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0038029&numberofmonths=24&showchangehistorylog=1 | 17-0038029 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1102 | 42271102 | FUSE | 681 | 20170407 | 1553 | 1751214 | 188 | Distribution Circuit | Vegetation | Tree - fell into line | 129 | 10155 | 38.2838 | -122.7101 | MTR5000011186 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0038029 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1272103 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0038046&numberofmonths=24&showchangehistorylog=1 | 17-0038046 | SONOMA | FIELD OPS NORTH | Tier 2 | GEYSERVILLE-1101 | 42891101 | FUSE | 4703 | 20170407 | 1640 | 1751350 | 155 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 775 | 38.6718 | -123.0456 | 3SPANSLDSIDEOF4703 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0038046 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1272117 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037613&numberofmonths=24&showchangehistorylog=1 | 17-0037613 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | OTHER | WIREDOWN14950BITTNER | 20170407 | 241 | 1749224 | 608 | Distribution Circuit | Vegetation | Tree - fell into line | 388 | 8532 | 38.4051 | -122.9491 | 3SPANSLDSIDEOFLR31814950BITTNERTAP | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037613 | OH | Sus | 0 | yes | 2017 | APR | Yes | Open Circuit | 1271840 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037575&numberofmonths=24&showchangehistorylog=1 | 17-0037575 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | OTHER | WIREDOWN4660AUSTINCREEK | 20170407 | 220 | 1749220 | 800 | Distribution Circuit | Vegetation | Tree - fell into line | 282 | 87211 | 38.5172 | -123.0803 | 4660AUSTINCREEKRD | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037575 | OH | Sus | 0 | yes | 2017 | APR | Yes | Open Circuit | 1271797 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0089338&numberofmonths=24&showchangehistorylog=1 | 17-0089338 | SONOMA | FIELD OPS NORTH | Tier 3 | CLOVERDALE-1102 | 42821102 | FUSE | 1381 | 20171008 | 2324 | 1906698 | 19846 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 27 | 535842 | 38.773 | -122.9082 | BEYONDFUSE1381 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0089338 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Open Circuit | 1309821 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0087122&numberofmonths=24&showchangehistorylog=1 | 17-0087122 | SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1101 | 43071101 | JUMPER | OJSHIGHSIDEOFFU3749 | 20171008 | 2335 | 1900094 | 16805 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 33 | 539330 | 38.4004 | -122.5687 | 3SPANSLDSIDEOF3749 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0087122 | OH | Sus | 0 | yes | 2017 | OCT | Yes | None | 1308133 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0087147&numberofmonths=24&showchangehistorylog=1 | 17-0087147 | SONOMA | FIELD OPS NORTH | Tier 3 | DUNBAR-1101 | 43071101 | JUMPER | OJSONFIRSTTOEASTLOADSIDEOF1251TOEO | 20171008 | 2154 | 1900167 | 19746 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 19746 | 38.4476 | -122.5735 | NYSTROMERIK10584087998799LoadsideofLcos1251EOLrightfork | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0087147 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Open Circuit | 1308148 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0087205&numberofmonths=24&showchangehistorylog=1 | 17-0087205 | SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1101 | 43071101 | JUMPER | OJSIFO352GREENSTMTR1009779560 | 20171008 | 2358 | 1900347 | 15332 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 33 | 468604 | 38.4172 | -122.5576 | LDSIDEOFOJSIFO352GREENSTMTR1009779560 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0087205 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1308194 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0087504&numberofmonths=24&showchangehistorylog=1 | 17-0087504 | SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1101 | 43071101 | JUMPER | OJSONHARDTAPMTR41L229TOEOL | 20171008 | 2154 | 1901286 | 14034 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 7 | 98238 | 38.4258 | -122.5626 | MTR41L229 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0087504 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Open Circuit | 1308481 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0087580&numberofmonths=24&showchangehistorylog=1 | 17-0087580 | SONOMA | FIELD OPS NORTH | Tier 3 | DUNBAR-1101 | 43071101 | JUMPER | OJ1SPANSOURCESIDEOF18261 | 20171008 | 2358 | s1308557 | 19690 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 6 | 81458 | 38.4122 | -122.5098 | 182611SPANLOADSIDEOF182611SPANFROMEOL | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0087580 | OH | Sus | 0 | yes | 2017 | OCT | Yes | None | 1308557 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0087678&numberofmonths=24&showchangehistorylog=1 | 17-0087678 | SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1101 | 43071101 | FUSE | 6597 | 20171008 | 2336 | 1901716 | 16517 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 198204 | 38.432 | -122.5709 | 2SPANSLDSIDEOF6597 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0087678 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Open Circuit | 1308649 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0088276&numberofmonths=24&showchangehistorylog=1 | 17-0088276 | SONOMA | FIELD OPS NORTH | Tier 3 | DUNBAR-1101 | 43071101 | FUSE | 4943 | 20171008 | 2335 | 1903260 | 16495 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 19 | 313405 | 38.3999 | -122.572 | LDSIDEOF4943 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0088276 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Open Circuit | 1309027 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0086444&numberofmonths=24&showchangehistorylog=1 | 17-0086444 | SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | FUSE | 8857 | 20171008 | 2350 | 1898756 | 12720 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 5 | 51364 | 38.3731 | -122.5241 | LDSIDEOF8857 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086444 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1307546 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0086901&numberofmonths=24&showchangehistorylog=1 | 17-0086901 | SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1103 | 43071103 | JUMPER | OJ1PNOFMTR5000038774 | 20171008 | 2350 | 1899662 | 15147 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 4 | 60588 | 38.3793 | -122.5111 | MTR5000038774 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086901 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1307923 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0085970&numberofmonths=24&showchangehistorylog=1 | 17-0085970 | SONOMA | FIELD OPS NORTH | Tier 2 | FULTON-1102 | 42561102 | FUSE | 751 | 20171008 | 2150 | 1897466 | 2410 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 87406 | 38.6311 | -122.77 | ONHARDTAPTOMTR1006874856 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0085970 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Three Phase Fault | 1307225 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0085384&numberofmonths=24&showchangehistorylog=1 | 17-0085384 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | TRIP-SAVER | 6917 | 20171008 | 2333 | 1894391 | 2437 | Distribution Circuit | Equipment Failure/Involved | Overhead | 77 | 187649 | 38.3873 | -122.9728 | 6SPANLDOF6917 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085384 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1306837 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0085772&numberofmonths=24&showchangehistorylog=1 | 17-0085772 | SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1101 | 43321101 | JUMPER | OJ1SPANSOF13169 | 20171008 | 2326 | 1896967 | 6704 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 60336 | 38.4637 | -122.6089 | 2SPANSFROM13169 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085772 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Line | 1307094 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0087394&numberofmonths=24&showchangehistorylog=1 | 17-0087394 | SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | FUSE | 7207 | 20171008 | 2317 | 1900887 | 19569 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 1 | 19569 | 38.5252 | -122.6619 | MTR1007803583 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0087394 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Open Circuit | 1308374 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0087420&numberofmonths=24&showchangehistorylog=1 | 17-0087420 | SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | FUSE | 2225 | 20171008 | 2317 | 1901016 | 9687 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 90 | 871830 | 38.5242 | -122.6544 | FUCO22251STSPANNOF2225 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0087420 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Open Circuit | 1308406 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0087422&numberofmonths=24&showchangehistorylog=1 | 17-0087422 | SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | RECLOSER | 5152 | 20171008 | 2317 | 1901028 | 21108 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 53 | 136988 | 38.5499 | -122.6678 | LEYENDECKERT6613430151Multiplelocations | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0087422 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1308408 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0087384&numberofmonths=24&showchangehistorylog=1 | 17-0087384 | SONOMA | FIELD OPS NORTH | Tier 3 | SANTA ROSA A-1104 | 42151104 | JUMPER | OJONTAPTOMTR1007530457 | 20171008 | 2240 | 1900838 | 11229 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 1 | 11229 | 38.5111 | -122.7161 | TRANSFPOLEATMTR1007530457 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0087384 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Open Circuit | 1308367 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0087517&numberofmonths=24&showchangehistorylog=1 | 17-0087517 | SONOMA | FIELD OPS NORTH | Tier 3 | SANTA ROSA A-1104 | 42151104 | FUSE | 6891 | 20171008 | 2240 | 1901320 | 18032 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 11 | 198352 | 38.502 | -122.6999 | LDSIDEOFFUCO6891 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0087517 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1308496 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0087522&numberofmonths=24&showchangehistorylog=1 | 17-0087522 | SONOMA | FIELD OPS NORTH | Tier 3 | SANTA ROSA A-1104 | 42151104 | FUSE | 8765 | 20171008 | 2331 | 1901328 | 12595 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 2 | 25190 | 38.4961 | -122.6838 | LDSIDEOF8765 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0087522 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1308501 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0087524&numberofmonths=24&showchangehistorylog=1 | 17-0087524 | SONOMA | FIELD OPS NORTH | Tier 3 | SANTA ROSA A-1104 | 42151104 | FUSE | 3679 | 20171008 | 2331 | 1901331 | 18409 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 46 | 846454 | 38.4966 | -122.6849 | BERRIOS5176linepastco3679 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0087524 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Line | 1308503 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0087553&numberofmonths=24&showchangehistorylog=1 | 17-0087553 | SONOMA | FIELD OPS NORTH | Tier 2 | SANTA ROSA A-1104 | 42151104 | FUSE | 15173 | 20171008 | 2240 | 1901380 | 12560 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 3 | 37680 | 38.5052 | -122.6923 | ATEOL | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0087553 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Force Out | 1308532 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0087723&numberofmonths=24&showchangehistorylog=1 | 17-0087723 | SONOMA | FIELD OPS NORTH | Tier 3 | SANTA ROSA A-1104 | 42151104 | FUSE | 12107 | 20171008 | 2331 | 1901847 | 12669 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 19 | 240711 | 38.4995 | -122.675 | 2175CALISTOGARD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0087723 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Force Out | 1308678 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0087940&numberofmonths=24&showchangehistorylog=1 | 17-0087940 | SONOMA | FIELD OPS NORTH | Tier 3 | SANTA ROSA A-1104 | 42151104 | FUSE | 3451 | 20171008 | 2240 | 1902478 | 19435 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 57 | 1106870 | 38.5114 | -122.7114 | 53815363WILSHIREDR | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0087940 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Force Out | 1308825 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0088077&numberofmonths=24&showchangehistorylog=1 | 17-0088077 | SONOMA | FIELD OPS NORTH | Tier 3 | SANTA ROSA A-1104 | 42151104 | FUSE | 8773 | 20171008 | 2240 | 1902794 | 15602 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 5 | 78010 | 38.5004 | -122.6941 | LDSIDEOFFUCO8773 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0088077 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Force Out | 1308884 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0088207&numberofmonths=24&showchangehistorylog=1 | 17-0088207 | SONOMA | FIELD OPS NORTH | Tier 3 | SANTA ROSA A-1104 | 42151104 | FUSE | 6583 | 20171008 | 2240 | 1903137 | 13945 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 2 | 27890 | 38.5075 | -122.7078 | LDSIDEOF6583 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0088207 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1308980 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0089504&numberofmonths=24&showchangehistorylog=1 | 17-0089504 | SONOMA | FIELD OPS NORTH | Tier 3 | SANTA ROSA A-1104 | 42151104 | JUMPER | OJS5SPANSSWOFFUCO1823 | 20171008 | 2240 | 1907299 | 19803 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 5 | 99015 | 38.5206 | -122.7121 | DANADR | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0089504 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1309968 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0085345&numberofmonths=24&showchangehistorylog=1 | 17-0085345 | SONOMA | FIELD OPS NORTH | Tier 3 | SONOMA-1102 | 42721102 | FUSE | 6939 | 20171008 | 2330 | 1894367 | 9843 | Distribution Circuit | Vegetation | Tree - bark fell into line | 15 | 50106 | 38.3193 | -122.4575 | 17355HIGHRD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085345 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1306795 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0086414&numberofmonths=24&showchangehistorylog=1 | 17-0086414 | SONOMA | FIELD OPS NORTH | Tier 3 | BELLEVUE-2103 | 43182103 | FUSE | 7197 | 20171009 | 313 | 1898660 | 13587 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 17 | 230979 | 38.3926 | -122.6062 | 3PLDSD7197 | Clear-32-90 F | Pole-Wood | Broken, wire on object | 17-0086414 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Open Circuit | 1307511 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0086452&numberofmonths=24&showchangehistorylog=1 | 17-0086452 | SONOMA | FIELD OPS NORTH | Tier 3 | BELLEVUE-2103 | 43182103 | FUSE | 11331 | 20171009 | 313 | 1898790 | 13693 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 581551 | 38.3916 | -122.5986 | 1PLOADSIDEOF11331HARDTAPTOWEST | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0086452 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1307558 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0087204&numberofmonths=24&showchangehistorylog=1 | 17-0087204 | SONOMA | FIELD OPS NORTH | Tier 2 | CLOVERDALE-1102 | 42821102 | FUSE | 15705 | 20171009 | 30 | 1900344 | 7846 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 31384 | 38.8681 | -123.0375 | LOADSIDEOF15705 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0087204 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Force Out | 1308193 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0086872&numberofmonths=24&showchangehistorylog=1 | 17-0086872 | SONOMA | FIELD OPS NORTH | Tier 3 | DUNBAR-1102 | 43071102 | FUSE | 7015 | 20171009 | 136 | 1899587 | 16703 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 9 | 150327 | 38.3667 | -122.5898 | 5800SONOMAMOUNTAINRD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086872 | OH | Sus | 0 | yes | 2017 | OCT | Yes | None | 1307902 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0087154&numberofmonths=24&showchangehistorylog=1 | 17-0087154 | SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | JUMPER | OPENDDE1PWOFLINEBUCKSOFC2904TWD | 20171009 | 417 | 1900182 | 19584 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 275 | 3394903 | 38.3646 | -122.5259 | 1PWOFLINEBUCKSOFC2904TWD246 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0087154 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Open Circuit | 1308152 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0087154&numberofmonths=24&showchangehistorylog=1 | 17-0087154 | SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | FUSE | 11177 | 20171009 | 417 | 1900920 | 12347 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 14 | 172858 | 38.3737 | -122.5458 | 3SPANSLOADSIDEOF11177 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0087154 | OH | Sus | 0 | yes | 2017 | OCT | Yes | None | 1308383 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0087779&numberofmonths=24&showchangehistorylog=1 | 17-0087779 | SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | JUMPER | OJS2SSSOFMTR1006220457 | 20171009 | 412 | 1902088 | 17673 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 1 | 17673 | 38.3675 | -122.52 | MTR1006220457 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0087779 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Multi-Fault | 1308713 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0085419&numberofmonths=24&showchangehistorylog=1 | 17-0085419 | SONOMA | FIELD OPS NORTH | Tier 2 | PENNGROVE-1101 | 43471101 | FUSE | 4683 | 20171009 | 36 | 1894682 | 2251 | Distribution Circuit | Vegetation | Tree - branch fell on line | 49 | 66143 | 38.3267 | -122.6316 | MTR1007686939 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085419 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1306870 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0086666&numberofmonths=24&showchangehistorylog=1 | 17-0086666 | SONOMA | FIELD OPS NORTH | Tier 2 | RINCON-1102 | 43321102 | FUSE | 15265 | 20171009 | 138 | 1896669 | 10977 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 19 | 208131 | 38.4896 | -122.6673 | LOADSIDEOF15265 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086666 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Line | 1307761 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0087371&numberofmonths=24&showchangehistorylog=1 | 17-0087371 | SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | FUSE | 14985 | 20171009 | 17 | 1900801 | 19756 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 3 | 59268 | 38.5505 | -122.6513 | MONSIBAISMANNY661599760414985 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0087371 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Open Circuit | 1308354 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0087372&numberofmonths=24&showchangehistorylog=1 | 17-0087372 | SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | FUSE | 2223 | 20171009 | 17 | 1900803 | 19704 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 43 | 847272 | 38.5471 | -122.6692 | 363WITTRD456POLESEOF2223 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0087372 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Line | 1308355 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0085746&numberofmonths=24&showchangehistorylog=1 | 17-0085746 | SONOMA | FIELD OPS NORTH | Tier 3 | SANTA ROSA A-1104 | 42151104 | FUSE | 69401 | 20171009 | 1605 | 1896824 | 2706 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 10824 | 38.4658 | -122.6936 | 1SPANSOFFUCO69401 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085746 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Line | 1307070 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0087473&numberofmonths=24&showchangehistorylog=1 | 17-0087473 | SONOMA | FIELD OPS NORTH | Tier 3 | SANTA ROSA A-1104 | 42151104 | FUSE | 7411 | 20171009 | 141 | 1901218 | 17881 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 18 | 321858 | 38.5117 | -122.692 | LDSIDEOF7411 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0087473 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1308459 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0087527&numberofmonths=24&showchangehistorylog=1 | 17-0087527 | SONOMA | FIELD OPS NORTH | Tier 3 | SANTA ROSA A-1104 | 42151104 | FUSE | 10107 | 20171009 | 211 | 1901335 | 13934 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 3 | 41802 | 38.5009 | -122.6864 | LEYENDECKERT66134301511PoleWOFUCO10107 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0087527 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Open Circuit | 1308506 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0087528&numberofmonths=24&showchangehistorylog=1 | 17-0087528 | SONOMA | FIELD OPS NORTH | Tier 2 | SANTA ROSA A-1104 | 42151104 | FUSE | 12711 | 20171009 | 211 | 1901336 | 12122 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 5 | 60610 | 38.4984 | -122.6862 | LDSIDEOFFUCO12711 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0087528 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1308507 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0087529&numberofmonths=24&showchangehistorylog=1 | 17-0087529 | SONOMA | FIELD OPS NORTH | Tier 2 | SANTA ROSA A-1104 | 42151104 | FUSE | 3943 | 20171009 | 211 | 1901338 | 20796 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 9 | 187164 | 38.5006 | -122.6863 | LDSIDEOF3945 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0087529 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Open Circuit | 1308508 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0088299&numberofmonths=24&showchangehistorylog=1 | 17-0088299 | SONOMA | FIELD OPS NORTH | Tier 3 | SANTA ROSA A-1104 | 42151104 | SWITCH | 9267 | 20171009 | 141 | 1903332 | 25429 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 49 | 974037 | 38.5168 | -122.6797 | EVERYWHERE | Clear-32-90 F | Other | Broken, wire on ground | 17-0088299 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Multi-Fault | 1309037 | NON | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0087806&numberofmonths=24&showchangehistorylog=1 | 17-0087806 | SONOMA | FIELD OPS NORTH | Tier 2 | SONOMA-1105 | 42721105 | SWITCH | 532235 | 20171009 | 147 | 1902150 | 19500 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 132 | 2574000 | 38.2927 | -122.4132 | MULTIPLE | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0087806 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Open Circuit | 1308726 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0089267&numberofmonths=24&showchangehistorylog=1 | 17-0089267 | SONOMA | FIELD OPS NORTH | Tier 3 | DUNBAR-1101 | 43071101 | JUMPER | OJSNOHOMEBEYOND | 20171020 | 1740 | 1906463 | 2767 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 5534 | 38.3989 | -122.5708 | 2577KAISERRD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0089267 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Force Out | 1309750 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0099652&numberofmonths=24&showchangehistorylog=1 | 17-0099652 | SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | FUSE | 81221 | 20171204 | 1131 | 1934989 | 424 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 4240 | 38.3819 | -122.5513 | 2555WARMSPRINGSRDEOFBENNETVLYRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0099652 | OH | Sus | 0 | yes | 2017 | DEC | Yes | Line to Line | 1317428 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0101716&numberofmonths=24&showchangehistorylog=1 | 18-0101716 | SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | TRIP-SAVER | 4947 | 20181121 | 521 | 219567 | 787 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 42298 | 38.5577 | -123.0969 | MTR1009718295 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0101716 | OH | Sus | 43584951 | yes | 2018 | NOV | Yes | Line to Line | 1393976 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0105199&numberofmonths=24&showchangehistorylog=1 | 18-0105199 | SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | TRIP-SAVER | 1285 | 20181129 | 1301 | 229048 | 720 | Distribution Circuit | Vegetation | Tree - branch fell on line | 59 | 40142 | 38.328 | -122.5221 | VegetationTreebranchfellonline | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0105199 | OH | Sus | 0 | yes | 2018 | NOV | Yes | Line to Ground | 1396365 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0105283&numberofmonths=24&showchangehistorylog=1 | 18-0105283 | SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1104 | 43321104 | FUSE | 2269 | 20181129 | 1611 | 229419 | 1329 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 31896 | 38.5183 | -122.6032 | 8570NEALCREEKRD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0105283 | OH | Sus | 0 | yes | 2018 | NOV | Yes | Line to Line | 1396392 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005503&numberofmonths=24&showchangehistorylog=1 | 19-0005503 | SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE | 4545 | 20190106 | 2009 | 257482 | 1021 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 9189 | 38.5928 | -123.3018 | 35905HOWSERBRIDGERD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005503 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1403951 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005073&numberofmonths=24&showchangehistorylog=1 | 19-0005073 | SONOMA | FIELD OPS NORTH | Tier 2 | GEYSERVILLE-1102 | 42891102 | FUSE | 523 | 20190106 | 1230 | 255247 | 155 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 4340 | 38.6573 | -122.8317 | Nott35691447ALEXANDERVALLEYRD | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005073 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Multi-Fault | 1403546 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005082&numberofmonths=24&showchangehistorylog=1 | 19-0005082 | SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | FUSE | 15035 | 20190106 | 1142 | 255169 | 378 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 4158 | 38.5466 | -122.6442 | 3POLESLDSIDEOF15035 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005082 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1403554 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0009930&numberofmonths=24&showchangehistorylog=1 | 19-0009930 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | FUSE | 2443 | 20190116 | 1434 | 267187 | 1531 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 13431 | 38.1938 | -122.911 | 1STAND2NDSPANLDSIDE2443 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009930 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1406801 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010286&numberofmonths=24&showchangehistorylog=1 | 19-0010286 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | OTHER | WIREDOWN310KINGRD | 20190116 | 1904 | 271160 | 1200 | Distribution Circuit | Vegetation | Tree - fell into line | 227 | 260078 | 38.2711 | -122.7155 | 310KINGRD | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010286 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407151 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0009868&numberofmonths=24&showchangehistorylog=1 | 19-0009868 | SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | TRIP-SAVER | 6751 | 20190116 | 1450 | 267251 | 256 | Distribution Circuit | Vegetation | Tree - branch fell on line | 134 | 15145 | 38.592 | -122.9622 | MOORED3612APPROX2POLESLOADSIDEFUSE781 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009868 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Three Phase Fault | 1406748 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0009997&numberofmonths=24&showchangehistorylog=1 | 19-0009997 | SONOMA | FIELD OPS NORTH | Tier 2 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 16211 | 20190116 | 1748 | 267899 | 2502 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 20397 | 38.5811 | -122.8913 | Rendon4754RO1700FELTARD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009997 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1406863 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010313&numberofmonths=24&showchangehistorylog=1 | 19-0010313 | SONOMA | FIELD OPS NORTH | Tier 2 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 6049 | 20190116 | 1900 | 269566 | 2454 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 9816 | 38.5986 | -122.912 | MTR10081050402955WALLACECREEKRD | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010313 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Open Circuit | 1407178 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010519&numberofmonths=24&showchangehistorylog=1 | 19-0010519 | SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | OTHER | HOTWIREDOWN3SSOF6263 | 20190116 | 1832 | 272312 | 1361 | Distribution Circuit | Vegetation | Tree - branch fell on line | 138 | 166097 | 38.5853 | -122.952 | 3SSOF62635707MILLCREEKRD | Overcast-Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0010519 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Open Circuit | 1407382 | CAW | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011389&numberofmonths=24&showchangehistorylog=1 | 19-0011389 | SONOMA | FIELD OPS NORTH | Tier 3 | FULTON-1107 | 42561107 | FUSE | 11889 | 20190116 | 1829 | 269281 | 2483 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 27313 | 38.5574 | -122.6791 | HESSONG3884LOADSIDEOF11889ATMTR1010344775 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on object | 19-0011389 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Force Out | 1407934 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0009962&numberofmonths=24&showchangehistorylog=1 | 19-0009962 | SONOMA | FIELD OPS NORTH | Tier 2 | GEYSERVILLE-1101 | 42891101 | FUSE | 5531 | 20190116 | 1455 | 267287 | 2980 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 51425 | 38.6773 | -123.0625 | 4SPANSLDSIDEOF793 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009962 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1406831 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0009869&numberofmonths=24&showchangehistorylog=1 | 19-0009869 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1101 | 42091101 | OTHER | 1SSSTO12061WIREDOWN | 20190116 | 1519 | 267795 | 3913 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 114879 | 38.4839 | -122.9149 | KOTULAJON43438350Martinellird | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009869 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Open Circuit | 1406749 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011618&numberofmonths=24&showchangehistorylog=1 | 19-0011618 | SONOMA | FIELD OPS NORTH | Tier 2 | MIRABEL-1101 | 42091101 | FUSE | 6485 | 20190116 | 2045 | 270806 | 2765 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 22120 | 38.4668 | -122.9087 | 750GIOVANETTIRD | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011618 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1408112 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011036&numberofmonths=24&showchangehistorylog=1 | 19-0011036 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 1335 | 20190116 | 2243 | 271679 | 2612 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 96644 | 38.4975 | -122.9417 | 11937PINERIDGERD | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0011036 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1407690 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010090&numberofmonths=24&showchangehistorylog=1 | 19-0010090 | SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1101 | 42571101 | FUSE | 1761 | 20190116 | 1522 | 267478 | 1588 | Distribution Circuit | Vegetation | Tree - branch fell on line | 33 | 52404 | 38.379 | -122.8978 | MooreS4308METER1004759381 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010090 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1406957 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010428&numberofmonths=24&showchangehistorylog=1 | 19-0010428 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1101 | 42571101 | FUSE | 6051 | 20190116 | 1812 | 269199 | 1149 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 90771 | 38.3819 | -122.9033 | MooreS4308808JONIVERD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010428 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1407293 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010518&numberofmonths=24&showchangehistorylog=1 | 19-0010518 | SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1101 | 42571101 | TRIP-SAVER | 891 | 20190116 | 1825 | 269411 | 2684 | Distribution Circuit | Vegetation | Tree - fell into line | 94 | 53036 | 38.3901 | -122.8854 | 413DUSTYLN | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010518 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407381 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0009804&numberofmonths=24&showchangehistorylog=1 | 19-0009804 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 7317 | 20190116 | 1453 | 267275 | 265 | Distribution Circuit | Vegetation | Tree - branch fell on line | 28 | 7420 | 38.3942 | -122.9218 | 2SPANSLDSIDEOF7317 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009804 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1406700 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010411&numberofmonths=24&showchangehistorylog=1 | 19-0010411 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 4899 | 20190116 | 1829 | 272008 | 2346 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 23028 | 38.4083 | -122.9373 | MooreS43084SPANSLDSIDEOF4899ONSINGLEPHASE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010411 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407276 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010577&numberofmonths=24&showchangehistorylog=1 | 19-0010577 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 11991 | 20190116 | 1626 | 272510 | 1658 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 46424 | 38.4388 | -122.9405 | 2SPANSLDSIDEOF11991 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010577 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407440 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010594&numberofmonths=24&showchangehistorylog=1 | 19-0010594 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 7183 | 20190116 | 1830 | 272660 | 1125 | Distribution Circuit | Vegetation | Tree - branch fell on line | 40 | 45000 | 38.3781 | -122.9683 | MooreS43082070JOYRIDGERD | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010594 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1407458 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0009575&numberofmonths=24&showchangehistorylog=1 | 19-0009575 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | TRIP-SAVER | 53477 | 20190116 | 1040 | 266734 | 343 | Distribution Circuit | Vegetation | Tree - branch fell on line | 56 | 18548 | 38.4961 | -123.0693 | BETFUCO8139ANDFUCO2579 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009575 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1406584 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0009960&numberofmonths=24&showchangehistorylog=1 | 19-0009960 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 15399 | 20190116 | 1609 | 267714 | 226 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 11978 | 38.4247 | -122.9608 | MTR5N6678 | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 19-0009960 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1406829 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010284&numberofmonths=24&showchangehistorylog=1 | 19-0010284 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | OTHER | WIREDOWN1SPLDSD1581 | 20190116 | 1721 | 270517 | 1511 | Distribution Circuit | Vegetation | Tree - branch fell on line | 505 | 471427 | 38.4929 | -123.0622 | MAINLINE1SPLDSIDE1581ANDAT26611STSPLDSD64758 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010284 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Open Circuit | 1407149 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011220&numberofmonths=24&showchangehistorylog=1 | 19-0011220 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 74315 | 20190116 | 1741 | 270792 | 2570 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 51400 | 38.491 | -123.0602 | 1STSPANLDSIDEOF74315 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011220 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407804 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011309&numberofmonths=24&showchangehistorylog=1 | 19-0011309 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE | 439 | 20190116 | 1958 | 270264 | 2894 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 43410 | 38.4631 | -123.0122 | 6POLESLOADSIDEFUSE439 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011309 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1407869 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0009626&numberofmonths=24&showchangehistorylog=1 | 19-0009626 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 2027 | 20190116 | 1207 | 266854 | 264 | Distribution Circuit | Vegetation | Tree - branch fell on line | 27 | 7128 | 38.5191 | -122.98 | 3SPANSLDSIDEOF2027 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009626 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1406621 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0009770&numberofmonths=24&showchangehistorylog=1 | 19-0009770 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 15609 | 20190116 | 1441 | 267208 | 324 | Distribution Circuit | Vegetation | Tree - branch fell on line | 98 | 31752 | 38.5128 | -122.9982 | LDSIDEOF15609 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009770 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1406675 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010452&numberofmonths=24&showchangehistorylog=1 | 19-0010452 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 1031 | 20190116 | 2025 | 270607 | 2543 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 61032 | 38.4926 | -122.9614 | 6SPANSLDSIDEOF1031 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010452 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407316 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010992&numberofmonths=24&showchangehistorylog=1 | 19-0010992 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | TRIP-SAVER | 1067 | 20190116 | 2010 | 270390 | 1052 | Distribution Circuit | Vegetation | Tree - fell into line | 109 | 114668 | 38.4934 | -123.0059 | 16731GUERENWOODAVE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010992 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407657 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011011&numberofmonths=24&showchangehistorylog=1 | 19-0011011 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 1993 | 20190116 | 2123 | 273321 | 1356 | Distribution Circuit | Vegetation | Tree - branch fell on line | 25 | 33900 | 38.5275 | -123.0008 | Nott356916881ARMSTRONGWOODSRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011011 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1407675 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011193&numberofmonths=24&showchangehistorylog=1 | 19-0011193 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 7709 | 20190116 | 2112 | 270941 | 2438 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 19504 | 38.5075 | -123.0294 | GOLLANS347315550CAMINODELARROYO | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011193 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1407790 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010085&numberofmonths=24&showchangehistorylog=1 | 19-0010085 | SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1108 | 42631108 | FUSE | 3331 | 20190116 | 1757 | 268867 | 2634 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 52680 | 38.194 | -122.7092 | MTR1008840836 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010085 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1406951 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011442&numberofmonths=24&showchangehistorylog=1 | 19-0011442 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | FUSE | 4571 | 20190117 | 2022 | 275008 | 1004 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2008 | 38.1681 | -122.8937 | 2PLDSIDEOF4571 | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 19-0011442 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Force Out | 1407982 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011665&numberofmonths=24&showchangehistorylog=1 | 19-0011665 | SONOMA | FIELD OPS NORTH | Tier 3 | FORT ROSS-1121 | 42851121 | TRIP-SAVER | 2987 | 20190117 | 459 | 272558 | 1962 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 154998 | 38.5419 | -123.09 | 1MILENOF2987 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011665 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1408151 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011667&numberofmonths=24&showchangehistorylog=1 | 19-0011667 | SONOMA | FIELD OPS NORTH | Tier 3 | FORT ROSS-1121 | 42851121 | FUSE | 11513 | 20190117 | 1629 | 274567 | 2630 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 26300 | 38.5314 | -123.1329 | LDSIDEOF11513BET2ND3RDPOLES | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011667 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1408152 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011668&numberofmonths=24&showchangehistorylog=1 | 19-0011668 | SONOMA | FIELD OPS NORTH | Tier 3 | FORT ROSS-1121 | 42851121 | FUSE | 13477 | 20190117 | 806 | 272990 | 1923 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1923 | 38.5271 | -123.1513 | 400COLINDARD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011668 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1408154 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011085&numberofmonths=24&showchangehistorylog=1 | 19-0011085 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | OTHER | HOTWIREDOWN1SNOF6543 | 20190117 | 702 | 274066 | 678 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 24066 | 38.3689 | -122.964 | 1865JOYRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011085 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407712 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010876&numberofmonths=24&showchangehistorylog=1 | 19-0010876 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 15455 | 20190117 | 823 | 273062 | 1680 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 8400 | 38.4761 | -122.9521 | 1SLDSIDEOFFUSES15455 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010876 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407583 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010966&numberofmonths=24&showchangehistorylog=1 | 19-0010966 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | TRIP-SAVER | 4859 | 20190117 | 802 | 272971 | 600 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 28800 | 38.4755 | -122.9527 | INGRAM425314025GREENVALLEYRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010966 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1407635 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011322&numberofmonths=24&showchangehistorylog=1 | 19-0011322 | SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1108 | 42631108 | OTHER | HOTWIREDOWN4SLSOF667 | 20190117 | 1052 | 274703 | 1455 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 5820 | 38.2184 | -122.7086 | 4SLSOF667 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011322 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Open Circuit | 1407876 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011487&numberofmonths=24&showchangehistorylog=1 | 19-0011487 | SONOMA | FIELD OPS NORTH | Tier 3 | SALMON CREEK-1101 | 43161101 | FUSE | 615 | 20190117 | 2320 | 275085 | 1177 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 3531 | 38.3639 | -122.9803 | 2SPANSAND4SPANSLDSIDEOF615 | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011487 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Multi-Fault | 1408029 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018037&numberofmonths=24&showchangehistorylog=1 | 19-0018037 | SONOMA | FIELD OPS NORTH | Tier 3 | DUNBAR-1101 | 43071101 | FUSE | 481459 | 20190204 | 1329 | 290547 | 365 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 730 | 38.4099 | -122.5735 | 1SWESTOF481459 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0018037 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1412310 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020377&numberofmonths=24&showchangehistorylog=1 | 19-0020377 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | RECLOSER | 132 | 20190209 | 1628 | 297191 | 1225 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1019 | 544883 | 38.2647 | -122.8057 | DeignanPat35715200MIDDLERD4SOC712 | Partly Cloudy-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0020377 | OH | Sus | 43672759 | yes | 2019 | FEB | Yes | Force Out | 1414050 | CSO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020629&numberofmonths=24&showchangehistorylog=1 | 19-0020629 | SONOMA | FIELD OPS NORTH | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE | 4585 | 20190210 | 912 | 297225 | 206 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 412 | 38.6609 | -123.2922 | 4SPANSSSOF4605 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020629 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1414320 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021884&numberofmonths=24&showchangehistorylog=1 | 19-0021884 | SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER | 134 | 20190212 | 1810 | 300950 | 1434 | Distribution Circuit | Vegetation | Tree - branch fell on line | 229 | 248170 | 38.5588 | -123.2702 | 5SOURCESIDEOFLR560 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021884 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Three Phase Fault | 1415329 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021522&numberofmonths=24&showchangehistorylog=1 | 19-0021522 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 12003 | 20190212 | 1520 | 300805 | 325 | Distribution Circuit | Vegetation | Tree - fell into line | 247 | 18338 | 38.4104 | -122.9539 | 15275COLEMANVALLEYRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021522 | OH | Sus | 43678033 | yes | 2019 | FEB | Yes | Line to Ground | 1414980 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021683&numberofmonths=24&showchangehistorylog=1 | 19-0021683 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 883 | 20190212 | 2254 | 301430 | 676 | Distribution Circuit | Vegetation | Tree - fell into line | 247 | 166972 | 38.4074 | -122.9484 | 3SPANSLOADSIDE883 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021683 | OH | Sus | 43678389 | yes | 2019 | FEB | Yes | Line to Ground | 1415130 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022647&numberofmonths=24&showchangehistorylog=1 | 19-0022647 | SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | RECLOSER | 24918 | 20190213 | 2208 | 305797 | 609 | Distribution Circuit | Vegetation | Tree - branch fell on line | 187 | 113883 | 38.5914 | -122.92 | HESSONG38842NDSPANLOADSIDELR249183450MILLCREEKRD | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022647 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1415880 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022552&numberofmonths=24&showchangehistorylog=1 | 19-0022552 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1101 | 42091101 | FUSE | 1939 | 20190213 | 1748 | 305424 | 1705 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 15345 | 38.4782 | -122.9384 | 2LDSIDEOFFUCO1939 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022552 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1415789 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022539&numberofmonths=24&showchangehistorylog=1 | 19-0022539 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 56225 | 20190213 | 1700 | 305331 | 1570 | Distribution Circuit | Vegetation | Tree - branch fell on line | 37 | 58090 | 38.4847 | -123.0587 | MTR1009705536 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022539 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1415778 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023156&numberofmonths=24&showchangehistorylog=1 | 19-0023156 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1102 | 42271102 | TRANSFORMER | 217930822751 | 20190214 | 1138 | 307125 | 545 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 1090 | 38.2891 | -122.722 | 1SPANLDSIDEOFCGC217933722757 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023156 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416347 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023075&numberofmonths=24&showchangehistorylog=1 | 19-0023075 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | FUSE | 3421 | 20190214 | 714 | 307326 | 1836 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 12852 | 38.2866 | -122.8527 | 15LDSIDEOF3421 | Overcast-Fog-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023075 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416276 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023305&numberofmonths=24&showchangehistorylog=1 | 19-0023305 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | FUSE | 4571 | 20190214 | 1335 | 309444 | 1705 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 3410 | 38.1681 | -122.8937 | 3LDSIDEOF4571 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023305 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416489 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022725&numberofmonths=24&showchangehistorylog=1 | 19-0022725 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1105 | 42271105 | RECLOSER | 99720 | 20190214 | 102 | 306093 | 1212 | Distribution Circuit | Vegetation | Tree - fell into line | 375 | 146016 | 38.3456 | -122.7784 | 4587BLANKRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022725 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1415963 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023097&numberofmonths=24&showchangehistorylog=1 | 19-0023097 | SONOMA | FIELD OPS NORTH | Tier 2 | MIRABEL-1101 | 42091101 | FUSE | 2007 | 20190214 | 822 | 307730 | 1878 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 9390 | 38.4524 | -122.9034 | FUCO2007 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023097 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1416294 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022908&numberofmonths=24&showchangehistorylog=1 | 19-0022908 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 49587 | 20190214 | 243 | 307636 | 1896 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 9480 | 38.5057 | -122.9565 | 1STSPANLDSIDEOF49587 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022908 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416142 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023155&numberofmonths=24&showchangehistorylog=1 | 19-0023155 | SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1101 | 42571101 | FUSE | 12801 | 20190214 | 809 | 307621 | 1800 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 7200 | 38.3644 | -122.8825 | LDSIDEOF12801 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023155 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1416346 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022797&numberofmonths=24&showchangehistorylog=1 | 19-0022797 | SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1102 | 42571102 | FUSE | 525 | 20190214 | 221 | 306375 | 519 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 19722 | 38.4049 | -122.8963 | 2SPANSLDSIDEOF525 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022797 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1416040 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023186&numberofmonths=24&showchangehistorylog=1 | 19-0023186 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 7499 | 20190214 | 1211 | 308918 | 1815 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 5445 | 38.4675 | -123.0167 | 21611HIGHLANDTERRACE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023186 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1416377 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023123&numberofmonths=24&showchangehistorylog=1 | 19-0023123 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 7927 | 20190214 | 201 | 307665 | 3328 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 49920 | 38.5048 | -123.0053 | 14742GABESROCKRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023123 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1416315 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023738&numberofmonths=24&showchangehistorylog=1 | 19-0023738 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | RECLOSER | 11132 | 20190214 | 2215 | 310977 | 3917 | Distribution Circuit | Vegetation | Tree - fell into line | 3897 | 403375 | 38.5037 | -122.9936 | RIVERRDATLR4890EASTENDOFKORBEL1SPANSSOFOFLR4890 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0023738 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Multi-Fault | 1416888 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022753&numberofmonths=24&showchangehistorylog=1 | 19-0022753 | SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1108 | 42631108 | RECLOSER | 636 | 20190214 | 245 | 306425 | 847 | Distribution Circuit | Vegetation | Tree - fell into line | 141 | 36769 | 38.2618 | -122.7158 | 1PLDSIDEOF2865ONMAINLINE | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022753 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1415993 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022833&numberofmonths=24&showchangehistorylog=1 | 19-0022833 | SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1108 | 42631108 | OTHER | WIREDOWN3SPANSLDSIDEOF7515 | 20190214 | 156 | 306893 | 916 | Distribution Circuit | Vegetation | Tree - fell into line | 138 | 86236 | 38.2212 | -122.6692 | 3SPANSLDSIDEOF7515 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022833 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416080 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022857&numberofmonths=24&showchangehistorylog=1 | 19-0022857 | SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1108 | 42631108 | FUSE | 1627 | 20190214 | 21 | 306046 | 921 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 49734 | 38.2416 | -122.6985 | 4SPANSLDSIDEOF1627 | Overcast-Fog-Lightning-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022857 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Three Phase Fault | 1416099 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022889&numberofmonths=24&showchangehistorylog=1 | 19-0022889 | SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1108 | 42631108 | FUSE | 12217 | 20190214 | 711 | 307157 | 769 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 2307 | 38.2234 | -122.6695 | 2NDSPANLDSIDEOF12217 | Overcast-Fog-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022889 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416126 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023589&numberofmonths=24&showchangehistorylog=1 | 19-0023589 | SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1108 | 42631108 | FUSE | 12223 | 20190214 | 1630 | 310194 | 1465 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1465 | 38.2429 | -122.7529 | 2SPANSLDSIDEOFFUCO12223 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023589 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1416737 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022920&numberofmonths=24&showchangehistorylog=1 | 19-0022920 | SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1109 | 42631109 | FUSE | 2621 | 20190214 | 235 | 306411 | 743 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 11145 | 38.1683 | -122.6739 | MTR1007932553 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022920 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Three Phase Fault | 1416153 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023646&numberofmonths=24&showchangehistorylog=1 | 19-0023646 | SONOMA | FIELD OPS NORTH | Tier 2 | SALMON CREEK-1101 | 43161101 | RECLOSER | 37368 | 20190214 | 1934 | 310741 | 1296 | Distribution Circuit | Equipment Failure/Involved | Overhead | 182 | 171819 | 38.3809 | -123.079 | 3SPANSLDSIDEOFSW409817 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023646 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416797 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028671&numberofmonths=24&showchangehistorylog=1 | 19-0028671 | SONOMA | FIELD OPS NORTH | Tier 2 | CLOVERDALE-1101 | 42821101 | FUSE | 1231 | 20190226 | 2230 | 325553 | 705 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 61694 | 38.8221 | -123.0239 | 2SPANSSSFU11511 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028671 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1420578 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0029041&numberofmonths=24&showchangehistorylog=1 | 19-0029041 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | FUSE | 4139 | 20190226 | 2256 | 327079 | 2382 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 2382 | 38.1731 | -122.8968 | 7LDSIDEOF4139 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0029041 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1420837 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028067&numberofmonths=24&showchangehistorylog=1 | 19-0028067 | SONOMA | FIELD OPS NORTH | Tier 3 | FORT ROSS-1121 | 42851121 | RECLOSER | 70288 | 20190226 | 217 | 323781 | 1056 | Distribution Circuit | Vegetation | Tree - fell into line | 156 | 30950 | 38.5287 | -123.1574 | INGRAM42532SPANSLSSW179993 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0028067 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1420178 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0029351&numberofmonths=24&showchangehistorylog=1 | 19-0029351 | SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE | 4271 | 20190226 | 1932 | 325162 | 2764 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 38696 | 38.5391 | -123.2764 | 1LDSIDEOFFUCO4271 | Clear-32-90 F | Conductor, Overhead | On Ground | 19-0029351 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Multi-Fault | 1421063 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0029861&numberofmonths=24&showchangehistorylog=1 | 19-0029861 | SONOMA | FIELD OPS NORTH | Tier 3 | FORT ROSS-1121 | 42851121 | FUSE | 4523 | 20190226 | 1930 | 325158 | 5563 | Distribution Circuit | Environmental/External | Flood/Erosion | 16 | 89008 | 38.536 | -123.1405 | 4SPANSNOF8971 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0029861 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1421350 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028881&numberofmonths=24&showchangehistorylog=1 | 19-0028881 | SONOMA | FIELD OPS NORTH | Tier 2 | GEYSERVILLE-1101 | 42891101 | FUSE | 2473 | 20190226 | 2220 | 325471 | 1214 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 43850 | 38.7106 | -122.925 | MTR1009810491 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | On Ground | 19-0028881 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1420756 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028499&numberofmonths=24&showchangehistorylog=1 | 19-0028499 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 433 | 20190226 | 1635 | 324876 | 4209 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 138897 | 38.5091 | -122.9283 | 12000WESTSIDERD | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028499 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1420408 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028600&numberofmonths=24&showchangehistorylog=1 | 19-0028600 | SONOMA | FIELD OPS NORTH | Tier 2 | MIRABEL-1102 | 42091102 | FUSE | 13669 | 20190226 | 1854 | 325128 | 4191 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 37719 | 38.509 | -122.8869 | 6SPANSLDSIDEFU13669 | Partly Cloudy-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028600 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1420506 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0029680&numberofmonths=24&showchangehistorylog=1 | 19-0029680 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 8457 | 20190226 | 2115 | 325305 | 4064 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 52832 | 38.5137 | -122.9329 | MTR1008125054 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | On Ground | 19-0029680 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1421251 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028903&numberofmonths=24&showchangehistorylog=1 | 19-0028903 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 15399 | 20190226 | 1717 | 324909 | 1513 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 58874 | 38.4247 | -122.9608 | 5600MIZPAHRD | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028903 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1420769 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028952&numberofmonths=24&showchangehistorylog=1 | 19-0028952 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 2561 | 20190226 | 1949 | 325181 | 2726 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 57246 | 38.4112 | -122.965 | 4615TIMBERLN | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0028952 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1420793 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0029113&numberofmonths=24&showchangehistorylog=1 | 19-0029113 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 3043 | 20190226 | 1310 | 324525 | 3230 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 25840 | 38.3919 | -122.948 | 2405MARRARD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0029113 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1420876 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028074&numberofmonths=24&showchangehistorylog=1 | 19-0028074 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 4001 | 20190226 | 339 | 323831 | 511 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 511 | 38.5378 | -123.0901 | 3SPANSLDSIDEOFFUCO4001 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028074 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1420185 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028605&numberofmonths=24&showchangehistorylog=1 | 19-0028605 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER | 256 | 20190226 | 2248 | 325487 | 4178 | Distribution Circuit | Environmental/External | Flood/Erosion | 1431 | 4432998 | 38.4698 | -123.0145 | 22455HWY161SPANSOF2595TWD23916 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0028605 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1420511 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0029297&numberofmonths=24&showchangehistorylog=1 | 19-0029297 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 2659 | 20190226 | 2229 | 327860 | 4131 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 152847 | 38.5068 | -123.0701 | 2LDSIDEOF2659 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0029297 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1421025 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0029299&numberofmonths=24&showchangehistorylog=1 | 19-0029299 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 3895 | 20190226 | 2029 | 325251 | 4268 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 46948 | 38.5154 | -123.0795 | 1SPANLDSIDEOF3895 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0029299 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1421026 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0029429&numberofmonths=24&showchangehistorylog=1 | 19-0029429 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | TRIP-SAVER | 2987 | 20190226 | 1556 | 324897 | 4590 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 362610 | 38.5419 | -123.09 | WIREDOWNATMTR1007821485TREETHROUGHLINE | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | On Ground | 19-0029429 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Multi-Fault | 1421098 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0029858&numberofmonths=24&showchangehistorylog=1 | 19-0029858 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 2579 | 20190226 | 2236 | 325505 | 5126 | Distribution Circuit | Environmental/External | Flood/Erosion | 10 | 51260 | 38.4982 | -123.0732 | 700KIDDCREEKRD | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0029858 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1421347 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028450&numberofmonths=24&showchangehistorylog=1 | 19-0028450 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | RECLOSER | 120 | 20190226 | 1536 | 324785 | 5870 | Distribution Circuit | Environmental/External | Flood/Erosion | 492 | 300853 | 38.4637 | -123.0083 | 9280BOHEMIANHWY | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0028450 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Multi-Fault | 1420378 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028092&numberofmonths=24&showchangehistorylog=1 | 19-0028092 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 2035 | 20190226 | 605 | 323868 | 5260 | Distribution Circuit | Vegetation | Tree - fell into line | 144 | 160137 | 38.5197 | -122.9776 | 1LDSIDE1SOURCESIDEOFFUCO15593 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028092 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1420198 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028795&numberofmonths=24&showchangehistorylog=1 | 19-0028795 | SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1108 | 42631108 | FUSE | 1621 | 20190226 | 2135 | 325329 | 2243 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 47603 | 38.2569 | -122.7072 | 311MONTEVISTA | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | On Ground | 19-0028795 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1420683 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028728&numberofmonths=24&showchangehistorylog=1 | 19-0028728 | SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER | 204 | 20190227 | 543 | 326383 | 3763 | Distribution Circuit | Environmental/External | Flood/Erosion | 117 | 245153 | 38.5286 | -123.2068 | FUCO99945WIREDOWNDUETOMUDSLIDE | Clear-32-90 F | Conductor, Overhead | On Ground | 19-0028728 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1420639 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0029828&numberofmonths=24&showchangehistorylog=1 | 19-0029828 | SONOMA | FIELD OPS NORTH | Tier 2 | MIRABEL-1102 | 42091102 | FUSE | 7711 | 20190227 | 1051 | 326672 | 4654 | Distribution Circuit | Environmental/External | Flood/Erosion | 35 | 23082 | 38.4935 | -122.8525 | 6SPANSOFWIREDOWNSTARTINGAT7711 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0029828 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1421326 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028695&numberofmonths=24&showchangehistorylog=1 | 19-0028695 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 467555 | 20190227 | 100 | 326056 | 2204 | Distribution Circuit | Vegetation | Tree - fell into line | 253 | 23104 | 38.3966 | -122.9397 | 1LDSIDEFU467555 | Clear-32-90 F | Cutout, fuse holder | Broken, wire on ground | 19-0028695 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1420606 | CFH | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0029052&numberofmonths=24&showchangehistorylog=1 | 19-0029052 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 4899 | 20190227 | 1336 | 327124 | 1377 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 4081 | 38.4083 | -122.9373 | 14139OCCIDENTALRD | Clear-32-90 F | Conductor, Overhead | On Ground | 19-0029052 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1420845 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0029555&numberofmonths=24&showchangehistorylog=1 | 19-0029555 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | RECLOSER | 250 | 20190227 | 54 | 325997 | 3944 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 244528 | 38.4816 | -123.0112 | BROKENPOLEDUETOTREEWIREDOWN8SPANSSSOF1011TWD12055 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0029555 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Multi-Fault | 1421124 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028857&numberofmonths=24&showchangehistorylog=1 | 19-0028857 | SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1109 | 42631109 | JUMPER | WIREDOWN | 20190227 | 748 | 326533 | 244 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 788 | 38.2028 | -122.6197 | 3340IST | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028857 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1420737 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028678&numberofmonths=24&showchangehistorylog=1 | 19-0028678 | SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | FUSE | 2223 | 20190227 | 40 | 326022 | 1092 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 48048 | 38.5471 | -122.6692 | 3611CALISTOGARD | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028678 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1420587 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0064689&numberofmonths=24&showchangehistorylog=1 | 19-0064689 | SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | TRIP-SAVER | 6751 | 20190608 | 1848 | 401789 | 1065 | Distribution Circuit | Vegetation | Tree - fell into line | 134 | 44664 | 38.592 | -122.9622 | 7559MILLCREEKRD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0064689 | OH | Sus | 0 | yes | 2019 | JUN | Yes | Line to Ground | 1446871 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0064576&numberofmonths=24&showchangehistorylog=1 | 19-0064576 | SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | FUSE | 2225 | 20190608 | 1017 | 401355 | 241 | Distribution Circuit | Vegetation | Tree - fell into line | 90 | 21690 | 38.5242 | -122.6544 | MTR10075123133166CALASTOGA | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0064576 | OH | Sus | 0 | yes | 2019 | JUN | Yes | Multi-Fault | 1446800 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0102604&numberofmonths=24&showchangehistorylog=1 | 19-0102604 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | OTHER | WIREDWN4SPLDSIDEOF2377 | 20190923 | 1452 | 607255 | 642 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 14 | 8708 | 38.5028 | -122.9298 | 10994TERRACEDRFORESTVILLE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0102604 | OH | Sus | 43964302 | yes | 2019 | SEP | Yes | Open Circuit | 1472157 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0109622&numberofmonths=24&showchangehistorylog=1 | 19-0109622 | SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1108 | 42631108 | FUSE | 8287 | 20191009 | 1056 | 650876 | 357 | Distribution Circuit | 3rd Party | Vehicle | 11 | 1127 | 38.2638 | -122.725 | 6POLESLSOF8287 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0109622 | OH | Sus | 0 | yes | 2019 | OCT | Yes | Line to Ground | 1477739 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0110133&numberofmonths=24&showchangehistorylog=1 | 19-0110133 | SONOMA | FIELD OPS NORTH | Tier 3 | SALMON CREEK-1101 | 43161101 | FUSE | 615 | 20191010 | 1439 | 653377 | 473 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 3 | 1419 | 38.3639 | -122.9803 | 1SPLSSIDE615 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0110133 | OH | Sus | 0 | yes | 2019 | OCT | Yes | Line to Ground | 1479227 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0126948&numberofmonths=24&showchangehistorylog=1 | 19-0126948 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1101 | 42091101 | FUSE | 15463 | 20191120 | 1400 | 711702 | 488 | Distribution Circuit | Vegetation | Tree - branch fell on line | 10 | 4880 | 38.4707 | -122.95 | 1SPANLDSIDEOFFUSES | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0126948 | OH | Sus | 0 | yes | 2019 | NOV | Yes | Line to Ground | 1493042 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0130309&numberofmonths=24&showchangehistorylog=1 | 19-0130309 | SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1108 | 42631108 | FUSE | 840899 | 20191127 | 1103 | 721010 | 344 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 1032 | 38.2234 | -122.6692 | 2SPANLDSIDE | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0130309 | OH | Sus | 0 | yes | 2019 | NOV | Yes | Line to Ground | 1495142 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0019030&numberofmonths=24&showchangehistorylog=1 | 20-0019030 | SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | RECLOSER | 694641 | 20200209 | 925 | 781601 | 669 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 40140 | 38.328 | -122.5222 | HESSONG3884LDSD6946412SPANSSCSDMTR1006981778 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0019030 | OH | Sus | 0 | yes | 2020 | FEB | Yes | Line to Ground | 1513044 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0019132&numberofmonths=24&showchangehistorylog=1 | 20-0019132 | SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | RECLOSER | 246 | 20200209 | 1053 | 782348 | 456 | Distribution Circuit | Vegetation | Tree - fell into line | 352 | 67040 | 38.3657 | -122.5275 | MCNAMEELEE3BENNETVALLYROADANDWARMSPRINGS | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0019132 | OH | Sus | 0 | yes | 2020 | FEB | Yes | Line to Ground | 1513153 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0019479&numberofmonths=24&showchangehistorylog=1 | 20-0019479 | SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | FUSE | 4889 | 20200209 | 1020 | 785843 | 738 | Distribution Circuit | Vegetation | Tree - fell into line | 114 | 84132 | 38.3723 | -122.5653 | 6421SONOMAMTNROAD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0019479 | OH | Sus | 0 | yes | 2020 | FEB | Yes | Line to Ground | 1513505 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0019175&numberofmonths=24&showchangehistorylog=1 | 20-0019175 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1101 | 42091101 | FUSE | 15441 | 20200209 | 1108 | 782144 | 284 | Distribution Circuit | Vegetation | Tree - branch fell on line | 10 | 2840 | 38.4735 | -122.9138 | MTR1009084369 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0019175 | OH | Sus | 0 | yes | 2020 | FEB | Yes | Line to Ground | 1513198 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0084737&numberofmonths=24&showchangehistorylog=1 | 20-0084737 | SONOMA | FIELD OPS NORTH | Tier 2 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 1297 | 20200816 | 455 | 1010637 | 707 | Distribution Circuit | Vegetation | Tree - branch fell on line | 179 | 126553 | 38.6213 | -122.8303 | 1940RedwoodLn | Partly Cloudy-Lightning-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0084737 | OH | Sus | 0 | yes | 2020 | AUG | Yes | Line to Ground | 1555208 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0084672&numberofmonths=24&showchangehistorylog=1 | 20-0084672 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | RECLOSER | 318 | 20200816 | 425 | 1010400 | 750 | Distribution Circuit | Vegetation | Tree - branch fell on line | 434 | 325500 | 38.4048 | -122.9485 | ALVAREZRAFAEL15695BITTNERRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0084672 | OH | Sus | 0 | yes | 2020 | AUG | Yes | Line to Ground | 1555142 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0084813&numberofmonths=24&showchangehistorylog=1 | 20-0084813 | SONOMA | FIELD OPS NORTH | Tier 3 | SANTA ROSA A-1104 | 42151104 | FUSE | 12111 | 20200816 | 448 | 1010564 | 860 | Distribution Circuit | Environmental/External | Lightning | 33 | 28380 | 38.4958 | -122.6993 | MULTILELOC5SPANSLDSIDEOF12111 | Overcast-Drizzle-Lightning-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0084813 | OH | Sus | 0 | yes | 2020 | AUG | Yes | Force Out | 1555286 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0102103&numberofmonths=24&showchangehistorylog=1 | 20-0102103 | SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | RECLOSER | 261774 | 20200927 | 1241 | 1095169 | 428 | Distribution Circuit | Vegetation | Tree - fell into line | 185 | 70828 | 38.3787 | -122.5531 | 1SPANLDSIDEOFCGC218388925910 | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 20-0102103 | OH | Sus | 31514675 | yes | 2020 | SEP | Yes | Line to Ground | 1566519 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0010120&numberofmonths=24&showchangehistorylog=1 | 21-0010120 | SONOMA | FIELD OPS NORTH | Tier 3 | DUNBAR-1101 | 43071101 | FUSE | 4829 | 20210119 | 154 | 1214097 | 916 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 2748 | 38.3971 | -122.575 | 2690BRISTOLRDKENWOOD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0010120 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Line | 1594087 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0010240&numberofmonths=24&showchangehistorylog=1 | 21-0010240 | SONOMA | FIELD OPS NORTH | Tier 3 | DUNBAR-1103 | 43071103 | FUSE | 13499 | 20210119 | 439 | 1214692 | 475 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 3325 | 38.3964 | -122.4716 | 4300TRINITYRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0010240 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1594219 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0010196&numberofmonths=24&showchangehistorylog=1 | 21-0010196 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER | 140 | 20210119 | 522 | 1214841 | 544 | Distribution Circuit | Vegetation | Tree - fell into line | 143 | 22766 | 38.4668 | -123.0158 | Arvig347121792MonteVistaTerraceMonteRio | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0010196 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Line | 1594163 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0010644&numberofmonths=24&showchangehistorylog=1 | 21-0010644 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE | 939 | 20210119 | 838 | 1215848 | 562 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 2811 | 38.4353 | -122.9729 | MTR5000012784 | Clear-32-90 F | Transformer (OH) | Broken, wire on ground | 21-0010644 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Line | 1594541 | TXO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0009976&numberofmonths=24&showchangehistorylog=1 | 21-0009976 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | TRIP-SAVER | 1989 | 20210119 | 28 | 1213521 | 551 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 23693 | 38.5219 | -122.9971 | 16395RIONIDORD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0009976 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Line | 1593926 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0010545&numberofmonths=24&showchangehistorylog=1 | 21-0010545 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 7709 | 20210119 | 822 | 1215729 | 305 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2440 | 38.5075 | -123.0294 | 4LDSIDEOF7709 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0010545 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Line | 1594480 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0010122&numberofmonths=24&showchangehistorylog=1 | 21-0010122 | SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1108 | 42631108 | RECLOSER | 208 | 20210119 | 331 | 1214425 | 607 | Distribution Circuit | Vegetation | Tree - branch fell on line | 185 | 65855 | 38.2261 | -122.7211 | 7SPANSSSSOF62907 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0010122 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1594089 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0013978&numberofmonths=24&showchangehistorylog=1 | 21-0013978 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1101 | 42091101 | FUSE | 1071 | 20210125 | 1130 | 1224312 | 588 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 4116 | 38.4744 | -122.9187 | 2SPANSLDSIDEOF1071 | Clear-32-90 F | Conductor, Overhead | On Ground | 21-0013978 | OH | Sus | 31528913 | No | 2021 | JAN | Yes | Line to Ground | 1596844 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0016230&numberofmonths=24&showchangehistorylog=1 | 21-0016230 | SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE | 4543 | 20210127 | 1214 | 1229742 | 440 | Distribution Circuit | Vegetation | Tree - branch fell on line | 10 | 4400 | 38.5896 | -123.3033 | 3SPANSLDSIDEOFFUCO4543 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0016230 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1598680 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0015258&numberofmonths=24&showchangehistorylog=1 | 21-0015258 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1101 | 42571101 | SWITCH | 1617 | 20210127 | 1545 | 1236487 | 12 | Distribution Circuit | Vegetation | Tree - fell into line | 95 | 1140 | 38.3732 | -122.9116 | BETWEEN163593239 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0015258 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1598921 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0017757&numberofmonths=24&showchangehistorylog=1 | 21-0017757 | SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | FUSE | 13193 | 20210128 | 1455 | 1239941 | 423 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 2961 | 38.538 | -122.6469 | 8SPANSLDSIDEOFFUCO13193 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0017757 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Line | 1599818 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0103653&numberofmonths=24&showchangehistorylog=1 | 21-0103653 | SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | FUSE | 3083 | 20210812 | 1137 | 1441120 | 636 | Distribution Circuit | Vegetation | Tree - branch fell on line | 37 | 23532 | 38.3601 | -122.5257 | 5SPANSLDSIDEOFFUCO3083 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0103653 | OH | Sus | 0 | No | 2021 | AUG | Yes | Line to Line | 1657017 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0135702&numberofmonths=24&showchangehistorylog=1 | 21-0135702 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1105 | 42271105 | RECLOSER | 36536 | 20211024 | 717 | 1508260 | 787 | Distribution Circuit | Vegetation | Tree - fell into line | 802 | 316449 | 38.3142 | -122.7365 | 2SPSOURCESIDE36536 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0135702 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Ground | 1677177 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0135646&numberofmonths=24&showchangehistorylog=1 | 21-0135646 | SONOMA | FIELD OPS NORTH | Tier 2 | FITCH MOUNTAIN-1113 | 42751113 | RECLOSER | 4566 | 20211024 | 619 | 1507973 | 723 | Distribution Circuit | Vegetation | Tree - fell into line | 303 | 149805 | 38.6063 | -122.8866 | REGEBOB2560WESTDRYCREEKRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0135646 | OH | Sus | 0 | No | 2021 | OCT | Yes | Three Phase Fault | 1677124 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0135949&numberofmonths=24&showchangehistorylog=1 | 21-0135949 | SONOMA | FIELD OPS NORTH | Tier 2 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 5525 | 20211024 | 719 | 1508233 | 659 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 61287 | 38.6367 | -122.8846 | 10SPANSLDSIDEOFFUCO5525 | Clear-32-90 F | Conductor, Overhead | On Ground | 21-0135949 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Ground | 1677418 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0136056&numberofmonths=24&showchangehistorylog=1 | 21-0136056 | SONOMA | FIELD OPS NORTH | Tier 2 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 1297 | 20211024 | 1016 | 1509854 | 576 | Distribution Circuit | Vegetation | Tree - fell into line | 178 | 102528 | 38.6212 | -122.8301 | 1963FITCHMOUNTAINRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0136056 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Line | 1677523 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0137073&numberofmonths=24&showchangehistorylog=1 | 21-0137073 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1101 | 42091101 | FUSE | 7271 | 20211024 | 1853 | 1517481 | 1436 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 72004 | 38.486 | -122.9629 | 1SPANLDSIDEOFFUCO15467ONMAINLINE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0137073 | OH | Sus | 0 | No | 2021 | OCT | Yes | Three Phase Fault | 1678527 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0135611&numberofmonths=24&showchangehistorylog=1 | 21-0135611 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | TRIP-SAVER | 1703 | 20211024 | 451 | 1507492 | 1470 | Distribution Circuit | Vegetation | Tree - fell into line | 788 | 759376 | 38.4835 | -123.0538 | 1497LASTSPANBEYONDTSV1703 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0135611 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Ground | 1677087 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0135611&numberofmonths=24&showchangehistorylog=1 | 21-0135611 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 2595 | 20211024 | 458 | 1510259 | 937 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 22488 | 38.4914 | -123.0595 | CGC216962630194 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0135611 | OH | Sus | 0 | No | 2021 | OCT | Yes | Force Out | 1677432 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0136120&numberofmonths=24&showchangehistorylog=1 | 21-0136120 | SONOMA | FIELD OPS NORTH | Tier 2 | MONTE RIO-1111 | 42811111 | FUSE | 7385 | 20211024 | 902 | 1508971 | 601 | Distribution Circuit | Vegetation | Tree - branch fell on line | 39 | 11790 | 38.4829 | -123.1468 | CGC216742530949 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0136120 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Line | 1677592 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0136182&numberofmonths=24&showchangehistorylog=1 | 21-0136182 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 429 | 20211024 | 1125 | 1510626 | 274 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 8494 | 38.4735 | -123.023 | 1101CENTERRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0136182 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Ground | 1677654 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0135977&numberofmonths=24&showchangehistorylog=1 | 21-0135977 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | TRIP-SAVER | 1067 | 20211024 | 732 | 1508323 | 798 | Distribution Circuit | Vegetation | Tree - branch fell on line | 109 | 86982 | 38.4933 | -123.006 | CGC217132430470 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0135977 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Line | 1677449 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0136068&numberofmonths=24&showchangehistorylog=1 | 21-0136068 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | TRIP-SAVER | 8299 | 20211024 | 809 | 1508688 | 589 | Distribution Circuit | Vegetation | Tree - branch fell on line | 51 | 30039 | 38.5034 | -123.0284 | 1STSPANSSLEADINGTOCGC217058530692 | Clear-32-90 F | Conductor, Overhead | On Ground | 21-0136068 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Line | 1677535 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0137794&numberofmonths=24&showchangehistorylog=1 | 21-0137794 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | FUSE | 2439 | 20211025 | 2235 | 1520550 | 994 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2982 | 38.2162 | -122.9225 | 1SPANSOFCGC313018163622 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0137794 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Ground | 1679080 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0137537&numberofmonths=24&showchangehistorylog=1 | 21-0137537 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 6697 | 20211025 | 1035 | 1518284 | 1632 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 14686 | 38.5241 | -123.0458 | CGC216996931590 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0137537 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Ground | 1678858 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0157492&numberofmonths=24&showchangehistorylog=1 | 21-0157492 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER | 64758 | 20211213 | 1746 | 1568275 | 318 | Distribution Circuit | Vegetation | Tree - branch fell on line | 813 | 139537 | 38.5087 | -123.0696 | WATTSCHAD1445AustinCreekRd | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0157492 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Line | 1694389 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0158463&numberofmonths=24&showchangehistorylog=1 | 21-0158463 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | FUSE | 1575 | 20211215 | 1345 | 1572745 | 240 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 798 | 38.2698 | -122.7695 | HARDTAP5SPANSLDSIDEOF1575 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0158463 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1695444 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0158550&numberofmonths=24&showchangehistorylog=1 | 21-0158550 | SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER | 124 | 20211215 | 1752 | 1573229 | 304 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 19206 | 38.5654 | -123.272 | LDSIDEOFCGC216362433051 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0158550 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1695537 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0160527&numberofmonths=24&showchangehistorylog=1 | 21-0160527 | SONOMA | FIELD OPS NORTH | Tier 3 | FULTON-1107 | 42561107 | RECLOSER | 145720 | 20211225 | 646 | 1581136 | 526 | Distribution Circuit | Vegetation | Tree - fell into line | 133 | 26068 | 38.5497 | -122.7184 | 6SSOF3557 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0160527 | OH | Sus | 31588285 | No | 2021 | DEC | Yes | Line to Line | 1697999 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0160519&numberofmonths=24&showchangehistorylog=1 | 21-0160519 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | OTHER | WIREDOWNSSOFCGC217248127956 | 20211225 | 419 | 1581093 | 736 | Distribution Circuit | Vegetation | Tree - fell into line | 387 | 75749 | 38.4303 | -122.9624 | CGC217248127956 | Clear-32-90F | Crossarm, Wood | Broken, wire on ground | 21-0160519 | OH | Sus | 31588363 | No | 2021 | DEC | Yes | Line to Ground | 1697990 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0161018&numberofmonths=24&showchangehistorylog=1 | 21-0161018 | SONOMA | FIELD OPS NORTH | Tier 3 | DUNBAR-1101 | 43071101 | FUSE | 2107 | 20211227 | 756 | 1585081 | 326 | Distribution Circuit | Equipment Failure/Involved | Overhead | 105 | 34230 | 38.3873 | -122.4955 | 12665MAPLEGLENRD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0161018 | OH | Sus | 45102085 | No | 2021 | DEC | Yes | Line to Ground | 1698557 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0161473&numberofmonths=24&showchangehistorylog=1 | 21-0161473 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | RECLOSER | 120 | 20211229 | 315 | 1587694 | 56 | Distribution Circuit | Vegetation | Tree - fell into line | 106 | 5936 | 38.4637 | -123.0083 | CGC21726562771939BOHEMIANHWY | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0161473 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Line | 1699215 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0161473&numberofmonths=24&showchangehistorylog=1 | 21-0161473 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | RECLOSER | 5040 | 20211229 | 315 | 1587697 | 869 | Distribution Circuit | Vegetation | Tree - fell into line | 387 | 336303 | 38.4323 | -122.9672 | CGC217265627719COPOLE589VANNESSANDBOHEMIANHWY | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0161473 | OH | Sus | 35314365 | No | 2021 | DEC | Yes | Line to Line | 1699216 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0161595&numberofmonths=24&showchangehistorylog=1 | 21-0161595 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | SWITCH | 1011 | 20211229 | 2212 | 1589134 | 8 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 440 | 38.4812 | -123.0001 | 2SPANSWOFCAPBANK778 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0161595 | OH | Sus | 45103122 | No | 2021 | DEC | Yes | Line to Ground | 1699539 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0138295&numberofmonths=24&showchangehistorylog=1 | 22-0138295 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1104 | 42271104 | FUSE | 12145 | 20221210 | 945 | 1881318 | 574 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 4018 | 38.3349 | -122.7298 | 217910024365BROKENPOLEWITHWIREDOWN | Clear-32-90F | Pole-Wood | Broken, wire on ground | 22-0138295 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Line | 1789128 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0138054&numberofmonths=24&showchangehistorylog=1 | 22-0138054 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER | 969182 | 20221210 | 522 | 1880319 | 421 | Distribution Circuit | Vegetation | Tree - branch fell on line | 565 | 118993 | 38.4901 | -123.0598 | Arvig3471atco8139onKiddcreekrdCazadero | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0138054 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1788879 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0138172&numberofmonths=24&showchangehistorylog=1 | 22-0138172 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER | 37520 | 20221210 | 831 | 1881056 | 414 | Distribution Circuit | Vegetation | Tree - branch fell on line | 76 | 30558 | 38.5086 | -123.0693 | ALVAREZRAFAEL38851NE3650CAZHWYONEAUSTINCREEKRD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0138172 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1789006 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0138463&numberofmonths=24&showchangehistorylog=1 | 22-0138463 | SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | FUSE | 2225 | 20221210 | 936 | 1881312 | 688 | Distribution Circuit | Vegetation | Tree - branch fell on line | 92 | 63296 | 38.5247 | -122.6543 | 3155CALISTOGARD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0138463 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1789290 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0142690&numberofmonths=24&showchangehistorylog=1 | 22-0142690 | SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | FUSE | 11121 | 20221231 | 1552 | 1904866 | 567 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2268 | 38.3755 | -122.5503 | 6SPANSLDSIDEOFFUCO11121 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0142690 | OH | Sus | 0 | No | 2022 | DEC | Yes | Open Circuit | 1794497 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0142684&numberofmonths=24&showchangehistorylog=1 | 22-0142684 | SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1101 | 42571101 | OTHER | 217436926073 | 20221231 | 1613 | 1904934 | 267 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 267 | 38.3794 | -122.8942 | 2SPANSLDSIDEOFFUCO18701 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0142684 | OH | Sus | 45612880 | No | 2022 | DEC | Yes | Line to Ground | 1794491 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0005652&numberofmonths=24&showchangehistorylog=1 | 23-0005652 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1102 | 42271102 | RECLOSER | 464 | 20230104 | 859 | 1912851 | 325 | Distribution Circuit | Vegetation | Tree - fell into line | 5315 | 377617 | 38.3002 | -122.7115 | TREEWIREDOWN1POLESSOF468DAMAGEOHWILLOWANDRAILROADBRANCHAT6651 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0005652 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1796081 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0006501&numberofmonths=24&showchangehistorylog=1 | 23-0006501 | SONOMA | FIELD OPS NORTH | Tier 2 | RINCON-1104 | 43321104 | OCB | 11042 | 20230104 | 1854 | 1917314 | 338 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4020 | 665256 | 38.4901 | -122.6661 | PEDERSONRYLEY34733801BrushCreekRoadSantaRosa | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0006501 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1796800 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0005559&numberofmonths=24&showchangehistorylog=1 | 23-0005559 | SONOMA | FIELD OPS NORTH | Tier 2 | SONOMA-1104 | 42721104 | FUSE | 12407 | 20230104 | 500 | 1912232 | 706 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 21886 | 38.3032 | -122.5518 | 1SSOFCGC218413223484 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 23-0005559 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Line | 1796021 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0012060&numberofmonths=24&showchangehistorylog=1 | 23-0012060 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | RECLOSER | 202 | 20230110 | 833 | 1943811 | 451 | Distribution Circuit | Vegetation | Tree - fell into line | 116 | 48411 | 38.4984 | -122.9914 | 6SPANSWOFCGC217202530464 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0012060 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1801840 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0016194&numberofmonths=24&showchangehistorylog=1 | 23-0016194 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1101 | 42091101 | JUMPER | WIREDOWNSSOFCGC217376729268 | 20230114 | 1048 | 1954369 | 362 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 2534 | 38.4676 | -122.9173 | NA | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0016194 | OH | Sus | 0 | No | 2023 | JAN | Yes | Open Circuit | 1804967 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0016861&numberofmonths=24&showchangehistorylog=1 | 23-0016861 | SONOMA | FIELD OPS NORTH | Tier 2 | FITCH MOUNTAIN-1112 | 42751112 | FUSE | 579 | 20230116 | 10 | 1956458 | 671 | Distribution Circuit | Vegetation | Tree - fell into line | 64 | 42944 | 38.6144 | -122.835 | 2SPANSSSOF3963 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0016861 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1805559 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0031516&numberofmonths=24&showchangehistorylog=1 | 23-0031516 | SONOMA | FIELD OPS NORTH | Tier 2 | FITCH MOUNTAIN-1112 | 42751112 | FUSE | 2345 | 20230221 | 1516 | 1992357 | 409 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 27403 | 38.6373 | -122.8818 | 5657 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0031516 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Line | 1815144 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0031364&numberofmonths=24&showchangehistorylog=1 | 23-0031364 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 1997 | 20230221 | 1345 | 1990934 | 379 | Distribution Circuit | Vegetation | Tree - branch fell on line | 112 | 42448 | 38.5018 | -123.0238 | 2LDSIDEOF1997 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0031364 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Ground | 1815013 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0033601&numberofmonths=24&showchangehistorylog=1 | 23-0033601 | SONOMA | FIELD OPS NORTH | Tier 2 | GEYSERVILLE-1101 | 42891101 | FUSE | 10787 | 20230224 | 102 | 2001448 | 973 | Distribution Circuit | Environmental/External | Ice or snow | 28 | 27244 | 38.7139 | -123.012 | 14450ROCKPILERD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 23-0033601 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Ground | 1816637 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0033786&numberofmonths=24&showchangehistorylog=1 | 23-0033786 | SONOMA | FIELD OPS NORTH | Tier 3 | GEYSERVILLE-1102 | 42891102 | FUSE | 3517 | 20230224 | 33 | 2001312 | 1109 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 16635 | 38.7345 | -122.8363 | 5SPANSLDSIDEOFCGC217577529189 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0033786 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Ground | 1816805 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0036236&numberofmonths=24&showchangehistorylog=1 | 23-0036236 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | FUSE | 2439 | 20230227 | 822 | 2011382 | 600 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1800 | 38.2162 | -122.9225 | 2SPANSFROMEOL | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0036236 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Ground | 1818956 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0044467&numberofmonths=24&showchangehistorylog=1 | 23-0044467 | SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER | 612266 | 20230314 | 324 | 2035161 | 910 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 35490 | 38.5329 | -123.2715 | 21001HWY1 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0044467 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1824733 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0044670&numberofmonths=24&showchangehistorylog=1 | 23-0044670 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1101 | 42091101 | RECLOSER | 933786 | 20230314 | 945 | 2035725 | 120 | Distribution Circuit | Vegetation | Tree - bark fell into line | 27 | 3240 | 38.4881 | -122.9208 | 12SPANSSSMTR1008891754 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0044670 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Line | 1824823 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0045056&numberofmonths=24&showchangehistorylog=1 | 23-0045056 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1101 | 42091101 | TRIP-SAVER | 4859 | 20230314 | 1022 | 2036689 | 640 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 28160 | 38.4756 | -122.9526 | 14025GREENVALLEYRD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0045056 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Line | 1825126 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0044508&numberofmonths=24&showchangehistorylog=1 | 23-0044508 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 6399 | 20230314 | 618 | 2035193 | 743 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 23033 | 38.5038 | -122.9115 | 1STSPANLOADSIDE6399 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0044508 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1824749 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0045447&numberofmonths=24&showchangehistorylog=1 | 23-0045447 | SONOMA | FIELD OPS NORTH | Tier 2 | MIRABEL-1102 | 42091102 | FUSE | 913 | 20230314 | 1520 | 2042765 | 401 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 2601 | 38.5168 | -122.8908 | 2SPANSLDSIDEOF913 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0045447 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Line | 1825423 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0044932&numberofmonths=24&showchangehistorylog=1 | 23-0044932 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | RECLOSER | 79306 | 20230314 | 1142 | 2037645 | 607 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 31266 | 38.3721 | -122.9117 | NOONAN3469VALLEYFORDFREESTONERDONEFROMCO10135 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0044932 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1825022 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0050587&numberofmonths=24&showchangehistorylog=1 | 23-0050587 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | JUMPER | 4LDSIDEOF17803WIREDOWN | 20230321 | 2234 | 2062466 | 1299 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 10920 | 38.5173 | -123.0982 | 4LDSIDEOF17803 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on object | 23-0050587 | OH | Sus | 0 | No | 2023 | MAR | Yes | Open Circuit | 1829118 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0049718&numberofmonths=24&showchangehistorylog=1 | 23-0049718 | SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | OTHER | 949673 | 20230321 | 1345 | 2056947 | 237 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 237 | 38.521 | -122.6229 | HESSONG3884SAINTHELENARDATCOS949673 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0049718 | OH | Sus | 0 | No | 2023 | MAR | Yes | Open Circuit | 1828440 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078046&numberofmonths=24&showchangehistorylog=1 | 13-0078046 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | RECLOSER | 1222 | 20131121 | 1828 | 908019 | 1004 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1299 | 294380 | 38.436 | -120.5558 | 2PSSOFL35677C1266 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078046 | OH | Sus | 0 | yes | 2013 | NOV | Yes | Line to Ground | 99251784 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078137&numberofmonths=24&showchangehistorylog=1 | 13-0078137 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE | L2133 | 20131121 | 2006 | 909124 | 654 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 23544 | 38.4891 | -120.589 | Bell191477036777POLESLOADSIDEOFL2133 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078137 | OH | Sus | 0 | yes | 2013 | NOV | Yes | Line to Ground | 99251762 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078128&numberofmonths=24&showchangehistorylog=1 | 13-0078128 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | 1303 | 20131121 | 1831 | 908725 | 1024 | Distribution Circuit | Vegetation | Tree - bark fell into line | 216 | 221184 | 38.4043 | -120.5056 | BRASWELLDAVIDBummervillerdWestPoint | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078128 | OH | Sus | 0 | yes | 2013 | NOV | Yes | Line to Ground | 99251765 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078189&numberofmonths=24&showchangehistorylog=1 | 13-0078189 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | OCB | OCB | 20131121 | 2252 | 908797 | 386 | Distribution Circuit | Equipment Failure/Involved | Other | 2148 | 135968 | 38.4205 | -120.5488 | DeValle17047684600CUTOUTPOLE98669 | Strong winds-32 - 90 F | Crossarm, Wood | Broken, wire on object | 13-0078189 | OH | Sus | 0 | yes | 2013 | NOV | Yes | None | 99251748 | CAW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078729&numberofmonths=24&showchangehistorylog=1 | 13-0078729 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | ELECTRA-1102 | 162161102 | FUSE | 2135 | 20131122 | 1600 | 912641 | 260 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 4940 | 38.3 | -120.6873 | 10909JESUSMARIARD | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078729 | OH | Sus | 0 | yes | 2013 | NOV | Yes |  | 99251474 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078046&numberofmonths=24&showchangehistorylog=1 | 13-0078046 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | SWITCH | L3065 | 20131122 | 1222 | 912000 | 233 | Distribution Circuit | Vegetation | Tree - branch fell on line | 55 | 12815 | 38.4452 | -120.5315 | MTR1004937638 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on object | 13-0078046 | OH | Sus | 0 | yes | 2013 | NOV | Yes |  | 99251544 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078682&numberofmonths=24&showchangehistorylog=1 | 13-0078682 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | SALT SPRINGS-2101 | 163692101 | FUSE | 4693 | 20131122 | 943 | 911634 | 997 | Distribution Circuit | Equipment Failure/Involved | Other | 23 | 15001 | 38.4474 | -120.0708 | Fort19666481791HWY4SHERMAN | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078682 | OH | Sus | 0 | yes | 2013 | NOV | Yes | Line to Ground | 99251494 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078275&numberofmonths=24&showchangehistorylog=1 | 13-0078275 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | SALT SPRINGS-2102 | 163692102 | RECLOSER | 8442 | 20131122 | 225 | 910516 | 1254 | Distribution Circuit | Vegetation | Tree - fell into line | 1998 | 1244943 | 38.4157 | -120.1344 | POLE2208PEOF9945 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078275 | OH | Sus | 31038457 | yes | 2013 | NOV | Yes | Line to Line | 99251251 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078547&numberofmonths=24&showchangehistorylog=1 | 13-0078547 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | 99353 | 20131122 | 742 | 911167 | 1113 | Distribution Circuit | Equipment Failure/Involved | Other | 6 | 6678 | 38.3757 | -120.5001 | 3980BLUEMOUNTAINRD | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0078547 | OH | Sus | 0 | yes | 2013 | NOV | Yes |  | 99251568 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078812&numberofmonths=24&showchangehistorylog=1 | 13-0078812 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | 1391 | 20131122 | 2007 | 913131 | 1168 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 47888 | 38.3305 | -120.5353 | CGC319861066975 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0078812 | OH | Sus | 0 | yes | 2013 | NOV | Yes | Line to Line | 99251186 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075476&numberofmonths=24&showchangehistorylog=1 | 14-0075476 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CLAY-1101 | 163341101 | FUSE | 749 | 20141211 | 951 | 1132634 | 1173 | Distribution Circuit | Vegetation | Tree - bark fell into line | 119 | 26835 | 38.3782 | -120.913 | BellD1914770367713175WILLOWCREEKRD | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075476 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99194340 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075411&numberofmonths=24&showchangehistorylog=1 | 14-0075411 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CORRAL-1101 | 162991101 | FUSE | 18719 | 20141211 | 1036 | 1132954 | 310 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 3594 | 38.1337 | -120.9224 | 2SSWOF18719 | Strong winds-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 14-0075411 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194891 | CSO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075405&numberofmonths=24&showchangehistorylog=1 | 14-0075405 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | ELECTRA-1101 | 162161101 | FUSE | L1697 | 20141211 | 944 | 1132405 | 1052 | Distribution Circuit | Equipment Failure/Involved | Other | 241 | 104024 | 38.3794 | -120.6378 | 11440GOLDTRRIKE | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0075405 | OH | Sus | 0 | yes | 2014 | DEC | Yes |  | 99194352 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075628&numberofmonths=24&showchangehistorylog=1 | 14-0075628 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE | L3829 | 20141211 | 1003 | 1132767 | 1598 | Distribution Circuit | Vegetation | Tree - fell into line | 116 | 51124 | 38.4697 | -120.5457 | NOFMTR1004935563 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075628 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99194313 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075526&numberofmonths=24&showchangehistorylog=1 | 14-0075526 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | SALT SPRINGS-2102 | 163692102 | FUSE | L485 | 20141211 | 1150 | 1134042 | 666 | Distribution Circuit | Vegetation | Tree - branch fell on line | 509 | 59610 | 38.2974 | -120.2742 | TAOSCHINOOK | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075526 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194807 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075436&numberofmonths=24&showchangehistorylog=1 | 14-0075436 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | RECLOSER | 36674 | 20141211 | 955 | 1132589 | 1141 | Distribution Circuit | Vegetation | Tree - fell into line | 304 | 346864 | 38.4876 | -120.5195 | 6SLDSIDELR36674 | Combination wind/rain/lightning-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075436 | OH | Sus | 0 | yes | 2014 | DEC | Yes |  | 99194346 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076108&numberofmonths=24&showchangehistorylog=1 | 14-0076108 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | FUSE | L1977 | 20141211 | 1024 | 1132842 | 1347 | Distribution Circuit | Equipment Failure/Involved | Other | 25 | 33675 | 38.4616 | -120.53 | LOADSIDEOFL1977 | Combination wind/rain/lightning-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076108 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99194170 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075361&numberofmonths=24&showchangehistorylog=1 | 14-0075361 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | L585 | 20141211 | 935 | 1132581 | 740 | Distribution Circuit | Equipment Failure/Involved | Other | 29 | 21460 | 38.384 | -120.5243 | METER1003128808 | Combination wind/rain/lightning-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075361 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194928 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075441&numberofmonths=24&showchangehistorylog=1 | 14-0075441 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | 1311 | 20141211 | 929 | 1132248 | 1182 | Distribution Circuit | Equipment Failure/Involved | Other | 81 | 20205 | 38.3833 | -120.5326 | REANOANTHONYINFEILD243STANLEY | Rain-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0075441 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99194869 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076084&numberofmonths=24&showchangehistorylog=1 | 14-0076084 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | OTHER |  | 20141211 | 1202 | 1135324 | 1023 | Distribution Circuit | Equipment Failure/Involved | Other | 6 | 6138 | 38.3958 | -120.4801 | UNKNOWN | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076084 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99194470 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076197&numberofmonths=24&showchangehistorylog=1 | 14-0076197 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | L1137 | 20141211 | 1154 | 1133389 | 1464 | Distribution Circuit | Equipment Failure/Involved | Other | 6 | 8784 | 38.4016 | -120.4889 |  | Combination wind/rain/lightning-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076197 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99194106 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076095&numberofmonths=24&showchangehistorylog=1 | 14-0076095 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | ELECTRA-1102 | 162161102 | FUSE | 1327 | 20141212 | 223 | 1136934 | 172 | Distribution Circuit | Equipment Failure/Involved | Other | 2 | 344 | 38.3403 | -120.6091 | MTR1004807082 | Heavy rain-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0076095 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99194175 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079128&numberofmonths=24&showchangehistorylog=1 | 14-0079128 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | ELECTRA-1101 | 162161101 | FUSE | L1697 | 20141230 | 1215 | 1152803 | 797 | Distribution Circuit | Vegetation | Tree - fell into line | 241 | 69294 | 38.3794 | -120.6378 | Coleman1722602799311855 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079128 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99190566 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079072&numberofmonths=24&showchangehistorylog=1 | 14-0079072 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | ELECTRA-1101 | 162161101 | OCB | OCB | 20141230 | 1309 | 1155815 | 641 | Distribution Circuit | Equipment Failure/Involved | Other | 1895 | 207213 | 38.3307 | -120.6715 | 12845ELDELLRD | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079072 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99190504 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079096&numberofmonths=24&showchangehistorylog=1 | 14-0079096 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | OTHER |  | 20141230 | 1127 | 1152406 | 832 | Distribution Circuit | Equipment Failure/Involved | Other | 150 | 115320 | 38.5011 | -120.6743 | 18200FIDDLETOWNRDFIDDLETOWN | Combination wind/rain/lightning-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079096 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99190595 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079260&numberofmonths=24&showchangehistorylog=1 | 14-0079260 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE | L359 | 20141230 | 1039 | 1151246 | 894 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 19318 | 38.3967 | -120.6592 | MTR1007718368 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079260 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99190473 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079517&numberofmonths=24&showchangehistorylog=1 | 14-0079517 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE | 5163 | 20141230 | 1340 | 1152368 | 1070 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 48560 | 38.438 | -120.5703 | Coleman1722602799324675 | Combination wind/rain/lightning-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 14-0079517 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99190122 | CSO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0078917&numberofmonths=24&showchangehistorylog=1 | 14-0078917 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | FUSE | L1977 | 20141230 | 836 | 1150510 | 601 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 15025 | 38.4616 | -120.53 | BRASWELLDAVIDStellaCt | Combination wind/rain/lightning-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0078917 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99190747 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0078900&numberofmonths=24&showchangehistorylog=1 | 14-0078900 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | RECLOSER | 77204 | 20141230 | 900 | 1150684 | 1793 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2021 | 1144821 | 38.3868 | -120.5243 | Coleman17226027993westpoint | Combination wind/rain/lightning-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0078900 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99190231 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0010828&numberofmonths=24&showchangehistorylog=1 | 15-0010828 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | OLETA-1101 | 163541101 | FUSE | L6599 | 20150206 | 2214 | 1179141 | 1006 | Distribution Circuit | Equipment Failure/Involved | Other | 4 | 1540 | 38.4863 | -120.9053 | BRASWELLDAVID7polesldsideL6599 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010828 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99184533 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0039368&numberofmonths=24&showchangehistorylog=1 | 15-0039368 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CORRAL-1101 | 162991101 | RECLOSER | 12612 | 20150608 | 1418 | 1245781 | 337 | Distribution Circuit | 3rd Party | Vehicle | 314 | 65168 | 38.1784 | -120.9271 | Laskowski18459929537hwy12eosouthworth | Clear-Above 90 F | Pole-Wood | Broken, wire on ground | 15-0039368 | OH | Sus | 31159870 | yes | 2015 | JUN | Yes | Line to Ground | 99164922 | PW | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0084811&numberofmonths=24&showchangehistorylog=1 | 15-0084811 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | OLETA-1101 | 163541101 | RECLOSER | 1208 | 20151213 | 1056 | 1361641 | 251 | Distribution Circuit | Vegetation | Tree - branch fell on line | 478 | 93486 | 38.4373 | -120.8358 | REANOANTHONYMTR1006418333 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084811 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1174479 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0013358&numberofmonths=24&showchangehistorylog=1 | 16-0013358 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | ELECTRA-1102 | 162161102 | RECLOSER | 77204 | 20160217 | 1813 | 1406173 | 717 | Distribution Circuit | Vegetation | Tree - fell into line | 209 | 46864 | 38.3444 | -120.5828 | REANOANTHONYRIDGEAND26 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013358 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Line to Line | 1186442 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0013480&numberofmonths=24&showchangehistorylog=1 | 16-0013480 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | ELECTRA-1102 | 162161102 | RECLOSER | 2646 | 20160217 | 1950 | 1406653 | 1189 | Distribution Circuit | Vegetation | Tree - fell into line | 204 | 120837 | 38.2992 | -120.6982 | 4POLESNEOFL5787 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013480 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Three Phase Fault | 1186568 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0013472&numberofmonths=24&showchangehistorylog=1 | 16-0013472 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | JUMPER | OJ2SPANSSEOFL6693 | 20160217 | 1906 | 1407515 | 504 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 10236 | 38.5016 | -120.6708 | 2SPANSSEOFL6693 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013472 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Open Circuit | 1186558 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0013512&numberofmonths=24&showchangehistorylog=1 | 16-0013512 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | WEST POINT-1102 | 163201102 | FUSE | 1315 | 20160217 | 1949 | 1406647 | 950 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 50350 | 38.3776 | -120.554 | 1SPANNEOFTXMTR1004974732 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013512 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Line to Line | 1186599 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0018160&numberofmonths=24&showchangehistorylog=1 | 16-0018160 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CLAY-1101 | 163341101 | FUSE | L3789 | 20160305 | 2034 | 1419051 | 1275 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 20100 | 38.4043 | -120.9079 | 6991TONZIROAD | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on object | 16-0018160 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1190032 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017953&numberofmonths=24&showchangehistorylog=1 | 16-0017953 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | ELECTRA-1101 | 162161101 | RECLOSER | 7104 | 20160305 | 2209 | 1420144 | 832 | Distribution Circuit | Vegetation | Tree - fell into line | 620 | 222586 | 38.3655 | -120.7152 | 1PNOF6335ONMAINLINEL3697 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017953 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1189815 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017895&numberofmonths=24&showchangehistorylog=1 | 16-0017895 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | OLETA-1101 | 163541101 | FUSE | 1179 | 20160305 | 2052 | 1419210 | 483 | Distribution Circuit | Vegetation | Tree - branch fell on line | 30 | 13971 | 38.483 | -121.0147 | REANOANTHONYMTR1009773709 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017895 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1189753 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0018028&numberofmonths=24&showchangehistorylog=1 | 16-0018028 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1101 | 163751101 | RECLOSER | 3170 | 20160305 | 2157 | 1419908 | 550 | Distribution Circuit | Vegetation | Tree - fell into line | 683 | 147306 | 38.4149 | -120.6847 | REANOANTHONYNEWYORKRANCHBETL589759431 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018028 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1189899 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0018279&numberofmonths=24&showchangehistorylog=1 | 16-0018279 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | WEST POINT-1102 | 163201102 | FUSE | 1487 | 20160305 | 2222 | 1421239 | 1101 | Distribution Circuit | Vegetation | Tree - branch fell on line | 13 | 14313 | 38.4033 | -120.5567 | BRASWELLDAVID380hidospinkrd | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018279 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190143 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0002884&numberofmonths=24&showchangehistorylog=1 | 17-0002884 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CLAY-1103 | 163341103 | RECLOSER | 59714 | 20170103 | 707 | 1615352 | 393 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 2002 | 38.3395 | -120.9268 | 23SPLDSIDEOF717 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0002884 | OH | Sus | 31292586 | yes | 2017 | JAN | Yes | Line to Line | 1243205 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005734&numberofmonths=24&showchangehistorylog=1 | 17-0005734 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | JUMPER | WIREDOWNATMTR1004902341 | 20170108 | 2026 | 1629108 | 501 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2263 | 401870 | 38.2029 | -120.5773 | McKinnon207457303945918MOUNTAINRANCHRD1SPANSOURCEOFMTR1004902341 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005734 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Open Circuit | 1245518 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005162&numberofmonths=24&showchangehistorylog=1 | 17-0005162 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | MARTELL-1101 | 163011101 | FUSE | 1025 | 20170108 | 920 | 1624332 | 335 | Distribution Circuit | Vegetation | Tree - fell into line | 105 | 15999 | 38.4044 | -120.717 | 1SPANLDOFMTR1004807511 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005162 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1244957 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005193&numberofmonths=24&showchangehistorylog=1 | 17-0005193 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | MARTELL-1103 | 163011103 | RECLOSER | 3152 | 20170108 | 950 | 1624448 | 873 | Distribution Circuit | Environmental/External | Flood/Erosion | 139 | 121347 | 38.3598 | -120.8199 | MACHIANDREW1852sutterranchosandhwy88jackson | Overcast-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0005193 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1244985 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005854&numberofmonths=24&showchangehistorylog=1 | 17-0005854 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE | L6827 | 20170108 | 2342 | 1629790 | 983 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2949 | 38.4121 | -120.6531 | 1LDSIDEOFL6827 | Overcast-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0005854 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245637 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0004886&numberofmonths=24&showchangehistorylog=1 | 17-0004886 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | TRIP-SAVER | 1305 | 20170108 | 16 | 1622373 | 907 | Distribution Circuit | Vegetation | Tree - fell into line | 94 | 63698 | 38.4009 | -120.5045 | 3WOF4SOFMTR1004935048 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004886 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1244685 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006006&numberofmonths=24&showchangehistorylog=1 | 17-0006006 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | MARTELL-1101 | 163011101 | FUSE | L3161 | 20170109 | 703 | 1630345 | 791 | Distribution Circuit | Equipment Failure/Involved | Overhead | 77 | 47611 | 38.4433 | -120.7568 | 610681LDSIDESSOPEN | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006006 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245755 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006122&numberofmonths=24&showchangehistorylog=1 | 17-0006122 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | JUMPER | WIREDOWNATMTR5000058384 | 20170109 | 950 | 1630756 | 1599 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 4797 | 38.4947 | -120.6197 | MTR5000058384 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006122 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Open Circuit | 1245844 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005879&numberofmonths=24&showchangehistorylog=1 | 17-0005879 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | RECLOSER | 4790 | 20170109 | 526 | 1630069 | 2154 | Distribution Circuit | Environmental/External | Flood/Erosion | 1910 | 403369 | 38.3868 | -120.5244 | LOCATION15SPANSLDSIDEOFL3231LOCATION21EOF1349 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0005879 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Multi-Fault | 1245663 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007140&numberofmonths=24&showchangehistorylog=1 | 17-0007140 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CLAY-1101 | 163341101 | OCB | 11012 | 20170110 | 2110 | 1637469 | 885 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1711 | 118689 | 38.3422 | -120.9349 | 1POLENORTHOFMTR1004975061 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007140 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246725 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006599&numberofmonths=24&showchangehistorylog=1 | 17-0006599 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | MARTELL-1101 | 163011101 | FUSE | L9705 | 20170110 | 1009 | 1632890 | 461 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1844 | 38.4325 | -120.7106 | 6LDSIDEOFL9705 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006599 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1246245 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006529&numberofmonths=24&showchangehistorylog=1 | 17-0006529 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1101 | 163751101 | RECLOSER | 3170 | 20170110 | 1044 | 1632967 | 434 | Distribution Circuit | Vegetation | Tree - fell into line | 686 | 49270 | 38.4149 | -120.6847 | WIREDOWN1SOF92011 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006529 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Three Phase Fault | 1246183 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006977&numberofmonths=24&showchangehistorylog=1 | 17-0006977 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1101 | 163751101 | FUSE | L4053 | 20170110 | 1939 | 1635597 | 1312 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 26240 | 38.4059 | -120.7178 | COROFSIERRACTTONYLN | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006977 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246560 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006384&numberofmonths=24&showchangehistorylog=1 | 17-0006384 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE | 789 | 20170110 | 52 | 1632443 | 998 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 3992 | 38.472 | -120.7052 | 2EOF789 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006384 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246092 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007333&numberofmonths=24&showchangehistorylog=1 | 17-0007333 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | JUMPER | MTR1004974072 | 20170110 | 2140 | 1638375 | 1412 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 4236 | 38.4608 | -120.6111 | MTR1004974072 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007333 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Open Circuit | 1246914 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006485&numberofmonths=24&showchangehistorylog=1 | 17-0006485 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | SALT SPRINGS-2102 | 163692102 | FUSE | L2065 | 20170110 | 748 | 1632710 | 483 | Distribution Circuit | Vegetation | Tree - fell into line | 332 | 65496 | 38.3008 | -120.2732 | IROQUIOSSIERRA | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006485 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1246162 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007269&numberofmonths=24&showchangehistorylog=1 | 17-0007269 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | SALT SPRINGS-2102 | 163692102 | RECLOSER | 8442 | 20170110 | 2337 | 1638099 | 3993 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2000 | 127889 | 38.4156 | -120.1341 | SILVATONY17051poless2675 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0007269 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1246849 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006468&numberofmonths=24&showchangehistorylog=1 | 17-0006468 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | L5685 | 20170110 | 730 | 1632588 | 711 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 6399 | 38.3779 | -120.5118 | MCCARTNEYMARK2024MT1004935513 | Overcast-Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0006468 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1246149 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007222&numberofmonths=24&showchangehistorylog=1 | 17-0007222 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | RECLOSER | 4790 | 20170110 | 2036 | 1636930 | 1332 | Distribution Circuit | Vegetation | Tree - fell into line | 1181 | 315066 | 38.3868 | -120.5244 | MCCARTNEYMARK2024LS4790 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007222 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1246801 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007682&numberofmonths=24&showchangehistorylog=1 | 17-0007682 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CLAY-1103 | 163341103 | FUSE | 721 | 20170111 | 614 | 1638735 | 1942 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 56982 | 38.308 | -120.974 | MTR1009937982 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007682 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Three Phase Fault | 1247183 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007774&numberofmonths=24&showchangehistorylog=1 | 17-0007774 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | ELECTRA-1101 | 162161101 | FUSE | L3341 | 20170111 | 132 | 1638401 | 1869 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 21930 | 38.3939 | -120.6381 | 12890TABEAUCT | Overcast-Fog-Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0007774 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1247243 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007667&numberofmonths=24&showchangehistorylog=1 | 17-0007667 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | ELECTRA-1102 | 162161102 | FUSE | 1321 | 20170111 | 145 | 1638461 | 2350 | Distribution Circuit | Vegetation | Tree - fell into line | 338 | 423252 | 38.3469 | -120.5816 | 2WOFMTR1004979689 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007667 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Three Phase Fault | 1247171 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007328&numberofmonths=24&showchangehistorylog=1 | 17-0007328 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | OCB | 11022 | 20170111 | 123 | 1638362 | 685 | Distribution Circuit | Vegetation | Tree - fell into line | 4383 | 622884 | 38.4128 | -120.6607 | MACHIANDREW1852hwy88andpinegrovevolcanord | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0007328 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Three Phase Fault | 1246909 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007823&numberofmonths=24&showchangehistorylog=1 | 17-0007823 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | OTHER | WIREDOWNMTR1008715746TAP | 20170111 | 559 | 1638729 | 2029 | Distribution Circuit | Vegetation | Tree - branch fell on line | 150 | 14098 | 38.4911 | -120.7109 | MTR1008715746 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007823 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Open Circuit | 1247283 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0010154&numberofmonths=24&showchangehistorylog=1 | 17-0010154 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE | 5361 | 20170118 | 1542 | 1646817 | 658 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 5214 | 38.1573 | -120.5383 | BennettTom3366COESMARELDADOGTOWNRD | Overcast-Fog-Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0010154 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Three Phase Fault | 1249166 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011814&numberofmonths=24&showchangehistorylog=1 | 17-0011814 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | SALT SPRINGS-2102 | 163692102 | RECLOSER | 97924 | 20170120 | 2059 | 1655172 | 8204 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 405005 | 38.4156 | -120.1341 | 10DIFFERENTLOCATIONSSWOF2469 | Overcast-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 17-0011814 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1250643 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011646&numberofmonths=24&showchangehistorylog=1 | 17-0011646 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | RECLOSER | 3142 | 20170120 | 1401 | 1654386 | 348 | Distribution Circuit | Vegetation | Tree - fell into line | 991 | 196316 | 38.3018 | -120.277 | SOURCESIDEOF7301 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011646 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Multi-Fault | 1250496 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011855&numberofmonths=24&showchangehistorylog=1 | 17-0011855 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | 5387 | 20170120 | 1401 | 1655154 | 5510 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 380190 | 38.289 | -120.2761 | SIOUXTRAILKAROCKRD | Overcast-Snow-Below 32 F | Crossarm, Wood | Broken, wire on ground | 17-0011855 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1250682 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011856&numberofmonths=24&showchangehistorylog=1 | 17-0011856 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L495 | 20170120 | 2018 | 1655127 | 5123 | Distribution Circuit | Vegetation | Tree - fell into line | 123 | 630129 | 38.2846 | -120.2766 | MTR1004241061 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0011856 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1250683 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013242&numberofmonths=24&showchangehistorylog=1 | 17-0013242 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L5381 | 20170120 | 2232 | 1661417 | 3899 | Distribution Circuit | Vegetation | Tree - fell into line | 72 | 280728 | 38.2518 | -120.3509 | MTR1004657171MTR1004656246 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0013242 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1252052 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0014509&numberofmonths=24&showchangehistorylog=1 | 17-0014509 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | JUMPER | UNNUMBEREDSBCOLDSIDEMTR1008755737 | 20170120 | 2223 | 1666221 | 6637 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 19911 | 38.2539 | -120.299 | 6SPANSLDSIDEOFTEMPSBCO | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0014509 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1253182 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012134&numberofmonths=24&showchangehistorylog=1 | 17-0012134 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | L1137 | 20170120 | 2332 | 1655312 | 3928 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 23568 | 38.4015 | -120.4879 | 8NNEOFL1137 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012134 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1250948 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011926&numberofmonths=24&showchangehistorylog=1 | 17-0011926 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | RECLOSER | 1222 | 20170121 | 811 | 1655890 | 587 | Distribution Circuit | Equipment Failure/Involved | Overhead | 973 | 494544 | 38.436 | -120.5561 | MTR1005017206 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0011926 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1250753 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011951&numberofmonths=24&showchangehistorylog=1 | 17-0011951 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE | L3829 | 20170121 | 520 | 1656196 | 1893 | Distribution Circuit | Vegetation | Tree - fell into line | 118 | 84069 | 38.4697 | -120.5457 | DORRISRYAN1914ASHLANSCTANDSUGARPINE | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0011951 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1250777 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012011&numberofmonths=24&showchangehistorylog=1 | 17-0012011 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE | L7193 | 20170121 | 434 | 1655869 | 1869 | Distribution Circuit | Vegetation | Tree - fell into line | 90 | 168210 | 38.4534 | -120.525 | 26840LAKEDR | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | On Ground | 17-0012011 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1250828 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012051&numberofmonths=24&showchangehistorylog=1 | 17-0012051 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE | L2131 | 20170121 | 428 | 1655504 | 888 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 13320 | 38.4867 | -120.5956 | 18300GOLDCREEKTRAIL | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012051 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1250864 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0014731&numberofmonths=24&showchangehistorylog=1 | 17-0014731 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | SALT SPRINGS-2102 | 163692102 | FUSE | L7287 | 20170121 | 812 | 1666897 | 6319 | Distribution Circuit | Equipment Failure/Involved | Overhead | 37 | 233803 | 38.3048 | -120.2587 | 305731893225CHUMASHCIRCLE | Clear-Below 32 F | Conductor, Overhead | On Ground | 17-0014731 | OH | Sus | 0 | yes | 2017 | JAN | Yes | None | 1253366 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011887&numberofmonths=24&showchangehistorylog=1 | 17-0011887 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1701 | 162821701 | FUSE | 2641 | 20170121 | 247 | 1655445 | 1150 | Distribution Circuit | Vegetation | Tree - fell into line | 75 | 86250 | 38.1863 | -120.3681 | 5520STAMPEDECANYONRD | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 17-0011887 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1250713 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011933&numberofmonths=24&showchangehistorylog=1 | 17-0011933 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | STANISLAUS-1701 | 162821701 | RECLOSER | 1812 | 20170121 | 917 | 1656126 | 4541 | Distribution Circuit | Vegetation | Tree - fell into line | 816 | 741085 | 38.183 | -120.3756 | Berry18538407095RanchoParadisoMTR1004165990 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011933 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1250763 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011894&numberofmonths=24&showchangehistorylog=1 | 17-0011894 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | RECLOSER | 1888 | 20170121 | 552 | 1655236 | 724 | Distribution Circuit | Vegetation | Tree - fell into line | 1373 | 994052 | 38.2367 | -120.3628 | 8SPANSLDSIDEOF18882315MUSTANGRD | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0011894 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Three Phase Fault | 1250720 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011896&numberofmonths=24&showchangehistorylog=1 | 17-0011896 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | OTHER | WIREDOWNCOROFINDIANROCKTOPANGA | 20170121 | 400 | 1655629 | 4661 | Distribution Circuit | Equipment Failure/Involved | Overhead | 114 | 520574 | 38.2938 | -120.2674 | COROFINDIANROCKTOPANGA | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0011896 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Open Circuit | 1250723 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011908&numberofmonths=24&showchangehistorylog=1 | 17-0011908 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | RECLOSER | 3142 | 20170121 | 623 | 1655779 | 3647 | Distribution Circuit | Vegetation | Tree - fell into line | 628 | 2260797 | 38.3018 | -120.277 | 626SIERRAPKWY | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0011908 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1250736 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012019&numberofmonths=24&showchangehistorylog=1 | 17-0012019 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L611 | 20170121 | 903 | 1656379 | 694 | Distribution Circuit | Vegetation | Tree - fell into line | 189 | 80646 | 38.2447 | -120.3642 | MTR1004240708 | Overcast-Fog-Below 32 F | Pole-Wood | Broken, wire on ground | 17-0012019 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1250836 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012029&numberofmonths=24&showchangehistorylog=1 | 17-0012029 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | RECLOSER | 37278 | 20170121 | 1014 | 1655642 | 1987 | Distribution Circuit | Vegetation | Tree - fell into line | 287 | 289340 | 38.2465 | -120.3643 | Laskowski3505various | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0012029 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Three Phase Fault | 1250845 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012105&numberofmonths=24&showchangehistorylog=1 | 17-0012105 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L2695 | 20170121 | 532 | 1656960 | 2017 | Distribution Circuit | Vegetation | Tree - fell into line | 64 | 86212 | 38.2617 | -120.3339 | 1SPWOFMTR1004652362 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0012105 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1250919 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012113&numberofmonths=24&showchangehistorylog=1 | 17-0012113 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L2371 | 20170121 | 448 | 1656981 | 5077 | Distribution Circuit | Vegetation | Tree - branch fell on line | 43 | 218311 | 38.2376 | -120.3184 | 4SPANSLDSIDEOFL2371 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0012113 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1250927 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012126&numberofmonths=24&showchangehistorylog=1 | 17-0012126 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | SWITCH | L3965 | 20170121 | 557 | 1657018 | 3607 | Distribution Circuit | Vegetation | Tree - fell into line | 153 | 551871 | 38.2517 | -120.3667 | BennettTom3366COL623 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0012126 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Force Out | 1250940 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012128&numberofmonths=24&showchangehistorylog=1 | 17-0012128 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | RECLOSER | 1804 | 20170121 | 1715 | 1657023 | 20 | Distribution Circuit | Vegetation | Tree - fell into line | 399 | 7980 | 38.2589 | -120.3477 | LDSIDEL2203 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012128 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Force Out | 1250942 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012133&numberofmonths=24&showchangehistorylog=1 | 17-0012133 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L2203 | 20170121 | 1717 | 1657042 | 41 | Distribution Circuit | Vegetation | Tree - branch fell on line | 61 | 2501 | 38.2599 | -120.3335 | LDSIDEL2203 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012133 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Open Circuit | 1250947 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011863&numberofmonths=24&showchangehistorylog=1 | 17-0011863 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | RECLOSER | 1804 | 20170121 | 114 | s1251084 | 5189 | Distribution Circuit | Vegetation | Tree - fell into line | 1137 | 1708981 | 38.2589 | -120.3477 | MULTIPLELOCS | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011863 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1251084 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012542&numberofmonths=24&showchangehistorylog=1 | 17-0012542 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L5047 | 20170121 | 1819 | 1657097 | 1213 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 52159 | 38.2491 | -120.3428 | 1869MICHELEWAY | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012542 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1251362 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012950&numberofmonths=24&showchangehistorylog=1 | 17-0012950 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L5141 | 20170121 | 1738 | 1657057 | 1555 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 29545 | 38.2458 | -120.3471 | MTR1004653128 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0012950 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1251770 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012987&numberofmonths=24&showchangehistorylog=1 | 17-0012987 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L5379 | 20170121 | 2232 | 1660173 | 780 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 7020 | 38.2519 | -120.3527 | 1SOFL5379 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | On Ground | 17-0012987 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1251808 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013222&numberofmonths=24&showchangehistorylog=1 | 17-0013222 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | 44955 | 20170121 | 534 | 1661350 | 6418 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 299962 | 38.3103 | -120.2781 | CAMPCONNELLSTORE | Clear-Below 32 F | Pole-Wood | Broken, wire on ground | 17-0013222 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Three Phase Fault | 1252031 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013243&numberofmonths=24&showchangehistorylog=1 | 17-0013243 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L5383 | 20170121 | 1307 | 1661429 | 3377 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 50655 | 38.2512 | -120.3521 | LDSIDEL5383 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013243 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1252054 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013267&numberofmonths=24&showchangehistorylog=1 | 17-0013267 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L491 | 20170121 | 40 | 1661647 | 6797 | Distribution Circuit | Vegetation | Tree - fell into line | 110 | 747670 | 38.3076 | -120.2664 | 1SSMTR1004236157 | Clear-Below 32 F | Pole-Wood | Broken, wire on ground | 17-0013267 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1252082 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013796&numberofmonths=24&showchangehistorylog=1 | 17-0013796 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L5083 | 20170121 | 1822 | 1664016 | 4016 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 52208 | 38.2408 | -120.3377 | METER1004655082 | Clear-32-90 F | Conductor, Overhead | On Ground | 17-0013796 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Three Phase Fault | 1252573 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013917&numberofmonths=24&showchangehistorylog=1 | 17-0013917 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L5013 | 20170121 | 114 | 1664476 | 5202 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 150858 | 38.2581 | -120.3175 | MTR1004655984 | Clear-Below 32 F | Pole-Wood | Broken, wire on ground | 17-0013917 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1252675 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011966&numberofmonths=24&showchangehistorylog=1 | 17-0011966 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | FUSE | L3309 | 20170121 | 429 | 1655532 | 2342 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 32788 | 38.4921 | -120.53 | MTR1004863146 | Strong Winds-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 17-0011966 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1250788 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011969&numberofmonths=24&showchangehistorylog=1 | 17-0011969 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | FUSE | L2217 | 20170121 | 4 | 1655328 | 2406 | Distribution Circuit | Equipment Failure/Involved | Overhead | 32 | 76992 | 38.4901 | -120.5282 | SSOFMTR1004980273 | Overcast-Fog-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 17-0011969 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1250789 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012006&numberofmonths=24&showchangehistorylog=1 | 17-0012006 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | RECLOSER | 12256 | 20170121 | 1209 | 1655655 | 1433 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1153 | 390401 | 38.4438 | -120.5087 | MACHIANDREW185226654wintonrd | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0012006 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Force Out | 1250824 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012032&numberofmonths=24&showchangehistorylog=1 | 17-0012032 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | JUMPER | OJSOFMTR1008788068 | 20170121 | 1050 | 1656565 | 616 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 616 | 38.4695 | -120.5311 | MTR1008788068 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012032 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1250848 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012161&numberofmonths=24&showchangehistorylog=1 | 17-0012161 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | FUSE | 1711 | 20170121 | 7 | 1657194 | 2706 | Distribution Circuit | Equipment Failure/Involved | Overhead | 83 | 224598 | 38.4983 | -120.5045 | MTR1004860557 | Strong Winds-Snow-32-90 F | Pole-Wood | Broken, wire on ground | 17-0012161 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1250975 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012015&numberofmonths=24&showchangehistorylog=1 | 17-0012015 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | L1981 | 20170121 | 446 | 1655550 | 1896 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 26544 | 38.4188 | -120.5196 | 914SKULLFLATRD | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | On Ground | 17-0012015 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1250832 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012688&numberofmonths=24&showchangehistorylog=1 | 17-0012688 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CORRAL-1101 | 162991101 | RECLOSER | 12608 | 20170122 | 322 | 1658391 | 508 | Distribution Circuit | Equipment Failure/Involved | Overhead | 413 | 98459 | 38.1339 | -120.9255 | 11989 | Overcast-Drizzle-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0012688 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1251511 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012972&numberofmonths=24&showchangehistorylog=1 | 17-0012972 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | ELECTRA-1101 | 162161101 | FUSE | L2347 | 20170122 | 537 | 1659046 | 715 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 20060 | 38.3737 | -120.6599 | MTR1004805616 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012972 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1251794 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012977&numberofmonths=24&showchangehistorylog=1 | 17-0012977 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | ELECTRA-1101 | 162161101 | FUSE | L3457 | 20170122 | 706 | 1659419 | 2042 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 10210 | 38.3703 | -120.6572 | ILDSIDEOFL3457 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 17-0012977 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1251799 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013200&numberofmonths=24&showchangehistorylog=1 | 17-0013200 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1101 | 163751101 | FUSE | 1065 | 20170122 | 550 | 1659134 | 707 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 11312 | 38.3787 | -120.6972 | 18228WCLINTONRD | Overcast-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0013200 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1252012 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013212&numberofmonths=24&showchangehistorylog=1 | 17-0013212 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | JUMPER | WIREDOWN2NOFL1149 | 20170122 | 1311 | 1661303 | 457 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1070 | 203063 | 38.4772 | -120.6267 | 2NOFL1149 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013212 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Force Out | 1252022 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013338&numberofmonths=24&showchangehistorylog=1 | 17-0013338 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | JUMPER | OJS1WOF63735 | 20170122 | 1318 | 1661997 | 2882 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 20482 | 38.2451 | -120.3711 | OJS1WOF63735 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013338 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Open Circuit | 1252153 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013394&numberofmonths=24&showchangehistorylog=1 | 17-0013394 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | 1151 | 20170122 | 1956 | 1662248 | 4250 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 30215 | 38.2774 | -120.3184 | SOFHARDTAP | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013394 | OH | Sus | 0 | yes | 2017 | JAN | Yes | None | 1252209 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0014330&numberofmonths=24&showchangehistorylog=1 | 17-0014330 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L5009 | 20170122 | 206 | 1658134 | 3591 | Distribution Circuit | Vegetation | Tree - branch fell on line | 21 | 75411 | 38.2641 | -120.3217 | ENDOFTAPLINELDSIDEOFL5009 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0014330 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1253061 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013697&numberofmonths=24&showchangehistorylog=1 | 17-0013697 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE | L3679 | 20170123 | 731 | 1663558 | 895 | Distribution Circuit | Equipment Failure/Involved | Overhead | 154 | 109984 | 38.4444 | -120.5319 | 1EOFL3539 | Overcast-Snow-32-90 F | Pole-Wood | Broken, wire on ground | 17-0013697 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Force Out | 1252500 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013751&numberofmonths=24&showchangehistorylog=1 | 17-0013751 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L5053 | 20170123 | 1010 | 1663742 | 1741 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 13928 | 38.2449 | -120.3375 | 1LOADSIDEOFL5053 | Overcast-32-90 F | Conductor, Overhead | On Ground | 17-0013751 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1252537 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0014334&numberofmonths=24&showchangehistorylog=1 | 17-0014334 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L2065 | 20170123 | 2037 | 1664970 | 2699 | Distribution Circuit | Environmental/External | Ice or snow | 154 | 415646 | 38.3008 | -120.2732 | DEVALLECLAY1704EVERYWHERE | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0014334 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Three Phase Fault | 1253062 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0014384&numberofmonths=24&showchangehistorylog=1 | 17-0014384 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L489 | 20170123 | 2037 | 1665800 | 2713 | Distribution Circuit | Vegetation | Tree - branch fell on line | 41 | 111233 | 38.3039 | -120.2723 | LDSIDE | Overcast-Fog-Below 32 F | Conductor, Overhead | On Ground | 17-0014384 | OH | Sus | 0 | yes | 2017 | JAN | Yes | None | 1253104 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0014426&numberofmonths=24&showchangehistorylog=1 | 17-0014426 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | JUMPER | OJMTR1004654255 | 20170123 | 2037 | 1665877 | 2699 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 72873 | 38.3045 | -120.2686 | MTR1004654255 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0014426 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1253129 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013704&numberofmonths=24&showchangehistorylog=1 | 17-0013704 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | FUSE | L2219 | 20170123 | 419 | 1662774 | 738 | Distribution Circuit | Vegetation | Tree - fell into line | 68 | 50184 | 38.4909 | -120.5268 | 1SPANSWOF27173ASHLANDPIONEER | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0013704 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1252506 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013767&numberofmonths=24&showchangehistorylog=1 | 17-0013767 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | FUSE | L2217 | 20170123 | 842 | 1663256 | 725 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 23200 | 38.4901 | -120.5282 | 2SPANSSWOFTXMTR1004980273 | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013767 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1252548 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013756&numberofmonths=24&showchangehistorylog=1 | 17-0013756 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | WEST POINT-1102 | 163201102 | TRANSFORMER | 319920669198 | 20170123 | 1440 | 1663376 | 139 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 834 | 38.4003 | -120.5288 | SOUTHEASTOFSW679 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013756 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Force Out | 1252541 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013878&numberofmonths=24&showchangehistorylog=1 | 17-0013878 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | TRIP-SAVER | L3733 | 20170123 | 906 | 1663699 | 1804 | Distribution Circuit | Vegetation | Tree - branch fell on line | 98 | 39137 | 38.3894 | -120.5252 | CGC319950668677 | Overcast-Snow-32-90 F | Conductor, Overhead | On Ground | 17-0013878 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1252643 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018600&numberofmonths=24&showchangehistorylog=1 | 17-0018600 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CORRAL-1103 | 162991103 | FUSE | 91311 | 20170207 | 1310 | 1680120 | 182 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 1670 | 38.1303 | -120.8642 | NOFMTR1004817147 | Overcast-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018600 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1256371 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0022518&numberofmonths=24&showchangehistorylog=1 | 17-0022518 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | ELECTRA-1101 | 162161101 | FUSE | L2347 | 20170217 | 1447 | 1696592 | 833 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 19738 | 38.3737 | -120.6599 | MCCARTNEYMARK20245PSEMT10033556177 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 17-0022518 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1259542 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0022632&numberofmonths=24&showchangehistorylog=1 | 17-0022632 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | FROGTOWN-1702 | 163451702 | FUSE | L6029 | 20170217 | 1916 | 1698213 | 595 | Distribution Circuit | Vegetation | Tree - fell into line | 168 | 33726 | 38.1328 | -120.4985 | MTR1009011304 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 17-0022632 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1259655 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0022892&numberofmonths=24&showchangehistorylog=1 | 17-0022892 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CORRAL-1101 | 162991101 | OTHER | WIREDOWNNOFB452 | 20170218 | 500 | 1699005 | 1027 | Distribution Circuit | Vegetation | Tree - fell into line | 110 | 26665 | 38.1202 | -120.8908 | NOFB452 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022892 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1259904 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024110&numberofmonths=24&showchangehistorylog=1 | 17-0024110 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | ELECTRA-1101 | 162161101 | FUSE | L2347 | 20170220 | 2019 | 1705859 | 431 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 8118 | 38.3737 | -120.6599 | MTR1004739463 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0024110 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1261074 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023681&numberofmonths=24&showchangehistorylog=1 | 17-0023681 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | FROGTOWN-1702 | 163451702 | FUSE | L3803 | 20170220 | 732 | 1702616 | 403 | Distribution Circuit | Equipment Failure/Involved | Overhead | 236 | 95108 | 38.1116 | -120.5083 | SILVATONY1705acrossfrom2643murphysgraderd | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023681 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1260682 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024818&numberofmonths=24&showchangehistorylog=1 | 17-0024818 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | RECLOSER | 93116 | 20170221 | 51 | 1707060 | 1197 | Distribution Circuit | Vegetation | Tree - fell into line | 339 | 118521 | 38.3838 | -120.527 | MTR1004974774 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024818 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1261787 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037200&numberofmonths=24&showchangehistorylog=1 | 17-0037200 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L611 | 20170406 | 1604 | 1745743 | 397 | Distribution Circuit | Vegetation | Tree - fell into line | 189 | 56748 | 38.2447 | -120.3642 | 2163CHAPPARRAL | Overcast-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0037200 | OH | Sus | 42985900 | yes | 2017 | APR | Yes | Three Phase Fault | 1271421 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037539&numberofmonths=24&showchangehistorylog=1 | 17-0037539 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | TRIP-SAVER | 1303 | 20170406 | 2359 | 1748927 | 592 | Distribution Circuit | Vegetation | Tree - fell into line | 215 | 127280 | 38.4044 | -120.5058 | MACHIANDREW18521303 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037539 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1271759 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037849&numberofmonths=24&showchangehistorylog=1 | 17-0037849 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | L5677 | 20170407 | 1039 | 1750513 | 351 | Distribution Circuit | Vegetation | Tree - branch fell on line | 29 | 10179 | 38.4257 | -120.4924 | 2893LILYGAPRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037849 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1272001 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0085394&numberofmonths=24&showchangehistorylog=1 | 17-0085394 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | WEST POINT-1102 | 163201102 | RECLOSER | 72036 | 20171009 | 446 | 1895664 | 843 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2466 | 312981 | 38.4129 | -120.5501 | 1236127412761308SPINKRDWESTPOINT5POLESEOFL2005MTR1004936640 | Strong Winds-Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0085394 | OH | Sus | 31356040 | yes | 2017 | OCT | Yes | Force Out | 1306847 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0099721&numberofmonths=24&showchangehistorylog=1 | 17-0099721 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | ELECTRA-1102 | 162161102 | FUSE | L4015 | 20171204 | 1341 | 1935278 | 725 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 3625 | 38.3518 | -120.5212 | REANOANTHONY2009L4015TOENDOFLINE | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0099721 | OH | Sus | 0 | yes | 2017 | DEC | Yes | Line to Ground | 1317477 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0099754&numberofmonths=24&showchangehistorylog=1 | 17-0099754 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | OTHER | WIREDWNMTR1004978329 | 20171204 | 1421 | 1935747 | 600 | Distribution Circuit | Vegetation | Tree - fell into line | 1311 | 97276 | 38.4451 | -120.5455 | MTR1004978329 | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0099754 | OH | Sus | 0 | yes | 2017 | DEC | Yes | Open Circuit | 1317501 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0100140&numberofmonths=24&showchangehistorylog=1 | 17-0100140 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | SALT SPRINGS-2101 | 163692101 | RECLOSER | 1216 | 20171204 | 1909 | 1936934 | 1510 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 75500 | 38.4988 | -120.2177 | 6SSOFFUCO1589 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0100140 | OH | Sus | 0 | yes | 2017 | DEC | Yes | Multi-Fault | 1317808 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0099809&numberofmonths=24&showchangehistorylog=1 | 17-0099809 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | SALT SPRINGS-2102 | 163692102 | FUSE | 1177 | 20171204 | 1731 | 1935962 | 1239 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 18585 | 38.3115 | -120.2779 | NOF1177 | Clear-Strong Winds-Below 32 F | Conductor, Overhead | On Ground | 17-0099809 | OH | Sus | 0 | yes | 2017 | DEC | Yes | Line to Ground | 1317551 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0099815&numberofmonths=24&showchangehistorylog=1 | 17-0099815 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | SALT SPRINGS-2102 | 163692102 | FUSE | 44955 | 20171204 | 1756 | 1935884 | 1213 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 41242 | 38.3103 | -120.2781 | 4PNOF44955 | Clear-Strong Winds-Below 32 F | Conductor, Overhead | On Ground | 17-0099815 | OH | Sus | 0 | yes | 2017 | DEC | Yes | Three Phase Fault | 1317556 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0099836&numberofmonths=24&showchangehistorylog=1 | 17-0099836 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | SALT SPRINGS-2102 | 163692102 | FUSE | L2065 | 20171204 | 1715 | 1935886 | 741 | Distribution Circuit | Vegetation | Tree - fell into line | 149 | 58016 | 38.3008 | -120.2732 | SILVATONY17051polesourcesideof6681 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0099836 | OH | Sus | 0 | yes | 2017 | DEC | Yes | Line to Line | 1317578 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0099850&numberofmonths=24&showchangehistorylog=1 | 17-0099850 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | SALT SPRINGS-2102 | 163692102 | FUSE | 81017 | 20171204 | 1720 | 1935841 | 1158 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 56508 | 38.313 | -120.2632 | 1084SHOSHONEDR | Clear-Strong Winds-Below 32 F | Pole-Wood | Broken, wire on ground | 17-0099850 | OH | Sus | 0 | yes | 2017 | DEC | Yes | Three Phase Fault | 1317590 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0099866&numberofmonths=24&showchangehistorylog=1 | 17-0099866 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | SALT SPRINGS-2102 | 163692102 | FUSE | 91563 | 20171204 | 1820 | 1935925 | 1200 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 30056 | 38.3186 | -120.2549 | 403POMOCIRCLE | Clear-Strong Winds-Below 32 F | Pole-Wood | Broken, wire on ground | 17-0099866 | OH | Sus | 31368344 | yes | 2017 | DEC | Yes | Line to Line | 1317603 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0099725&numberofmonths=24&showchangehistorylog=1 | 17-0099725 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | RECLOSER | 37276 | 20171204 | 1452 | 1935616 | 853 | Distribution Circuit | Vegetation | Tree - fell into line | 769 | 167781 | 38.2391 | -120.3364 | Berry185384070951107CypressPointDr | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0099725 | OH | Sus | 0 | yes | 2017 | DEC | Yes | Line to Ground | 1317479 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0099706&numberofmonths=24&showchangehistorylog=1 | 17-0099706 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | OTHER | WIREDOWNMTR1004976890 | 20171204 | 1327 | 1935513 | 601 | Distribution Circuit | Vegetation | Tree - fell into line | 348 | 29088 | 38.4012 | -120.5053 | MTR1004976890 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0099706 | OH | Sus | 0 | yes | 2017 | DEC | Yes | Line to Ground | 1317469 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0102264&numberofmonths=24&showchangehistorylog=1 | 17-0102264 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | SALT SPRINGS-2101 | 163692101 | JUMPER | WIREDOWN | 20171216 | 2107 | 1945975 | 982 | Distribution Circuit | Vegetation | Tree - fell into line | 908 | 42056 | 38.4476 | -120.0708 | FUCO4693 | Strong Winds-Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0102264 | OH | Sus | 0 | yes | 2017 | DEC | Yes | Open Circuit | 1320173 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0023260&numberofmonths=24&showchangehistorylog=1 | 18-0023260 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE | 1357 | 20180316 | 559 | 45235 | 662 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 19198 | 38.2319 | -120.5473 | 3NOF1357 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 18-0023260 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1336158 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0023561&numberofmonths=24&showchangehistorylog=1 | 18-0023561 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE | 1715 | 20180316 | 1606 | 46157 | 2919 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 117621 | 38.494 | -120.5107 | BETWWENMTR1004862419MTR1004979898 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023561 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1336353 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0023578&numberofmonths=24&showchangehistorylog=1 | 18-0023578 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE | 1595 | 20180316 | 1636 | 46176 | 3054 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 76350 | 38.4832 | -120.5209 | 1WOF1595 | Overcast-Fog-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on ground | 18-0023578 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1336369 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0023751&numberofmonths=24&showchangehistorylog=1 | 18-0023751 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE | L6007 | 20180316 | 1705 | 46261 | 4132 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 49584 | 38.5075 | -120.4895 | FOUND3PHASESDOWN5LDSIDEOFL6007IN6LOCATIONS | Overcast-Fog-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on ground | 18-0023751 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Multi-Fault | 1336544 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0023352&numberofmonths=24&showchangehistorylog=1 | 18-0023352 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | STANISLAUS-1701 | 162821701 | RECLOSER | 1812 | 20180316 | 1058 | 45419 | 2936 | Distribution Circuit | Vegetation | Tree - fell into line | 912 | 271973 | 38.183 | -120.3756 | SPNOFFUSES1331MTR1004654474BUCK1SPLDSDMTR1004236190 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023352 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Three Phase Fault | 1336241 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0023711&numberofmonths=24&showchangehistorylog=1 | 18-0023711 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1701 | 162821701 | FUSE | 1113 | 20180316 | 1751 | 46238 | 2463 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 38310 | 38.2084 | -120.3676 | 4EOF1113 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023711 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1336509 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0023313&numberofmonths=24&showchangehistorylog=1 | 18-0023313 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L2709 | 20180316 | 741 | 45310 | 507 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 11154 | 38.236 | -120.3354 | 3SOFL2709 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 18-0023313 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1336209 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0023317&numberofmonths=24&showchangehistorylog=1 | 18-0023317 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | 2383 | 20180316 | 715 | 45282 | 418 | Distribution Circuit | Vegetation | Tree - branch fell on line | 281 | 117458 | 38.2351 | -120.344 | MTR1004820768 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023317 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1336215 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0023419&numberofmonths=24&showchangehistorylog=1 | 18-0023419 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | RECLOSER | 75348 | 20180316 | 1255 | 45876 | 1523 | Distribution Circuit | Vegetation | Tree - fell into line | 418 | 636614 | 38.2622 | -120.3292 | SILVATONY1705915meadow | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023419 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Three Phase Fault | 1336282 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0023526&numberofmonths=24&showchangehistorylog=1 | 18-0023526 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | 6857 | 20180316 | 1341 | 45949 | 501 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 16032 | 38.2328 | -120.3488 | 1SSOFL5111 | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023526 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1336332 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0023618&numberofmonths=24&showchangehistorylog=1 | 18-0023618 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L433 | 20180316 | 1839 | 46308 | 2597 | Distribution Circuit | Vegetation | Tree - branch fell on line | 171 | 266265 | 38.2549 | -120.351 | 2LDSIDEOFL5381 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 18-0023618 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1336396 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0023735&numberofmonths=24&showchangehistorylog=1 | 18-0023735 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | 1183 | 20180316 | 1201 | 46634 | 2838 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 28380 | 38.236 | -120.3214 | MTR1008965898 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 18-0023735 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1336527 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0023755&numberofmonths=24&showchangehistorylog=1 | 18-0023755 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L5009 | 20180316 | 1913 | 46305 | 1212 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 25452 | 38.2641 | -120.3217 | 2PFROMTHEEOL | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | On Ground | 18-0023755 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1336548 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0023507&numberofmonths=24&showchangehistorylog=1 | 18-0023507 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | TIGER CREEK-0201 | 161380201 | FUSE | 1743 | 20180316 | 1447 | 46059 | 4380 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 13140 | 38.4492 | -120.4908 | HELOPATROLNOLOCATIONORFAULTREPORTED | Overcast-Drizzle-32-90 F | Insulator | Broken, wire on object | 18-0023507 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1336322 | INS | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0023417&numberofmonths=24&showchangehistorylog=1 | 18-0023417 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | RECLOSER | 12256 | 20180316 | 1042 | 45719 | 3347 | Distribution Circuit | Vegetation | Tree - fell into line | 1472 | 1227672 | 38.4438 | -120.5087 | 6POLESLDSDSWL931MTR1004861704MTR1004860886 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 18-0023417 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Three Phase Fault | 1336285 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0023736&numberofmonths=24&showchangehistorylog=1 | 18-0023736 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | FUSE | L2217 | 20180316 | 1050 | 45729 | 3331 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 63250 | 38.4901 | -120.5282 | MTR1005017236 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023736 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1336528 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0023880&numberofmonths=24&showchangehistorylog=1 | 18-0023880 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | FUSE | L3233 | 20180316 | 1054 | 47310 | 4496 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 26976 | 38.382 | -120.5086 | 4132TREELN | Overcast-Fog-Snow-32-90 F | Pole-Wood | Broken, wire on ground | 18-0023880 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1336684 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0023303&numberofmonths=24&showchangehistorylog=1 | 18-0023303 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | 1773 | 20180316 | 812 | 45340 | 3360 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 168000 | 38.4343 | -120.445 | ATMTR1008768455 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 18-0023303 | OH | Sus | 31384483 | yes | 2018 | MAR | Yes | Three Phase Fault | 1336196 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0023488&numberofmonths=24&showchangehistorylog=1 | 18-0023488 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | TRIP-SAVER | 1303 | 20180316 | 1154 | 45697 | 2002 | Distribution Circuit | Vegetation | Tree - fell into line | 137 | 155249 | 38.4044 | -120.5058 | 1SSOFMTR1004934599MTR1008991600 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023488 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Three Phase Fault | 1336315 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0023619&numberofmonths=24&showchangehistorylog=1 | 18-0023619 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | TRIP-SAVER | 1305 | 20180316 | 1321 | 45911 | 3168 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 278099 | 38.4009 | -120.5045 | 3EOF1305FOUNDFLOATINGCONDUCTOR2SPANSSWOF6805WIREDOWNAND5SWOF6805FOUNDBROKENCROSSARM | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023619 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1336397 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0090288&numberofmonths=24&showchangehistorylog=1 | 18-0090288 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | RECLOSER | 1222 | 20181014 | 1936 | 195004 | 2635 | Distribution Circuit | Vegetation | Tree - fell into line | 623 | 1641605 | 38.436 | -120.5561 | REAROF16534ALPINELANE | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 18-0090288 | OH | Sus | 0 | yes | 2018 | OCT | Yes | Line to Line | 1385494 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0090290&numberofmonths=24&showchangehistorylog=1 | 18-0090290 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | RECLOSER | 93116 | 20181014 | 1956 | 195020 | 2893 | Distribution Circuit | Vegetation | Tree - fell into line | 609 | 1694964 | 38.3838 | -120.527 | L36072SOF52969 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 18-0090290 | OH | Sus | 0 | yes | 2018 | OCT | Yes | Line to Ground | 1385496 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0105202&numberofmonths=24&showchangehistorylog=1 | 18-0105202 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | FROGTOWN-1702 | 163451702 | OCB | 17022 | 20181129 | 1527 | 229315 | 1389 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4024 | 523222 | 38.0572 | -120.5343 | 4POLESLDSIDEOF2255ONMAINLINE1SOFHARDTAPTWD2255 | Overcast-Drizzle-Lightning-32-90 F | Conductor, Overhead | Broken, wire on object | 18-0105202 | OH | Sus | 0 | yes | 2018 | NOV | Yes | Line to Ground | 1396366 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0104893&numberofmonths=24&showchangehistorylog=1 | 18-0104893 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | WEST POINT-1102 | 163201102 | FUSE | 91241 | 20181129 | 752 | 228013 | 336 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 336 | 38.2827 | -120.5514 | 1SPANLDSIDEOF91241 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0104893 | OH | Sus | 0 | yes | 2018 | NOV | Yes | Line to Line | 1396181 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005297&numberofmonths=24&showchangehistorylog=1 | 19-0005297 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE | 1679 | 20190106 | 1728 | 255894 | 430 | Distribution Circuit | Vegetation | Tree - fell into line | 66 | 28380 | 38.2982 | -120.7035 | ATMTR1004738324 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005297 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1403762 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005591&numberofmonths=24&showchangehistorylog=1 | 19-0005591 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CLAY-1101 | 163341101 | FUSE | 1833 | 20190106 | 1909 | 256855 | 1511 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 3528 | 38.3895 | -120.9067 | TAPTWDNORTH2EOF1833 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005591 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1404043 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005229&numberofmonths=24&showchangehistorylog=1 | 19-0005229 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CLAY-1103 | 163341103 | RECLOSER | 7142 | 20190106 | 1751 | 256076 | 1609 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 110371 | 38.3168 | -120.9417 | LDSIDEOFC2992AT3025JACKSONVALLEYRD | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005229 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Multi-Fault | 1403699 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005261&numberofmonths=24&showchangehistorylog=1 | 19-0005261 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | ELECTRA-1101 | 162161101 | RECLOSER | 61816 | 20190106 | 1813 | 256272 | 615 | Distribution Circuit | Vegetation | Tree - fell into line | 372 | 141559 | 38.3634 | -120.6486 | 8SOF8787 | Partly Cloudy-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005261 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Three Phase Fault | 1403732 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005220&numberofmonths=24&showchangehistorylog=1 | 19-0005220 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | FROGTOWN-1702 | 163451702 | FUSE | L6029 | 20190106 | 1741 | 255991 | 1216 | Distribution Circuit | Vegetation | Tree - fell into line | 239 | 145852 | 38.1328 | -120.4985 | MTR1009733515 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005220 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1403690 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005159&numberofmonths=24&showchangehistorylog=1 | 19-0005159 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L559 | 20190106 | 1603 | 255579 | 535 | Distribution Circuit | Equipment Failure/Involved | Overhead | 28 | 5568 | 38.2469 | -120.3053 | 2LDSIDEOFMTR1008755737 | Overcast-Fog-Snow-Strong Winds-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0005159 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1403630 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005424&numberofmonths=24&showchangehistorylog=1 | 19-0005424 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | WEST POINT-1102 | 163201102 | FUSE | 1289 | 20190106 | 1659 | 257996 | 887 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 12418 | 38.2828 | -120.5572 | 1SOF1289 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005424 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1403876 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0009917&numberofmonths=24&showchangehistorylog=1 | 19-0009917 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CORRAL-1101 | 162991101 | FUSE | 16065 | 20190116 | 1617 | 267328 | 651 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 10080 | 38.1486 | -120.9177 | 5567AMOS | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 19-0009917 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1406789 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010026&numberofmonths=24&showchangehistorylog=1 | 19-0010026 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CORRAL-1103 | 162991103 | FUSE | L1991 | 20190116 | 1700 | 268230 | 200 | Distribution Circuit | Equipment Failure/Involved | Overhead | 39 | 4740 | 38.1269 | -120.845 | AT6219USHERDR | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010026 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1406891 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010826&numberofmonths=24&showchangehistorylog=1 | 19-0010826 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | ELECTRA-1101 | 162161101 | FUSE | L1279 | 20190116 | 2333 | 271922 | 2293 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 23704 | 38.3765 | -120.6406 | DORRISRYAN1914ENDOFLINE | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010826 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407549 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010669&numberofmonths=24&showchangehistorylog=1 | 19-0010669 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | MARTELL-1101 | 163011101 | FUSE | L5669 | 20190116 | 2323 | 271866 | 1190 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 16660 | 38.4295 | -120.7363 | MTR1009719615 | Overcast-Fog-Heavy Rain-Lightning-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010669 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1407486 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011256&numberofmonths=24&showchangehistorylog=1 | 19-0011256 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | MARTELL-1101 | 163011101 | FUSE | L2363 | 20190116 | 2327 | 271901 | 2048 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 16384 | 38.4567 | -120.7864 | GOSSETTDANIELADAML2363 | Overcast-Fog-Heavy Rain-Lightning-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011256 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1407826 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010743&numberofmonths=24&showchangehistorylog=1 | 19-0010743 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | TRIP-SAVER | 1765 | 20190116 | 2355 | 272062 | 835 | Distribution Circuit | Vegetation | Tree - fell into line | 99 | 67965 | 38.4433 | -120.5355 | MACHIANDREW1852meadowvistard | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010743 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1407516 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010339&numberofmonths=24&showchangehistorylog=1 | 19-0010339 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | WEST POINT-1102 | 163201102 | RECLOSER | 4788 | 20190116 | 2230 | 271610 | 1021 | Distribution Circuit | Vegetation | Tree - fell into line | 711 | 625611 | 38.3314 | -120.5187 | 2PWOF91241 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010339 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Three Phase Fault | 1407204 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010994&numberofmonths=24&showchangehistorylog=1 | 19-0010994 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | CALAVERAS CEMENT-1101 | 162211101 | FUSE | L3231 | 20190117 | 1205 | 273879 | 1781 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 16029 | 38.3802 | -120.5157 | 2NDAND3RDPOLESNOF3231 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0010994 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407659 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011361&numberofmonths=24&showchangehistorylog=1 | 19-0011361 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | TRIP-SAVER | 585 | 20190117 | 1710 | 274685 | 1042 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 80234 | 38.1398 | -120.6624 | 6SOF585 | Overcast-Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0011361 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Three Phase Fault | 1407907 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010586&numberofmonths=24&showchangehistorylog=1 | 19-0010586 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CORRAL-1102 | 162991102 | FUSE | 19471 | 20190117 | 545 | 272568 | 415 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 830 | 38.1179 | -120.8859 | JNO19471 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010586 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407449 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010560&numberofmonths=24&showchangehistorylog=1 | 19-0010560 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | FROGTOWN-1702 | 163451702 | OTHER | WIREDOWNMTR1004819778 | 20190117 | 58 | 272179 | 1070 | Distribution Circuit | Vegetation | Tree - fell into line | 239 | 38430 | 38.116 | -120.4996 | MTR1004819778 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010560 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Force Out | 1407422 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010499&numberofmonths=24&showchangehistorylog=1 | 19-0010499 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE | L2751 | 20190117 | 0 | 272074 | 493 | Distribution Circuit | Vegetation | Tree - branch fell on line | 62 | 30566 | 38.4339 | -120.5822 | MTR1010444413 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010499 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1407362 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010514&numberofmonths=24&showchangehistorylog=1 | 19-0010514 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | SALT SPRINGS-2102 | 163692102 | TRIP-SAVER | L491 | 20190117 | 15 | 272322 | 1518 | Distribution Circuit | 3rd Party | Vehicle | 111 | 168498 | 38.3076 | -120.2664 | MTR1004236132 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0010514 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407377 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010782&numberofmonths=24&showchangehistorylog=1 | 19-0010782 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | SALT SPRINGS-2102 | 163692102 | FUSE | 6681 | 20190117 | 200 | 272307 | 1418 | Distribution Circuit | Vegetation | Tree - fell into line | 73 | 54478 | 38.3079 | -120.2672 | 3353POCATELLOCIR | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010782 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1407535 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010959&numberofmonths=24&showchangehistorylog=1 | 19-0010959 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | SALT SPRINGS-2102 | 163692102 | TRIP-SAVER | L485 | 20190117 | 729 | 272834 | 1930 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 42636 | 38.2974 | -120.2742 | SILVATONY17053308elcaminobootstrap | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010959 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1407631 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010460&numberofmonths=24&showchangehistorylog=1 | 19-0010460 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | RECLOSER | 75348 | 20190117 | 13 | 272173 | 758 | Distribution Circuit | Vegetation | Tree - fell into line | 418 | 117666 | 38.2622 | -120.3292 | MTR1005396024 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010460 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407324 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0017029&numberofmonths=24&showchangehistorylog=1 | 19-0017029 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | FROGTOWN-1702 | 163451702 | FUSE | L2657 | 20190202 | 751 | 286893 | 503 | Distribution Circuit | Vegetation | Tree - branch fell on line | 31 | 7079 | 38.0915 | -120.4714 | NOFMTR1004819873 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017029 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1411482 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0017131&numberofmonths=24&showchangehistorylog=1 | 19-0017131 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1701 | 162821701 | FUSE | 1103 | 20190202 | 1030 | 287195 | 550 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 36850 | 38.1918 | -120.365 | MTR1004818465 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017131 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1411569 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0017012&numberofmonths=24&showchangehistorylog=1 | 19-0017012 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | RECLOSER | 6028 | 20190202 | 802 | 286877 | 1854 | Distribution Circuit | Vegetation | Tree - fell into line | 947 | 411236 | 38.2369 | -120.3646 | L3589 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0017012 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1411466 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0017827&numberofmonths=24&showchangehistorylog=1 | 19-0017827 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1101 | 163751101 | FUSE | 869011 | 20190204 | 458 | 289473 | 900 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 18900 | 38.4073 | -120.7119 | 17410ROBINSONROAD | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0017827 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1412185 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0017737&numberofmonths=24&showchangehistorylog=1 | 19-0017737 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE | 1439 | 20190204 | 727 | 289520 | 442 | Distribution Circuit | Vegetation | Tree - fell into line | 237 | 16842 | 38.4905 | -120.7134 | MTR1010296394 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0017737 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1412140 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018191&numberofmonths=24&showchangehistorylog=1 | 19-0018191 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | RECLOSER | 13438 | 20190204 | 2207 | 291131 | 955 | Distribution Circuit | Vegetation | Tree - fell into line | 955 | 111619 | 38.4738 | -120.6265 | MTR1004863161 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018191 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1412433 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018203&numberofmonths=24&showchangehistorylog=1 | 19-0018203 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | RECLOSER | 3172 | 20190204 | 2348 | 291212 | 3968 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4362 | 5966430 | 38.4101 | -120.6517 | JEOL19551SPSOF958016PSSOFMTR10049373001SPWOFL167 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018203 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1412444 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019078&numberofmonths=24&showchangehistorylog=1 | 19-0019078 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE | L1971 | 20190204 | 2348 | 294150 | 3933 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 66861 | 38.4607 | -120.5192 | MTR1010056662 | Partly Cloudy-Fog-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0019078 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1413122 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019376&numberofmonths=24&showchangehistorylog=1 | 19-0019376 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | JUMPER | JWOMTR1005018251 | 20190204 | 2348 | 294845 | 4940 | Distribution Circuit | Vegetation | Tree - fell into line | 114 | 415230 | 38.4444 | -120.5162 | DORRISRYAN1914RO16555EVELYNWAY | Overcast-Fog-Snow-Below 32 F | Crossarm, Wood | Broken, wire on ground | 19-0019376 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1413308 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019560&numberofmonths=24&showchangehistorylog=1 | 19-0019560 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE | 1485 | 20190204 | 2207 | 295231 | 5302 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 79530 | 38.4866 | -120.6121 | WESTALLENRDALLENRDNOSHAKERIDGERDVOLCANO | Clear-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0019560 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1413453 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019749&numberofmonths=24&showchangehistorylog=1 | 19-0019749 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | JUMPER | OJ2WOFCGC224250028465 | 20190204 | 2348 | 295544 | 5519 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 5519 | 38.4388 | -120.5189 | CGC224250028465 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0019749 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1413540 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0017698&numberofmonths=24&showchangehistorylog=1 | 19-0017698 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | RECLOSER | 34416 | 20190204 | 508 | 289485 | 408 | Distribution Circuit | Vegetation | Tree - fell into line | 450 | 75420 | 38.3988 | -120.5256 | MCCARTNEYMARK20241389HIDDENVALLEYRDWESTPOINT | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | On Ground | 19-0017698 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1412111 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019771&numberofmonths=24&showchangehistorylog=1 | 19-0019771 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | FUSE | L5679 | 20190204 | 1651 | s1413559 | 6591 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 32955 | 38.4231 | -120.4911 | LDSIDE | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0019771 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1413559 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018236&numberofmonths=24&showchangehistorylog=1 | 19-0018236 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | CALAVERAS CEMENT-1101 | 162211101 | SWITCH | 1349 | 20190205 | 239 | 292459 | 3035 | Distribution Circuit | Vegetation | Tree - fell into line | 131 | 397585 | 38.2827 | -120.5281 | 91241MULTIPLEBROKENCROSSARMSANDCASESOFTROUBLEBET1349ANDL4191 | Overcast-Fog-Snow-Below 32 F | Crossarm, Wood | Broken, wire on ground | 19-0018236 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1412623 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018437&numberofmonths=24&showchangehistorylog=1 | 19-0018437 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE | L1635 | 20190205 | 754 | 291945 | 1920 | Distribution Circuit | Equipment Failure/Involved | Overhead | 33 | 29200 | 38.2398 | -120.5144 | MTR1004817419 | Clear-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0018437 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1412626 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018566&numberofmonths=24&showchangehistorylog=1 | 19-0018566 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | CALAVERAS CEMENT-1101 | 162211101 | FUSE | L477 | 20190205 | 1139 | 292553 | 2984 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 10720 | 38.2743 | -120.5056 | 6438OLDEMIGRANTTRAIL | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0018566 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1412691 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019333&numberofmonths=24&showchangehistorylog=1 | 19-0019333 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | CALAVERAS CEMENT-1101 | 162211101 | JUMPER | OJAT3620SWISSRANCHRD | 20190205 | 105 | 294675 | 5149 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 30894 | 38.2639 | -120.4823 | OJAT3620SWISS | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0019333 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1413268 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019447&numberofmonths=24&showchangehistorylog=1 | 19-0019447 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | JUMPER | 91241HIGHSIDEJPRS | 20190205 | 239 | 294962 | 3388 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 3388 | 38.2828 | -120.5514 | LOADSIDEOF91241 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0019447 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1413380 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018715&numberofmonths=24&showchangehistorylog=1 | 19-0018715 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | ELECTRA-1101 | 162161101 | OTHER | WIREDOWNONMAINLINEFEEDINGMTR10049782 | 20190205 | 1504 | 292931 | 845 | Distribution Circuit | Vegetation | Tree - fell into line | 624 | 107164 | 38.4012 | -120.6474 | DORRISRYAN191413453TABEAURD | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0018715 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1412781 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018332&numberofmonths=24&showchangehistorylog=1 | 19-0018332 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | FROGTOWN-1701 | 163451701 | FUSE | L2117 | 20190205 | 550 | 291667 | 625 | Distribution Circuit | Equipment Failure/Involved | Overhead | 101 | 37682 | 38.1369 | -120.4567 | MTR1004817946 | Overcast-Fog-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0018332 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1412544 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018737&numberofmonths=24&showchangehistorylog=1 | 19-0018737 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | FROGTOWN-1701 | 163451701 | JUMPER | WIREDOWN2SPLOADSIDEOFL563 | 20190205 | 1541 | 293545 | 1502 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 78423 | 38.1348 | -120.4208 | BENNETTTOM18512111SKUNKRANCHRD | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0018737 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1412803 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019268&numberofmonths=24&showchangehistorylog=1 | 19-0019268 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | FROGTOWN-1701 | 163451701 | OTHER | WIREDOWNLDSIDEOFL301 | 20190205 | 1149 | 294504 | 2828 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 8484 | 38.2275 | -120.4493 | LDSIDEATL301 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0019268 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1413225 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018683&numberofmonths=24&showchangehistorylog=1 | 19-0018683 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1101 | 163751101 | TRIP-SAVER | 1021 | 20190205 | 1518 | 292941 | 1587 | Distribution Circuit | Vegetation | Tree - fell into line | 107 | 25958 | 38.414 | -120.6755 | 1SPNOFMTR10047389322XBROKENTX | Overcast-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0018683 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1412763 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018333&numberofmonths=24&showchangehistorylog=1 | 19-0018333 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | RECLOSER | 83098 | 20190205 | 718 | 291856 | 2375 | Distribution Circuit | Vegetation | Tree - fell into line | 198 | 467194 | 38.4174 | -120.5969 | 1SOF95801 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018333 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1412546 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018353&numberofmonths=24&showchangehistorylog=1 | 19-0018353 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE | L1117 | 20190205 | 544 | 292108 | 2463 | Distribution Circuit | Vegetation | Tree - fell into line | 150 | 369450 | 38.4916 | -120.7129 | 1EOFL11173EOFL1117WIREDOWN | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0018353 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1412558 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018413&numberofmonths=24&showchangehistorylog=1 | 19-0018413 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE | 76055 | 20190205 | 733 | 292405 | 2155 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 2155 | 38.4254 | -120.5913 | LDSIDE76055 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | On Ground | 19-0018413 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1412614 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018429&numberofmonths=24&showchangehistorylog=1 | 19-0018429 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | OTHER | WIREDOWN4SSOUTHOF12765IRISHTOWNRD | 20190205 | 900 | 292454 | 490 | Distribution Circuit | Vegetation | Tree - fell into line | 535 | 27685 | 38.3906 | -120.6732 | 4SPANSSOF12765IRISHTOWNRD12691IRISHTOWNRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0018429 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1412622 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018608&numberofmonths=24&showchangehistorylog=1 | 19-0018608 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE | L2217 | 20190205 | 900 | 292843 | 2163 | Distribution Circuit | Environmental/External | Ice or snow | 32 | 69216 | 38.4901 | -120.5282 | SHAFFERA2234ALLOVER | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018608 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1412712 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018360&numberofmonths=24&showchangehistorylog=1 | 19-0018360 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE | L3685 | 20190205 | 900 | 292943 | 1843 | Distribution Circuit | Equipment Failure/Involved | Overhead | 68 | 125324 | 38.4075 | -120.6507 | 13920GOLDMINEROAD | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018360 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1412739 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019045&numberofmonths=24&showchangehistorylog=1 | 19-0019045 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE | 1699 | 20190205 | 1918 | 293668 | 2707 | Distribution Circuit | Vegetation | Tree - fell into line | 975 | 227161 | 38.4259 | -120.5909 | FORTRESSLODESTAR23191VANDEHEIRANCHRD | Partly Cloudy-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0019045 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1413100 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019346&numberofmonths=24&showchangehistorylog=1 | 19-0019346 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE | L3109 | 20190205 | 900 | 294714 | 3337 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 83425 | 38.4443 | -120.6258 | L1327 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0019346 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1413279 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019561&numberofmonths=24&showchangehistorylog=1 | 19-0019561 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE | L9769 | 20190205 | 900 | 295243 | 4773 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 38184 | 38.4888 | -120.6188 | KRUPENSDOUG559908852922000FIDDLETOWNRD | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0019561 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1413455 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020162&numberofmonths=24&showchangehistorylog=1 | 19-0020162 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | SALT SPRINGS-2101 | 163692101 | FUSE | 1589 | 20190205 | 1645 | 293028 | 10075 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 473525 | 38.5273 | -120.2307 | LDSIDE1589 | Partly Cloudy-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020162 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1413849 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018519&numberofmonths=24&showchangehistorylog=1 | 19-0018519 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | STANISLAUS-1701 | 162821701 | RECLOSER | 59119 | 20190205 | 1226 | 292648 | 1502 | Distribution Circuit | Vegetation | Tree - fell into line | 137 | 50889 | 38.1699 | -120.4066 | SSOFL33571POLEEOFL3357 | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 19-0018519 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1412669 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018209&numberofmonths=24&showchangehistorylog=1 | 19-0018209 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | RECLOSER | 4790 | 20190205 | 20 | 291260 | 5333 | Distribution Circuit | Vegetation | Tree - fell into line | 739 | 2006234 | 38.3868 | -120.5244 | 5SPEOF83887NOF84543JUSTSOF84543 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018209 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1412450 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018209&numberofmonths=24&showchangehistorylog=1 | 19-0018209 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | SWITCH | L3867 | 20190205 | 20 | 291610 | 5322 | Distribution Circuit | Vegetation | Tree - fell into line | 95 | 505590 | 38.3641 | -120.5611 | HWY261MILEFROMDEARDORFRDBETL5167ANDB2117 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018209 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1412489 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018256&numberofmonths=24&showchangehistorylog=1 | 19-0018256 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | TRIP-SAVER | 1303 | 20190205 | 8 | 291225 | 3977 | Distribution Circuit | Vegetation | Tree - fell into line | 111 | 441447 | 38.4044 | -120.5058 | BUMMERVILLEWINTON | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018256 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1412495 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018397&numberofmonths=24&showchangehistorylog=1 | 19-0018397 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | FUSE | L609 | 20190205 | 20 | 292308 | 2875 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 48875 | 38.2989 | -120.5039 | 2POLESSOURCESIDEOFMTR1004736932 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018397 | OH | Sus | 0 | yes | 2019 | FEB | Yes | None | 1412600 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018435&numberofmonths=24&showchangehistorylog=1 | 19-0018435 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | TRIP-SAVER | L3733 | 20190205 | 44 | 291750 | 2275 | Distribution Circuit | Vegetation | Tree - fell into line | 97 | 220675 | 38.3892 | -120.5256 | BEYONDL37331535 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018435 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1412625 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018624&numberofmonths=24&showchangehistorylog=1 | 19-0018624 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | JUMPER | OJCORNEROFWINTONRDSKULLFLATRD | 20190205 | 44 | 292901 | 3944 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 15776 | 38.4039 | -120.5201 | LDSIDEWINTONRDSKULLFLATRD | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0018624 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1412723 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018685&numberofmonths=24&showchangehistorylog=1 | 19-0018685 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | JUMPER | OJEOFMTR1004935533 | 20190205 | 44 | 293004 | 2275 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2275 | 38.3888 | -120.512 | EOFMTR1004935533 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018685 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1412764 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018725&numberofmonths=24&showchangehistorylog=1 | 19-0018725 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | WEST POINT-1101 | 163201101 | FUSE | L1481 | 20190205 | 20 | 293110 | 3518 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 56288 | 38.3881 | -120.5429 | GOSSETTDANIELADAM599stanley | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0018725 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1412789 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018749&numberofmonths=24&showchangehistorylog=1 | 19-0018749 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | RECLOSER | 36676 | 20190205 | 20 | 293663 | 4020 | Distribution Circuit | Vegetation | Tree - fell into line | 175 | 703500 | 38.3724 | -120.5066 | MANYLOCLDSIDEOFLR | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018749 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1412815 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018760&numberofmonths=24&showchangehistorylog=1 | 19-0018760 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | FUSE | 99353 | 20190205 | 20 | 293696 | 4020 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 24120 | 38.3756 | -120.5004 | BEYOND99353 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on object | 19-0018760 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1412827 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019217&numberofmonths=24&showchangehistorylog=1 | 19-0019217 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | FUSE | 86823 | 20190205 | 44 | 294411 | 3944 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 59160 | 38.4035 | -120.5268 | ONSKULLFLATRD | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0019217 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1413195 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019344&numberofmonths=24&showchangehistorylog=1 | 19-0019344 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | FUSE | L871 | 20190205 | 900 | 294555 | 2088 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 29232 | 38.4108 | -120.5571 | LDSIDE | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | On Ground | 19-0019344 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1413277 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020300&numberofmonths=24&showchangehistorylog=1 | 19-0020300 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | FUSE | L5679 | 20190209 | 927 | 296794 | 4848 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 24240 | 38.4231 | -120.4911 | LDSIDE | Overcast-Fog-32-90 F | Conductor, Overhead | On Ground | 19-0020300 | OH | Sus | 0 | yes | 2019 | FEB | Yes | None | 1413999 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020382&numberofmonths=24&showchangehistorylog=1 | 19-0020382 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | WEST POINT-1101 | 163201101 | FUSE | 1417 | 20190209 | 1022 | 296844 | 1819 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 10911 | 38.3245 | -120.507 | 5SPANSLDSIDEOF1417 | Overcast-Fog-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0020382 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1414055 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020552&numberofmonths=24&showchangehistorylog=1 | 19-0020552 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | RECLOSER | 47968 | 20190210 | 502 | 298003 | 2398 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1157 | 229279 | 38.2323 | -120.5512 | 1NOF1727BROKENINSULATOR5SPANSLOADSIDEOFL875WIREDOWN | Overcast-Fog-32-90 F | Insulator | Broken, wire on ground | 19-0020552 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1414230 | INS | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020604&numberofmonths=24&showchangehistorylog=1 | 19-0020604 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | RECLOSER | 80930 | 20190210 | 622 | 298092 | 708 | Distribution Circuit | Vegetation | Tree - fell into line | 806 | 505850 | 38.1945 | -120.5851 | 1EOFL5227 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020604 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Three Phase Fault | 1414294 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020563&numberofmonths=24&showchangehistorylog=1 | 19-0020563 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | ELECTRA-1101 | 162161101 | RECLOSER | 61816 | 20190210 | 551 | 298046 | 625 | Distribution Circuit | Vegetation | Tree - fell into line | 360 | 191610 | 38.3634 | -120.6486 | 1PEOFCGC223846725959 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020563 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1414242 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020696&numberofmonths=24&showchangehistorylog=1 | 19-0020696 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | ELECTRA-1102 | 162161102 | RECLOSER | 2646 | 20190210 | 742 | 298370 | 629 | Distribution Circuit | Vegetation | Tree - fell into line | 309 | 147456 | 38.2992 | -120.6982 | MCCARTNEYMARK202477204 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020696 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1414400 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020719&numberofmonths=24&showchangehistorylog=1 | 19-0020719 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | FROGTOWN-1702 | 163451702 | FUSE | L1147 | 20190210 | 829 | 298386 | 578 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 3468 | 38.1053 | -120.4659 | 8LOADSIDEOFFUCO | Overcast-Snow-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0020719 | OH | Sus | 0 | yes | 2019 | FEB | Yes | None | 1414423 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020636&numberofmonths=24&showchangehistorylog=1 | 19-0020636 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | MARTELL-1101 | 163011101 | OTHER | WIREDOWN1NOFL1669 | 20190210 | 629 | 298159 | 775 | Distribution Circuit | Equipment Failure/Involved | Overhead | 84 | 27748 | 38.447 | -120.6839 | 1NOFL1699 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020636 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1414331 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020764&numberofmonths=24&showchangehistorylog=1 | 19-0020764 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | OLETA-1102 | 163541102 | FUSE | L2325 | 20190210 | 556 | 298050 | 870 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 46980 | 38.5193 | -120.7332 | IRO17850TYLER | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020764 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1414465 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020740&numberofmonths=24&showchangehistorylog=1 | 19-0020740 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1101 | 163751101 | OTHER | WIREDOWNNOF90281 | 20190210 | 434 | 298489 | 893 | Distribution Circuit | Vegetation | Tree - fell into line | 330 | 161234 | 38.3946 | -120.6784 | MCCARTNEYMARK2024TOYONRDANDHWY88 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020740 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1414442 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020591&numberofmonths=24&showchangehistorylog=1 | 19-0020591 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | RECLOSER | 36674 | 20190210 | 751 | 298123 | 167 | Distribution Circuit | 3rd Party | Vehicle | 100 | 16700 | 38.4875 | -120.5197 | BEYONDL33551711 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on object | 19-0020591 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1414280 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020633&numberofmonths=24&showchangehistorylog=1 | 19-0020633 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | JUMPER | OJATCRNOFSHAKERIDGERDANDWANDERINGHIL | 20190210 | 534 | 298529 | 768 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 5376 | 38.5082 | -120.5089 | OJATCRNOFSHAKERIDGERDANDWANDERINGHILLSRD | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020633 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1414327 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020689&numberofmonths=24&showchangehistorylog=1 | 19-0020689 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | OTHER | WIREDOWN5PSOF1715 | 20190210 | 535 | 298021 | 660 | Distribution Circuit | Equipment Failure/Involved | Overhead | 67 | 42108 | 38.4913 | -120.5109 | 5PSOF1715 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020689 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1414393 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021682&numberofmonths=24&showchangehistorylog=1 | 19-0021682 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | RECLOSER | 80930 | 20190212 | 2158 | 301268 | 1006 | Distribution Circuit | Equipment Failure/Involved | Overhead | 320 | 296876 | 38.1945 | -120.5851 | 2SPANSSWOF1363 | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 19-0021682 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1415129 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021688&numberofmonths=24&showchangehistorylog=1 | 19-0021688 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE | L3469 | 20190212 | 2158 | 301646 | 899 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 899 | 38.2 | -120.5828 | 5665LUCKYJIMMINERD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021688 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1415135 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021994&numberofmonths=24&showchangehistorylog=1 | 19-0021994 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE | 1601 | 20190212 | 2158 | 303503 | 1213 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 4852 | 38.2662 | -120.5857 | 2SPFROMEOL | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021994 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1415409 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022521&numberofmonths=24&showchangehistorylog=1 | 19-0022521 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | JUMPER | OJ3PSSMTR1010028731 | 20190212 | 2158 | 305441 | 5313 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 5313 | 38.2729 | -120.5798 | MTR1010028731 | Overcast-32-90 F | Conductor, Overhead | On Ground | 19-0022521 | OH | Sus | 0 | yes | 2019 | FEB | Yes | None | 1415760 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021705&numberofmonths=24&showchangehistorylog=1 | 19-0021705 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | ELECTRA-1102 | 162161102 | RECLOSER | 2646 | 20190212 | 2147 | 301202 | 2600 | Distribution Circuit | Equipment Failure/Involved | Overhead | 309 | 283608 | 38.2992 | -120.6982 | L57971SPEOFL5797 | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 19-0021705 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1415153 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021636&numberofmonths=24&showchangehistorylog=1 | 19-0021636 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | RECLOSER | 13438 | 20190212 | 2201 | 301211 | 665 | Distribution Circuit | Vegetation | Tree - branch fell on line | 970 | 397339 | 38.4738 | -120.6265 | 26229SHAKERIDGERD | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021636 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1415082 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021737&numberofmonths=24&showchangehistorylog=1 | 19-0021737 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | OTHER | WIREDOWN1NOFLUEDERSCTONBERTONE | 20190212 | 2206 | 301439 | 896 | Distribution Circuit | Vegetation | Tree - fell into line | 312 | 38519 | 38.5023 | -120.7042 | 1NOFLUEDERSCTONBERTONE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021737 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1415200 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022237&numberofmonths=24&showchangehistorylog=1 | 19-0022237 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | JUMPER | OJ1SPNOFMTR1008768919 | 20190212 | 2309 | 304538 | 1129 | Distribution Circuit | Vegetation | Tree - fell into line | 68 | 10810 | 38.441 | -120.5525 | EOFMTR1008768919 | Overcast-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0022237 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1415565 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021926&numberofmonths=24&showchangehistorylog=1 | 19-0021926 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | STANISLAUS-1701 | 162821701 | FUSE | 2631 | 20190212 | 2344 | 301573 | 1061 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 11671 | 38.1687 | -120.4111 | 3657BRICESTARD | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021926 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1415359 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021682&numberofmonths=24&showchangehistorylog=1 | 19-0021682 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | SWITCH | 1349 | 20190212 | 2158 | 305355 | 2399 | Distribution Circuit | Vegetation | Tree - fell into line | 141 | 338259 | 38.2827 | -120.5281 | 1PWOF9604596045 | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 19-0021682 | OH | Sus | 0 | yes | 2019 | FEB | Yes | None | 1415738 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023879&numberofmonths=24&showchangehistorylog=1 | 19-0023879 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | 5889 | 20190212 | 2208 | 301311 | 3753 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 86319 | 38.3549 | -120.5322 | MTR1004975762 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023879 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1417012 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021927&numberofmonths=24&showchangehistorylog=1 | 19-0021927 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | STANISLAUS-1701 | 162821701 | FUSE | 43569 | 20190213 | 537 | 302980 | 240 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 1395 | 38.1693 | -120.4117 | 3657BRICESTARD | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021927 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1415360 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021834&numberofmonths=24&showchangehistorylog=1 | 19-0021834 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | TRIP-SAVER | L3733 | 20190213 | 419 | 302626 | 863 | Distribution Circuit | Vegetation | Tree - fell into line | 98 | 84574 | 38.3892 | -120.5256 | 212BARNEYWAY | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0021834 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1415284 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022721&numberofmonths=24&showchangehistorylog=1 | 19-0022721 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | RECLOSER | 4786 | 20190214 | 45 | 306057 | 1032 | Distribution Circuit | Vegetation | Tree - fell into line | 499 | 207326 | 38.232 | -120.5345 | 7265SRAILROADFLATRD | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 19-0022721 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Three Phase Fault | 1415956 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022883&numberofmonths=24&showchangehistorylog=1 | 19-0022883 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | RECLOSER | 47968 | 20190214 | 725 | 307292 | 1878 | Distribution Circuit | Vegetation | Tree - fell into line | 149 | 42123 | 38.2323 | -120.5512 | GOSSETTDANIELADAMl1631 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022883 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416120 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022953&numberofmonths=24&showchangehistorylog=1 | 19-0022953 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | RECLOSER | 36880 | 20190214 | 834 | 307824 | 505 | Distribution Circuit | Vegetation | Tree - fell into line | 279 | 89151 | 38.2019 | -120.6895 | BENNETTTOM1851ACROSSSTFROM482GOLDSTRIKERD | Overcast-Fog-Heavy Rain-Lightning-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022953 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Three Phase Fault | 1416181 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022883&numberofmonths=24&showchangehistorylog=1 | 19-0022883 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | JUMPER | OJSSSOFL5249 | 20190214 | 703 | 310391 | 1947 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 9735 | 38.2747 | -120.5914 | LOADSIDEOFL5249 | Overcast-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0022883 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1416711 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023585&numberofmonths=24&showchangehistorylog=1 | 19-0023585 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE | 2123 | 20190214 | 933 | 310174 | 1773 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 21276 | 38.2329 | -120.5324 | 1NOFMTR1004214175MTR1NWOFMTR1009761810MTR4NWOFMTR1009761810MTR1SOFMTR5000158740 | Overcast-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0023585 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1416733 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022868&numberofmonths=24&showchangehistorylog=1 | 19-0022868 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | ELECTRA-1101 | 162161101 | FUSE | 8787 | 20190214 | 557 | 307096 | 276 | Distribution Circuit | Vegetation | Tree - fell into line | 138 | 20703 | 38.3653 | -120.7147 | 9SPLOADSIDEORSEOF8787 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022868 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1416107 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023377&numberofmonths=24&showchangehistorylog=1 | 19-0023377 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | ELECTRA-1102 | 162161102 | FUSE | 185043 | 20190214 | 1430 | 309676 | 1630 | Distribution Circuit | Environmental/External | Water | 1 | 1630 | 38.2439 | -120.688 | 5EOF185043 | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0023377 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1416531 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023309&numberofmonths=24&showchangehistorylog=1 | 19-0023309 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE | 1699 | 20190214 | 818 | 307704 | 1611 | Distribution Circuit | Vegetation | Tree - bark fell into line | 123 | 81827 | 38.4259 | -120.5909 | MTR10049806262SPANSDOWNGOINGTOTHENORTHWEST | Overcast-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023309 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1416491 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022935&numberofmonths=24&showchangehistorylog=1 | 19-0022935 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | RECLOSER | 4790 | 20190214 | 825 | 307719 | 554 | Distribution Circuit | Vegetation | Tree - fell into line | 1065 | 267879 | 38.3868 | -120.5244 | JSOL5183FUCO2111SEE190023496 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022935 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416165 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022998&numberofmonths=24&showchangehistorylog=1 | 19-0022998 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | FUSE | L5217 | 20190214 | 27 | 308001 | 1080 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2160 | 38.2786 | -120.5069 | LDSIDEOFL5217 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022998 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1416220 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023158&numberofmonths=24&showchangehistorylog=1 | 19-0023158 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | WEST POINT-1101 | 163201101 | TRIP-SAVER | 1341 | 20190214 | 1140 | 308760 | 1340 | Distribution Circuit | Vegetation | Tree - fell into line | 86 | 115240 | 38.3173 | -120.5209 | 3LDSIDEOF1341 | Overcast-Fog-Heavy Rain-Lightning-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023158 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1416349 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024085&numberofmonths=24&showchangehistorylog=1 | 19-0024085 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE | 9149 | 20190215 | 1304 | 312173 | 1392 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 7455 | 38.2112 | -120.6848 | MTR1004717234 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024085 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1417177 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024267&numberofmonths=24&showchangehistorylog=1 | 19-0024267 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE | L3433 | 20190215 | 1805 | 312802 | 2583 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 51432 | 38.2895 | -120.5996 | 1SPANNORTHOFMTR1008960834 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024267 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1417345 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023840&numberofmonths=24&showchangehistorylog=1 | 19-0023840 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L5041 | 20190215 | 442 | 311324 | 873 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 31767 | 38.2494 | -120.3386 | 2LDSIDEOFL5041 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023840 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1416980 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024011&numberofmonths=24&showchangehistorylog=1 | 19-0024011 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | JUMPER | OJS1PEOFMTR1004819624 | 20190215 | 1156 | 312361 | 421 | Distribution Circuit | Vegetation | Tree - fell into line | 670 | 22318 | 38.2363 | -120.3362 | brokenlineandbuckcrossarmsonmurphysdriveandtamarackandwiredownat2157calaveritasdr | Overcast-Fog-Snow-Below 32 F | Crossarm, Wood | Broken, wire on ground | 19-0024011 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1417197 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025153&numberofmonths=24&showchangehistorylog=1 | 19-0025153 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE | 1853 | 20190217 | 1216 | 315830 | 1732 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 90064 | 38.4942 | -120.5124 | 27110EINSPERATIONDR | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025153 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1418232 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025203&numberofmonths=24&showchangehistorylog=1 | 19-0025203 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | RECLOSER | 13438 | 20190217 | 1455 | 316342 | 1724 | Distribution Circuit | Vegetation | Tree - fell into line | 946 | 337775 | 38.4738 | -120.6265 | EOFL4035BYL373 | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025203 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1418282 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025518&numberofmonths=24&showchangehistorylog=1 | 19-0025518 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | JUMPER | TREETHROUGHLINELASTSPANBEYONDL5981 | 20190217 | 2132 | 317122 | 875 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 5894 | 38.2673 | -120.3209 | DEVALLECLAY1704136UPPERMORANRD | Partly Cloudy-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025518 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1418575 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025037&numberofmonths=24&showchangehistorylog=1 | 19-0025037 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | OTHER | WIREDOWN27555ASHLANDDR | 20190217 | 638 | 315356 | 2010 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 21210 | 38.5023 | -120.5152 | 27555ASHLAND | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025037 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1418114 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025721&numberofmonths=24&showchangehistorylog=1 | 19-0025721 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | FUSE | L2189 | 20190217 | 1612 | 316477 | 2825 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 42375 | 38.4839 | -120.5224 | 2SPFROMEOL | Overcast-Snow-32-90 F | Pole-Wood | Broken, wire on ground | 19-0025721 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1418767 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028537&numberofmonths=24&showchangehistorylog=1 | 19-0028537 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | RECLOSER | 1888 | 20190226 | 1955 | 325192 | 608 | Distribution Circuit | Vegetation | Tree - fell into line | 1464 | 166100 | 38.2367 | -120.3628 | MTR10046566807 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028537 | OH | Sus | 31426840 | yes | 2019 | FEB | Yes | Line to Ground | 1420445 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0110003&numberofmonths=24&showchangehistorylog=1 | 19-0110003 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CORRAL-1102 | 162991102 | JUMPER | WIREDOWNATTRANSPOLE10198 | 20191010 | 419 | 652929 | 614 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 3070 | 38.1297 | -120.9038 | TRANSPOLE10198 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0110003 | OH | Sus | 43986879 | yes | 2019 | OCT | Yes | Open Circuit | 1478917 | CSO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0115158&numberofmonths=24&showchangehistorylog=1 | 19-0115158 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CLAY-1103 | 163341103 | OCB | 11032 | 20191023 | 1221 | 677569 | 277 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1506 | 18960 | 38.3422 | -120.935 | MTR1005551197 | Clear-32-90 F | Pole-Wood | Broken, wire on object | 19-0115158 | OH | Sus | 0 | yes | 2019 | OCT | Yes | Force Out | 1482089 | PW | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0128739&numberofmonths=24&showchangehistorylog=1 | 19-0128739 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CORRAL-1102 | 162991102 | OTHER | WIREDOWN5479PLEASANTOAKRD | 20191126 | 833 | 715107 | 343 | Distribution Circuit | Equipment Failure/Involved | Overhead | 123 | 41683 | 38.1386 | -120.8902 | COLLINSEAN20285479pleasantoaksdr | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0128739 | OH | Sus | 44107399 | yes | 2019 | NOV | Yes | Line to Ground | 1494074 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0129963&numberofmonths=24&showchangehistorylog=1 | 19-0129963 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE | L3679 | 20191127 | 657 | 720348 | 173 | Distribution Circuit | Vegetation | Tree - fell into line | 153 | 25845 | 38.4444 | -120.5319 | SINGLEPHASEHARDTAPSEOFL3539 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0129963 | OH | Sus | 0 | yes | 2019 | NOV | Yes | Line to Line | 1494922 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0129963&numberofmonths=24&showchangehistorylog=1 | 19-0129963 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | JUMPER | OJSEOFL3539 | 20191127 | 712 | 720941 | 708 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 708 | 38.4449 | -120.5201 | SINGLEPHASEHARDTAPSEOFL3539 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0129963 | OH | Sus | 0 | yes | 2019 | NOV | Yes | Line to Line | 1495019 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0130339&numberofmonths=24&showchangehistorylog=1 | 19-0130339 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE | 1075 | 20191127 | 414 | 720133 | 931 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 51205 | 38.4832 | -120.6106 | DORRISRYAN1914RO22314ALLANRD | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0130339 | OH | Sus | 0 | yes | 2019 | NOV | Yes | Line to Ground | 1495160 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0130126&numberofmonths=24&showchangehistorylog=1 | 19-0130126 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | STANISLAUS-1702 | 162821702 | FUSE | 1117 | 20191127 | 650 | 720327 | 570 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 12540 | 38.1708 | -120.3789 | 5712DARBYRUSSELLRD | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0130126 | OH | Sus | 0 | yes | 2019 | NOV | Yes | Force Out | 1495020 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0010610&numberofmonths=24&showchangehistorylog=1 | 20-0010610 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | RECLOSER | 13438 | 20200117 | 1048 | 764762 | 375 | Distribution Circuit | Vegetation | Tree - fell into line | 539 | 89920 | 38.4738 | -120.6265 | MITCHELLJEREMY23394shakeridgerd | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0010610 | OH | Sus | 0 | yes | 2020 | JAN | Yes | Line to Ground | 1507317 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0010393&numberofmonths=24&showchangehistorylog=1 | 20-0010393 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | FUSE | L2245 | 20200117 | 24 | 763772 | 448 | Distribution Circuit | Vegetation | Tree - fell into line | 676 | 147619 | 38.4986 | -120.5293 | 1E1NOFL224520061PINEWESTDR | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0010393 | OH | Sus | 0 | yes | 2020 | JAN | Yes | Line to Ground | 1507114 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0010476&numberofmonths=24&showchangehistorylog=1 | 20-0010476 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | FUSE | L2217 | 20200117 | 709 | 763865 | 302 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 9966 | 38.4901 | -120.5282 | MTR1005017239 | Partly Cloudy-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 20-0010476 | OH | Sus | 0 | yes | 2020 | JAN | Yes | Line to Ground | 1507181 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0032171&numberofmonths=24&showchangehistorylog=1 | 20-0032171 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | SALT SPRINGS-2102 | 163692102 | RECLOSER | 8442 | 20200315 | 252 | 851712 | 896 | Distribution Circuit | Vegetation | Tree - fell into line | 2007 | 70311 | 38.4156 | -120.1341 | SMITHTHOMASSAP101278059 | Overcast-Snow-Below 32 F | Crossarm, Wood | Broken, wire on ground | 20-0032171 | OH | Sus | 0 | yes | 2020 | MAR | Yes | Three Phase Fault | 1521504 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0032820&numberofmonths=24&showchangehistorylog=1 | 20-0032820 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | SWITCH | L4045 | 20200316 | 1254 | 855570 | 342 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 19836 | 38.2425 | -120.5155 | CGC319965063455 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0032820 | OH | Sus | 0 | yes | 2020 | MAR | Yes | Force Out | 1522122 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0009579&numberofmonths=24&showchangehistorylog=1 | 21-0009579 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | SALT SPRINGS-2102 | 163692102 | RECLOSER | 8442 | 20210118 | 618 | 1212119 | 703 | Distribution Circuit | Vegetation | Tree - fell into line | 2008 | 275749 | 38.4157 | -120.1342 | 1LDSIDEOF4796 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 21-0009579 | OH | Sus | 0 | No | 2021 | JAN | Yes | Three Phase Fault | 1593621 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0010266&numberofmonths=24&showchangehistorylog=1 | 21-0010266 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L485 | 20210119 | 317 | 1214377 | 774 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 21548 | 38.2974 | -120.2741 | INMANJESS20962972793188ELCAMINOBOOTSTRAP | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0010266 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Line | 1594247 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0010394&numberofmonths=24&showchangehistorylog=1 | 21-0010394 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L5009 | 20210119 | 813 | 1215295 | 270 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 5670 | 38.2641 | -120.3217 | NOFMETER1004654227 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 21-0010394 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1594360 | CSO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0010504&numberofmonths=24&showchangehistorylog=1 | 21-0010504 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L2049 | 20210119 | 717 | 1216152 | 629 | Distribution Circuit | Vegetation | Tree - fell into line | 118 | 74222 | 38.2996 | -120.2715 | 2SOF | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0010504 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Line | 1594451 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0010491&numberofmonths=24&showchangehistorylog=1 | 21-0010491 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | WEST POINT-1102 | 163201102 | RECLOSER | 72036 | 20210119 | 917 | 1216087 | 432 | Distribution Circuit | Vegetation | Tree - fell into line | 2799 | 890430 | 38.413 | -120.55 | WIREDOWNBOTHSIDESOFSW679TREEFELLTHRULINESEOF679 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0010491 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Line | 1594436 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0011070&numberofmonths=24&showchangehistorylog=1 | 21-0011070 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | L2011 | 20210119 | 1717 | 1217783 | 138 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 2346 | 38.3544 | -120.5197 | 3PWOF319963167530 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0011070 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1594855 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0013680&numberofmonths=24&showchangehistorylog=1 | 21-0013680 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | CALAVERAS CEMENT-1101 | 162211101 | OTHER | WIREDOWN1WOFAND1SOF666931 | 20210125 | 526 | 1224366 | 898 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 4490 | 38.3327 | -120.5221 | 1WOFAND1SOF666931 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0013680 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1596767 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0013820&numberofmonths=24&showchangehistorylog=1 | 21-0013820 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | ELECTRA-1101 | 162161101 | FUSE | L3857 | 20210125 | 325 | 1223243 | 654 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 8525 | 38.3497 | -120.6591 | 1STSPANWOFL3857 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0013820 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1596741 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0013586&numberofmonths=24&showchangehistorylog=1 | 21-0013586 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1101 | 163751101 | OCB | 11012 | 20210125 | 349 | 1223291 | 883 | Distribution Circuit | Vegetation | Tree - fell into line | 1376 | 247531 | 38.4127 | -120.6608 | RobertsRon2099866628sap101257171 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 21-0013586 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Line | 1596575 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0013821&numberofmonths=24&showchangehistorylog=1 | 21-0013821 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE | L3101 | 20210125 | 437 | 1223338 | 616 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 1848 | 38.4466 | -120.6278 | MTR1004974082 | Clear-32-90F | Crossarm, Wood | Broken, wire on ground | 21-0013821 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1596742 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0014249&numberofmonths=24&showchangehistorylog=1 | 21-0014249 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | JUMPER | WIREDOWN1PSWOFCGC223836927246 | 20210126 | 58 | 1225470 | 526 | Distribution Circuit | Vegetation | Tree - fell into line | 280 | 52292 | 38.4056 | -120.6623 | RobertsRon209986662813670spagnolimineroad | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0014249 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1597045 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0015686&numberofmonths=24&showchangehistorylog=1 | 21-0015686 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | L2011 | 20210127 | 201 | 1232322 | 514 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 8738 | 38.3544 | -120.5197 | LINEBUCKTWDCGC319963167530 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0015686 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Line | 1598236 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0129113&numberofmonths=24&showchangehistorylog=1 | 21-0129113 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | MARTELL-1103 | 163011103 | FUSE | L1247 | 20211011 | 1354 | 1493753 | 181 | Distribution Circuit | Vegetation | Tree - branch fell on line | 27 | 4887 | 38.3449 | -120.8667 | 2PSOURCESIDEOFL1247 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0129113 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Line | 1673120 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0129505&numberofmonths=24&showchangehistorylog=1 | 21-0129505 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | SALT SPRINGS-2102 | 163692102 | RECLOSER | 8442 | 20211011 | 2320 | 1495372 | 944 | Distribution Circuit | Vegetation | Tree - bark fell into line | 4470 | 2637835 | 38.4157 | -120.1342 | 28PSWOF320955069160 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 21-0129505 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Line | 1673392 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0132234&numberofmonths=24&showchangehistorylog=1 | 21-0132234 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CORRAL-1101 | 162991101 | RECLOSER | 12612 | 20211017 | 2302 | 1500403 | 897 | Distribution Circuit | 3rd Party | Vehicle | 322 | 69356 | 38.1783 | -120.927 | 2PNOFD4719 | Strong Winds-Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0132234 | OH | Sus | 35296048 | No | 2021 | OCT | Yes | Three Phase Fault | 1675044 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0136441&numberofmonths=24&showchangehistorylog=1 | 21-0136441 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1101 | 163751101 | FUSE | 1761 | 20211024 | 1548 | 1513915 | 142 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 2840 | 38.4152 | -120.6884 | CGC223771027417 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0136441 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Ground | 1677923 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0137138&numberofmonths=24&showchangehistorylog=1 | 21-0137138 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE | L5247 | 20211025 | 1038 | 1518293 | 179 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 537 | 38.2445 | -120.615 | 7456DOSTERRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0137138 | OH | Sus | 0 | No | 2021 | OCT | Yes | Open Circuit | 1678575 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0136802&numberofmonths=24&showchangehistorylog=1 | 21-0136802 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | ELECTRA-1101 | 162161101 | RECLOSER | 61816 | 20211025 | 137 | 1516238 | 751 | Distribution Circuit | Vegetation | Tree - fell into line | 375 | 42917 | 38.3633 | -120.6486 | 3EOFCGC223695525615 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 21-0136802 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Line | 1678302 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0136890&numberofmonths=24&showchangehistorylog=1 | 21-0136890 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | MARTELL-1101 | 163011101 | RECLOSER | 6074 | 20211025 | 540 | 1517030 | 570 | Distribution Circuit | Vegetation | Tree - branch fell on line | 35 | 5070 | 38.3928 | -120.7926 | NORTHTAP2SPANSSWOFL3547 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0136890 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Ground | 1678389 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0137229&numberofmonths=24&showchangehistorylog=1 | 21-0137229 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | RECLOSER | 97924 | 20211025 | 1127 | 1518511 | 407 | Distribution Circuit | Vegetation | Tree - branch fell on line | 541 | 115868 | 38.3231 | -120.2534 | 1SPANSOURCESIDEOFCGC321049170023 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0137229 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Line | 1678640 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0157044&numberofmonths=24&showchangehistorylog=1 | 21-0157044 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | MARTELL-1101 | 163011101 | OCB | 11012 | 20211213 | 949 | 1566246 | 369 | Distribution Circuit | Vegetation | Tree - bark fell into line | 2275 | 82471 | 38.3688 | -120.7965 | L3777 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0157044 | OH | Sus | 0 | No | 2021 | DEC | Yes | Multi-Fault | 1693949 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0157540&numberofmonths=24&showchangehistorylog=1 | 21-0157540 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1101 | 163751101 | RECLOSER | 3170 | 20211213 | 1846 | 1568471 | 227 | Distribution Circuit | Vegetation | Tree - fell into line | 679 | 54313 | 38.4151 | -120.6853 | JUSTSOUTHWESTOFL5897BETWEEN49859FUCOAND92011 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0157540 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1694434 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0158043&numberofmonths=24&showchangehistorylog=1 | 21-0158043 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1101 | 163751101 | OTHER | WIREDOWN16739TONYLN | 20211213 | 1218 | 1570263 | 1654 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 4039 | 38.4136 | -120.718 | CGC223675527485 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0158043 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1694962 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0157351&numberofmonths=24&showchangehistorylog=1 | 21-0157351 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | L5677 | 20211213 | 1221 | 1567081 | 504 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 6191 | 38.4261 | -120.4924 | CGC320070570405 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 21-0157351 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Line | 1694256 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0157947&numberofmonths=24&showchangehistorylog=1 | 21-0157947 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | FROGTOWN-1701 | 163451701 | FUSE | L483 | 20211214 | 800 | 1570100 | 244 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 488 | 38.2145 | -120.4468 | 1LDSIDE | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0157947 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Line | 1694874 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0157930&numberofmonths=24&showchangehistorylog=1 | 21-0157930 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE | L1161 | 20211214 | 426 | 1569581 | 784 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 7808 | 38.4166 | -120.6414 | CGC223911027648 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0157930 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Line | 1694854 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0160678&numberofmonths=24&showchangehistorylog=1 | 21-0160678 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | FUSE | 614959 | 20211226 | 133 | 1581988 | 587 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 30524 | 38.4942 | -120.5125 | CGC224232730436 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 21-0160678 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Line | 1698163 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0138620&numberofmonths=24&showchangehistorylog=1 | 22-0138620 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | RECLOSER | 4786 | 20221210 | 1711 | 1883787 | 289 | Distribution Circuit | Vegetation | Tree - fell into line | 166 | 29022 | 38.2321 | -120.5349 | 1SPANWOFL5207 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0138620 | OH | Sus | 0 | No | 2022 | DEC | Yes | Three Phase Fault | 1789449 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0138260&numberofmonths=24&showchangehistorylog=1 | 22-0138260 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | L5677 | 20221210 | 852 | 1881014 | 298 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 4517 | 38.4261 | -120.4924 | 3855TREELNWESTPOINT | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0138260 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Line | 1789096 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0142569&numberofmonths=24&showchangehistorylog=1 | 22-0142569 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | RECLOSER | 269286 | 20221231 | 1217 | 1903871 | 175 | Distribution Circuit | Vegetation | Tree - fell into line | 2692 | 182904 | 38.4019 | -120.6362 | LASKOWSKIRICK424522671alaireln | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0142569 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1794367 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0142631&numberofmonths=24&showchangehistorylog=1 | 22-0142631 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | OTHER | 1PHWIREDOWNSOFL3293 | 20221231 | 1458 | 1904907 | 242 | Distribution Circuit | Vegetation | Tree - fell into line | 1779 | 155290 | 38.4579 | -120.5172 | LASKOWSKIRICK42451southofL3293onantelope | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0142631 | OH | Sus | 0 | No | 2022 | DEC | Yes | Open Circuit | 1794460 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0005724&numberofmonths=24&showchangehistorylog=1 | 23-0005724 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE | 91241 | 20230104 | 53 | 1912612 | 676 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 676 | 38.2831 | -120.5514 | 2SPANSSOF91241 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0005724 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Line | 1796132 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0007053&numberofmonths=24&showchangehistorylog=1 | 23-0007053 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | SWITCH | FIF | 20230105 | 755 | 1921332 | 436 | Distribution Circuit | Vegetation | Tree - fell into line | 134 | 58424 | 38.4532 | -120.5276 | MCCARTNEYMARK202427096SILVERDR | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0007053 | OH | Sus | 0 | No | 2023 | JAN | Yes | Multi-Fault | 1797416 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0012186&numberofmonths=24&showchangehistorylog=1 | 23-0012186 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | ELECTRA-1101 | 162161101 | FUSE | 1065 | 20230110 | 949 | 1944308 | 294 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 4410 | 38.3787 | -120.6973 | LOADSIDEOF1065 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0012186 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Line | 1801949 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0011885&numberofmonths=24&showchangehistorylog=1 | 23-0011885 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | OLETA-1102 | 163541102 | RECLOSER | 186326 | 20230110 | 414 | 1941794 | 232 | Distribution Circuit | Vegetation | Tree - fell into line | 876 | 203232 | 38.482 | -120.8432 | 3SPANSWOFCGC223374029925l1STAND2NDPOLESWOFCGC223374029925 | Overcast-Fog-Drizzle-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 23-0011885 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Line | 1801652 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0011905&numberofmonths=24&showchangehistorylog=1 | 23-0011905 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | OCB | 11022 | 20230110 | 434 | 1942529 | 265 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 15105 | 38.4208 | -120.549 | L4027 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 23-0011905 | OH | Sus | 0 | No | 2023 | JAN | Yes | Three Phase Fault | 1801675 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0011905&numberofmonths=24&showchangehistorylog=1 | 23-0011905 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | WEST POINT-1102 | 163201102 | RECLOSER | 4788 | 20230110 | 435 | 1943261 | 898 | Distribution Circuit | Vegetation | Tree - fell into line | 605 | 543290 | 38.3314 | -120.5186 | MCCARTNEYMARK20242PSOLR4788 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 23-0011905 | OH | Sus | 0 | No | 2023 | JAN | Yes | None | 1801763 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0011905&numberofmonths=24&showchangehistorylog=1 | 23-0011905 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | RECLOSER | 34416 | 20230110 | 435 | 1943300 | 887 | Distribution Circuit | Vegetation | Tree - fell into line | 424 | 376088 | 38.3988 | -120.5255 | HENNESSCORYMichael1030HiddenValley | Overcast-Fog-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 23-0011905 | OH | Sus | 0 | No | 2023 | JAN | Yes | None | 1801771 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0011905&numberofmonths=24&showchangehistorylog=1 | 23-0011905 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | WEST POINT-1102 | 163201102 | RECLOSER | 72036 | 20230110 | 435 | 1943407 | 268 | Distribution Circuit | Vegetation | Tree - fell into line | 118 | 31624 | 38.413 | -120.55 | L4027 | Overcast-Fog-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 23-0011905 | OH | Sus | 0 | No | 2023 | JAN | Yes | Force Out | 1801788 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0011905&numberofmonths=24&showchangehistorylog=1 | 23-0011905 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | RECLOSER | 93116 | 20230110 | 435 | 1943417 | 894 | Distribution Circuit | Vegetation | Tree - fell into line | 593 | 530142 | 38.3839 | -120.5267 | L4027 | Overcast-Fog-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 23-0011905 | OH | Sus | 0 | No | 2023 | JAN | Yes | None | 1801789 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0011905&numberofmonths=24&showchangehistorylog=1 | 23-0011905 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | SWITCH | L1047 | 20230110 | 435 | 1943958 | 881 | Distribution Circuit | Vegetation | Tree - fell into line | 410 | 361210 | 38.4135 | -120.5488 | MCCARTNEYMARK2024PINECRESTANDHWY88 | Overcast-Fog-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on ground | 23-0011905 | OH | Sus | 0 | No | 2023 | JAN | Yes | Multi-Fault | 1801851 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0011905&numberofmonths=24&showchangehistorylog=1 | 23-0011905 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | RECLOSER | 4790 | 20230110 | 435 | 1944174 | 890 | Distribution Circuit | Vegetation | Tree - fell into line | 506 | 450340 | 38.3869 | -120.5242 | MCCARTNEYMARK2024NOSOURCETOLR4790 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0011905 | OH | Sus | 0 | No | 2023 | JAN | Yes | Force Out | 1801900 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0017104&numberofmonths=24&showchangehistorylog=1 | 23-0017104 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | SALT SPRINGS-2102 | 163692102 | SWITCH | L531 | 20230116 | 917 | 1957583 | 628 | Distribution Circuit | Vegetation | Tree - fell into line | 471 | 295788 | 38.2961 | -120.2742 | 1SPLDSIDECGC320650365363 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0017104 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1805795 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0017341&numberofmonths=24&showchangehistorylog=1 | 23-0017341 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | SALT SPRINGS-2102 | 163692102 | RECLOSER | 3142 | 20230116 | 1736 | 1958650 | 129 | Distribution Circuit | Vegetation | Tree - fell into line | 316 | 40764 | 38.3016 | -120.277 | 2SPSSCGC320682265719 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0017341 | OH | Sus | 0 | No | 2023 | JAN | Yes | Force Out | 1806015 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0034248&numberofmonths=24&showchangehistorylog=1 | 23-0034248 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1101 | 163751101 | OCB | 11012 | 20230224 | 1520 | 2006053 | 189 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1408 | 49295 | 38.4127 | -120.6608 | 2SPANSNOF8787 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0034248 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Ground | 1817203 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0035011&numberofmonths=24&showchangehistorylog=1 | 23-0035011 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE | 53709 | 20230224 | 2202 | 2007457 | 646 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 646 | 38.4756 | -120.7051 | 1EOF53709 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0035011 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Line | 1817878 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0036669&numberofmonths=24&showchangehistorylog=1 | 23-0036669 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | RECLOSER | 45292 | 20230227 | 1707 | 2013218 | 34 | Distribution Circuit | Vegetation | Tree - fell into line | 308 | 10472 | 38.4535 | -120.5298 | CGC224126729426 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 23-0036669 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Ground | 1819233 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0036613&numberofmonths=24&showchangehistorylog=1 | 23-0036613 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | L609 | 20230227 | 1435 | 2012700 | 389 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 6613 | 38.299 | -120.5037 | 4SPANSNOFL609 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0036613 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Ground | 1819187 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0037906&numberofmonths=24&showchangehistorylog=1 | 23-0037906 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | ELECTRA-1101 | 162161101 | JUMPER | OJONHARDTAP1WOH69623 | 20230228 | 2128 | 2017511 | 1026 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2052 | 38.393 | -120.6403 | HARDTAP1WOF69263FUCO | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0037906 | OH | Sus | 0 | No | 2023 | FEB | Yes | Force Out | 1820241 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0037575&numberofmonths=24&showchangehistorylog=1 | 23-0037575 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | STANISLAUS-1701 | 162821701 | RECLOSER | 1812 | 20230228 | 1550 | 2016092 | 84 | Distribution Circuit | Vegetation | Tree - fell into line | 108 | 9072 | 38.1832 | -120.3754 | CGC320388561559 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 23-0037575 | OH | Sus | 0 | No | 2023 | FEB | Yes | Multi-Fault | 1819919 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0042304&numberofmonths=24&showchangehistorylog=1 | 23-0042304 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | VALLEY SPRINGS-1101 | 168891101 | FUSE | 2119 | 20230309 | 1552 | 2027953 | 269 | Distribution Circuit | Equipment Failure/Involved | Overhead | 498 | 46808 | 38.1853 | -120.8238 | 1SPLDSIDECGC319098561060 | Clear-32-90F | Conductor, Overhead | On Ground | 23-0042304 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1823171 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0044675&numberofmonths=24&showchangehistorylog=1 | 23-0044675 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | MARTELL-1101 | 163011101 | FUSE | L3801 | 20230314 | 918 | 2035466 | 298 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 25330 | 38.4354 | -120.7477 | 4SOFSIDEOFL3801 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0044675 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1824827 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0049990&numberofmonths=24&showchangehistorylog=1 | 23-0049990 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | ELECTRA-1102 | 162161102 | FUSE | L3841 | 20230321 | 1700 | 2058895 | 359 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 553 | 38.2488 | -120.717 | 3POLESNOFCGC319370063700 | Partly Cloudy-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0049990 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Line | 1828677 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0078110&numberofmonths=24&showchangehistorylog=1 | 13-0078110 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1702 | 163661702 | FUSE | 6677 | 20131121 | 1922 | 908563 | 386 | Distribution Circuit | Vegetation | Tree - fell into line | 81 | 25274 | 38.0588 | -120.2669 | 24217APPALOOSAWAY | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078110 | OH | Sus | 41991609 | yes | 2013 | NOV | Yes |  | 99251971 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0073206&numberofmonths=24&showchangehistorylog=1 | 14-0073206 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | FUSE | 23243 | 20141203 | 757 | 1121939 | 287 | Distribution Circuit | Vegetation | Tree - fell into line | 132 | 12054 | 37.9852 | -120.282 | McKinnon20745730394CORTEPRIMERO | Combination wind/rain/lightning-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073206 | OH | Sus | 31118857 | yes | 2014 | DEC | Yes | Line to Ground | 99196959 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075233&numberofmonths=24&showchangehistorylog=1 | 14-0075233 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | BEAR VALLEY-2105 | 252192105 | RECLOSER | 9560 | 20141211 | 924 | 1132229 | 643 | Distribution Circuit | Vegetation | Tree - fell into line | 652 | 195121 | 37.6977 | -120.1164 | Devine209355997434121n9560 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075233 | OH | Sus | 42295242 | yes | 2014 | DEC | Yes | Line to Ground | 99195039 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075858&numberofmonths=24&showchangehistorylog=1 | 14-0075858 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | COARSEGOLD-2102 | 254432102 | FUSE | 5536 | 20141211 | 1941 | 1135767 | 325 | Distribution Circuit | Equipment Failure/Involved | Other | 109 | 10387 | 37.3064 | -119.6137 |  | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075858 | OH | Sus | 0 | yes | 2014 | DEC | Yes | None | 99194596 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0075604&numberofmonths=24&showchangehistorylog=1 | 14-0075604 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | L2213 | 20141211 | 1204 | 1133731 | 532 | Distribution Circuit | Vegetation | Tree - branch fell on line | 41 | 21812 | 38.0199 | -120.2222 | MTR1004861511 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075604 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99194746 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079484&numberofmonths=24&showchangehistorylog=1 | 14-0079484 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2102 | 254432102 | OCB | OCB | 20141230 | 1707 | 1155014 | 2766 | Distribution Circuit | Vegetation | Tree - fell into line | 1271 | 764428 | 37.2272 | -119.6902 | 1SPEOF11816BETC84610222 | Combination wind/rain/lightning-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079484 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99189722 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079562&numberofmonths=24&showchangehistorylog=1 | 14-0079562 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | COARSEGOLD-2102 | 254432102 | FUSE | 24198 | 20141230 | 1621 | 1155989 | 891 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 12849 | 37.3368 | -119.6138 | MTR1008782320 | Combination wind/rain/lightning-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079562 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99190106 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079361&numberofmonths=24&showchangehistorylog=1 | 14-0079361 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1102 | 254421102 | OCB | OCB | 20141230 | 1740 | 1154727 | 583 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1116 | 323217 | 37.322 | -119.6347 | MTR10063803372SPSOF10100 | Combination wind/rain/lightning-32 - 90 F | Transformer | Broken, wire on ground | 14-0079361 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99190153 | TX | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079321&numberofmonths=24&showchangehistorylog=1 | 14-0079321 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1103 | 254421103 | RECLOSER | 77384 | 20141230 | 1646 | 1154124 | 859 | Distribution Circuit | Vegetation | Tree - fell into line | 460 | 267251 | 37.3391 | -119.5851 | Dahlem18475594938472RD432BASSLAKE | Combination wind/rain/lightning-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079321 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99190159 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079597&numberofmonths=24&showchangehistorylog=1 | 14-0079597 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1103 | 254421103 | FUSE | 10289 | 20141230 | 2024 | 1155444 | 1242 | Distribution Circuit | Vegetation | Tree - branch fell on line | 23 | 28566 | 37.3525 | -119.6032 | DANIELIPRESTON41695RD222OAKHURST | Combination wind/rain/lightning-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079597 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99190090 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079412&numberofmonths=24&showchangehistorylog=1 | 14-0079412 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SAN JOAQUIN #3 PH-1101 | 252531101 | RECLOSER | 10060 | 20141230 | 1811 | 1154678 | 1254 | Distribution Circuit | Vegetation | Tree - fell into line | 112 | 62419 | 37.2925 | -119.5318 | Lafata18484703284OAKHURST | Combination wind/rain/lightning-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079412 | OH | Sus | 31123825 | yes | 2014 | DEC | Yes | Line to Ground | 99190141 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0011639&numberofmonths=24&showchangehistorylog=1 | 15-0011639 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1103 | 254421103 | OTHER |  | 20150208 | 1425 | 1183027 | 1414 | Distribution Circuit | Vegetation | Tree - branch fell on line | 663 | 102749 | 37.347 | -119.5975 | Lafata184847032842SPANSWOFFUCO93279 | Lightning-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011639 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182836 | CO | OH | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0087145&numberofmonths=24&showchangehistorylog=1 | 15-0087145 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE | 6285 | 20151224 | 1603 | 1371220 | 405 | Distribution Circuit | Vegetation | Tree - fell into line | 220 | 24840 | 37.191 | -119.789 | 1SPANNOFMTR1005616473 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0087145 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Line | 1177221 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0087054&numberofmonths=24&showchangehistorylog=1 | 15-0087054 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1701 | 163781701 | FUSE | 20082 | 20151224 | 334 | 1370699 | 573 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 5730 | 37.8578 | -120.1928 | 13051BOITANORD | Overcast-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 15-0087054 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Line | 1177123 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0013219&numberofmonths=24&showchangehistorylog=1 | 16-0013219 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE | 10337 | 20160217 | 1510 | 1405530 | 384 | Distribution Circuit | Vegetation | Tree - fell into line | 68 | 7716 | 37.2654 | -119.6963 | MTR1005061353 | Strong Winds-Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 16-0013219 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Line to Ground | 1186319 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0013478&numberofmonths=24&showchangehistorylog=1 | 16-0013478 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | FUSE | L1109 | 20160217 | 2032 | 1407085 | 501 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 15777 | 37.9481 | -120.2363 | TXMTR1005713018 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013478 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Line to Ground | 1186564 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0013527&numberofmonths=24&showchangehistorylog=1 | 16-0013527 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | RECLOSER | 9210 | 20160217 | 2009 | 1406999 | 1529 | Distribution Circuit | Vegetation | Tree - fell into line | 157 | 143966 | 37.8183 | -120.0961 | 1006424549 | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 16-0013527 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Three Phase Fault | 1186613 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0013320&numberofmonths=24&showchangehistorylog=1 | 16-0013320 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | CURTIS-1704 | 163351704 | FUSE | 1691 | 20160217 | 1710 | 1405975 | 794 | Distribution Circuit | Vegetation | Tree - fell into line | 145 | 104216 | 38.0208 | -120.3582 | MTR1004738009 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 16-0013320 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Line to Ground | 1186404 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0013585&numberofmonths=24&showchangehistorylog=1 | 16-0013585 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1704 | 163351704 | FUSE | 20811 | 20160217 | 1941 | 1406828 | 880 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 8800 | 37.988 | -120.332 | 20255PHOENIXLAKERDMTR1004902612 | Overcast-Rain-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 16-0013585 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Line to Ground | 1186665 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0013458&numberofmonths=24&showchangehistorylog=1 | 16-0013458 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1705 | 163351705 | FUSE | L1773 | 20160217 | 1940 | 1406627 | 402 | Distribution Circuit | Vegetation | Tree - branch fell on line | 251 | 100902 | 37.9584 | -120.3215 | MTR1004903525 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013458 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Line to Line | 1186541 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0013041&numberofmonths=24&showchangehistorylog=1 | 16-0013041 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MARIPOSA-2101 | 254452101 | FUSE | 10215 | 20160217 | 952 | 1404747 | 372 | Distribution Circuit | Vegetation | Tree - branch fell on line | 123 | 6386 | 37.4639 | -119.7394 | 1PLDSIDEOFMTR1006387665 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013041 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Line to Ground | 1186202 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0013398&numberofmonths=24&showchangehistorylog=1 | 16-0013398 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1703 | 163761703 | FUSE | L347 | 20160217 | 1905 | 1406346 | 425 | Distribution Circuit | Vegetation | Tree - branch fell on line | 50 | 9160 | 38.0361 | -120.4261 | MTR1004899490 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013398 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Line to Ground | 1186481 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005473&numberofmonths=24&showchangehistorylog=1 | 17-0005473 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | FUSE | 23246 | 20170108 | 1311 | 1626709 | 409 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 3272 | 37.9831 | -120.28 | WOFMTR1004738111 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0005473 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245257 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005278&numberofmonths=24&showchangehistorylog=1 | 17-0005278 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2102 | 254452102 | OTHER | WIREDOWNSSOF4569 | 20170108 | 1202 | 1625979 | 950 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 14250 | 37.4793 | -119.8685 | SSOF45692LDSIDEMTR5000020046 | Overcast-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0005278 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Multi-Fault | 1245068 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005489&numberofmonths=24&showchangehistorylog=1 | 17-0005489 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1703 | 163761703 | FUSE | S1933 | 20170108 | 1428 | 1627326 | 302 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 3322 | 38.0109 | -120.4198 | MTR1004736625 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | On Ground | 17-0005489 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245272 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0005904&numberofmonths=24&showchangehistorylog=1 | 17-0005904 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | FUSE | 1715 | 20170109 | 523 | 1630215 | 301 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 13271 | 37.9194 | -120.3504 | MTR1004858499 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005904 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1245688 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007281&numberofmonths=24&showchangehistorylog=1 | 17-0007281 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE | 10569 | 20170110 | 2259 | 1638008 | 267 | Distribution Circuit | Vegetation | Tree - fell into line | 91 | 17955 | 37.1908 | -119.7639 | MTR1006378623 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007281 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1246861 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007385&numberofmonths=24&showchangehistorylog=1 | 17-0007385 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | RECLOSER | 9210 | 20170110 | 2200 | 1637832 | 3708 | Distribution Circuit | Vegetation | Tree - fell into line | 602 | 332739 | 37.8183 | -120.0961 | SIUDZINSKIMARK3polesbeyondsws1215wiredownfor5spans | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007385 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Three Phase Fault | 1246972 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006800&numberofmonths=24&showchangehistorylog=1 | 17-0006800 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | CURTIS-1704 | 163351704 | FUSE | L537 | 20170110 | 1533 | 1634069 | 668 | Distribution Circuit | Vegetation | Tree - fell into line | 95 | 63460 | 38.0345 | -120.3763 | LINEANDBUCKNOFMTR1004720079 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0006800 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Three Phase Fault | 1246387 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007153&numberofmonths=24&showchangehistorylog=1 | 17-0007153 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MARIPOSA-2101 | 254452101 | FUSE | 4642 | 20170110 | 2039 | 1636923 | 565 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 14690 | 37.5589 | -119.931 | Lafata184847032846562HWY1401POLEWOFMTR1006387865 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007153 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246737 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006975&numberofmonths=24&showchangehistorylog=1 | 17-0006975 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1702 | 163661702 | RECLOSER | 8060 | 20170110 | 1904 | 1635913 | 550 | Distribution Circuit | Vegetation | Tree - branch fell on line | 918 | 245988 | 38.068 | -120.1867 | BREAUXPARIS4062behindLongBarnCalTransyardatmeter1003872417 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0006975 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Multi-Fault | 1246558 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007396&numberofmonths=24&showchangehistorylog=1 | 17-0007396 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1701 | 163781701 | FUSE | 20183 | 20170110 | 1902 | 1635853 | 992 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 5952 | 37.8448 | -120.3526 | 3LDSIDEOF20183 | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007396 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1246984 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007267&numberofmonths=24&showchangehistorylog=1 | 17-0007267 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1704 | 163761704 | OCB | 17042 | 20170110 | 2337 | 1638092 | 219 | Distribution Circuit | Vegetation | Tree - fell into line | 677 | 112231 | 37.9799 | -120.4136 | 3SEOFS1341 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007267 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Three Phase Fault | 1246847 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0006933&numberofmonths=24&showchangehistorylog=1 | 17-0006933 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SPRING GAP-1701 | 162831701 | FUSE | L1293 | 20170110 | 1737 | 1634756 | 1039 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 14546 | 38.1906 | -120.0004 | BREAUXPARIS4062109PinecrestLakeRd | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 17-0006933 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1246515 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0007288&numberofmonths=24&showchangehistorylog=1 | 17-0007288 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SPRING GAP-1701 | 162831701 | FUSE | 21523 | 20170110 | 1927 | 1636153 | 1003 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 45135 | 38.2368 | -119.9927 | MTR1010152512 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007288 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1246869 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0010357&numberofmonths=24&showchangehistorylog=1 | 17-0010357 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1703 | 163761703 | FUSE | 5957 | 20170118 | 1723 | 1647381 | 338 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 5070 | 38.033 | -120.3999 | 2WOFMTR1005716816 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010357 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1249369 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0010667&numberofmonths=24&showchangehistorylog=1 | 17-0010667 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE | 6165 | 20170119 | 449 | 1649895 | 541 | Distribution Circuit | Vegetation | Tree - fell into line | 204 | 21764 | 37.2004 | -119.7555 | MTR1009709862 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0010667 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1249683 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011778&numberofmonths=24&showchangehistorylog=1 | 17-0011778 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2103 | 254432103 | FUSE | 5868 | 20170120 | 1917 | 1655070 | 1182 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 35460 | 37.2051 | -119.7165 | MTR1005024142 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 17-0011778 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1250608 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011538&numberofmonths=24&showchangehistorylog=1 | 17-0011538 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | RECLOSER | 9210 | 20170120 | 1006 | 1653644 | 805 | Distribution Circuit | Vegetation | Tree - fell into line | 158 | 57890 | 37.8183 | -120.0961 | BET2389C9430 | Overcast-Fog-Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0011538 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Multi-Fault | 1250403 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011858&numberofmonths=24&showchangehistorylog=1 | 17-0011858 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | OTHER | WIREDOWNMTR1004211477 | 20170120 | 2341 | 1655320 | 1243 | Distribution Circuit | Equipment Failure/Involved | Overhead | 41 | 23708 | 38.063 | -120.1871 | TAPOFFOFMTR1004211477 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0011858 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Open Circuit | 1250685 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011965&numberofmonths=24&showchangehistorylog=1 | 17-0011965 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | S1219 | 20170120 | 2107 | 1656225 | 5553 | Distribution Circuit | Vegetation | Tree - bark fell into line | 404 | 1861104 | 38.0581 | -120.1864 | 20609HALAPOMTR10048203612261FUCO23989WAKALUTRAIL | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0011965 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Multi-Fault | 1250787 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011870&numberofmonths=24&showchangehistorylog=1 | 17-0011870 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SPRING GAP-1701 | 162831701 | RECLOSER | 10720 | 20170120 | 2321 | 1655300 | 2459 | Distribution Circuit | Vegetation | Tree - fell into line | 153 | 376227 | 38.1994 | -120.0206 | 10POLESNOF10720 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0011870 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1250697 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012069&numberofmonths=24&showchangehistorylog=1 | 17-0012069 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | CURTIS-1702 | 163351702 | FUSE | 2543 | 20170121 | 645 | 1655701 | 1935 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 30960 | 38.0423 | -120.3197 | 1NOF2543 | Overcast-Fog-Below 32 F | Insulator | Broken, wire on object | 17-0012069 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1250881 | INS | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012139&numberofmonths=24&showchangehistorylog=1 | 17-0012139 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | CURTIS-1702 | 163351702 | FUSE | S1563 | 20170121 | 734 | 1655773 | 2111 | Distribution Circuit | Vegetation | Tree - grew into line | 32 | 23872 | 38.0265 | -120.2865 | MTR1004980657 | Overcast-Fog-Below 32 F | Pole-Wood | Broken, wire on ground | 17-0012139 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1250955 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012155&numberofmonths=24&showchangehistorylog=1 | 17-0012155 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | CURTIS-1705 | 163351705 | FUSE | S2041 | 20170121 | 132 | 1655410 | 3348 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 63152 | 37.9906 | -120.2417 | 1ANDHALFSPANSEOFMTR1004820347 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012155 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1250970 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011915&numberofmonths=24&showchangehistorylog=1 | 17-0011915 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 20327 | 20170121 | 537 | 1655724 | 1938 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 25194 | 38.0267 | -120.2229 | GonzalesB2077631146222263CEDARSPRINGSRD | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | On Ground | 17-0011915 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1250743 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011932&numberofmonths=24&showchangehistorylog=1 | 17-0011932 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 20325 | 20170121 | 535 | 1655723 | 657 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 17082 | 38.0279 | -120.224 | GonzalesB2077631146222361ROBINHOODDR | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011932 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1250759 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011991&numberofmonths=24&showchangehistorylog=1 | 17-0011991 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 356738 | 20170121 | 803 | 1655833 | 3678 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 117696 | 38.0561 | -120.1969 | 23883PINELAKEDR | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0011991 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1250808 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0011998&numberofmonths=24&showchangehistorylog=1 | 17-0011998 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | RECLOSER | 10600 | 20170121 | 720 | 1656246 | 3730 | Distribution Circuit | Vegetation | Tree - fell into line | 304 | 791514 | 38.066 | -120.1888 | MTR1004720452 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0011998 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1250815 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012014&numberofmonths=24&showchangehistorylog=1 | 17-0012014 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 22625 | 20170121 | 701 | 1655730 | 4570 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 49023 | 38.0608 | -120.1985 | ENDOFLINEBEYOND22625 | Overcast-Fog-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0012014 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1250831 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012061&numberofmonths=24&showchangehistorylog=1 | 17-0012061 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 67455 | 20170121 | 1000 | 1656374 | 3277 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 51073 | 38.0643 | -120.1896 | LDSIDE67455 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0012061 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1250875 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012073&numberofmonths=24&showchangehistorylog=1 | 17-0012073 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | S2251 | 20170121 | 359 | 1655805 | 1062 | Distribution Circuit | Vegetation | Tree - fell into line | 354 | 343329 | 38.0355 | -120.2262 | HIGHLANDDRBLACKHAWKDR | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012073 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1250885 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012081&numberofmonths=24&showchangehistorylog=1 | 17-0012081 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 523056 | 20170121 | 1024 | 1656248 | 3537 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 53055 | 38.061 | -120.1958 | 2SOF523056 | Overcast-Fog-Snow-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0012081 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1250893 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012114&numberofmonths=24&showchangehistorylog=1 | 17-0012114 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 2067 | 20170121 | 504 | 1656221 | 4786 | Distribution Circuit | Vegetation | Tree - branch fell on line | 79 | 378094 | 38.0583 | -120.1867 | 2071MUHELIRD | Overcast-Fog-Snow-32-90 F | Pole-Wood | Broken, wire on ground | 17-0012114 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1250928 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012136&numberofmonths=24&showchangehistorylog=1 | 17-0012136 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 20329 | 20170121 | 652 | 1655708 | 4804 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 110492 | 38.0185 | -120.2185 | 21585MTPROVORD | Overcast-Fog-32-90 F | Pole-Wood | Broken, wire on ground | 17-0012136 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1250951 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012821&numberofmonths=24&showchangehistorylog=1 | 17-0012821 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | RECLOSER | 8050 | 20170121 | 1843 | 1659135 | 1558 | Distribution Circuit | Vegetation | Tree - fell into line | 872 | 957431 | 38.0569 | -120.203 | McKinnon207457303941POLEEOFMTR1001004976478POLESAPID101045045 | Overcast-Fog-Below 32 F | Pole-Wood | Broken, wire on ground | 17-0012821 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Multi-Fault | 1251643 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013218&numberofmonths=24&showchangehistorylog=1 | 17-0013218 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 1871 | 20170121 | 2056 | 1657288 | 3778 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 196456 | 38.0679 | -120.1872 | 4TO5SPANSLOADSIDEOF1871 | Overcast-Below 32 F | Conductor, Overhead | On Ground | 17-0013218 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1252027 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013385&numberofmonths=24&showchangehistorylog=1 | 17-0013385 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 2263 | 20170121 | 744 | 1655680 | 3410 | Distribution Circuit | Vegetation | Tree - fell into line | 91 | 264966 | 38.0743 | -120.173 | BREAUXPARIS406224822QuartzAve | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0013385 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Three Phase Fault | 1252199 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013433&numberofmonths=24&showchangehistorylog=1 | 17-0013433 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 2527 | 20170121 | 944 | 1656171 | 4626 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 60138 | 38.0699 | -120.1842 | 1LOADSIDEOF2527 | Overcast-Fog-Below 32 F | Conductor, Overhead | On Ground | 17-0013433 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1252250 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013264&numberofmonths=24&showchangehistorylog=1 | 17-0013264 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | PINECREST-0401 | 163160401 | FUSE | 1861 | 20170121 | 1935 | 1657181 | 2586 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 77580 | 38.1867 | -119.9939 | 204SUGARPINE | Clear-Below 32 F | Conductor, Overhead | On Ground | 17-0013264 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1252079 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0012085&numberofmonths=24&showchangehistorylog=1 | 17-0012085 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SAN JOAQUIN #3 PH-1103 | 252531103 | FUSE | 22593 | 20170121 | 1410 | 1656676 | 266 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 2926 | 37.2286 | -119.4574 | MTR1006375661 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012085 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1250898 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013897&numberofmonths=24&showchangehistorylog=1 | 17-0013897 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SPRING GAP-1701 | 162831701 | FUSE | 26307 | 20170121 | 1305 | 1664382 | 6026 | Distribution Circuit | Vegetation | Tree - branch fell on line | 106 | 638756 | 38.1552 | -120.0561 | 29462SHASTADR | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013897 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1252656 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0014523&numberofmonths=24&showchangehistorylog=1 | 17-0014523 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SPRING GAP-1701 | 162831701 | JUMPER | OJS1SOFCGC321275160280 | 20170121 | 1553 | 1666433 | 5873 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 58730 | 38.1539 | -120.0572 | 3SPANSLOADSIDEOFCGC321275160280 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0014523 | OH | Sus | 0 | yes | 2017 | JAN | Yes | None | 1253194 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013276&numberofmonths=24&showchangehistorylog=1 | 17-0013276 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1704 | 163351704 | RECLOSER | 11290 | 20170122 | 4 | 1658371 | 3815 | Distribution Circuit | Equipment Failure/Involved | Overhead | 130 | 147843 | 38.0065 | -120.347 | TRUJILLOMANUEL22380LYONSBALDMT | Overcast-Fog-Rain-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0013276 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1252091 | CSO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013168&numberofmonths=24&showchangehistorylog=1 | 17-0013168 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 2525 | 20170122 | 1341 | 1661133 | 2846 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 35642 | 38.0594 | -120.2154 | Kitchell201192552537512polesfrommtr1004213122 | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013168 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1251979 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013996&numberofmonths=24&showchangehistorylog=1 | 17-0013996 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | S2281 | 20170122 | 724 | 1664771 | 3269 | Distribution Circuit | Equipment Failure/Involved | Overhead | 41 | 134029 | 38.0629 | -120.1863 | 24352KOMERDMIWUK | Clear-Below 32 F | Crossarm, Wood | Broken, wire on ground | 17-0013996 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1252745 | CAW | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013033&numberofmonths=24&showchangehistorylog=1 | 17-0013033 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1103 | 254421103 | RECLOSER | 10190 | 20170122 | 808 | 1659678 | 739 | Distribution Circuit | Vegetation | Tree - fell into line | 676 | 467067 | 37.4144 | -119.6272 | 7724SUMMITRDFISHCAMP | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0013033 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1251853 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013406&numberofmonths=24&showchangehistorylog=1 | 17-0013406 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1103 | 254421103 | RECLOSER | 77384 | 20170122 | 1929 | 1662203 | 1360 | Distribution Circuit | Vegetation | Tree - fell into line | 455 | 183281 | 37.3389 | -119.5843 | Lafata1848470328453275ROAD432 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013406 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1252223 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013958&numberofmonths=24&showchangehistorylog=1 | 17-0013958 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SPRING GAP-1701 | 162831701 | FUSE | 20321 | 20170122 | 914 | 1664628 | 3581 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 204117 | 38.148 | -120.0718 | SNOWWHITERIDGEANDSHERWOODFORESTLN | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013958 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Force Out | 1252712 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013644&numberofmonths=24&showchangehistorylog=1 | 17-0013644 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | COARSEGOLD-2102 | 254432102 | FUSE | 1617 | 20170123 | 217 | 1663088 | 537 | Distribution Circuit | Vegetation | Tree - branch fell on line | 95 | 51015 | 37.3126 | -119.6207 | MTR1006019987 | Overcast-Snow-32-90 F | Conductor, Overhead | On Ground | 17-0013644 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Force Out | 1252460 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013784&numberofmonths=24&showchangehistorylog=1 | 17-0013784 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | COARSEGOLD-2102 | 254432102 | TRIP-SAVER | 10207 | 20170123 | 908 | 1663394 | 588 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 26460 | 37.2983 | -119.6165 | 2SOUTHOF10207 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013784 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1252560 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013774&numberofmonths=24&showchangehistorylog=1 | 17-0013774 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE | 10788 | 20170123 | 906 | 1663374 | 659 | Distribution Circuit | Vegetation | Tree - fell into line | 76 | 22439 | 37.2869 | -119.6558 | MTR1006640754 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 17-0013774 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1252553 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013824&numberofmonths=24&showchangehistorylog=1 | 17-0013824 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 2487 | 20170123 | 1257 | 1664078 | 504 | Distribution Circuit | Vegetation | Tree - fell into line | 98 | 49392 | 38.0618 | -120.1974 | BREAUXPARIS4062variouslocations | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0013824 | OH | Sus | 0 | yes | 2017 | JAN | Yes | None | 1252599 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0014015&numberofmonths=24&showchangehistorylog=1 | 17-0014015 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 20311 | 20170123 | 1659 | 1664595 | 1355 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 7439 | 38.0952 | -120.1277 | 26075NORTHFORKROAD | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0014015 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1252762 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0014027&numberofmonths=24&showchangehistorylog=1 | 17-0014027 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 20319 | 20170123 | 1726 | 1664713 | 1243 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 12979 | 38.0405 | -120.2159 | 1PWOFMTR1004934916 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0014027 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1252773 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013981&numberofmonths=24&showchangehistorylog=1 | 17-0013981 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1702 | 163661702 | OTHER | WIREDOWN6SOF6821 | 20170123 | 1000 | 1663553 | 1730 | Distribution Circuit | Equipment Failure/Involved | Overhead | 40 | 65870 | 38.0538 | -120.2759 | 6SOF6821 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013981 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1252733 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013968&numberofmonths=24&showchangehistorylog=1 | 17-0013968 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1101 | 254421101 | FUSE | 5533 | 20170123 | 823 | 1664670 | 2042 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 4084 | 37.4213 | -119.7113 | BET23PEOF5533 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013968 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1252722 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013934&numberofmonths=24&showchangehistorylog=1 | 17-0013934 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | OAKHURST-1103 | 254421103 | FUSE | 2035 | 20170123 | 1120 | 1663805 | 550 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 6801 | 37.3579 | -119.6396 | 2POLESWESTAND2SOUTHOF2035FIRSTLINEBUCK | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013934 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1252688 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0014033&numberofmonths=24&showchangehistorylog=1 | 17-0014033 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1103 | 254421103 | FUSE | 5725 | 20170123 | 1122 | 1663782 | 1474 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 47168 | 37.3745 | -119.6301 | 1SPANLDSIDEOFFUCO5725 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0014033 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1252780 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0013580&numberofmonths=24&showchangehistorylog=1 | 17-0013580 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SAN JOAQUIN #3 PH-1101 | 252531101 | FUSE | 86105 | 20170123 | 145 | 1662662 | 2076 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 45672 | 37.3243 | -119.5664 | 1SNOFFUCO86105 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013580 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1252402 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0014034&numberofmonths=24&showchangehistorylog=1 | 17-0014034 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SPRING GAP-1701 | 162831701 | FUSE | L1707 | 20170123 | 1304 | 1664106 | 3120 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 45808 | 38.1872 | -120.0021 | MTR1010089908 | Partly Cloudy-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0014034 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1252781 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0014381&numberofmonths=24&showchangehistorylog=1 | 17-0014381 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SPRING GAP-1701 | 162831701 | FUSE | 26312 | 20170123 | 1257 | 1664076 | 3139 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 65919 | 38.1963 | -120.0118 | McKinnon2074573039428349RIVERRD | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 17-0014381 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1253100 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018069&numberofmonths=24&showchangehistorylog=1 | 17-0018069 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1704 | 163351704 | FUSE | 20771 | 20170207 | 103 | 1677320 | 706 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 14874 | 38.0494 | -120.3707 | LDSIDEOFMTR1004975307 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018069 | OH | Sus | 31304303 | yes | 2017 | FEB | Yes | Line to Line | 1255924 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018129&numberofmonths=24&showchangehistorylog=1 | 17-0018129 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2102 | 254452102 | FUSE | 12294 | 20170207 | 404 | 1677711 | 531 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 8282 | 37.4115 | -119.8198 | MTR1005637059 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018129 | OH | Sus | 42939896 | yes | 2017 | FEB | Yes | Line to Ground | 1255992 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018653&numberofmonths=24&showchangehistorylog=1 | 17-0018653 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2102 | 254452102 | FUSE | 7429 | 20170207 | 1111 | 1679892 | 1618 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 17334 | 37.3736 | -119.8729 | 3SPANSSSOFMTR1009070657 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018653 | OH | Sus | 31304498 | yes | 2017 | FEB | Yes | Line to Ground | 1256422 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018605&numberofmonths=24&showchangehistorylog=1 | 17-0018605 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1702 | 163661702 | FUSE | 2513 | 20170207 | 1211 | 1680090 | 681 | Distribution Circuit | Vegetation | Tree - fell into line | 72 | 18663 | 38.0363 | -120.2505 | MTR1004859076 | Overcast-Drizzle-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0018605 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1256376 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0019623&numberofmonths=24&showchangehistorylog=1 | 17-0019623 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | BEAR VALLEY-2101 | 252192101 | RECLOSER | 10000 | 20170209 | 1728 | 1683971 | 594 | Distribution Circuit | Vegetation | Tree - fell into line | 196 | 53959 | 37.5694 | -120.1175 | Lafata184847032847531HUNTERSVALLEYRD | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0019623 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1257094 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0022157&numberofmonths=24&showchangehistorylog=1 | 17-0022157 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | BEAR VALLEY-2101 | 252192101 | RECLOSER | 10000 | 20170217 | 927 | 1693299 | 322 | Distribution Circuit | Vegetation | Tree - fell into line | 196 | 41981 | 37.5694 | -120.1175 | 7531HUNTERSVALLEYRD | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022157 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Multi-Fault | 1259236 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0022662&numberofmonths=24&showchangehistorylog=1 | 17-0022662 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | BEAR VALLEY-2105 | 252192105 | RECLOSER | 4170 | 20170217 | 1709 | 1697621 | 1461 | Distribution Circuit | Vegetation | Tree - fell into line | 900 | 590508 | 37.6103 | -120.1339 | Elam191655976017745166schilling | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0022662 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1259686 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0022408&numberofmonths=24&showchangehistorylog=1 | 17-0022408 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | CURTIS-1702 | 163351702 | FUSE | 2545 | 20170217 | 1311 | 1695876 | 733 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 19791 | 38.0417 | -120.3191 | 1EOFMTR1004860333 | Overcast-Fog-Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0022408 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1259450 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0022767&numberofmonths=24&showchangehistorylog=1 | 17-0022767 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | FUSE | 56337 | 20170217 | 1540 | 1698618 | 1526 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 13734 | 37.9521 | -120.2367 | TXMTR1004732686 | Overcast-Fog-Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0022767 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1259783 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0022730&numberofmonths=24&showchangehistorylog=1 | 17-0022730 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | KERCKHOFF-1101 | 252561101 | FUSE | 19022 | 20170217 | 1742 | 1697863 | 1675 | Distribution Circuit | Equipment Failure/Involved | Overhead | 23 | 14793 | 37.0914 | -119.6169 | 4POLESLOADSIDEOF10044 | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0022730 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1259746 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0022417&numberofmonths=24&showchangehistorylog=1 | 17-0022417 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2101 | 254452101 | FUSE | 2272 | 20170217 | 1341 | 1696056 | 1530 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 44370 | 37.4914 | -119.8274 | Kitchell201192552537515705meadowln | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0022417 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1259459 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0022326&numberofmonths=24&showchangehistorylog=1 | 17-0022326 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MARIPOSA-2102 | 254452102 | JUMPER | WIREDWNNOFMTR1007100638 | 20170217 | 1230 | 1696483 | 1753 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1753 | 37.4236 | -119.9332 | NOFMTR1007100638 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022326 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Open Circuit | 1259383 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0022335&numberofmonths=24&showchangehistorylog=1 | 17-0022335 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 20327 | 20170217 | 1218 | 1695543 | 800 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 1904 | 38.0267 | -120.2229 | 1004858967 | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022335 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1259390 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0022774&numberofmonths=24&showchangehistorylog=1 | 17-0022774 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 2275 | 20170217 | 1935 | 1698261 | 1565 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 87640 | 38.0901 | -120.1394 | BREAUXPARIS406225785LongBarnSugarpineRd | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0022774 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1259790 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0022963&numberofmonths=24&showchangehistorylog=1 | 17-0022963 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1702 | 163661702 | FUSE | 92593 | 20170217 | 1747 | 1697933 | 1293 | Distribution Circuit | Vegetation | Tree - fell into line | 290 | 319070 | 38.0594 | -120.268 | 1SWOF92593 | Overcast-Fog-Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0022963 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Three Phase Fault | 1259977 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023866&numberofmonths=24&showchangehistorylog=1 | 17-0023866 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | BEAR VALLEY-2105 | 252192105 | RECLOSER | 9560 | 20170220 | 1501 | 1703616 | 826 | Distribution Circuit | Vegetation | Tree - fell into line | 657 | 245117 | 37.6978 | -120.1162 | 1EOFMTR1005640574SSOF10261 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0023866 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1260846 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023724&numberofmonths=24&showchangehistorylog=1 | 17-0023724 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2102 | 254432102 | JUMPER | OJMTR1005028543 | 20170220 | 1010 | 1702901 | 201 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 201 | 37.2093 | -119.5373 | DEPOLE | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0023724 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Force Out | 1260716 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023882&numberofmonths=24&showchangehistorylog=1 | 17-0023882 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | FUSE | 1723 | 20170220 | 1418 | 1703495 | 567 | Distribution Circuit | Vegetation | Tree - fell into line | 81 | 10487 | 37.9318 | -120.336 | 1LDSIDE | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0023882 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1260860 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024595&numberofmonths=24&showchangehistorylog=1 | 17-0024595 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1705 | 163351705 | JUMPER | L1759 | 20170220 | 1828 | 1706344 | 557 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 5551 | 37.9302 | -120.28 | 6SPANSSOURCESIDEOFMTR1004933998 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024595 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1261561 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024006&numberofmonths=24&showchangehistorylog=1 | 17-0024006 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | RECLOSER | 10600 | 20170220 | 1729 | 1704921 | 514 | Distribution Circuit | Vegetation | Tree - fell into line | 847 | 360667 | 38.066 | -120.1888 | MTR1004903963 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0024006 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Three Phase Fault | 1260975 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024084&numberofmonths=24&showchangehistorylog=1 | 17-0024084 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1702 | 163661702 | OTHER | WIREDOWN | 20170220 | 1812 | 1705891 | 793 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 10309 | 38.0374 | -120.2333 | 22903GOLFCLUBRD | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024084 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Force Out | 1261051 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024077&numberofmonths=24&showchangehistorylog=1 | 17-0024077 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1703 | 163761703 | FUSE | L347 | 20170220 | 1829 | 1705151 | 345 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 17250 | 38.0361 | -120.4261 | 2WOFMTR1004717804 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024077 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1261042 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024773&numberofmonths=24&showchangehistorylog=1 | 17-0024773 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | RECLOSER | 90320 | 20170221 | 43 | 1706981 | 433 | Distribution Circuit | Vegetation | Tree - fell into line | 995 | 136819 | 37.8474 | -120.2023 | MTR1004861349 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024773 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1261744 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0024994&numberofmonths=24&showchangehistorylog=1 | 17-0024994 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | FUSE | 21017 | 20170221 | 311 | 1707281 | 934 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 37360 | 37.7994 | -119.8753 | 3EOFMTR1008696918 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024994 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Three Phase Fault | 1261951 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025032&numberofmonths=24&showchangehistorylog=1 | 17-0025032 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MIWUK-1702 | 163661702 | JUMPER | WIREDOWNATINTOFRIDGEVIEWCREEKSIDE | 20170221 | 934 | 1708246 | 393 | Distribution Circuit | Vegetation | Tree - fell into line | 162 | 60858 | 38.0117 | -120.2762 | 16680CREEKSIDEDR | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025032 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Three Phase Fault | 1261978 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025713&numberofmonths=24&showchangehistorylog=1 | 17-0025713 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | JUMPER | WIREDWN5NOF22182 | 20170222 | 1429 | 1710873 | 246 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 492 | 37.9796 | -120.3107 | 5NOF22182 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025713 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Open Circuit | 1262512 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0025762&numberofmonths=24&showchangehistorylog=1 | 17-0025762 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | FUSE | 19689 | 20170222 | 1645 | 1711109 | 1013 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 5065 | 37.9372 | -120.3829 | 20SPANSLDSIDE19689 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025762 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Three Phase Fault | 1262549 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037414&numberofmonths=24&showchangehistorylog=1 | 17-0037414 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | BEAR VALLEY-2105 | 252192105 | RECLOSER | 9560 | 20170406 | 2250 | 1746649 | 1019 | Distribution Circuit | Vegetation | Tree - fell into line | 657 | 337855 | 37.6978 | -120.1162 | WOF44573LDSIDE | Overcast-Drizzle-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0037414 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1271627 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037524&numberofmonths=24&showchangehistorylog=1 | 17-0037524 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | FUSE | L2297 | 20170406 | 2012 | 1746573 | 883 | Distribution Circuit | Vegetation | Tree - fell into line | 65 | 43910 | 37.843 | -120.1959 | SPANEASTOFMTR1004717618 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 17-0037524 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Line | 1271741 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037621&numberofmonths=24&showchangehistorylog=1 | 17-0037621 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | FUSE | 2071 | 20170406 | 2018 | 1746627 | 1152 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 46554 | 37.83 | -120.2037 | 1SOFMTR1004901764 | Overcast-Drizzle-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0037621 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Line | 1271846 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037385&numberofmonths=24&showchangehistorylog=1 | 17-0037385 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MARIPOSA-2101 | 254452101 | FUSE | 44913 | 20170406 | 2019 | 1746872 | 734 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2202 | 37.5184 | -119.9171 | MTR1007099601 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 17-0037385 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1271595 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037600&numberofmonths=24&showchangehistorylog=1 | 17-0037600 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 2057 | 20170406 | 2254 | 1748568 | 873 | Distribution Circuit | Vegetation | Tree - fell into line | 100 | 65460 | 38.0647 | -120.1848 | LOADSIDESOURCESIDEOFFUCO2059 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037600 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Line | 1271824 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037401&numberofmonths=24&showchangehistorylog=1 | 17-0037401 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1705 | 163781705 | RECLOSER | 70198 | 20170406 | 2131 | 1747854 | 1400 | Distribution Circuit | Vegetation | Tree - fell into line | 1453 | 585827 | 37.9573 | -120.4383 | BET4THAND5THPNWOF21453 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037401 | OH | Sus | 0 | yes | 2017 | APR | Yes | Three Phase Fault | 1271613 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037649&numberofmonths=24&showchangehistorylog=1 | 17-0037649 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | BEAR VALLEY-2105 | 252192105 | JUMPER | WIREDOWN4SPANSWOF4172HWY132 | 20170407 | 528 | 1749492 | 471 | Distribution Circuit | Vegetation | Tree - fell into line | 207 | 11226 | 37.7156 | -120.2026 | WIREDOWN4SPANSWOF4172HWY132COULTERVILLE | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037649 | OH | Sus | 0 | yes | 2017 | APR | Yes | Open Circuit | 1271868 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037885&numberofmonths=24&showchangehistorylog=1 | 17-0037885 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2104 | 254432104 | JUMPER | 1SOFMETER1005028923 | 20170407 | 1225 | 1750653 | 180 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 180 | 37.2539 | -119.7141 | 1SOFMETER1005028923 | Overcast-Rain-32-90 F | Insulator | Broken, wire on ground | 17-0037885 | OH | Sus | 0 | yes | 2017 | APR | Yes | Open Circuit | 1272022 | INS | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037588&numberofmonths=24&showchangehistorylog=1 | 17-0037588 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2101 | 254452101 | FUSE | 4585 | 20170407 | 338 | 1749338 | 827 | Distribution Circuit | Vegetation | Tree - fell into line | 125 | 51895 | 37.4545 | -119.8243 | 4THSPANSEOFMTR38P256 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037588 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1271812 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037651&numberofmonths=24&showchangehistorylog=1 | 17-0037651 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2102 | 254452102 | FUSE | 83411 | 20170407 | 805 | 1749567 | 782 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 4485 | 37.4194 | -119.8739 | 2SPANSNOF83411 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0037651 | OH | Sus | 0 | yes | 2017 | APR | Yes | Force Out | 1271870 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0037882&numberofmonths=24&showchangehistorylog=1 | 17-0037882 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2102 | 254452102 | JUMPER | WIREDOWN2SPANSNOF1005639096 | 20170407 | 557 | 1750837 | 1011 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 13630 | 37.4757 | -119.8573 | 2SPANSNOF1005639096 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037882 | OH | Sus | 0 | yes | 2017 | APR | Yes | Open Circuit | 1272019 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0038164&numberofmonths=24&showchangehistorylog=1 | 17-0038164 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1703 | 163761703 | RECLOSER | 8120 | 20170407 | 2158 | 1752019 | 173 | Distribution Circuit | Vegetation | Tree - fell into line | 421 | 72833 | 38.0254 | -120.405 | 21862SAWMILLFLATRD | Overcast-Rain-32-90 F | Conductor, Overhead | On Ground | 17-0038164 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1272223 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0099860&numberofmonths=24&showchangehistorylog=1 | 17-0099860 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1103 | 254421103 | RECLOSER | 10140 | 20171204 | 2239 | 1936143 | 501 | Distribution Circuit | Vegetation | Tree - fell into line | 1025 | 303452 | 37.3666 | -119.6295 | Lafata1848470328439443EIDYLWILD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0099860 | OH | Sus | 31368360 | yes | 2017 | DEC | Yes | Line to Ground | 1317597 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0023455&numberofmonths=24&showchangehistorylog=1 | 18-0023455 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | CURTIS-1702 | 163351702 | FUSE | 22797 | 20180316 | 1231 | 45965 | 654 | Distribution Circuit | Vegetation | Tree - branch fell on line | 100 | 17304 | 38.0425 | -120.2491 | MTR1004236757 | Overcast-Fog-Below 32 F | Pole-Wood | Broken, wire on ground | 18-0023455 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1336304 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0023597&numberofmonths=24&showchangehistorylog=1 | 18-0023597 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 20319 | 20180316 | 939 | 46303 | 2141 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 36397 | 38.0405 | -120.2159 | 23039TwainHarteDr | Overcast-Fog-Below 32 F | Pole-Wood | Broken, wire on ground | 18-0023597 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Force Out | 1336382 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0023543&numberofmonths=24&showchangehistorylog=1 | 18-0023543 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1702 | 163661702 | FUSE | S1555 | 20180316 | 1111 | 45874 | 1835 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 135790 | 38.065 | -120.2728 | MTR1004235936 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 18-0023543 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1336340 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0023545&numberofmonths=24&showchangehistorylog=1 | 18-0023545 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1702 | 163661702 | FUSE | 22785 | 20180316 | 1153 | 45960 | 404 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 3636 | 38.0505 | -120.2271 | 1NOFL2047 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 18-0023545 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1336342 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0023546&numberofmonths=24&showchangehistorylog=1 | 18-0023546 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1702 | 163661702 | RECLOSER | 6018 | 20180316 | 1421 | 46035 | 1776 | Distribution Circuit | Vegetation | Tree - fell into line | 614 | 856508 | 38.0441 | -120.2479 | 2SOF2351416596CADDOCIR | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 18-0023546 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1336343 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0023559&numberofmonths=24&showchangehistorylog=1 | 18-0023559 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1702 | 163661702 | FUSE | S1551 | 20180316 | 1421 | 46156 | 1645 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 27965 | 38.0628 | -120.2735 | MTR1004717646 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 18-0023559 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Force Out | 1336352 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0023616&numberofmonths=24&showchangehistorylog=1 | 18-0023616 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1702 | 163661702 | FUSE | S1557 | 20180316 | 1423 | 46334 | 1643 | Distribution Circuit | Vegetation | Tree - fell into line | 135 | 221805 | 38.0657 | -120.2752 | WIREDOWN1WOFS1557ASWELLASWIREDOWN4WOFS1557 | Overcast-Fog-Below 32 F | Crossarm, Wood | Broken, wire on ground | 18-0023616 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1336394 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0104659&numberofmonths=24&showchangehistorylog=1 | 18-0104659 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | S1219 | 20181129 | 8 | 227311 | 483 | Distribution Circuit | Vegetation | Tree - fell into line | 403 | 194649 | 38.0581 | -120.1864 | ATMTR1004211257 | Overcast-Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 18-0104659 | OH | Sus | 0 | yes | 2018 | NOV | Yes | Three Phase Fault | 1395973 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0104767&numberofmonths=24&showchangehistorylog=1 | 18-0104767 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | S2281 | 20181129 | 413 | 227701 | 987 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 29079 | 38.0629 | -120.1863 | MTR1004820339 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 18-0104767 | OH | Sus | 0 | yes | 2018 | NOV | Yes | Line to Line | 1396080 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005556&numberofmonths=24&showchangehistorylog=1 | 19-0005556 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1705 | 163351705 | FUSE | 24459 | 20190106 | 1838 | 256566 | 1322 | Distribution Circuit | Vegetation | Tree - branch fell on line | 13 | 7682 | 37.9505 | -120.3024 | CGC320569752623 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005556 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1404006 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005406&numberofmonths=24&showchangehistorylog=1 | 19-0005406 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MERCED FALLS-1102 | 252811102 | FUSE | 8522 | 20190106 | 1855 | 256767 | 891 | Distribution Circuit | Equipment Failure/Involved | Overhead | 544 | 43545 | 37.6559 | -120.3488 | 10014ALAMO | Overcast-Fog-Heavy Rain-32-90 F | Insulator | Broken, wire on ground | 19-0005406 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1403854 | INS | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005274&numberofmonths=24&showchangehistorylog=1 | 19-0005274 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 2477 | 20190106 | 1737 | 255964 | 1337 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 29414 | 38.02 | -120.2224 | 2SPANSWOF2477 | Overcast-Fog-Snow-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005274 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1403746 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005331&numberofmonths=24&showchangehistorylog=1 | 19-0005331 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 2489 | 20190106 | 1739 | 255977 | 1446 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 40226 | 38.0632 | -120.1945 | ATMTR1004718504 | Overcast-Fog-Snow-Strong Winds-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0005331 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1403782 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010502&numberofmonths=24&showchangehistorylog=1 | 19-0010502 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2101 | 254452101 | FUSE | 10507 | 20190116 | 2345 | 272021 | 1137 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 23877 | 37.508 | -119.8642 | MTR1006955560 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0010502 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1407367 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010410&numberofmonths=24&showchangehistorylog=1 | 19-0010410 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | S1787 | 20190116 | 2137 | 271839 | 1320 | Distribution Circuit | Vegetation | Tree - fell into line | 112 | 141240 | 38.0651 | -120.1851 | 2057FUSES2059FUSES | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on object | 19-0010410 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Three Phase Fault | 1407275 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010983&numberofmonths=24&showchangehistorylog=1 | 19-0010983 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 523056 | 20190116 | 2335 | 273854 | 1292 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 19380 | 38.061 | -120.1958 | LDSIDEOF523056 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on object | 19-0010983 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407649 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010113&numberofmonths=24&showchangehistorylog=1 | 19-0010113 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1702 | 163661702 | RECLOSER | 1808 | 20190116 | 1936 | 269994 | 1396 | Distribution Circuit | Vegetation | Tree - fell into line | 280 | 122341 | 38.0301 | -120.245 | MTR1004211396 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0010113 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1406982 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010458&numberofmonths=24&showchangehistorylog=1 | 19-0010458 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | CURTIS-1703 | 163351703 | RECLOSER | 9240 | 20190117 | 26 | 272170 | 885 | Distribution Circuit | Vegetation | Tree - fell into line | 2643 | 1033194 | 37.8315 | -120.2371 | BET84411and78439all3phasedown2span18823FOOTESTTREEONLINE | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010458 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407322 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011065&numberofmonths=24&showchangehistorylog=1 | 19-0011065 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | OTHER | WIREDOWNONGRDSOURCESIDEOFL1207 | 20190117 | 1309 | 274086 | 1201 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1269 | 82537 | 37.8933 | -120.3066 | SOURCESIDEOFL1207 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011065 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407700 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011525&numberofmonths=24&showchangehistorylog=1 | 19-0011525 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | FUSE | 2317 | 20190117 | 1409 | 275202 | 1809 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 8898 | 37.8394 | -119.9857 | ATMTR1009632689 | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0011525 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Three Phase Fault | 1408070 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010831&numberofmonths=24&showchangehistorylog=1 | 19-0010831 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1704 | 163351704 | FUSE | L1473 | 20190117 | 2 | 272081 | 2163 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 21945 | 38.0425 | -120.3774 | 1NOF1004861034 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0010831 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407553 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010833&numberofmonths=24&showchangehistorylog=1 | 19-0010833 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1705 | 163351705 | FUSE | 24458 | 20190117 | 635 | 272681 | 1727 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 13816 | 37.9479 | -120.2991 | MTR1010318870 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010833 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1407555 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010443&numberofmonths=24&showchangehistorylog=1 | 19-0010443 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | OCB | 17012 | 20190117 | 13 | 272123 | 1254 | Distribution Circuit | Vegetation | Tree - fell into line | 2841 | 1041827 | 38.0529 | -120.2172 | 2PNEOF90432SP3SPSOF2487MTR1004715736 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0010443 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1407307 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0010572&numberofmonths=24&showchangehistorylog=1 | 19-0010572 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 2477 | 20190117 | 212 | 272325 | 932 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 20504 | 38.02 | -120.2224 | 22035CEDARSPRINGSRD | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010572 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1407435 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011074&numberofmonths=24&showchangehistorylog=1 | 19-0011074 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 2261 | 20190117 | 1209 | 273894 | 386 | Distribution Circuit | Vegetation | Tree - fell into line | 186 | 71796 | 38.0594 | -120.1807 | MTR1004212461 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011074 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1407704 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011654&numberofmonths=24&showchangehistorylog=1 | 19-0011654 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1702 | 163661702 | JUMPER | WIEREDOWN | 20190117 | 715 | 272786 | 2065 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 2515 | 38.0225 | -120.2561 | 1PWOFS1579 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011654 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Force Out | 1408144 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011723&numberofmonths=24&showchangehistorylog=1 | 19-0011723 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1701 | 163781701 | FUSE | 1921 | 20190117 | 619 | 275675 | 2072 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 12432 | 37.8622 | -120.2314 | MTR1004901834 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0011723 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Three Phase Fault | 1408175 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0016964&numberofmonths=24&showchangehistorylog=1 | 19-0016964 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | BEAR VALLEY-2105 | 252192105 | FUSE | 4636 | 20190202 | 534 | 286531 | 828 | Distribution Circuit | Animal | Other | 33 | 20102 | 37.7191 | -120.1895 | MTR1010509303 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0016964 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1411422 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0017193&numberofmonths=24&showchangehistorylog=1 | 19-0017193 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | FUSE | S1999 | 20190202 | 1207 | 287373 | 401 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 1840 | 37.8265 | -119.9688 | TWDMTR1008663367 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017193 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1411620 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0017053&numberofmonths=24&showchangehistorylog=1 | 19-0017053 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1701 | 163781701 | FUSE | 1997 | 20190202 | 532 | 286525 | 485 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 5820 | 37.8156 | -120.3004 | 4POLESSOF1997 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | On Ground | 19-0017053 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1411504 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018110&numberofmonths=24&showchangehistorylog=1 | 19-0018110 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE | 5679 | 20190204 | 1559 | 290667 | 308 | Distribution Circuit | Vegetation | Tree - fell into line | 122 | 37576 | 37.2396 | -119.778 | 4NWOF5679 | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0018110 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1412353 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0017879&numberofmonths=24&showchangehistorylog=1 | 19-0017879 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | RECLOSER | 9210 | 20190204 | 1057 | 290037 | 4853 | Distribution Circuit | Vegetation | Tree - fell into line | 158 | 227913 | 37.8183 | -120.0961 | MCKINNON207457303949polesloadsideSBCO21015 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0017879 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Three Phase Fault | 1412216 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0017701&numberofmonths=24&showchangehistorylog=1 | 19-0017701 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | OAKHURST-1103 | 254421103 | JUMPER | WIREDOWNMTR1005968059 | 20190204 | 356 | 289483 | 791 | Distribution Circuit | Vegetation | Tree - fell into line | 3921 | 44912 | 37.3434 | -119.6524 | MTR1005968059 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017701 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1412115 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018046&numberofmonths=24&showchangehistorylog=1 | 19-0018046 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1103 | 254421103 | RECLOSER | 5120 | 20190204 | 1458 | 290572 | 4393 | Distribution Circuit | Vegetation | Tree - fell into line | 405 | 1778127 | 37.4809 | -119.6372 | HOOVERWAYCHILNUALNAFALLSCEDARTREEONLINE19567WIREDOWNSOURCESIDEOF5552DUETOTREEFALLINGTHROUGHLINEANDWI | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0018046 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1412315 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018163&numberofmonths=24&showchangehistorylog=1 | 19-0018163 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1103 | 254421103 | RECLOSER | 77384 | 20190204 | 2124 | 291114 | 1256 | Distribution Circuit | Vegetation | Tree - fell into line | 466 | 201670 | 37.3389 | -119.5843 | MTR1009757690POLEMTR1008877564WIREDOWN | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018163 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1412404 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018207&numberofmonths=24&showchangehistorylog=1 | 19-0018207 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1103 | 254421103 | FUSE | 10813 | 20190204 | 1641 | 290715 | 4003 | Distribution Circuit | Vegetation | Tree - fell into line | 140 | 439643 | 37.4042 | -119.625 | 45141CEDARBROOKRD | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0018207 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1412448 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018502&numberofmonths=24&showchangehistorylog=1 | 19-0018502 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1103 | 254421103 | FUSE | 5585 | 20190204 | 1935 | 290897 | 2694 | Distribution Circuit | Environmental/External | Ice or snow | 33 | 88902 | 37.3996 | -119.63 | LOADSIDEOF5585 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0018502 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1412665 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018959&numberofmonths=24&showchangehistorylog=1 | 19-0018959 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1103 | 254421103 | FUSE | 23987 | 20190204 | 1911 | 292665 | 4110 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 83195 | 37.3362 | -119.6137 | 40643TAYLORMOUNTAINRD | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0018959 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1413025 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018141&numberofmonths=24&showchangehistorylog=1 | 19-0018141 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SAN JOAQUIN #3 PH-1101 | 252531101 | RECLOSER | 10060 | 20190204 | 1913 | 290889 | 1020 | Distribution Circuit | Vegetation | Tree - fell into line | 111 | 80823 | 37.2927 | -119.5325 | 4EOF54478SPANSWOF105872EOFMTR1006617725 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018141 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1412385 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018372&numberofmonths=24&showchangehistorylog=1 | 19-0018372 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | BEAR VALLEY-2105 | 252192105 | RECLOSER | 4170 | 20190205 | 917 | 292153 | 376 | Distribution Circuit | Vegetation | Tree - fell into line | 416 | 155480 | 37.6103 | -120.1339 | LDSIDE | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0018372 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1412572 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018428&numberofmonths=24&showchangehistorylog=1 | 19-0018428 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | BEAR VALLEY-2105 | 252192105 | FUSE | 10714 | 20190205 | 29 | 292453 | 2511 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 22599 | 37.7217 | -120.0946 | MTR1006736617 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018428 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1412621 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018744&numberofmonths=24&showchangehistorylog=1 | 19-0018744 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | BEAR VALLEY-2105 | 252192105 | FUSE | 23942 | 20190205 | 29 | 293666 | 2511 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 198369 | 37.716 | -120.0973 | MTR1006383701 | Partly Cloudy-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018744 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1412816 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018651&numberofmonths=24&showchangehistorylog=1 | 19-0018651 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | COARSEGOLD-2102 | 254432102 | FUSE | 2254 | 20190205 | 325 | 292939 | 2275 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 86187 | 37.3172 | -119.6067 | ECHOVALLEYMOUNTAINQUAILRD | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018651 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1412738 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018767&numberofmonths=24&showchangehistorylog=1 | 19-0018767 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE | 10443 | 20190205 | 835 | 292039 | 3543 | Distribution Circuit | Equipment Failure/Involved | Overhead | 64 | 47139 | 37.3101 | -119.6468 | CGC322487529553 | Overcast-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0018767 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1412834 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018218&numberofmonths=24&showchangehistorylog=1 | 19-0018218 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | RECLOSER | 68380 | 20190205 | 116 | 291286 | 3940 | Distribution Circuit | Vegetation | Tree - fell into line | 158 | 520747 | 38.0151 | -120.2744 | CRESTVIEWATCREEKSIDE | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018218 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Three Phase Fault | 1412458 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018245&numberofmonths=24&showchangehistorylog=1 | 19-0018245 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | RECLOSER | 8000 | 20190205 | 335 | 291292 | 3774 | Distribution Circuit | Vegetation | Tree - fell into line | 246 | 876060 | 38.0084 | -120.3011 | 21902GLENWOOD21313PHEONIXLAKEROAD4EOFLR8000 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0018245 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1412483 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018388&numberofmonths=24&showchangehistorylog=1 | 19-0018388 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | FUSE | 37158 | 20190205 | 329 | 292224 | 2075 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 10375 | 37.9813 | -120.3055 | NOF2283 | Overcast-Fog-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0018388 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Three Phase Fault | 1412587 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018398&numberofmonths=24&showchangehistorylog=1 | 19-0018398 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | FUSE | 2505 | 20190205 | 49 | 292339 | 4338 | Distribution Circuit | Vegetation | Tree - fell into line | 204 | 884952 | 38.0137 | -120.2848 | WASSONPHILLIP21952glenwoodrd | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on object | 19-0018398 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1412601 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018407&numberofmonths=24&showchangehistorylog=1 | 19-0018407 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | SWITCH | 111443 | 20190205 | 49 | 292372 | 4367 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 235818 | 38.0168 | -120.2812 | MTR1004903440 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on object | 19-0018407 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1412610 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018550&numberofmonths=24&showchangehistorylog=1 | 19-0018550 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | CURTIS-1702 | 163351702 | FUSE | 2439 | 20190205 | 116 | 292733 | 3940 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 149720 | 38.0216 | -120.2717 | 2NWOF2439 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0018550 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1412681 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018632&numberofmonths=24&showchangehistorylog=1 | 19-0018632 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | FUSE | S2263 | 20190205 | 429 | 291709 | 3653 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 51142 | 37.9853 | -120.2902 | NOFS2263 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018632 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1412727 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018713&numberofmonths=24&showchangehistorylog=1 | 19-0018713 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | FUSE | 22184 | 20190205 | 602 | 293063 | 3460 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 20760 | 37.9736 | -120.2622 | 3NOF22184 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | On Ground | 19-0018713 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1412780 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018754&numberofmonths=24&showchangehistorylog=1 | 19-0018754 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | FUSE | L2155 | 20190205 | 602 | 293674 | 3188 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 47820 | 37.9491 | -120.2563 | MTR1004934026 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0018754 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1412821 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018770&numberofmonths=24&showchangehistorylog=1 | 19-0018770 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | FUSE | 22955 | 20190205 | 602 | 293723 | 3288 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 23016 | 37.9949 | -120.2908 | 16071AVENIDADELSOL | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018770 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1412837 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018263&numberofmonths=24&showchangehistorylog=1 | 19-0018263 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | FUSE | 89917 | 20190205 | 602 | 293975 | 4853 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 57423 | 38.0272 | -120.3209 | BREAUXPARIS406222495YerbaSanta | Overcast-Fog-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0018263 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1413061 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019034&numberofmonths=24&showchangehistorylog=1 | 19-0019034 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | TRIP-SAVER | 9111 | 20190205 | 602 | 294031 | 2300 | Distribution Circuit | Vegetation | Tree - fell into line | 266 | 525355 | 38.0127 | -120.3073 | 21937ELCOYOTEDR | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0019034 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1413078 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019594&numberofmonths=24&showchangehistorylog=1 | 19-0019594 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | CURTIS-1702 | 163351702 | FUSE | 85609 | 20190205 | 116 | 295287 | 3940 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 31520 | 38.0181 | -120.2712 | EOL | Clear-Below 32 F | Conductor, Overhead | On Ground | 19-0019594 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1413472 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019632&numberofmonths=24&showchangehistorylog=1 | 19-0019632 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | FUSE | 2535 | 20190205 | 116 | 295365 | 4001 | Distribution Circuit | Vegetation | Tree - fell into line | 160 | 640160 | 38.0154 | -120.2733 | MTR1004901596MTR1004235622 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0019632 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1413492 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019811&numberofmonths=24&showchangehistorylog=1 | 19-0019811 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | CURTIS-1702 | 163351702 | JUMPER | OJ4SWOFMTR1004235694 | 20190205 | 335 | 295829 | 6178 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 6178 | 38.0329 | -120.2831 | mtr1004235694 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0019811 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1413595 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018224&numberofmonths=24&showchangehistorylog=1 | 19-0018224 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | CURTIS-1703 | 163351703 | RECLOSER | 9330 | 20190205 | 129 | 291313 | 2431 | Distribution Circuit | Vegetation | Tree - fell into line | 276 | 101536 | 37.8312 | -120.2369 | 5EOF27334 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018224 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1412464 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019778&numberofmonths=24&showchangehistorylog=1 | 19-0019778 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | CURTIS-1703 | 163351703 | FUSE | L1927 | 20190205 | 12 | 295701 | 4173 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 95979 | 37.8003 | -120.1413 |  | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0019778 | OH | Sus | 0 | yes | 2019 | FEB | Yes | None | 1413566 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018284&numberofmonths=24&showchangehistorylog=1 | 19-0018284 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1704 | 163351704 | RECLOSER | 11290 | 20190205 | 710 | 291831 | 4570 | Distribution Circuit | Vegetation | Tree - branch fell on line | 132 | 113685 | 38.0065 | -120.347 | BREAUXPARIS406222380LyonsBaldMountainRd | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018284 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1412518 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018961&numberofmonths=24&showchangehistorylog=1 | 19-0018961 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1704 | 163351704 | FUSE | L1413 | 20190205 | 1905 | 293635 | 697 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 19516 | 38.0595 | -120.3828 | MTR1004937489 | Partly Cloudy-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0018961 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1413028 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018962&numberofmonths=24&showchangehistorylog=1 | 19-0018962 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1704 | 163351704 | JUMPER | JPRSOPEN1EOFMTR1004937489 | 20190205 | 1905 | 293856 | 2915 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 5830 | 38.0552 | -120.3829 | MTR1004937489 | Partly Cloudy-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0018962 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1413029 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018977&numberofmonths=24&showchangehistorylog=1 | 19-0018977 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | CURTIS-1704 | 163351704 | JUMPER | WIREDOWN4SPLOADSIDE20807 | 20190205 | 1930 | 293662 | 1038 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 20016 | 38.0356 | -120.3693 | MTR1005428414 | Partly Cloudy-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018977 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1413037 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019232&numberofmonths=24&showchangehistorylog=1 | 19-0019232 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1704 | 163351704 | OTHER | WIREDOWN1SLOADSIDEOF22357 | 20190205 | 812 | 291982 | 1918 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 7672 | 37.9799 | -120.3297 | 1LOADSIDEOF22357 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0019232 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1413204 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018463&numberofmonths=24&showchangehistorylog=1 | 19-0018463 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1705 | 163351705 | FUSE | 19472 | 20190205 | 143 | 291320 | 2285 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 25135 | 37.9814 | -120.2746 | MTR1004898648 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0018463 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1412641 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018489&numberofmonths=24&showchangehistorylog=1 | 19-0018489 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1705 | 163351705 | FUSE | 19464 | 20190205 | 759 | 292598 | 4456 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 13368 | 37.976 | -120.3008 | 19499SERRANORD | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0018489 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1412657 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018565&numberofmonths=24&showchangehistorylog=1 | 19-0018565 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1705 | 163351705 | FUSE | 21473 | 20190205 | 455 | 292759 | 4595 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 18380 | 37.9658 | -120.2784 | 16579TUOLUMNERD | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018565 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1412689 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018581&numberofmonths=24&showchangehistorylog=1 | 19-0018581 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1705 | 163351705 | FUSE | 21469 | 20190205 | 759 | 292784 | 528 | Distribution Circuit | Environmental/External | Ice or snow | 162 | 58285 | 37.9647 | -120.2847 | SOFONMAINLINEMTR100489872418040ROBRICRD | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018581 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1412698 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018690&numberofmonths=24&showchangehistorylog=1 | 19-0018690 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1705 | 163351705 | JUMPER | JPRSBUCKHORNMOUNTAINRDROBRICRD | 20190205 | 755 | 293014 | 3030 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 27270 | 37.9515 | -120.2767 | MTR1004900385 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0018690 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1412766 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018723&numberofmonths=24&showchangehistorylog=1 | 19-0018723 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1705 | 163351705 | JUMPER | JPRSANDRADRBLACKOAKRD | 20190205 | 629 | 293099 | 2061 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 39159 | 37.9676 | -120.2842 | 1NOF1EOFL2097 | Overcast-Fog-Snow-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0018723 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1412787 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018309&numberofmonths=24&showchangehistorylog=1 | 19-0018309 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1705 | 163351705 | SWITCH | L1021 | 20190205 | 759 | 293920 | 1978 | Distribution Circuit | Vegetation | Tree - fell into line | 112 | 219631 | 37.9789 | -120.2883 | BET19469L1021 | Overcast-Fog-Snow-32-90 F | Pole-Wood | Broken, wire on ground | 19-0018309 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1413042 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019111&numberofmonths=24&showchangehistorylog=1 | 19-0019111 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | CURTIS-1705 | 163351705 | FUSE | S2041 | 20190205 | 226 | 294198 | 2385 | Distribution Circuit | Equipment Failure/Involved | Overhead | 46 | 109710 | 37.9906 | -120.2417 | MTR1004820299 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0019111 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1413138 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019131&numberofmonths=24&showchangehistorylog=1 | 19-0019131 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | CURTIS-1705 | 163351705 | FUSE | 2473 | 20190205 | 226 | 294231 | 3485 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 209100 | 37.9987 | -120.234 | SOURCESIDEOF19514 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0019131 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1413146 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019132&numberofmonths=24&showchangehistorylog=1 | 19-0019132 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1705 | 163351705 | FUSE | 19514 | 20190205 | 226 | 294234 | 3485 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 45305 | 37.9968 | -120.2409 | BEYOND19514TOEOL | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0019132 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1413147 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018659&numberofmonths=24&showchangehistorylog=1 | 19-0018659 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 2525 | 20190205 | 446 | 291615 | 2333 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 30329 | 38.0594 | -120.2154 | MTR1004213122 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018659 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1412743 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018222&numberofmonths=24&showchangehistorylog=1 | 19-0018222 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MIWUK-1702 | 163661702 | RECLOSER | 47143 | 20190205 | 120 | 291213 | 2457 | Distribution Circuit | Vegetation | Tree - fell into line | 183 | 414415 | 38.0046 | -120.2628 | CRYSTALFALLSDRBET88247ANDL626 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018222 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1412462 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018244&numberofmonths=24&showchangehistorylog=1 | 19-0018244 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1702 | 163661702 | OCB | 17022 | 20190205 | 330 | 291297 | 2522 | Distribution Circuit | Vegetation | Tree - fell into line | 3248 | 2051686 | 38.0529 | -120.2172 | WIREDOWNSOF1771BROKENPOLES1AND3SPANSSOURCESIDEOF368883POLESSOURCESIDEOF251322942SOUTHFORKRD17892GOOD | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0018244 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Three Phase Fault | 1412482 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018410&numberofmonths=24&showchangehistorylog=1 | 19-0018410 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1103 | 254421103 | FUSE | 5541 | 20190205 | 807 | 291898 | 571 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 48535 | 37.364 | -119.6134 | MTR1006638808 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018410 | OH | Sus | 31424289 | yes | 2019 | FEB | Yes | Line to Line | 1412611 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018772&numberofmonths=24&showchangehistorylog=1 | 19-0018772 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1103 | 254421103 | FUSE | 10293 | 20190205 | 1141 | 292923 | 4360 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 34580 | 37.3237 | -119.6038 | CGC322618530 | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0018772 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1412838 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019368&numberofmonths=24&showchangehistorylog=1 | 19-0019368 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1103 | 254421103 | FUSE | 19617 | 20190205 | 1820 | 293145 | 2664 | Distribution Circuit | Vegetation | Tree - branch fell on line | 226 | 102889 | 37.4606 | -119.6406 | 19617TWDSOUTH | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0019368 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1413300 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018287&numberofmonths=24&showchangehistorylog=1 | 19-0018287 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1701 | 163781701 | RECLOSER | 69124 | 20190205 | 712 | 291840 | 1986 | Distribution Circuit | Vegetation | Tree - fell into line | 168 | 333648 | 37.8554 | -120.225 | 3NORTHOF80105 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018287 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1412520 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018294&numberofmonths=24&showchangehistorylog=1 | 19-0018294 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1701 | 163781701 | RECLOSER | 3186 | 20190205 | 635 | 291777 | 3281 | Distribution Circuit | Vegetation | Tree - fell into line | 645 | 452257 | 37.8621 | -120.2265 | MTR1004719337 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0018294 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1412523 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018399&numberofmonths=24&showchangehistorylog=1 | 19-0018399 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1703 | 163761703 | RECLOSER | 9190 | 20190205 | 1007 | 292342-2 | 1755 | Distribution Circuit | Vegetation | Tree - fell into line | 791 | 838169 | 38.0049 | -120.4056 | LDSIDEOFMTR1004490083 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0018399 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1412607 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019036&numberofmonths=24&showchangehistorylog=1 | 19-0019036 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1703 | 163761703 | JUMPER | JPRS1NOF320294755490 | 20190205 | 1007 | 294032 | 2962 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 5924 | 38.0248 | -120.399 | CGC320294755490 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0019036 | OH | Sus | 0 | yes | 2019 | FEB | Yes | None | 1413080 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019064&numberofmonths=24&showchangehistorylog=1 | 19-0019064 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | RACETRACK-1703 | 163761703 | SWITCH | UNNUM | 20190205 | 1007 | 294131 | 2945 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 58900 | 38.0272 | -120.3783 | BET2635522953 | Overcast-Snow-Below 32 F | Conductor, Overhead | On Ground | 19-0019064 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1413113 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019240&numberofmonths=24&showchangehistorylog=1 | 19-0019240 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1703 | 163761703 | JUMPER | OJ749SHAWSFLAT | 20190205 | 846 | 294448 | 3209 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 6418 | 37.9948 | -120.3888 | SHAWSFLAT | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0019240 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1413207 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019273&numberofmonths=24&showchangehistorylog=1 | 19-0019273 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1703 | 163761703 | FUSE | 26384 | 20190205 | 1341 | 292776 | 4424 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 4424 | 37.992 | -120.3987 | DEADENDPOLE | Overcast-Drizzle-32-90 F | Conductor, Overhead | On Ground | 19-0019273 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1413229 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018600&numberofmonths=24&showchangehistorylog=1 | 19-0018600 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SAN JOAQUIN #3 PH-1101 | 252531101 | RECLOSER | 673480 | 20190205 | 842 | 292065 | 1620 | Distribution Circuit | Vegetation | Tree - fell into line | 889 | 546452 | 37.2881 | -119.5197 | EOF1187439402BEAVERRDMTR1006377801 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018600 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1412707 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019298&numberofmonths=24&showchangehistorylog=1 | 19-0019298 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SAN JOAQUIN #3 PH-1101 | 252531101 | FUSE | 10212 | 20190205 | 1815 | 294471 | 2460 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 19680 | 37.2871 | -119.5191 | SAPID101027555 | Partly Cloudy-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0019298 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1413243 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018528&numberofmonths=24&showchangehistorylog=1 | 19-0018528 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | SAN JOAQUIN #3 PH-1103 | 252531103 | OTHER | WIREDOWNMTR1008929795 | 20190205 | 715 | 291830 | 699 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 959 | 37.2454 | -119.5053 | MTR1008929795 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018528 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1412673 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018272&numberofmonths=24&showchangehistorylog=1 | 19-0018272 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | SWITCH | 5424 | 20190205 | 630 | 291604 | 3270 | Distribution Circuit | Equipment Failure/Involved | Overhead | 179 | 6474 | 37.2233 | -119.5098 | LINEBUCKSINGLEPHASEJUMPERSGOINGTOMTR1009946447 | Overcast-Snow-Below 32 F | Crossarm, Wood | Broken, wire on ground | 19-0018272 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1412509 | CAW | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018443&numberofmonths=24&showchangehistorylog=1 | 19-0018443 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | FUSE | 10236 | 20190205 | 516 | 291635 | 888 | Distribution Circuit | Vegetation | Tree - fell into line | 100 | 88800 | 37.2397 | -119.5549 | 2NEOFMTR1005027836 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0018443 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1412629 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018802&numberofmonths=24&showchangehistorylog=1 | 19-0018802 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | FUSE | 70225 | 20190205 | 727 | 291864 | 1644 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 16440 | 37.2104 | -119.5271 | 2SOURCESIDEOFMTR1006022023 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018802 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1412868 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020474&numberofmonths=24&showchangehistorylog=1 | 19-0020474 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1704 | 163351704 | TRANSFORMER | 320303056730 | 20190209 | 2220 | 297487 | 2189 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2189 | 38.0583 | -120.3953 | SIUDZINSKIMARK24035PONCERD | Rain-Overcast-32-90 F | Transformer | Broken, wire on ground | 19-0020474 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1414151 | TX | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020388&numberofmonths=24&showchangehistorylog=1 | 19-0020388 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1103 | 254421103 | FUSE | 19617 | 20190209 | 1451 | 297222 | 1464 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 43920 | 37.4606 | -119.6406 | 2SOF5571 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020388 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1414062 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020653&numberofmonths=24&showchangehistorylog=1 | 19-0020653 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1103 | 254421103 | FUSE | 10277 | 20190209 | 2124 | 298732 | 2382 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2382 | 37.4422 | -119.6359 | DEPOLE | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020653 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1414351 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020666&numberofmonths=24&showchangehistorylog=1 | 19-0020666 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | BEAR VALLEY-2105 | 252192105 | FUSE | 7277 | 20190210 | 532 | 298014 | 1898 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 49382 | 37.7763 | -120.17 | 2100INCENSECEDAR | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020666 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1414365 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020620&numberofmonths=24&showchangehistorylog=1 | 19-0020620 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | CURTIS-1702 | 163351702 | FUSE | 19526 | 20190210 | 542 | 298029 | 663 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 19160 | 37.9718 | -120.2261 | CGC320794453640 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020620 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1414310 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020568&numberofmonths=24&showchangehistorylog=1 | 19-0020568 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | RECLOSER | 9210 | 20190210 | 645 | 298026 | 1126 | Distribution Circuit | Vegetation | Tree - fell into line | 158 | 150544 | 37.8183 | -120.0961 | S1999 | Overcast-Fog-Snow-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0020568 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1414250 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020594&numberofmonths=24&showchangehistorylog=1 | 19-0020594 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | CURTIS-1704 | 163351704 | JUMPER | OJTWDMTR1004720077 | 20190210 | 802 | 298856 | 714 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 714 | 38.0338 | -120.372 | MTR1004720077 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0020594 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1414386 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020720&numberofmonths=24&showchangehistorylog=1 | 19-0020720 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1704 | 163351704 | FUSE | 20811 | 20190210 | 900 | 298461 | 710 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 8520 | 37.988 | -120.332 | MTR1004902615 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020720 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1414424 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020660&numberofmonths=24&showchangehistorylog=1 | 19-0020660 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1705 | 163351705 | RECLOSER | 39256 | 20190210 | 943 | 298591 | 337 | Distribution Circuit | Vegetation | Tree - fell into line | 521 | 69186 | 37.9571 | -120.3085 | BETL120927298 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020660 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1414358 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020587&numberofmonths=24&showchangehistorylog=1 | 19-0020587 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MARIPOSA-2101 | 254452101 | FUSE | 10493 | 20190210 | 720 | 298268 | 567 | Distribution Circuit | Vegetation | Tree - fell into line | 156 | 88452 | 37.5639 | -119.8548 | MTR10070944577190HITES7130HITESCOVERD | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020587 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1414275 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020626&numberofmonths=24&showchangehistorylog=1 | 19-0020626 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MARIPOSA-2101 | 254452101 | FUSE | 79097 | 20190210 | 629 | 298472 | 657 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 7884 | 37.5864 | -119.8512 | MTR1006119894 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0020626 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1414317 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020606&numberofmonths=24&showchangehistorylog=1 | 19-0020606 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1703 | 163761703 | OTHER | WIREDOWNFUCO26389 | 20190210 | 544 | 298288 | 650 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3508 | 366649 | 37.9881 | -120.3882 | SALYERSS19046613420807fuco26389 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0020606 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1414296 | PW | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020582&numberofmonths=24&showchangehistorylog=1 | 19-0020582 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1704 | 163761704 | FUSE | L2627 | 20190210 | 702 | 298156 | 192 | Distribution Circuit | Equipment Failure/Involved | Overhead | 555 | 34605 | 37.9708 | -120.4482 | SIUDZINSKIMARK2polesloadsideofmtr1004935291 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020582 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1414267 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020702&numberofmonths=24&showchangehistorylog=1 | 19-0020702 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SAN JOAQUIN #3 PH-1101 | 252531101 | FUSE | 10256 | 20190210 | 1011 | 298642 | 479 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 14849 | 37.3106 | -119.58 | BEYOND10256 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020702 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1414406 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020721&numberofmonths=24&showchangehistorylog=1 | 19-0020721 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SAN JOAQUIN #3 PH-1101 | 252531101 | RECLOSER | 10060 | 20190210 | 1315 | 298972 | 295 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 13580 | 37.2927 | -119.5325 | 1W2SOF10023 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020721 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1414425 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020641&numberofmonths=24&showchangehistorylog=1 | 19-0020641 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | TAR FLAT-0401 | 163240401 | FUSE | 1879 | 20190210 | 723 | 298200 | 339 | Distribution Circuit | Vegetation | Tree - branch fell on line | 41 | 8166 | 37.989 | -120.3765 | OJ2PNO1879 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020641 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1414336 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021752&numberofmonths=24&showchangehistorylog=1 | 19-0021752 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2101 | 254452101 | JUMPER | BUCKLINEDOWN1E1SOFMTR1006926367 | 20190212 | 2351 | 302499 | 890 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 26700 | 37.4628 | -119.7824 | BUCKLINEDOWN1E1SOFMTR1006926367 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021752 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1415204 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021738&numberofmonths=24&showchangehistorylog=1 | 19-0021738 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | BEAR VALLEY-2105 | 252192105 | RECLOSER | 9560 | 20190213 | 246 | 302244 | 979 | Distribution Circuit | Vegetation | Tree - fell into line | 662 | 308990 | 37.6978 | -120.1162 | MTR1006384740 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 19-0021738 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Three Phase Fault | 1415188 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022034&numberofmonths=24&showchangehistorylog=1 | 19-0022034 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | JUMPER | WIREDOWN2NWOFMTR1004898423 | 20190213 | 806 | 303130 | 469 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 469 | 38.0167 | -120.304 | 2NWOFMTR1004898423 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022034 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1415434 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022218&numberofmonths=24&showchangehistorylog=1 | 19-0022218 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MARIPOSA-2101 | 254452101 | FUSE | 10219 | 20190213 | 720 | 302991 | 2065 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 8478 | 37.4815 | -119.7777 | MTR1006384361TOEOL | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0022218 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Three Phase Fault | 1415552 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021739&numberofmonths=24&showchangehistorylog=1 | 19-0021739 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2102 | 254452102 | RECLOSER | 10250 | 20190213 | 205 | 301872 | 48 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 48 | 37.4632 | -119.9479 | BEYONDMETER | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 19-0021739 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Three Phase Fault | 1415189 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021776&numberofmonths=24&showchangehistorylog=1 | 19-0021776 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | RECLOSER | 953336 | 20190213 | 433 | 302650 | 558 | Distribution Circuit | Vegetation | Tree - fell into line | 360 | 147520 | 38.0681 | -120.1867 | MTR1010307147 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021776 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1415227 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021822&numberofmonths=24&showchangehistorylog=1 | 19-0021822 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | RECLOSER | 79118 | 20190213 | 632 | 302899 | 736 | Distribution Circuit | Vegetation | Tree - fell into line | 139 | 66400 | 38.0384 | -120.2274 | 1289 | Overcast-Heavy Rain-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0021822 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1415272 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022332&numberofmonths=24&showchangehistorylog=1 | 19-0022332 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1703 | 163761703 | JUMPER | WIREDOWN | 20190213 | 740 | 304757 | 465 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 930 | 38.0132 | -120.4055 | 21570SHAWSFLATRD | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022332 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1415630 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022980&numberofmonths=24&showchangehistorylog=1 | 19-0022980 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | BEAR VALLEY-2105 | 252192105 | FUSE | 23937 | 20190214 | 655 | 307259 | 6355 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 7441 | 37.7147 | -120.1143 | 1EOF23937 | Overcast-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0022980 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Three Phase Fault | 1416204 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023251&numberofmonths=24&showchangehistorylog=1 | 19-0023251 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | BEAR VALLEY-2105 | 252192105 | FUSE | 4629 | 20190214 | 1109 | 308494 | 1785 | Distribution Circuit | Vegetation | Tree - fell into line | 129 | 230265 | 37.7103 | -120.1113 | 25SPNOF4609 | Overcast-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0023251 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1416444 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023307&numberofmonths=24&showchangehistorylog=1 | 19-0023307 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | BEAR VALLEY-2105 | 252192105 | FUSE | 10714 | 20190214 | 1109 | 309451 | 3288 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 29592 | 37.7217 | -120.0946 | 3PLOADSIDEOF10714 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0023307 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1416490 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023274&numberofmonths=24&showchangehistorylog=1 | 19-0023274 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | BEAR VALLEY-2105 | 252192105 | RECLOSER | 9560 | 20190214 | 1231 | 309804 | 1663 | Distribution Circuit | Vegetation | Tree - fell into line | 520 | 172967 | 37.6978 | -120.1162 | MTR1006384750 | Overcast-Heavy Rain-Lightning-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023274 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416568 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023624&numberofmonths=24&showchangehistorylog=1 | 19-0023624 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | BEAR VALLEY-2105 | 252192105 | FUSE | 23943 | 20190214 | 1541 | 310011 | 1694 | Distribution Circuit | Vegetation | Tree - bark fell into line | 8 | 13552 | 37.7082 | -120.1137 | MTR1005642833 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023624 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416772 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024031&numberofmonths=24&showchangehistorylog=1 | 19-0024031 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | BEAR VALLEY-2105 | 252192105 | FUSE | 10268 | 20190214 | 1723 | 312097 | 4252 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 29764 | 37.7948 | -120.1788 | MTR1009698662 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024031 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1417137 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023307&numberofmonths=24&showchangehistorylog=1 | 19-0023307 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | BEAR VALLEY-2105 | 252192105 | FUSE | 23939 | 20190214 | 1109 | 312712 | 1918 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 5754 | 37.7126 | -120.1088 | IDLESINGLEPHASETAP | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023307 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1417297 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023285&numberofmonths=24&showchangehistorylog=1 | 19-0023285 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | COARSEGOLD-2102 | 254432102 | RECLOSER | 5380 | 20190214 | 1308 | 309344 | 4357 | Distribution Circuit | Vegetation | Tree - fell into line | 137 | 71879 | 37.3089 | -119.5849 | DAHLEM184755949384724PSOUTHOFCGC322621829752 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0023285 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Three Phase Fault | 1416472 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023104&numberofmonths=24&showchangehistorylog=1 | 19-0023104 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | COARSEGOLD-2104 | 254432104 | FUSE | 10275 | 20190214 | 1035 | 308712 | 203 | Distribution Circuit | Vegetation | Tree - bark fell into line | 123 | 24969 | 37.2901 | -119.6314 | CGC322541028770 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023104 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416374 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0022848&numberofmonths=24&showchangehistorylog=1 | 19-0022848 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | CURTIS-1703 | 163351703 | RECLOSER | 9240 | 20190214 | 628 | 307191 | 645 | Distribution Circuit | Vegetation | Tree - fell into line | 2474 | 654340 | 37.8315 | -120.2371 | MTR1004817694 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0022848 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Three Phase Fault | 1416093 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023182&numberofmonths=24&showchangehistorylog=1 | 19-0023182 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | RECLOSER | 9210 | 20190214 | 1205 | 308894 | 532 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 36708 | 37.8183 | -120.0961 | McCordBillfound2blownfusesdownwirereportedittotman | Overcast-Heavy Rain-Lightning-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023182 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1416372 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023349&numberofmonths=24&showchangehistorylog=1 | 19-0023349 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | FUSE | L2287 | 20190214 | 1302 | 309596 | 1763 | Distribution Circuit | Vegetation | Tree - fell into line | 98 | 172774 | 37.8458 | -120.201 | MTR10047177701004717778 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0023349 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Three Phase Fault | 1416515 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023182&numberofmonths=24&showchangehistorylog=1 | 19-0023182 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | SWITCH | S1215 | 20190214 | 1205 | 310867 | 3294 | Distribution Circuit | Vegetation | Tree - fell into line | 89 | 209390 | 37.825 | -119.9652 | McCordBillfound2blownfusesdownwirereportedittotman | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023182 | OH | Sus | 0 | yes | 2019 | FEB | Yes | None | 1416839 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023359&numberofmonths=24&showchangehistorylog=1 | 19-0023359 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1705 | 163781705 | FUSE | 20829 | 20190214 | 641 | 307244 | 912 | Distribution Circuit | Vegetation | Tree - branch fell on line | 101 | 68652 | 37.905 | -120.4125 | 1POLEEOF19482 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023359 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1416520 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0023399&numberofmonths=24&showchangehistorylog=1 | 19-0023399 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1705 | 163781705 | FUSE | 53401 | 20190214 | 1110 | 308497 | 588 | Distribution Circuit | Vegetation | Tree - bark fell into line | 22 | 12936 | 37.9655 | -120.402 | 9EOF53401 | Overcast-Heavy Rain-Lightning-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023399 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1416552 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024219&numberofmonths=24&showchangehistorylog=1 | 19-0024219 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | CURTIS-1703 | 163351703 | RECLOSER | 9330 | 20190215 | 1735 | 312723 | 1098 | Distribution Circuit | Vegetation | Tree - fell into line | 371 | 287294 | 37.8312 | -120.2369 | DANIELSJOHNBEYOND5651PRIMARYRISERPOLE23663 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 19-0024219 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1417299 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024219&numberofmonths=24&showchangehistorylog=1 | 19-0024219 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | SWITCH | 6323 | 20190215 | 1735 | 313231 | 1085 | Distribution Circuit | Vegetation | Tree - bark fell into line | 156 | 169260 | 37.8245 | -120.144 | 20991ANDBEYONDFUSE5651 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 19-0024219 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1417461 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024630&numberofmonths=24&showchangehistorylog=1 | 19-0024630 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | FUSE | 5651 | 20190215 | 1737 | 314639 | 2611 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 20888 | 37.8246 | -120.1426 | 20991 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 19-0024630 | OH | Sus | 0 | yes | 2019 | FEB | Yes | None | 1417701 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025144&numberofmonths=24&showchangehistorylog=1 | 19-0025144 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | JUMPER | DDE1PSOF20991 | 20190215 | 1737 | 315882 | 2903 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 14515 | 37.8265 | -120.1471 | NOFDDE1PSOF20991 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025144 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1418222 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025145&numberofmonths=24&showchangehistorylog=1 | 19-0025145 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | JUMPER | OJ1PN3PWOF5651 | 20190215 | 1737 | 315885 | 5663 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 11469 | 37.8257 | -120.1439 | NOFMTR1004857265 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025145 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1418223 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024204&numberofmonths=24&showchangehistorylog=1 | 19-0024204 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2102 | 254452102 | FUSE | 4553 | 20190215 | 1610 | 312565 | 206 | Distribution Circuit | Vegetation | Tree - fell into line | 95 | 19570 | 37.4215 | -119.9674 | TROUBLEIS31MILESSOF4553ONBENHURRD | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024204 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1417284 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024287&numberofmonths=24&showchangehistorylog=1 | 19-0024287 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1103 | 254421103 | RECLOSER | 5120 | 20190215 | 2042 | 312996 | 2338 | Distribution Circuit | Vegetation | Tree - fell into line | 669 | 1235032 | 37.4809 | -119.6372 | 1NOSW5459 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0024287 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1417369 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024690&numberofmonths=24&showchangehistorylog=1 | 19-0024690 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 2525 | 20190216 | 1424 | 314599 | 1685 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 21905 | 38.0594 | -120.2154 | MIDDLECAMPROADCONFIDECESOUTHFORK | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024690 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1417765 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024703&numberofmonths=24&showchangehistorylog=1 | 19-0024703 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 2481 | 20190216 | 1749 | 314878 | 140 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 7280 | 38.0327 | -120.2247 | 3PEOF2481 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0024703 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1417777 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024755&numberofmonths=24&showchangehistorylog=1 | 19-0024755 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 2523 | 20190216 | 1749 | 315045 | 2916 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2916 | 38.0592 | -120.2204 | MTR1004720824 | Overcast-Fog-Snow-Below 32 F | Crossarm, Wood | Broken, wire on ground | 19-0024755 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1417831 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025095&numberofmonths=24&showchangehistorylog=1 | 19-0025095 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | S2251 | 20190216 | 1807 | 314908 | 2847 | Distribution Circuit | Vegetation | Tree - fell into line | 355 | 805589 | 38.0355 | -120.2262 | MTR1004860617 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025095 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Three Phase Fault | 1418172 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025234&numberofmonths=24&showchangehistorylog=1 | 19-0025234 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | L2213 | 20190216 | 1657 | 315774 | 4117 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 32138 | 38.0199 | -120.2222 | 7POLESEOF20329 | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025234 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1418309 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024598&numberofmonths=24&showchangehistorylog=1 | 19-0024598 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1702 | 163661702 | RECLOSER | 8090 | 20190216 | 1353 | 314559 | 1664 | Distribution Circuit | Environmental/External | Ice or snow | 611 | 220748 | 38.0489 | -120.2345 | NOF20971 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024598 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1417674 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024698&numberofmonths=24&showchangehistorylog=1 | 19-0024698 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1702 | 163661702 | RECLOSER | 1808 | 20190216 | 1742 | 314873 | 3067 | Distribution Circuit | Vegetation | Tree - fell into line | 208 | 124801 | 38.0301 | -120.245 | MTR1010341159 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0024698 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1417771 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025060&numberofmonths=24&showchangehistorylog=1 | 19-0025060 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1702 | 163661702 | TRIP-SAVER | S2247 | 20190216 | 2119 | 315193 | 2609 | Distribution Circuit | Vegetation | Tree - fell into line | 194 | 152040 | 38.0369 | -120.2384 | 18468TATUAVEMTR1004211004 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025060 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1418136 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024467&numberofmonths=24&showchangehistorylog=1 | 19-0024467 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SAN JOAQUIN #3 PH-1101 | 252531101 | RECLOSER | 10060 | 20190216 | 1003 | 313840 | 481 | Distribution Circuit | Equipment Failure/Involved | Overhead | 109 | 11398 | 37.2927 | -119.5325 | MTR1005670791 | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024467 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1417553 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0024502&numberofmonths=24&showchangehistorylog=1 | 19-0024502 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SPRING GAP-1702 | 162831702 | RECLOSER | 9690 | 20190216 | 1055 | 313959 | 4412 | Distribution Circuit | Vegetation | Tree - fell into line | 687 | 201858 | 38.1885 | -120.0082 | SIUDZINSKIMARKLDSOFUCO2387BOYSCOUNTCAMPOFFJENNESSROAD | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0024502 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1417586 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025065&numberofmonths=24&showchangehistorylog=1 | 19-0025065 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 2481 | 20190217 | 453 | 315233 | 949 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 49348 | 38.0327 | -120.2247 | ROBINHOODDRKINGAUTHURCT | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025065 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1418140 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025122&numberofmonths=24&showchangehistorylog=1 | 19-0025122 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | OCB | 17012 | 20190217 | 1142 | 315741 | 391 | Distribution Circuit | Vegetation | Tree - fell into line | 3739 | 345369 | 38.0529 | -120.2172 | 4NOFS1409MTR1004209367 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025122 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1418202 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025202&numberofmonths=24&showchangehistorylog=1 | 19-0025202 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 851 | 20190217 | 1329 | 315995 | 2788 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 55760 | 38.0437 | -120.2085 | REAROF23223HWY108 | Overcast-Fog-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0025202 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1418280 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025313&numberofmonths=24&showchangehistorylog=1 | 19-0025313 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 2261 | 20190217 | 1809 | 316637 | 1521 | Distribution Circuit | Vegetation | Tree - fell into line | 186 | 89104 | 38.0594 | -120.1807 | MTR1004718021 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025313 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1418365 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025367&numberofmonths=24&showchangehistorylog=1 | 19-0025367 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 2525 | 20190217 | 1916 | 316743 | 1546 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 20098 | 38.0594 | -120.2154 | 1PSOF252523935CONFINDENCESOUTHFORKRD | Partly Cloudy-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025367 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1418423 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025206&numberofmonths=24&showchangehistorylog=1 | 19-0025206 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1702 | 163661702 | RECLOSER | 1808 | 20190217 | 1505 | 317521 | 2493 | Distribution Circuit | Vegetation | Tree - fell into line | 185 | 442429 | 38.0301 | -120.245 | WIREDOWNBETWEENLR1808ANDSTEPDOWNTWH2MTR1004857281MTR1004859778 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025206 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1418647 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025209&numberofmonths=24&showchangehistorylog=1 | 19-0025209 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1101 | 254421101 | FUSE | 5533 | 20190217 | 940 | 315503 | 1594 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 3188 | 37.4199 | -119.7116 | EOLBEYOND5533 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025209 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1418288 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028420&numberofmonths=24&showchangehistorylog=1 | 19-0028420 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1705 | 163781705 | FUSE | 53401 | 20190226 | 1336 | 324566 | 667 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 4831 | 37.9655 | -120.402 | MTR1004860342 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028420 | OH | Sus | 31426754 | yes | 2019 | FEB | Yes | Line to Line | 1420353 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0102785&numberofmonths=24&showchangehistorylog=1 | 19-0102785 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | FUSE | 1993 | 20190923 | 2304 | 608006 | 1208 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 24160 | 37.8233 | -120.1928 | BET13TH14THPOLELDSIDEOF1993 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0102785 | OH | Sus | 31473062 | yes | 2019 | SEP | Yes | Line to Line | 1472279 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0130133&numberofmonths=24&showchangehistorylog=1 | 19-0130133 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MARIPOSA-2101 | 254452101 | RECLOSER | 439030 | 20191127 | 947 | 720969 | 399 | Distribution Circuit | Equipment Failure/Involved | Overhead | 398 | 158802 | 37.4657 | -119.7562 | 2SPWOF69755 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0130133 | OH | Sus | 0 | yes | 2019 | NOV | Yes | Line to Ground | 1495023 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0130160&numberofmonths=24&showchangehistorylog=1 | 19-0130160 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MARIPOSA-2101 | 254452101 | FUSE | 19165 | 20191127 | 859 | 720816 | 684 | Distribution Circuit | Vegetation | Tree - bark fell into line | 3 | 2052 | 37.5124 | -119.9004 | 12SPAMLDSIDEOF19165 | Overcast-Fog-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 19-0130160 | OH | Sus | 0 | yes | 2019 | NOV | Yes | Line to Ground | 1495039 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0130432&numberofmonths=24&showchangehistorylog=1 | 19-0130432 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2101 | 254452101 | TRANSFORMER | 321690936488 | 20191127 | 829 | 721762 | 605 | Distribution Circuit | Vegetation | Tree - bark fell into line | 1 | 605 | 37.5006 | -119.919 | 5666BLACKBERRYCREEKRD | Snow-Overcast-Fog-32-90 F | Transformer | Broken, wire on ground | 19-0130432 | OH | Sus | 0 | yes | 2019 | NOV | Yes | Line to Ground | 1495204 | TX | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0129973&numberofmonths=24&showchangehistorylog=1 | 19-0129973 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2102 | 254452102 | OTHER | WIREDOWN1SEOF42875 | 20191127 | 207 | 720359 | 927 | Distribution Circuit | Vegetation | Tree - fell into line | 515 | 94402 | 37.5056 | -119.8436 | 1SEOF42875 | Overcast-Fog-32-90 F | Pole-Wood | Broken, wire on ground | 19-0129973 | OH | Sus | 0 | yes | 2019 | NOV | Yes | Open Circuit | 1494930 | PW | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0018918&numberofmonths=24&showchangehistorylog=1 | 20-0018918 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | SAN JOAQUIN #3 PH-1103 | 252531103 | FUSE | 6095 | 20200209 | 716 | 781175 | 608 | Distribution Circuit | Vegetation | Tree - fell into line | 96 | 58368 | 37.2381 | -119.519 | 1SPLDSIDEOF60951SPSSMTR1005674792 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0018918 | OH | Sus | 44182951 | yes | 2020 | FEB | Yes | Line to Line | 1512959 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0032283&numberofmonths=24&showchangehistorylog=1 | 20-0032283 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SPRING GAP-1702 | 162831702 | RECLOSER | 9690 | 20200315 | 1046 | 852234 | 501 | Distribution Circuit | Vegetation | Tree - fell into line | 687 | 344187 | 38.1885 | -120.0082 | 15SPLDSIDEOF5955 | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0032283 | OH | Sus | 0 | yes | 2020 | MAR | Yes | Line to Ground | 1521614 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0032980&numberofmonths=24&showchangehistorylog=1 | 20-0032980 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | CURTIS-1702 | 163351702 | FUSE | 19526 | 20200316 | 1401 | 855544 | 221 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 8840 | 37.9718 | -120.2261 | 2NOFMTR1004862126 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0032980 | OH | Sus | 0 | yes | 2020 | MAR | Yes | None | 1522118 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0032792&numberofmonths=24&showchangehistorylog=1 | 20-0032792 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | CURTIS-1704 | 163351704 | FUSE | 20809 | 20200316 | 1058 | 854413 | 384 | Distribution Circuit | Vegetation | Tree - branch fell on line | 50 | 19200 | 38.0332 | -120.3676 | MTR1004860989 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0032792 | OH | Sus | 0 | yes | 2020 | MAR | Yes | Line to Line | 1522035 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0033119&numberofmonths=24&showchangehistorylog=1 | 20-0033119 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2101 | 254452101 | FUSE | 10302 | 20200316 | 2316 | 856114 | 1226 | Distribution Circuit | Vegetation | Tree - fell into line | 148 | 141152 | 37.5067 | -119.8246 | MARTINBLAIR55947452965899GLACIERPOINT | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 20-0033119 | OH | Sus | 0 | yes | 2020 | MAR | Yes | Line to Line | 1522265 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0033114&numberofmonths=24&showchangehistorylog=1 | 20-0033114 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1103 | 254421103 | FUSE | 10204 | 20200316 | 2326 | 856117 | 1174 | Distribution Circuit | Environmental/External | Ice or snow | 19 | 8698 | 37.4771 | -119.6427 | MTR1005963411 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 20-0033114 | OH | Sus | 31497454 | yes | 2020 | MAR | Yes | Line to Ground | 1522259 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0032871&numberofmonths=24&showchangehistorylog=1 | 20-0032871 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1703 | 163761703 | FUSE | 2443 | 20200316 | 1222 | 855076 | 411 | Distribution Circuit | Vegetation | Tree - branch fell on line | 117 | 48087 | 38.0312 | -120.4258 | 1POLEWESTOFMTR1006424179 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0032871 | OH | Sus | 0 | yes | 2020 | MAR | Yes | Line to Ground | 1522072 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0010698&numberofmonths=24&showchangehistorylog=1 | 21-0010698 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | INDIAN FLAT-1104 | 252691104 | OTHER | WIREDOWN1211YOSEMITEWAY | 20210119 | 612 | 1215499 | 780 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 61 | 38155 | 37.6993 | -119.7531 | 1211YOSEMITEWAYYOSEMITENATIONALPARK | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 21-0010698 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1594590 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0010175&numberofmonths=24&showchangehistorylog=1 | 21-0010175 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 22618 | 20210119 | 406 | 1217697 | 942 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 27318 | 38.0514 | -120.2135 | LDSIDEOF22618 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0010175 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1594804 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0010941&numberofmonths=24&showchangehistorylog=1 | 21-0010941 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | OAKHURST-1101 | 254421101 | JUMPER | OJ2POLESSOF5422 | 20210119 | 912 | 1217448 | 469 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 3094 | 37.359 | -119.7259 | 2POLESSOF5422l1POLESOF5422 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0010941 | OH | Sus | 0 | No | 2021 | JAN | Yes | Open Circuit | 1594752 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0013806&numberofmonths=24&showchangehistorylog=1 | 21-0013806 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | FUSE | S1795 | 20210125 | 814 | 1224186 | 508 | Distribution Circuit | Equipment Failure/Involved | Overhead | 185 | 93980 | 37.9553 | -120.2445 | 1SOURCESIDEOFCGC320724552840 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 21-0013806 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1596733 | CSO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0013596&numberofmonths=24&showchangehistorylog=1 | 21-0013596 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | FUSE | 21665 | 20210125 | 243 | 1223111 | 867 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 53754 | 37.8173 | -120.1285 | POLEATFUCO2181 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0013596 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Line | 1596585 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0013719&numberofmonths=24&showchangehistorylog=1 | 21-0013719 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1704 | 163351704 | FUSE | 6825 | 20210125 | 354 | 1223872 | 624 | Distribution Circuit | Equipment Failure/Involved | Overhead | 149 | 92976 | 37.9903 | -120.3341 | LDSIDEOFMTR101052276510564MTBROWRD | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 21-0013719 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1596663 | CSO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0013688&numberofmonths=24&showchangehistorylog=1 | 21-0013688 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1705 | 163351705 | FUSE | L1773 | 20210125 | 351 | 1223284 | 435 | Distribution Circuit | Equipment Failure/Involved | Overhead | 261 | 90068 | 37.9586 | -120.3217 | 1SPLDSIDEOFL1773 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 21-0013688 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1596637 | CSO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0013585&numberofmonths=24&showchangehistorylog=1 | 21-0013585 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1703 | 163761703 | RECLOSER | 6014 | 20210125 | 341 | 1223279 | 102 | Distribution Circuit | Vegetation | Tree - branch fell on line | 446 | 45492 | 38.0048 | -120.4064 | 1SPANFROMCGC320241755012 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0013585 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1596574 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0013937&numberofmonths=24&showchangehistorylog=1 | 21-0013937 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | JUMPER | WIREDOWN1WOF19102 | 20210125 | 18 | 1224516 | 1082 | Distribution Circuit | Vegetation | Tree - branch fell on line | 247 | 35745 | 37.2226 | -119.5506 | SPANWOFFUSE19102EOFMAINLINE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0013937 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1596822 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0017155&numberofmonths=24&showchangehistorylog=1 | 21-0017155 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | COARSEGOLD-2102 | 254432102 | FUSE | 10022 | 20210128 | 116 | 1238248 | 824 | Distribution Circuit | Vegetation | Tree - fell into line | 75 | 61800 | 37.3041 | -119.6009 | CGC322597529160 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0017155 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Line | 1599457 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0137086&numberofmonths=24&showchangehistorylog=1 | 21-0137086 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1705 | 163351705 | FUSE | 19463 | 20211025 | 119 | 1516277 | 1214 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 4856 | 37.9743 | -120.3019 | CGC320575553670 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0137086 | OH | Sus | 0 | No | 2021 | OCT | Yes | Multi-Fault | 1678536 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0136851&numberofmonths=24&showchangehistorylog=1 | 21-0136851 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1103 | 254421103 | OTHER | WIREDOWN3SSOFCGC100000037108 | 20211025 | 116 | 1516833 | 621 | Distribution Circuit | Vegetation | Tree - fell into line | 91 | 56511 | 8e-05 | -127.4887 | CGC1000000371083SPANSSSOFCGC100000037108 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0136851 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Ground | 1678349 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0136865&numberofmonths=24&showchangehistorylog=1 | 21-0136865 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1103 | 254421103 | RECLOSER | 10190 | 20211025 | 419 | 1516886 | 687 | Distribution Circuit | Vegetation | Tree - fell into line | 726 | 259365 | 37.4145 | -119.6272 | 10354 | Clear-32-90 F | Crossarm, Wood | Broken, wire on object | 21-0136865 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Ground | 1678363 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0157884&numberofmonths=24&showchangehistorylog=1 | 21-0157884 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | FUSE | 2093 | 20211214 | 523 | 1569737 | 635 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 46990 | 38.0336 | -120.326 | 1SPANSOFMTR1004860019 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0157884 | OH | Sus | 0 | No | 2021 | DEC | Yes | Three Phase Fault | 1694795 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0158125&numberofmonths=24&showchangehistorylog=1 | 21-0158125 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | FUSE | 56337 | 20211214 | 540 | 1569722 | 717 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 4199 | 37.9524 | -120.2366 | 1SPANWOFCGC320767352881 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0158125 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1695042 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0160737&numberofmonths=24&showchangehistorylog=1 | 21-0160737 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | OAKHURST-1103 | 254421103 | OTHER | 322485738261 | 20211226 | 453 | 1582365 | 493 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 20809 | 37.5488 | -119.6437 | BEBOUTROB188255967613252POLESNOCO5728 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0160737 | OH | Sus | 0 | No | 2021 | DEC | Yes | Open Circuit | 1698227 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0161276&numberofmonths=24&showchangehistorylog=1 | 21-0161276 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2102 | 254452102 | FUSE | 10519 | 20211227 | 2141 | 1586360 | 981 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 29187 | 37.4722 | -119.88 | 1PLDSIDEOFCGC321776935914 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0161276 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1698883 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0161101&numberofmonths=24&showchangehistorylog=1 | 21-0161101 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | OAKHURST-1103 | 254421103 | FUSE | 10247 | 20211227 | 1048 | 1585627 | 259 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 14245 | 37.541 | -119.6476 | 5576 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0161101 | OH | Sus | 0 | No | 2021 | DEC | Yes | Force Out | 1698669 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0161015&numberofmonths=24&showchangehistorylog=1 | 21-0161015 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1703 | 163761703 | FUSE | 26389 | 20211227 | 720 | 1584778 | 633 | Distribution Circuit | Vegetation | Tree - fell into line | 464 | 189292 | 37.9879 | -120.3884 | GRIMESCURTIS2096175264iro20936ShawsFlatRd | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 21-0161015 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1698554 | CAW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0161145&numberofmonths=24&showchangehistorylog=1 | 21-0161145 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | SAN JOAQUIN #3 PH-1103 | 252531103 | OTHER | 10385 | 20211227 | 1454 | 1585940 | 113 | Distribution Circuit | Vegetation | Tree - branch fell on line | 212 | 23956 | 37.2352 | -119.5101 | 2SPANSSOF1SPANNOFCGC322880626891 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0161145 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1698722 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0006974&numberofmonths=24&showchangehistorylog=1 | 23-0006974 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | BEAR VALLEY-2105 | 252192105 | FUSE | 43781 | 20230105 | 151 | 1920312 | 653 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1959 | 37.7482 | -120.1352 | CGC321059645378 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0006974 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1797277 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0007187&numberofmonths=24&showchangehistorylog=1 | 23-0007187 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MARIPOSA-2102 | 254452102 | FUSE | 10317 | 20230105 | 653 | 1920796 | 787 | Distribution Circuit | Vegetation | Tree - fell into line | 64 | 21458 | 37.4653 | -119.7357 | 2LDSIDEOFCGC322239735249 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 23-0007187 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1797467 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0008760&numberofmonths=24&showchangehistorylog=1 | 23-0008760 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2103 | 254432103 | FUSE | 10217 | 20230107 | 1013 | 1926319 | 296 | Distribution Circuit | Equipment Failure/Involved | Overhead | 96 | 12936 | 37.184 | -119.7662 | CGC322142425030 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 23-0008760 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Line | 1798636 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0010835&numberofmonths=24&showchangehistorylog=1 | 23-0010835 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | BEAR VALLEY-2105 | 252192105 | RECLOSER | 13430 | 20230109 | 540 | 1935901 | 600 | Distribution Circuit | Vegetation | Tree - fell into line | 129 | 77400 | 37.7499 | -120.1362 | 1SPSSOF7277ONMAINLINE | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0010835 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Line | 1800691 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0011139&numberofmonths=24&showchangehistorylog=1 | 23-0011139 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE | 10788 | 20230109 | 1030 | 1937640 | 266 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 20482 | 37.2869 | -119.6558 | 49135SHADOWCREEKRD | Clear-32-90F | Conductor, Overhead | On Ground | 23-0011139 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Line | 1800947 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0011883&numberofmonths=24&showchangehistorylog=1 | 23-0011883 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | COARSEGOLD-2102 | 254432102 | RECLOSER | 10040 | 20230110 | 437 | 1942284 | 844 | Distribution Circuit | Equipment Failure/Involved | Overhead | 425 | 209316 | 37.3104 | -119.5846 | CGC322559529595 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0011883 | OH | Sus | 0 | No | 2023 | JAN | Yes | Three Phase Fault | 1801650 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0011949&numberofmonths=24&showchangehistorylog=1 | 23-0011949 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2104 | 254432104 | RECLOSER | 10110 | 20230110 | 616 | 1942993 | 3448 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1068 | 108166 | 37.267 | -119.7114 | CGC322451228612 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 23-0011949 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1801727 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0011897&numberofmonths=24&showchangehistorylog=1 | 23-0011897 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1705 | 163351705 | RECLOSER | 65908 | 20230110 | 444 | 1942407 | 887 | Distribution Circuit | Vegetation | Tree - fell into line | 673 | 219896 | 37.9574 | -120.3132 | HEADINGSTHOMAS5593955674SWITCH96519 | Overcast-Fog-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0011897 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1801666 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0011902&numberofmonths=24&showchangehistorylog=1 | 23-0011902 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1702 | 163661702 | RECLOSER | 8130 | 20230110 | 447 | 1942567 | 2198 | Distribution Circuit | Vegetation | Tree - fell into line | 431 | 297449 | 38.0278 | -120.2567 | 2SPLDSIDEOF20345 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0011902 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Line | 1801672 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0011898&numberofmonths=24&showchangehistorylog=1 | 23-0011898 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1702 | 163661702 | FUSE | 6821 | 20230110 | 446 | 1944475 | 835 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 35905 | 38.0554 | -120.2748 | SIUDZINSKIMARK180623461packtrail | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0011898 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1801957 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0011937&numberofmonths=24&showchangehistorylog=1 | 23-0011937 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1103 | 254421103 | RECLOSER | 77384 | 20230110 | 558 | 1944321 | 651 | Distribution Circuit | Vegetation | Tree - fell into line | 468 | 168550 | 37.3391 | -119.585 | BET6723955079MAINLINE | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0011937 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1801920 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0017281&numberofmonths=24&showchangehistorylog=1 | 23-0017281 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | S2251 | 20230116 | 1159 | 1957937 | 321 | Distribution Circuit | Vegetation | Tree - fell into line | 362 | 81552 | 38.0355 | -120.2262 | 2SWOFCGC320778855815 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0017281 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Line | 1805960 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0017056&numberofmonths=24&showchangehistorylog=1 | 23-0017056 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SPRING GAP-1702 | 162831702 | RECLOSER | 693441 | 20230116 | 906 | 1957423 | 630 | Distribution Circuit | Vegetation | Tree - fell into line | 491 | 200052 | 38.1877 | -120.0025 | 1POLEEOFCGC321458761475 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0017056 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Line | 1805756 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0030517&numberofmonths=24&showchangehistorylog=1 | 23-0030517 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | COARSEGOLD-2102 | 254432102 | RECLOSER | 10050 | 20230219 | 300 | 1988470 | 566 | Distribution Circuit | 3rd Party | Gun Shot | 2323 | 807587 | 37.3104 | -119.5845 | DAHLEMJUSTIN184740203rd222 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0030517 | OH | Sus | 45679421 | No | 2023 | FEB | Yes | Multi-Fault | 1814255 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0031430&numberofmonths=24&showchangehistorylog=1 | 23-0031430 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1701 | 163781701 | OCB | 17012 | 20230221 | 1557 | 1992869 | 346 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1921 | 539322 | 37.9035 | -120.497 | MITCHELLJEREMY1713Simsrd3polesnorthofhwy120 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0031430 | OH | Sus | 0 | No | 2023 | FEB | Yes | Multi-Fault | 1815064 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0034447&numberofmonths=24&showchangehistorylog=1 | 23-0034447 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2102 | 254452102 | FUSE | 10373 | 20230224 | 1520 | 2005969 | 304 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 6080 | 37.4783 | -119.8689 | 2SPANSNOFCGC321866135583 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0034447 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Line | 1817300 | CO | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0036222&numberofmonths=24&showchangehistorylog=1 | 23-0036222 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 2481 | 20230227 | 802 | 2011317 | 717 | Distribution Circuit | Equipment Failure/Involved | Overhead | 54 | 38718 | 38.0325 | -120.2248 | ATCGC320806055829l1POLENOFCGC320806055829l2POLESSOFCGC320806055829 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 23-0036222 | OH | Sus | 0 | No | 2023 | FEB | Yes | Three Phase Fault | 1818947 | PW | OH | Yes | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0037206&numberofmonths=24&showchangehistorylog=1 | 23-0037206 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1705 | 163351705 | FUSE | 19515 | 20230228 | 712 | 2014844 | 410 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 15580 | 37.9969 | -120.2396 | 2SPANSSOUTHCGC320753554990 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 23-0037206 | OH | Sus | 0 | No | 2023 | FEB | Yes | Force Out | 1819679 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0041906&numberofmonths=24&showchangehistorylog=1 | 23-0041906 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1103 | 254421103 | FUSE | 10753 | 20230309 | 54 | 2027145 | 585 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 19890 | 37.3669 | -119.6576 | CGC322482031880 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0041906 | OH | Sus | 0 | No | 2023 | MAR | Yes | Force Out | 1823044 | CO | OH | Yes | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0049375&numberofmonths=24&showchangehistorylog=1 | 23-0049375 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MARIPOSA-2101 | 254452101 | FUSE | 10498 | 20230321 | 1045 | 2054004 | 459 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 19278 | 37.4644 | -119.7603 | 2ND3RD4TH5TH6THSPANSSOF10498 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0049375 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Line | 1828159 | CO | OH | Yes | No

## Metric 3.01
Metric 3.01: Wires Down MEDs (Distribution)
Definition | (# Events/HFTD Circuit Miles (D))*1000
2022 HFTD Circuit Miles (D) | 25270.5
2023 HFTD Circuit Miles (D) | 25059.94
2023 Target | 66.02
Year | WD Events | WD Events/1,000 Miles
2013 | 131 | 5.1839
2014 | 443 | 17.5303
2015 | 389 | 15.3934
2016 | 181 | 7.1625
2017 | 1739 | 68.8154
2018 | 116 | 4.5903
2019 | 1405 | 55.5984
2020 | 130 | 5.1443
2021 | 277 | 10.9614
2022 | 43 | 1.7016
2023 (YTD - June) | 257 | 10.2554
|  | 23.4052 | STD
|  | 19.2082 | Average
|  | 42.6134 | 1 STD
|  | 66.0186 | 2 STD

## HFTD WD MED Summary
HFTD WIRE-DOWN OUTAGE DETAILS (2013 - Jun 2023)
DISTRIBUTION CIRCUIT & TRANSFORMER-ONLY OUTAGES
(2.5b ME Days Only)
System | Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
SYSTEM | 2013 | 0 | 0 | 0 | 40 | 0 | 1 | 0 | 0 | 0 | 0 | 90 | 0 | 131
SYSTEM | 2014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 441 | 443
SYSTEM | 2015 | 0 | 285 | 0 | 1 | 0 | 5 | 7 | 0 | 0 | 2 | 0 | 89 | 389
SYSTEM | 2016 | 0 | 49 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 181
SYSTEM | 2017 | 939 | 486 | 0 | 112 | 0 | 2 | 0 | 0 | 12 | 139 | 0 | 49 | 1739
SYSTEM | 2018 | 0 | 0 | 55 | 0 | 0 | 0 | 8 | 0 | 0 | 5 | 48 | 0 | 116
SYSTEM | 2019 | 329 | 1022 | 0 | 0 | 0 | 11 | 0 | 1 | 5 | 15 | 22 | 0 | 1405
SYSTEM | 2020 | 60 | 19 | 22 | 0 | 0 | 0 | 0 | 24 | 4 | 1 | 0 | 0 | 130
SYSTEM | 2021 | 134 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 2 | 58 | 0 | 79 | 277
SYSTEM | 2022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 39 | 43
SYSTEM | 2023 | 143 | 71 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 257
System | Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
10-Year Averages (2013-2022) | Count of Events | 146.2 | 186.1 | 19.7 | 15.3 | 0 | 1.9 | 1.5 | 3.1 | 2.7 | 23.2 | 16 | 69.7 | 485.4
| Monthly Percentage | 30.12% | 38.34% | 4.059% | 3.152% | 0% | 0.3914% | 0.309% | 0.6386% | 0.5562% | 4.78% | 3.296% | 14.36% | 100%
System | Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Targets | 2023 | 19.8849 | 25.3117 | 2.6794 | 2.081 | 0 | 0.25842 | 0.20402 | 0.42164 | 0.36723 | 3.1555 | 2.1762 | 9.48 | 66.02
System | Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Events | 2023 | 143 | 71 | 43 | 0 | 0 | 0 | [6 empty] | 257
Monthly Metric | 2023 | 5.7063 | 2.8332 | 1.7159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.2554
YTD Metric | 2023 | 5.7063 | 8.5395 | 10.2554 | 10.2554 | 10.2554 | 10.2554 | 10.2554 | 10.2554 | 10.2554 | 10.2554 | 10.2554 | 10.2554

## OH Dlines in HFTD
Source: Extracted from EDGIS as of 1/1/2023.
CIRCUITNAME | CIRCUITID | TOTALMILES | T3MILES | T2MILES | Z1MILES | T1MILES
2101 | 259932101 | 12.23 |  | 3.79 | 0.49 | 7.95
18TH STREET 0401 | 22390401 | 1.27 |  |  |  | 1.27
18TH STREET 0402 | 22390402 | 1.82 |  |  |  | 1.82
21ST AVENUE 0401 | 22550401 | 1.89 |  |  |  | 1.89
21ST AVENUE 0402 | 22550402 | 3.27 |  |  |  | 3.27
21ST AVENUE 0403 | 22550403 | 1.84 |  |  |  | 1.84
6TH AVENUE 0401 | 22530401 | 1.27 |  |  |  | 1.27
6TH AVENUE 0402 | 22530402 | 1.22 |  |  |  | 1.22
6TH AVENUE 0403 | 22530403 | 1.78 |  |  |  | 1.78
7TH STANDARD 2101 | 254582101 | 2.56 |  |  |  | 2.56
7TH STANDARD 2102 | 254582102 | 13.3 |  |  |  | 13.3
7TH STANDARD 2103 | 254582103 | 22.46 |  |  |  | 22.46
7TH STANDARD 2104 | 254582104 | 0.04 |  |  |  | 0.04
8TH AVENUE 0401 | 12670401 | 4.89 |  |  |  | 4.89
ACTON 0401 | 22470401 | 3.87 |  |  |  | 3.87
ACTON 0402 | 22470402 | 4.44 |  |  |  | 4.44
AIRWAYS 1101 | 252041101 | 1.48 |  |  |  | 1.48
AIRWAYS 1102 | 252041102 | 7.65 |  |  |  | 7.65
AIRWAYS 1103 | 252041103 | 7.65 |  |  |  | 7.65
AIRWAYS 1104 | 252041104 | 2 |  |  |  | 2
AIRWAYS 1105 | 252041105 | 1.35 |  |  |  | 1.35
AIRWAYS 1106 | 252041106 | 8.18 |  |  |  | 8.18
AIRWAYS 1107 | 252041107 | 43.6 |  |  |  | 43.6
AIRWAYS 1108 | 252041108 | 11.64 |  |  |  | 11.64
ALHAMBRA 1101 | 14101101 | 8.4 |  |  |  | 8.4
ALHAMBRA 1102 | 14101102 | 14.11 |  | 0.13 |  | 13.98
ALHAMBRA 1105 | 14101105 | 45.1 | 0.85 | 36.9 |  | 7.35
ALLEGHANY 1101 | 152101101 | 77.01 | 32.35 | 27.11 | 7.07 | 10.48
ALLEGHANY 1102 | 152101102 | 17.69 | 17.69 |  |  | 0
ALMADEN 1101 | 82311101 | 18.33 |  |  |  | 18.33
ALMADEN 1102 | 82311102 | 21.83 |  |  |  | 21.83
ALMADEN 1110 | 82311110 | 8.45 |  |  |  | 8.45
ALMADEN 1111 | 82311111 | 9.78 |  |  |  | 9.78
ALPAUGH 1103 | 254001103 | 26.94 |  |  |  | 26.94
ALPAUGH 1104 | 254001104 | 55.72 |  |  |  | 55.72
ALPAUGH 1106 | 254001106 | 52.45 |  |  |  | 52.45
ALPINE 1101 | 163561101 | 0.87 |  |  |  | 0.87
ALTO 1120 | 42031120 | 20.38 |  | 3.9 |  | 16.48
ALTO 1121 | 42031121 | 16.46 |  |  | 0.34 | 16.12
ALTO 1122 | 42031122 | 22.26 | 9.14 | 3.65 | 0.18 | 9.29
ALTO 1123 | 42031123 | 10.32 |  | 0.47 |  | 9.85
ALTO 1124 | 42031124 | 35 | 27.96 |  |  | 7.04
ALTO 1125 | 42031125 | 44.79 | 26.36 | 10.96 |  | 7.47
AMES 1101 | 83901101 | 0.12 |  |  |  | 0.12
AMES 1102 | 83901102 | 3.29 |  |  |  | 3.29
ANDERSON 1101 | 103261101 | 19.91 |  | 11.03 |  | 8.88
ANDERSON 1102 | 103261102 | 3.75 |  |  |  | 3.75
ANDERSON 1103 | 103261103 | 31.66 |  | 7.13 |  | 24.53
ANGIOLA 1102 | 252151102 | 35.82 |  |  |  | 35.82
ANGIOLA 1103 | 252151103 | 46.05 |  |  |  | 46.05
ANGIOLA 1104 | 252151104 | 19.61 |  |  |  | 19.61
ANITA 1101 | 102841101 | 34.47 |  |  |  | 34.47
ANITA 1102 | 102841102 | 34.8 |  |  |  | 34.8
ANITA 1105 | 102841105 | 16.84 |  |  |  | 16.84
ANITA 1106 | 102841106 | 90.29 |  | 0.48 |  | 89.81
ANNAPOLIS 1101 | 42861101 | 51 |  | 51 |  | 0
ANTELOPE 1101 | 252021101 | 39.88 |  | 0.92 |  | 38.96
ANTELOPE 1102 | 252021102 | 25.34 |  |  |  | 25.34
ANTLER 1101 | 103271101 | 61.21 | 8.17 | 51.94 |  | 1.1
APPLE HILL 1103 | 153661103 | 59.82 | 14.77 | 35.12 |  | 9.93
APPLE HILL 1104 | 153661104 | 95.48 | 55.35 | 35.42 |  | 4.71
APPLE HILL 2102 | 153662102 | 364.72 | 123.52 | 228.47 |  | 12.73
ARANA 0401 | 83010401 | 3.49 |  |  |  | 3.49
ARANA 0402 | 83010402 | 2.98 |  |  |  | 2.98
ARBUCKLE 1101 | 62081101 | 42.78 |  |  |  | 42.78
ARBUCKLE 1102 | 62081102 | 62.84 |  |  |  | 62.84
ARBUCKLE 1103 | 62081103 | 0.04 |  |  |  | 0.04
ARBUCKLE 1104 | 62081104 | 94.76 |  | 1.92 |  | 92.84
ARCATA 1105 | 192021105 | 43.95 |  |  |  | 43.95
ARCATA 1106 | 192021106 | 10.16 |  |  |  | 10.16
ARCATA 1121 | 192021121 | 28.95 |  | 6.84 |  | 22.11
ARCATA 1122 | 192021122 | 68.05 |  | 20.44 |  | 47.61
ARCATA 1123 | 192021123 | 5.97 |  |  |  | 5.97
ARCATA 1124 | 192021124 | 0 |  |  |  | 0
ARLINGTON 0401 | 13700401 | 4.17 |  | 0.94 |  | 3.23
ARVIN 1101 | 253801101 | 30.09 |  | 0.1 |  | 29.99
ARVIN 1102 | 253801102 | 17.87 |  |  |  | 17.87
ARVIN 1103 | 253801103 | 20.6 |  |  |  | 20.6
ASHLAN AVE 1102 | 252051102 | 13.21 |  |  |  | 13.21
ASHLAN AVE 1103 | 252051103 | 9.29 |  |  |  | 9.29
ASHLAN AVE 1104 | 252051104 | 14.01 |  |  |  | 14.01
ASHLAN AVE 1106 | 252051106 | 16.98 |  |  |  | 16.98
ASHLAN AVE 1107 | 252051107 | 8.32 |  |  |  | 8.32
ASHLAN AVE 1108 | 252051108 | 11.18 |  |  |  | 11.18
ASHLAN AVE 1109 | 252051109 | 15.66 |  |  |  | 15.66
ASHLAN AVE 1111 | 252051111 | 6.76 |  |  |  | 6.76
ASHLAN AVE 1112 | 252051112 | 9.52 |  |  |  | 9.52
ASHLAN AVE 1113 | 252051113 | 9.82 |  |  |  | 9.82
ASHLAN AVE 1114 | 252051114 | 8.36 |  |  |  | 8.36
ASHLAN AVE 1116 | 252051116 | 19.06 |  |  |  | 19.06
ASHLAN AVE 2101 | 252052101 | 2.23 |  |  |  | 2.23
ASHLAN AVE 2105 | 252052105 | 16.39 |  |  |  | 16.39
ASHLAN AVE 2110 | 252052110 | 6.72 |  |  |  | 6.72
ASHLAN AVE 2115 | 252052115 | 5.51 |  |  |  | 5.51
ASHLAN AVE 2117 | 252052117 | 1.88 |  |  |  | 1.88
ASHLAN AVE 2118 | 252052118 | 9.56 |  |  |  | 9.56
ASHLAN AVE 2119 | 252052119 | 14.08 |  |  |  | 14.08
ATASCADERO 1101 | 182541101 | 62.26 | 13.74 | 32.02 |  | 16.5
ATASCADERO 1102 | 182541102 | 17.38 |  | 3.4 |  | 13.98
ATASCADERO 1103 | 182541103 | 127.77 | 37.11 | 55.99 |  | 34.67
ATWATER 1102 | 253611102 | 84.23 |  |  |  | 84.23
ATWATER 1103 | 253611103 | 23.19 |  |  |  | 23.19
ATWATER 1104 | 253611104 | 12.89 |  |  |  | 12.89
ATWATER 1105 | 253611105 | 6.8 |  |  |  | 6.8
ATWATER 1106 | 253611106 | 36.74 |  |  |  | 36.74
ATWATER 1107 | 253611107 | 30.58 |  |  |  | 30.58
ATWATER 1108 | 253611108 | 61.07 |  |  |  | 61.07
AUBERRY 1101 | 254151101 | 241.34 | 32.07 | 206.96 |  | 2.31
AUBERRY 1102 | 254151102 | 129.03 |  | 129.03 |  | 0
AUBURN 1101 | 152161101 | 4.92 |  | 3.14 |  | 1.78
AUBURN 1102 | 152161102 | 8.96 |  | 2.98 |  | 5.98
AVENA 1701 | 163571701 | 90.74 |  |  |  | 90.74
AVENA 1702 | 163571702 | 80.23 |  |  |  | 80.23
AVENAL 2101 | 255002101 | 63.31 |  |  |  | 63.31
AVENAL 2102 | 255002102 | 2.46 |  |  |  | 2.46
AVENAL 2103 | 255002103 | 2.45 |  |  |  | 2.45
BABEL 0401 | 13850401 | 3.08 |  |  |  | 3.08
BAHIA 1101 | 43251101 | 3.06 |  |  |  | 3.06
BAHIA 1102 | 43251102 | 14.2 |  |  |  | 14.2
BAHIA 1103 | 43251103 | 11.04 |  |  |  | 11.04
BAHIA 1104 | 43251104 | 18.33 |  |  |  | 18.33
BAHIA 1105 | 43251105 | 13.99 |  |  |  | 13.99
BAIR 1103 | 24261103 | 0.53 |  |  |  | 0.53
BAIR 1105 | 24261105 | 2.15 |  |  |  | 2.15
BAKERSFIELD 1101 | 253371101 | 7.45 |  |  |  | 7.45
BAKERSFIELD 1102 | 253371102 | 17.62 |  |  |  | 17.62
BAKERSFIELD 1105 | 253371105 | 6.46 |  |  |  | 6.46
BAKERSFIELD 1106 | 253371106 | 11.77 |  |  |  | 11.77
BAKERSFIELD 1107 | 253371107 | 3.68 |  |  |  | 3.68
BAKERSFIELD 1110 | 253371110 | 5.95 |  |  |  | 5.95
BAKERSFIELD 1114 | 253371114 | 15.73 |  |  |  | 15.73
BAKERSFIELD 1115 | 253371115 | 5.68 |  |  |  | 5.68
BAKERSFIELD 1116 | 253371116 | 16.76 |  |  |  | 16.76
BAKERSFIELD 1118 | 253371118 | 11.39 |  |  |  | 11.39
BAKERSFIELD 2104 | 253372104 | 34.92 |  |  |  | 34.92
BAKERSFIELD 2106 | 253372106 | 31.5 |  |  |  | 31.5
BAKERSFIELD 2107 | 253372107 | 0.01 |  |  |  | 0.01
BAKERSFIELD 2109 | 253372109 | 32.08 |  |  |  | 32.08
BALCH NO 1 1101 | 252501101 | 14.65 |  | 14.65 |  | 0
BALFOUR 1101 | 14321101 | 49.93 |  |  |  | 49.93
BANCROFT 0401 | 13030401 | 8.41 |  | 0 |  | 8.41
BANCROFT 0402 | 13030402 | 4.59 |  | 0.12 |  | 4.47
BANGOR 1101 | 103191101 | 198 | 1.73 | 188.06 |  | 8.21
BANTA 1101 | 162471101 | 32.94 |  |  |  | 32.94
BANTA 1102 | 162471102 | 15.2 |  |  |  | 15.2
BANTA 1103 | 162471103 | 60.59 |  |  |  | 60.59
BARRETT 0401 | 13020401 | 6.59 |  |  |  | 6.59
BARRETT 0402 | 13020402 | 5.89 |  |  |  | 5.89
BARRY 1101 | 152111101 | 32.02 |  |  |  | 32.02
BARRY 1102 | 152111102 | 17.71 |  |  |  | 17.71
BARRY 1103 | 152111103 | 33.06 |  |  |  | 33.06
BARTON 1101 | 253571101 | 5.98 |  |  |  | 5.98
BARTON 1102 | 253571102 | 4.5 |  |  |  | 4.5
BARTON 1104 | 253571104 | 11.68 |  |  |  | 11.68
BARTON 1105 | 253571105 | 4.79 |  |  |  | 4.79
BARTON 1106 | 253571106 | 5.96 |  |  |  | 5.96
BARTON 1108 | 253571108 | 18.95 |  |  |  | 18.95
BARTON 1109 | 253571109 | 7.17 |  |  |  | 7.17
BARTON 1110 | 253571110 | 16.36 |  |  |  | 16.36
BARTON 1111 | 253571111 | 15.57 |  |  |  | 15.57
BARTON 1112 | 253571112 | 3.34 |  |  |  | 3.34
BARTON 1114 | 253571114 | 12.8 |  |  |  | 12.8
BARTON 1115 | 253571115 | 15.3 |  |  |  | 15.3
BARTON 1116 | 253571116 | 9.32 |  |  |  | 9.32
BASALT 1101 | 42461101 | 10.84 |  |  |  | 10.84
BASALT 1104 | 42461104 | 0.67 |  |  |  | 0.67
BASALT 1105 | 42461105 | 1.65 |  |  |  | 1.65
BASALT 1106 | 42461106 | 68.66 |  | 1.67 |  | 66.99
BAY MEADOWS 1102 | 24011102 | 4.99 |  |  |  | 4.99
BAY MEADOWS 1103 | 24011103 | 6.84 |  |  |  | 6.84
BAY MEADOWS 1104 | 24011104 | 16.71 |  |  |  | 16.71
BAY MEADOWS 1105 | 24011105 | 6.64 |  |  |  | 6.64
BAY MEADOWS 1106 | 24011106 | 0.86 |  |  |  | 0.86
BAY MEADOWS 1107 | 24011107 | 3.17 |  |  |  | 3.17
BAY MEADOWS 1108 | 24011108 | 1.05 |  |  |  | 1.05
BAY MEADOWS 2101 | 24012101 | 17.87 |  |  |  | 17.87
BAY MEADOWS 2102 | 24012102 | 14.26 |  | 3.98 |  | 10.28
BAY MEADOWS 2103 | 24012103 | 0 |  |  |  | 0
BAYWOOD 1101 | 182801101 | 29.06 |  | 3.37 |  | 25.69
BEACH (Q) 0402 | 22340402 | 2.01 |  |  |  | 2.01
BEAR VALLEY 2101 | 252192101 | 166.69 |  | 100.85 |  | 65.84
BEAR VALLEY 2105 | 252192105 | 157.18 | 7.5 | 149.68 |  | 0
BECK STREET 0401 | 12640401 | 1.58 |  |  |  | 1.58
BELL 1107 | 152701107 | 50.39 |  | 42.56 |  | 7.83
BELL 1108 | 152701108 | 66.64 |  | 54.7 |  | 11.94
BELL 1109 | 152701109 | 18.2 |  | 14.03 |  | 4.17
BELL 1110 | 152701110 | 11.18 |  | 0.16 |  | 11.02
BELLE HAVEN 0401 | 24020401 | 9.43 |  |  |  | 9.43
BELLE HAVEN 0402 | 24020402 | 4.67 |  |  |  | 4.67
BELLE HAVEN 0403 | 24020403 | 5.51 |  |  |  | 5.51
BELLE HAVEN 0404 | 24020404 | 8.64 |  |  |  | 8.64
BELLE HAVEN 0405 | 24020405 | 7.39 |  |  |  | 7.39
BELLE HAVEN 0406 | 24020406 | 9.28 |  |  |  | 9.28
BELLE HAVEN 0407 | 24020407 | 6.35 |  |  |  | 6.35
BELLE HAVEN 0408 | 24020408 | 5.2 |  |  |  | 5.2
BELLE HAVEN 0409 | 24020409 | 3.86 |  |  |  | 3.86
BELLE HAVEN 1101 | 24021101 | 1.59 |  |  |  | 1.59
BELLE HAVEN 1102 | 24021102 | 1.68 |  |  |  | 1.68
BELLE HAVEN 1103 | 24021103 | 1.89 |  |  |  | 1.89
BELLE HAVEN 1104 | 24021104 | 5.68 |  |  |  | 5.68
BELLE HAVEN 1105 | 24021105 | 10.56 |  |  |  | 10.56
BELLE HAVEN 1106 | 24021106 | 15.57 |  |  |  | 15.57
BELLE HAVEN 1107 | 24021107 | 1.27 |  |  |  | 1.27
BELLEVUE 1102 | 43181102 | 43.24 |  | 0.16 |  | 43.08
BELLEVUE 1104 | 43181104 | 12.56 |  |  |  | 12.56
BELLEVUE 2101 | 43182101 | 66.04 | 7.02 | 19 |  | 40.02
BELLEVUE 2103 | 43182103 | 5.72 |  |  |  | 5.72
BELLEVUE 2105 | 43182105 | 4.02 |  |  |  | 4.02
BELLEVUE 2107 | 43182107 | 11.32 |  |  |  | 11.32
BELMONT 0401 | 24030401 | 5.89 |  |  |  | 5.89
BELMONT 0402 | 24030402 | 6.99 |  |  |  | 6.99
BELMONT 0403 | 24030403 | 4.65 |  |  |  | 4.65
BELMONT 0406 | 24030406 | 5.02 |  |  |  | 5.02
BELMONT 1102 | 24031102 | 15.15 |  |  |  | 15.15
BELMONT 1103 | 24031103 | 18.58 |  | 3.37 |  | 15.21
BELMONT 1104 | 24031104 | 7.05 |  |  |  | 7.05
BELMONT 1105 | 24031105 | 0.64 |  |  |  | 0.64
BELMONT 1106 | 24031106 | 1.65 |  |  |  | 1.65
BELMONT 1107 | 24031107 | 0.97 |  |  |  | 0.97
BELMONT 1109 | 24031109 | 0 |  |  |  | 0
BELMONT 1110 | 24031110 | 24.15 |  | 0.11 |  | 24.04
BELRIDGE 1A 1101 | 254371101 | 0.09 |  |  |  | 0.09
BELRIDGE 1B 1101 | 254381101 | 0.01 |  |  |  | 0.01
BEN LOMOND 0401 | 83040401 | 23.05 | 23.05 |  |  | 0
BEN LOMOND 1101 | 83041101 | 15.12 | 15.12 |  |  | 0
BERESFORD 0401 | 24040401 | 1.08 |  |  |  | 1.08
BERESFORD 0402 | 24040402 | 2.38 |  |  |  | 2.38
BERESFORD 0403 | 24040403 | 12.19 |  | 5.39 |  | 6.8
BERESFORD 0404 | 24040404 | 5.74 |  |  |  | 5.74
BERKELEY F 0401 | 12060401 | 0 |  |  |  | 0
BERKELEY F 0402 | 12060402 | 2.13 |  | 0.14 |  | 1.99
BERKELEY F 0403 | 12060403 | 2.19 |  |  |  | 2.19
BERKELEY F 0404 | 12060404 | 3.68 |  |  |  | 3.68
BERKELEY F 0405 | 12060405 | 0.97 |  |  |  | 0.97
BERKELEY F 0406 | 12060406 | 3.79 |  |  |  | 3.79
BERKELEY F 0407 | 12060407 | 0.01 |  |  |  | 0.01
BERKELEY F 0408 | 12060408 | 0.79 |  |  |  | 0.79
BERKELEY F 0409 | 12060409 | 3.58 |  |  |  | 3.58
BERKELEY F 0410 | 12060410 | 2.86 |  |  |  | 2.86
BERKELEY F 0411 | 12060411 | 4.42 |  |  |  | 4.42
BERKELEY F 1102 | 12061102 | 0.27 |  |  |  | 0.27
BERKELEY F 1103 | 12061103 | 6.52 | 1.96 |  |  | 4.56
BERKELEY F 1104 | 12061104 | 3.25 |  |  |  | 3.25
BERKELEY F 1105 | 12061105 | 11.37 |  | 1.78 |  | 9.59
BERKELEY T 0401 | 12660401 | 2.5 |  |  |  | 2.5
BERKELEY T 0402 | 12660402 | 1.35 |  |  |  | 1.35
BERKELEY T 0403 | 12660403 | 0.86 |  |  |  | 0.86
BERKELEY T 0404 | 12660404 | 1.08 |  |  |  | 1.08
BERRENDA A 1101 | 254261101 | 0.02 |  |  |  | 0.02
BERRENDA C 0401 | 254480401 | 0.02 |  |  |  | 0.02
BETHEL BANK 0401 | 18150401 | 0.78 |  |  |  | 0.78
BIG BASIN 1101 | 82841101 | 54.98 | 54.98 |  |  | 0
BIG BASIN 1102 | 82841102 | 66.99 | 63.85 | 3.14 |  | 0
BIG BEND 1101 | 103751101 | 56.91 | 42.41 | 14.49 |  | 0.01
BIG BEND 1102 | 103751102 | 18.14 | 18.04 |  |  | 0.1
BIG MEADOWS 2101 | 102812101 | 70.18 |  | 53.01 |  | 17.17
BIG RIVER 1101 | 43081101 | 86.02 |  | 69.95 |  | 16.07
BIOLA 1101 | 252211101 | 90.07 |  |  |  | 90.07
BIOLA 1102 | 252211102 | 32.39 |  |  |  | 32.39
BIOLA 1103 | 252211103 | 80.25 |  |  |  | 80.25
BIOLA 1104 | 252211104 | 50.08 |  |  |  | 50.08
BLACKWELL 1102 | 254681102 | 30.4 |  |  |  | 30.4
BLACKWELL 2101 | 254682101 | 22.89 |  |  |  | 22.89
BLUE LAKE 1101 | 192181101 | 7.32 |  |  | 0.31 | 7.01
BLUE LAKE 1102 | 192181102 | 68.77 |  |  | 0.02 | 68.75
BOGARD 1101 | 103301101 | 0.51 |  | 0.51 |  | 0
BOGUE 1102 | 153781102 | 17.69 |  |  |  | 17.69
BOGUE 1103 | 153781103 | 16.17 |  |  |  | 16.17
BOGUE 1104 | 153781104 | 9.44 |  |  |  | 9.44
BOGUE 1105 | 153781105 | 10.46 |  |  |  | 10.46
BOGUE 1106 | 153781106 | 59.4 |  |  |  | 59.4
BOGUE 1107 | 153781107 | 15.81 |  |  |  | 15.81
BOGUE 1108 | 63781108 | 0.54 |  |  |  | 0.54
BOLINAS 1101 | 42261101 | 51.63 | 27.17 | 7.48 |  | 16.98
BOLTHOUSE FARMS 1101 | 258181101 | 0.02 |  |  |  | 0.02
BONITA 1101 | 255391101 | 53.96 |  |  |  | 53.96
BONITA 1102 | 255391102 | 30.43 |  |  |  | 30.43
BONITA 1103 | 255391103 | 44.61 |  |  |  | 44.61
BONNIE NOOK 1101 | 152301101 | 14.44 | 14.44 |  |  | 0
BONNIE NOOK 1102 | 152301102 | 33.99 | 33.99 |  |  | 0
BONNIE NOOK 1103 | 152301103 | 0.33 | 0.33 |  |  | 0
BORDEN 1101 | 255121101 | 68.11 |  |  |  | 68.11
BORDEN 1102 | 255121102 | 25.89 |  |  |  | 25.89
BORDEN 1103 | 255121103 | 86.39 |  |  |  | 86.39
BORONDA 1101 | 182461101 | 7.92 |  |  |  | 7.92
BORONDA 1102 | 182461102 | 4.35 |  |  |  | 4.35
BOSWELL 1101 | 254941101 | 0.02 |  |  |  | 0.02
BOWLES 1101 | 253531101 | 69.15 |  |  |  | 69.15
BOWLES 1102 | 253531102 | 33.46 |  |  |  | 33.46
BOWLES 1103 | 253531103 | 26.61 |  |  |  | 26.61
BOWLES 1104 | 253531104 | 41.49 |  |  |  | 41.49
BRENTWOOD 2104 | 14592104 | 2.34 |  |  |  | 2.34
BRENTWOOD 2105 | 14592105 | 78.65 |  | 10.38 |  | 68.27
BRENTWOOD 2106 | 14592106 | 5.97 |  |  |  | 5.97
BRENTWOOD 2108 | 14592108 | 6.13 |  |  |  | 6.13
BRENTWOOD 2109 | 14592109 | 1.28 |  |  |  | 1.28
BRENTWOOD 2110 | 14592110 | 3.44 |  |  |  | 3.44
BRENTWOOD 2111 | 14592111 | 7.29 |  |  |  | 7.29
BRENTWOOD 2112 | 14592112 | 94.53 |  |  |  | 94.53
BRENTWOOD 2113 | 14592113 | 8.18 |  |  |  | 8.18
BRIDGEVILLE 1101 | 192461101 | 24.84 | 4.67 | 17.93 |  | 2.24
BRIDGEVILLE 1102 | 192461102 | 43.26 | 20.63 | 10.32 |  | 12.31
BRITTON 1104 | 83611104 | 1.18 |  |  |  | 1.18
BRITTON 1105 | 83611105 | 5.11 |  |  |  | 5.11
BRITTON 1106 | 83611106 | 3.72 |  |  |  | 3.72
BRITTON 1107 | 83611107 | 5.45 |  |  |  | 5.45
BRITTON 1108 | 83611108 | 1.73 |  |  |  | 1.73
BRITTON 1109 | 83611109 | 2.44 |  |  |  | 2.44
BRITTON 1110 | 83611110 | 11.66 |  |  |  | 11.66
BRITTON 1111 | 83611111 | 1.27 |  |  |  | 1.27
BRITTON 1112 | 83611112 | 1.84 |  |  |  | 1.84
BRITTON 1113 | 83611113 | 1.35 |  |  |  | 1.35
BRITTON 1114 | 83611114 | 4.99 |  |  |  | 4.99
BRITTON 1115 | 83611115 | 1.12 |  |  |  | 1.12
BROOKSIDE 0401 | 13210401 | 3.69 |  |  |  | 3.69
BROWNS VALLEY 1101 | 152921101 | 66.44 |  | 44.15 |  | 22.29
BRUNSWICK 1102 | 152481102 | 54.25 | 46.98 | 4.7 |  | 2.57
BRUNSWICK 1103 | 152481103 | 66.02 | 40.51 | 17.91 |  | 7.6
BRUNSWICK 1104 | 152481104 | 57.96 | 26.28 | 29.68 |  | 2
BRUNSWICK 1105 | 152481105 | 118.4 | 113.95 | 4.2 |  | 0.25
BRUNSWICK 1106 | 152481106 | 178.45 | 119.58 | 49.39 |  | 9.48
BRUNSWICK 1107 | 152481107 | 19.52 | 3.13 | 5.71 |  | 10.68
BRUNSWICK 1110 | 152481110 | 32.9 |  | 22.79 |  | 10.11
BUCKS CREEK 1102 | 102211102 | 0.03 | 0.03 |  |  | 0
BUCKS CREEK 1103 | 102211103 | 12.87 | 9.91 | 2.66 |  | 0.3
BUELLTON 1101 | 183041101 | 104.22 | 4.83 | 72.61 |  | 26.78
BUELLTON 1102 | 183041102 | 28.19 |  | 16.03 |  | 12.16
BUENA VISTA 1101 | 182261101 | 0.71 |  |  |  | 0.71
BUENA VISTA 1102 | 182261102 | 11.11 |  |  |  | 11.11
BUENA VISTA 1103 | 182261103 | 7.59 |  |  |  | 7.59
BUENA VISTA 1104 | 182261104 | 3.97 |  |  |  | 3.97
BUENA VISTA 1106 | 182261106 | 12.92 |  |  |  | 12.92
BULLARD 1101 | 253961101 | 14.34 |  |  |  | 14.34
BULLARD 1102 | 253961102 | 2.78 |  |  |  | 2.78
BULLARD 1103 | 253961103 | 8.11 |  |  |  | 8.11
BULLARD 1104 | 253961104 | 8.04 |  |  |  | 8.04
BULLARD 1105 | 253961105 | 3.46 |  |  |  | 3.46
BULLARD 1106 | 253961106 | 3.69 |  |  |  | 3.69
BULLARD 1107 | 253961107 | 2.4 |  |  |  | 2.4
BULLARD 1108 | 253961108 | 1.62 |  |  |  | 1.62
BULLARD 1109 | 253961109 | 5.4 |  |  |  | 5.4
BULLARD 1110 | 253961110 | 4.21 |  |  |  | 4.21
BULLARD 1113 | 253961113 | 5.22 |  |  |  | 5.22
BULLARD 2111 | 253962111 | 4.45 |  |  |  | 4.45
BULLARD 2112 | 253962112 | 11.11 |  |  |  | 11.11
BULLARD 2114 | 253962114 | 5.36 |  |  |  | 5.36
BURLINGAME 0401 | 24050401 | 3.14 |  |  |  | 3.14
BURLINGAME 0402 | 24050402 | 5.89 |  |  |  | 5.89
BURLINGAME 0403 | 24050403 | 3.86 |  |  |  | 3.86
BURLINGAME 0404 | 24050404 | 3.98 |  |  |  | 3.98
BURLINGAME 0405 | 24050405 | 3.25 |  |  |  | 3.25
BURLINGAME 2101 | 24052101 | 6.82 |  |  |  | 6.82
BURNEY 1101 | 103311101 | 59.78 |  | 50.93 |  | 8.85
BURNEY 1102 | 103311102 | 4.06 |  | 0.64 |  | 3.42
BURNS 2101 | 183582101 | 29.14 | 29.14 |  |  | 0
BUTTE 1103 | 103081103 | 60.18 |  |  |  | 60.18
BUTTE 1104 | 103081104 | 52.15 |  |  |  | 52.15
BUTTE 1105 | 103081105 | 37.8 | 26.62 | 3.43 |  | 7.75
BUTTE 1106 | 103081106 | 11.84 |  |  |  | 11.84
BUTTE 1107 | 103081107 | 109.39 |  |  |  | 109.39
CABRILLO 1103 | 183101103 | 102.06 |  | 57.4 |  | 44.66
CABRILLO 1104 | 183101104 | 76.03 |  | 30.33 |  | 45.7
CADET 1101 | 254821101 | 0.03 |  |  |  | 0.03
CAL WATER 1102 | 255451102 | 26.43 |  | 3.72 |  | 22.71
CAL WATER 1103 | 255451103 | 8.81 |  |  |  | 8.81
CALAVERAS CEMENT 1101 | 162211101 | 242.75 | 7.77 | 218.19 |  | 16.79
CALFLAX 1101 | 253441101 | 27.49 |  |  |  | 27.49
CALFLAX 1102 | 253441102 | 20.43 |  |  |  | 20.43
CALFLAX 1103 | 253441103 | 29.03 |  |  |  | 29.03
CALFLAX 1104 | 253441104 | 18.61 |  |  |  | 18.61
CALIFORNIA AVE 1102 | 252281102 | 11.42 |  |  |  | 11.42
CALIFORNIA AVE 1103 | 252281103 | 7.76 |  |  |  | 7.76
CALIFORNIA AVE 1104 | 252281104 | 3.58 |  |  |  | 3.58
CALIFORNIA AVE 1106 | 252281106 | 9.78 |  |  |  | 9.78
CALIFORNIA AVE 1108 | 252281108 | 9.61 |  |  |  | 9.61
CALIFORNIA AVE 1110 | 252281110 | 11.08 |  |  |  | 11.08
CALIFORNIA AVE 1111 | 252281111 | 6.73 |  |  |  | 6.73
CALIFORNIA AVE 1112 | 252281112 | 4.93 |  |  |  | 4.93
CALIFORNIA AVE 1113 | 252281113 | 6.5 |  |  |  | 6.5
CALIFORNIA AVE 1114 | 252281114 | 19.38 |  |  |  | 19.38
CALIFORNIA AVE 1116 | 252281116 | 9.35 |  |  |  | 9.35
CALIFORNIA AVE 1117 | 252281117 | 1.27 |  |  |  | 1.27
CALISTOGA 1101 | 42711101 | 115.63 | 83.32 | 15.49 |  | 16.82
CALISTOGA 1102 | 42711102 | 45.68 | 22.32 | 1.53 |  | 21.83
CALPELLA 1101 | 43411101 | 101.17 | 4.03 | 77.84 |  | 19.3
CALPELLA 1102 | 43411102 | 7.52 |  | 1.79 |  | 5.73
CALPINE 1144 | 48011144 | 30.59 | 28.37 | 2.22 |  | 0
CALPINE 1146 | 48011146 | 5.61 | 5.61 |  |  | 0
CAMBRIA 1101 | 182771101 | 31.04 |  | 24.35 |  | 6.69
CAMBRIA 1102 | 182771102 | 27.24 |  | 15.77 |  | 11.47
CAMDEN 1102 | 252301102 | 40.15 |  |  |  | 40.15
CAMDEN 1103 | 252301103 | 127.81 |  |  |  | 127.81
CAMDEN 1104 | 252301104 | 77.5 |  |  |  | 77.5
CAMDEN 1105 | 252301105 | 58.83 |  |  |  | 58.83
CAMP EVERS 2103 | 83622103 | 61.29 | 44.84 | 0.83 |  | 15.62
CAMP EVERS 2104 | 83622104 | 36.49 | 26.64 | 0.58 |  | 9.27
CAMP EVERS 2105 | 83622105 | 78.47 | 73.46 | 2.13 |  | 2.88
CAMP EVERS 2106 | 83622106 | 145.75 | 132.84 | 2.97 |  | 9.94
CAMPHORA 0401 | 182070401 | 0.43 |  |  |  | 0.43
CAMPHORA 1101 | 182071101 | 51.89 |  | 3.89 |  | 48
CANAL 1101 | 252091101 | 56.42 |  |  |  | 56.42
CANAL 1102 | 252091102 | 15.33 |  |  |  | 15.33
CANAL 1103 | 252091103 | 53.58 |  |  |  | 53.58
CANAL 1104 | 252091104 | 9.93 |  |  |  | 9.93
CANAL 1105 | 252091105 | 17.32 |  |  |  | 17.32
CANAL 1106 | 252091106 | 7.86 |  |  |  | 7.86
CANTUA 1101 | 253591101 | 24.04 |  |  |  | 24.04
CANTUA 1102 | 253591102 | 47.75 |  |  |  | 47.75
CANTUA 1103 | 253591103 | 35.78 |  |  |  | 35.78
CANTUA 1104 | 253591104 | 0.17 |  |  |  | 0.17
CANTUA 1105 | 253591105 | 15.12 |  |  |  | 15.12
CANTUA 1106 | 253591106 | 0.16 |  |  |  | 0.16
CAPAY 1101 | 102111101 | 48.81 |  |  |  | 48.81
CAPAY 1102 | 102111102 | 73.95 |  |  |  | 73.95
CARBONA 1101 | 163091101 | 39.11 |  |  |  | 39.11
CARBONA 1103 | 163091103 | 3.63 |  |  |  | 3.63
CARLOTTA 1121 | 192291121 | 51.97 |  | 21.08 |  | 30.89
CARNATION 2101 | 255282101 | 0.01 |  |  |  | 0.01
CARNERAS 1102 | 252321102 | 16.83 |  |  |  | 16.83
CARNERAS 1103 | 252321103 | 41.62 |  |  |  | 41.62
CAROLANDS 0401 | 24060401 | 4.52 |  |  |  | 4.52
CAROLANDS 0402 | 24060402 | 0.03 |  |  |  | 0.03
CAROLANDS 0403 | 24060403 | 13.35 |  |  |  | 13.35
CAROLANDS 0404 | 24060404 | 10.2 |  | 4.16 |  | 6.04
CARQUINEZ 1103 | 43281103 | 14.67 |  |  |  | 14.67
CARQUINEZ 1104 | 43281104 | 0.38 |  |  |  | 0.38
CARQUINEZ 1105 | 43281105 | 5.68 |  |  |  | 5.68
CARRIZO PLAINS 1101 | 253461101 | 105.92 |  |  |  | 105.92
CARUTHERS 1101 | 252371101 | 81.8 |  |  |  | 81.8
CARUTHERS 1102 | 252371102 | 69.76 |  |  |  | 69.76
CARUTHERS 1104 | 252371104 | 80.71 |  |  |  | 80.71
CARUTHERS 1105 | 252371105 | 56.41 |  |  |  | 56.41
CASSERLY 0401 | 83110401 | 3.07 |  |  |  | 3.07
CASSIDY 2107 | 254272107 | 59.41 |  |  |  | 59.41
CASSIDY 2108 | 254272108 | 34.09 |  |  |  | 34.09
CASTRO 0401 | 22480401 | 2.93 |  |  |  | 2.93
CASTRO 0402 | 22480402 | 2.62 |  |  |  | 2.62
CASTRO VALLEY 1102 | 14091102 | 22.74 | 0.35 | 1.15 |  | 21.24
CASTRO VALLEY 1103 | 14091103 | 15.67 |  |  |  | 15.67
CASTRO VALLEY 1104 | 14091104 | 7.33 |  |  |  | 7.33
CASTRO VALLEY 1105 | 14091105 | 30.22 |  | 2.18 |  | 28.04
CASTRO VALLEY 1107 | 14091107 | 16.06 |  |  |  | 16.06
CASTRO VALLEY 1108 | 14091108 | 38.75 | 12.59 | 4.16 |  | 22
CASTRO VALLEY 1109 | 14091109 | 8.02 |  |  |  | 8.02
CASTRO VALLEY 1110 | 14091110 | 24.81 | 15.57 | 6.7 |  | 2.54
CASTRO VALLEY 1111 | 14091111 | 7.89 | 1.54 | 3.92 |  | 2.43
CASTROVILLE 2103 | 182352103 | 81.37 |  |  |  | 81.37
CASTROVILLE 2104 | 182352104 | 50.51 |  |  |  | 50.51
CATLETT 1101 | 153761101 | 0.03 |  |  |  | 0.03
CATLETT 1102 | 153761102 | 106.14 |  |  |  | 106.14
CATLETT 1105 | 153761105 | 54.16 |  |  |  | 54.16
CAWELO B 1101 | 252621101 | 0.01 |  |  |  | 0.01
CAWELO C 1101 | 252631101 | 0.02 |  |  |  | 0.02
CAYETANO 2109 | 14422109 | 49.59 | 12.1 | 21.65 |  | 15.84
CAYETANO 2111 | 14422111 | 12.25 |  | 5.36 |  | 6.89
CAYUCOS 1101 | 182551101 | 46.25 |  | 0.46 |  | 45.79
CAYUCOS 1102 | 182551102 | 57.27 | 9.06 | 4.98 |  | 43.23
CEDAR CREEK 1101 | 103321101 | 109.66 | 20.98 | 88.68 |  | 0
CELERON 1101 | 255271101 | 0.15 |  |  |  | 0.15
CHALLENGE 1101 | 103201101 | 48.27 | 48.04 | 0.23 |  | 0
CHALLENGE 1102 | 103201102 | 62.85 | 60.21 | 2.64 |  | 0
CHANNEL 1101 | 163071101 | 9.93 |  |  |  | 9.93
CHANNEL 1102 | 163071102 | 8.38 |  |  |  | 8.38
CHARCA 1102 | 254501102 | 47.97 |  |  |  | 47.97
CHARCA 1103 | 254501103 | 41.41 |  |  |  | 41.41
CHARCA 1106 | 254501106 | 18.69 |  |  |  | 18.69
CHEROKEE 1101 | 163651101 | 19.87 |  |  |  | 19.87
CHEROKEE 1102 | 163651102 | 36.3 |  |  |  | 36.3
CHESTER 1101 | 103181101 | 8.16 |  | 2.12 |  | 6.04
CHESTER 1102 | 103181102 | 5.3 |  | 2.31 |  | 2.99
CHICO A 0401 | 102050401 | 2.2 |  |  |  | 2.2
CHICO A 0402 | 102050402 | 5.65 |  |  |  | 5.65
CHICO A 1101 | 102051101 | 8.09 |  |  |  | 8.09
CHICO A 1102 | 102051102 | 9.3 |  |  |  | 9.3
CHICO A 1103 | 102051103 | 4.86 |  |  |  | 4.86
CHICO B 1101 | 102491101 | 4.56 |  |  |  | 4.56
CHICO B 1103 | 102491103 | 8.02 |  |  |  | 8.02
CHICO B 1105 | 102491105 | 10.85 |  |  |  | 10.85
CHICO B 1106 | 102491106 | 2.01 |  |  |  | 2.01
CHICO C 0401 | 102650401 | 2.77 |  |  |  | 2.77
CHOLAME 1101 | 182561101 | 96.97 |  |  |  | 96.97
CHOLAME 2102 | 182562102 | 215.33 |  | 59 |  | 156.33
CHOWCHILLA 1101 | 254101101 | 63.03 |  |  |  | 63.03
CHOWCHILLA 1102 | 254101102 | 13.15 |  |  |  | 13.15
CHOWCHILLA 1103 | 254101103 | 46.85 |  |  |  | 46.85
CHOWCHILLA 1104 | 254101104 | 80.6 |  |  |  | 80.6
CHOWCHILLA 1105 | 254101105 | 11.89 |  |  |  | 11.89
CHOWCHILLA 1106 | 254101106 | 54.75 |  |  |  | 54.75
CLARK ROAD 1101 | 103091101 | 0.02 |  | 0.02 |  | 0
CLARK ROAD 1102 | 103091102 | 136.63 | 32.87 | 89.63 |  | 14.13
CLARKSVILLE 2103 | 153612103 | 50.41 | 19.61 | 10.52 |  | 20.28
CLARKSVILLE 2104 | 153612104 | 75.66 | 41.19 | 21.88 |  | 12.59
CLARKSVILLE 2105 | 153612105 | 13.34 | 5.79 | 4.75 |  | 2.8
CLARKSVILLE 2106 | 153612106 | 2.21 |  | 0.48 |  | 1.73
CLARKSVILLE 2109 | 153612109 | 12.26 | 1.98 | 1.96 |  | 8.32
CLARKSVILLE 2110 | 153612110 | 7.03 |  |  |  | 7.03
CLAY 1101 | 163341101 | 40.58 |  | 26.32 |  | 14.26
CLAY 1102 | 163341102 | 2.09 |  | 0.82 |  | 1.27
CLAY 1103 | 163341103 | 112.62 |  | 49.68 |  | 62.94
CLAYTON 1103 | 12021103 | 4.33 |  |  |  | 4.33
CLAYTON 1104 | 12021104 | 13.4 |  |  |  | 13.4
CLAYTON 2211 | 12022211 | 10.48 |  |  |  | 10.48
CLAYTON 2212 | 12022212 | 58.62 | 28.9 | 18.66 |  | 11.06
CLAYTON 2213 | 12022213 | 4.84 |  | 2.51 |  | 2.33
CLAYTON 2214 | 12022214 | 5.89 |  |  |  | 5.89
CLAYTON 2215 | 12022215 | 30.8 | 2.92 | 5.47 |  | 22.41
CLAYTON 2216 | 12022216 | 18.71 |  |  |  | 18.71
CLAYTON 2217 | 12022217 | 19.79 |  |  |  | 19.79
CLAYTON 2218 | 12022218 | 8.34 |  |  |  | 8.34
CLEAR LAKE 1101 | 42141101 | 112.61 | 6.05 | 12.29 |  | 94.27
CLEAR LAKE 1102 | 42141102 | 36.63 |  | 3.97 |  | 32.66
CLOVERDALE 1101 | 42821101 | 36.64 |  | 24.35 |  | 12.29
CLOVERDALE 1102 | 42821102 | 108.77 | 47.23 | 30.21 |  | 31.33
CLOVIS 1101 | 254081101 | 3.97 |  |  |  | 3.97
CLOVIS 1102 | 254081102 | 25.59 |  |  |  | 25.59
CLOVIS 1103 | 254081103 | 1.95 |  |  |  | 1.95
CLOVIS 1104 | 254081104 | 0.43 |  |  |  | 0.43
CLOVIS 1105 | 254081105 | 7.73 |  |  |  | 7.73
CLOVIS 1106 | 254081106 | 4.99 |  |  |  | 4.99
CLOVIS 1107 | 254081107 | 10.71 |  |  |  | 10.71
CLOVIS 1108 | 254081108 | 11.47 |  |  |  | 11.47
CLOVIS 2109 | 254082109 | 3.85 |  |  |  | 3.85
CLOVIS 2110 | 254082110 | 11.47 |  |  |  | 11.47
CLOVIS 2111 | 254082111 | 8.84 |  |  |  | 8.84
CMC 1101 | 183111101 | 2.01 |  | 2.01 |  | 0
CMC 1102 | 183111102 | 0.48 |  | 0.48 |  | 0
COALINGA NO 1 1106 | 252161106 | 8.96 |  |  |  | 8.96
COALINGA NO 1 1107 | 252161107 | 4.04 |  |  |  | 4.04
COALINGA NO 1 1108 | 252161108 | 60.22 |  |  |  | 60.22
COALINGA NO 1 1109 | 252161109 | 27.26 |  |  |  | 27.26
COALINGA NO 2 1104 | 252381104 | 0.16 |  |  |  | 0.16
COALINGA NO 2 1105 | 252381105 | 76.34 |  |  |  | 76.34
COALINGA NO 2 1106 | 252381106 | 42.94 |  |  |  | 42.94
COALINGA NO 2 1107 | 252381107 | 38.43 |  |  |  | 38.43
COARSEGOLD 2102 | 254432102 | 72.98 | 58.15 | 14.83 |  | 0
COARSEGOLD 2103 | 254432103 | 122.4 |  | 93.29 |  | 29.11
COARSEGOLD 2104 | 254432104 | 265.16 | 2.83 | 243.51 |  | 18.82
COLONY 1101 | 162231101 | 28.9 |  |  |  | 28.9
COLONY 1102 | 162231102 | 47.74 |  |  |  | 47.74
COLUMBIA HILL 1101 | 152471101 | 89.55 | 71.94 | 17.61 |  | 0
COLUMBUS 1103 | 253951103 | 7.87 |  |  |  | 7.87
COLUMBUS 1104 | 253951104 | 8.27 |  |  |  | 8.27
COLUMBUS 1105 | 253951105 | 16.06 |  |  |  | 16.06
COLUMBUS 1106 | 253951106 | 14.29 |  |  |  | 14.29
COLUMBUS 1109 | 253951109 | 5.58 |  |  |  | 5.58
COLUMBUS 1110 | 253951110 | 6.52 |  |  |  | 6.52
COLUSA 1100 | 62021100 | 0.02 |  |  |  | 0.02
COLUSA 1101 | 62021101 | 113.67 |  |  |  | 113.67
COLUSA JUNCTION 1101 | 62071101 | 29 |  |  |  | 29
CONCORD NO 1 0401 | 12960401 | 4.75 |  |  |  | 4.75
CONCORD NO 1 0402 | 12960402 | 3.77 |  |  |  | 3.77
CONTRA COSTA 2103 | 13652103 | 22.62 |  |  |  | 22.62
CONTRA COSTA 2104 | 13652104 | 10.89 |  |  |  | 10.89
CONTRA COSTA 2105 | 13652105 | 0.04 |  |  |  | 0.04
CONTRA COSTA 2106 | 13652106 | 0.02 |  |  |  | 0.02
CONTRA COSTA 2107 | 13652107 | 12.73 |  |  |  | 12.73
CONTRA COSTA 2108 | 13652108 | 0.88 |  |  |  | 0.88
CONTRA COSTA 2109 | 13652109 | 13.87 |  |  |  | 13.87
CONTRA COSTA 2110 | 13652110 | 0.55 |  |  |  | 0.55
CONTRA COSTA 2112 | 13652112 | 0.04 |  |  |  | 0.04
CONTRA COSTA 2113 | 13652113 | 15.09 |  |  |  | 15.09
CONTRA COSTA 2114 | 13652114 | 1.91 |  |  |  | 1.91
CONTRA COSTA 2115 | 13652115 | 6.76 |  |  |  | 6.76
CONTRA COSTA 2116 | 13652116 | 23.1 |  |  |  | 23.1
COPPERMINE 1104 | 252411104 | 102.71 |  | 9.04 |  | 93.67
COPPERMINE 1106 | 252411106 | 7.93 |  |  |  | 7.93
COPPERMINE 1112 | 252411112 | 15.85 |  |  |  | 15.85
COPPERMINE 2110 | 252412110 | 0 |  |  |  | 0
COPUS 1102 | 253871102 | 30.83 |  |  |  | 30.83
COPUS 1103 | 253871103 | 24.39 |  |  |  | 24.39
COPUS 1104 | 253871104 | 39.16 |  |  |  | 39.16
CORCORAN 1101 | 252171101 | 0.52 |  |  |  | 0.52
CORCORAN 1102 | 252171102 | 0.04 |  |  |  | 0.04
CORCORAN 1104 | 252171104 | 26.71 |  |  |  | 26.71
CORCORAN 1106 | 252171106 | 45.04 |  |  |  | 45.04
CORCORAN 1108 | 252171108 | 23.47 |  |  |  | 23.47
CORCORAN 1112 | 252171112 | 45.42 |  |  |  | 45.42
CORCORAN 1116 | 252171116 | 56.58 |  |  |  | 56.58
CORCORAN 1117 | 252171117 | 0.54 |  |  |  | 0.54
CORCORAN 1118 | 252171118 | 52.18 |  |  |  | 52.18
CORDELIA 1101 | 62701101 | 0.02 |  |  |  | 0.02
CORDELIA 1102 | 62701102 | 0.04 |  |  |  | 0.04
CORDELIA 1104 | 62701104 | 61.99 |  |  |  | 61.99
CORDELIA 1110 | 62701110 | 8.94 |  |  |  | 8.94
CORDELIA 1112 | 62701112 | 16.1 |  |  |  | 16.1
CORNING 1101 | 103331101 | 143.58 |  | 49.53 |  | 94.05
CORNING 1102 | 103331102 | 192.36 |  | 79.8 |  | 112.56
CORNING 1103 | 103331103 | 66.42 |  |  |  | 66.42
CORNING 1104 | 103331104 | 106.3 |  |  |  | 106.3
CORONA 1101 | 43491101 | 22.81 |  |  |  | 22.81
CORONA 1102 | 43491102 | 1.38 |  |  |  | 1.38
CORONA 1103 | 43491103 | 17.44 |  | 0.46 |  | 16.98
CORRAL 1101 | 162991101 | 170.22 |  | 119.68 |  | 50.54
CORRAL 1102 | 162991102 | 64.32 |  | 48.46 |  | 15.86
CORRAL 1103 | 162991103 | 80.53 |  | 17.68 |  | 62.85
CORTINA 1101 | 63121101 | 76.57 |  | 1.32 |  | 75.25
COTATI 1102 | 42271102 | 34.61 |  | 15.6 |  | 19.01
COTATI 1103 | 42271103 | 110.88 |  | 84.03 |  | 26.85
COTATI 1104 | 42271104 | 19.32 |  | 8.43 |  | 10.89
COTATI 1105 | 42271105 | 131.49 |  | 42.8 |  | 88.69
COTTLE 1701 | 163711701 | 89.87 |  |  |  | 89.87
COTTLE 1702 | 163711702 | 37 |  |  |  | 37
COTTLE 1703 | 163711703 | 26.78 |  |  |  | 26.78
COTTLE 1704 | 163711704 | 14.6 |  |  |  | 14.6
COTTLE 1707 | 163711707 | 47.15 |  |  |  | 47.15
COTTLE 1708 | 163711708 | 129.9 |  |  |  | 129.9
COTTONWOOD 1101 | 102931101 | 100.91 |  | 69.99 |  | 30.92
COTTONWOOD 1102 | 102931102 | 82.71 |  | 55.8 |  | 26.91
COTTONWOOD 1103 | 102931103 | 161.03 |  | 133.87 |  | 27.16
COUNTRY CLUB 0401 | 163120401 | 2.11 |  |  |  | 2.11
COUNTRY CLUB 0402 | 163120402 | 4.65 |  |  |  | 4.65
COUNTRY CLUB 0403 | 163120403 | 2.7 |  |  |  | 2.7
COUNTRY CLUB 1101 | 163121101 | 12 |  |  |  | 12
COUNTRY CLUB 1102 | 163121102 | 1.34 |  |  |  | 1.34
COUNTRY CLUB 1103 | 163121103 | 6.25 |  |  |  | 6.25
COUNTRY CLUB 1104 | 163121104 | 7.2 |  |  |  | 7.2
COUNTRY CLUB 1105 | 163121105 | 1.64 |  |  |  | 1.64
COUNTRY CLUB 1106 | 163121106 | 8.96 |  |  |  | 8.96
COVELO 1101 | 43061101 | 120.63 |  | 17.54 |  | 103.09
CRESCENT MILLS 2101 | 103132101 | 79.32 |  | 42.08 |  | 37.24
CRESSEY 2103 | 254702103 | 152.7 |  |  |  | 152.7
CRESSEY 2104 | 254702104 | 94.86 |  |  |  | 94.86
CRESTA 1101 | 102251101 | 1.7 | 0.41 | 1.3 |  | -0.01
CROWS LANDING 1101 | 163251101 | 44.59 |  |  |  | 44.59
CROWS LANDING 1102 | 163251102 | 7.56 |  |  |  | 7.56
CURTIS 1701 | 163351701 | 20.14 |  | 12.23 |  | 7.91
CURTIS 1702 | 163351702 | 117.69 | 22.46 | 87.13 |  | 8.1
CURTIS 1703 | 163351703 | 197.92 | 17.43 | 177.18 |  | 3.31
CURTIS 1704 | 163351704 | 75.97 | 24.28 | 51.12 |  | 0.57
CURTIS 1705 | 163351705 | 88.26 | 14.37 | 69.8 |  | 4.09
CUYAMA 1103 | 253141103 | 79.98 |  | 2.58 |  | 77.4
CUYAMA 1104 | 253141104 | 17.89 |  |  |  | 17.89
CUYAMA 2101 | 253142101 | 63.13 |  | 3.39 |  | 59.74
CUYAMA 2102 | 253142102 | 35.86 |  |  |  | 35.86
DAIRYLAND 1102 | 252421102 | 81.4 |  |  |  | 81.4
DAIRYLAND 1105 | 252421105 | 64.77 |  |  |  | 64.77
DAIRYLAND 1109 | 252421109 | 48.59 |  |  |  | 48.59
DAIRYLAND 1110 | 252421110 | 35 |  |  |  | 35
DAIRYLAND 1111 | 252421111 | 26.7 |  |  |  | 26.7
DAIRYLAND 1112 | 252421112 | 62.34 |  |  |  | 62.34
DAIRYLAND 1113 | 252421113 | 83.52 |  |  |  | 83.52
DAIRYVILLE 1101 | 103341101 | 43.01 |  |  |  | 43.01
DALY CITY 0401 | 22640401 | 5.65 |  |  |  | 5.65
DALY CITY 1101 | 22641101 | 3.43 |  |  |  | 3.43
DALY CITY 1102 | 22641102 | 7.54 |  |  |  | 7.54
DALY CITY 1103 | 22641103 | 4.73 |  |  |  | 4.73
DALY CITY 1104 | 22641104 | 10.98 |  |  |  | 10.98
DALY CITY 1105 | 22641105 | 10.65 |  |  |  | 10.65
DALY CITY 1106 | 22641106 | 9.94 |  |  |  | 9.94
DALY CITY 1107 | 22641107 | 5.3 |  |  |  | 5.3
DALY CITY 1108 | 22641108 | 2.92 |  |  |  | 2.92
DALY CITY 1109 | 22641109 | 6.23 |  |  |  | 6.23
DALY CITY 1110 | 22641110 | 1.78 |  |  |  | 1.78
DALY CITY 1111 | 22641111 | 6.94 |  |  |  | 6.94
DALY CITY 1112 | 22641112 | 14.04 |  |  |  | 14.04
DALY CITY 1115 | 22641115 | 0.03 |  |  |  | 0.03
DAVIS 1101 | 62041101 | 37.51 |  |  |  | 37.51
DAVIS 1102 | 62041102 | 6.46 |  |  |  | 6.46
DAVIS 1103 | 62041103 | 5.85 |  |  |  | 5.85
DAVIS 1104 | 62041104 | 5.72 |  |  |  | 5.72
DAVIS 1105 | 62041105 | 8.02 |  |  |  | 8.02
DAVIS 1106 | 62041106 | 42.71 |  |  |  | 42.71
DAVIS 1107 | 62041107 | 84.37 |  |  |  | 84.37
DAVIS 1108 | 62041108 | 3.34 |  |  |  | 3.34
DAVIS 1109 | 62041109 | 4.45 |  |  |  | 4.45
DAVIS 1110 | 62041110 | 1.83 |  |  |  | 1.83
DAVIS 1111 | 62041111 | 7.24 |  |  |  | 7.24
DAVIS 1112 | 62041112 | 46.6 |  |  |  | 46.6
DAYTON ROAD 0401 | 102940401 | 2.11 |  |  |  | 2.11
DEEPWATER 1105 | 63621105 | 4.12 |  |  |  | 4.12
DEEPWATER 1106 | 63621106 | 0.06 |  |  |  | 0.06
DEEPWATER 1107 | 63621107 | 28.7 |  |  |  | 28.7
DEEPWATER 1108 | 63621108 | 0.09 |  |  |  | 0.09
DEEPWATER 1109 | 63621109 | 4.17 |  |  |  | 4.17
DEER CREEK PH 0401 | 158450401 | 1.12 | 1.12 |  |  | 0
DEL MAR 1103 | 152581103 | 13.01 |  |  |  | 13.01
DEL MAR 1104 | 152581104 | 0 |  |  |  | 0
DEL MAR 2105 | 152582105 | 13.85 |  |  |  | 13.85
DEL MAR 2106 | 152582106 | 3.18 |  |  |  | 3.18
DEL MAR 2109 | 152582109 | 6.88 |  | 2.03 |  | 4.85
DEL MAR 2110 | 152582110 | 1.77 |  |  |  | 1.77
DEL MONTE 1101 | 182221101 | 14.88 |  | 0.49 |  | 14.39
DEL MONTE 2102 | 182222102 | 16.27 |  | 0.66 |  | 15.61
DEL MONTE 2103 | 182222103 | 36.72 |  | 12.3 |  | 24.42
DEL MONTE 2104 | 182222104 | 59.25 |  | 43.85 |  | 15.4
DEL MONTE 2105 | 182222105 | 20.14 |  | 1.04 |  | 19.1
DELEVAN 1101 | 69551101 | 0.6 |  |  |  | 0.6
DELEVAN 1102 | 69551102 | 0.61 |  |  |  | 0.61
DESCHUTES 1101 | 103351101 | 130.44 | 7.48 | 99.43 |  | 23.53
DESCHUTES 1104 | 103351104 | 112.8 |  | 60.22 |  | 52.58
DEVILS DEN 1101 | 253451101 | 44.8 |  |  |  | 44.8
DEVILS DEN 1102 | 253451102 | 33.33 |  |  |  | 33.33
DIAMOND SPRINGS 1103 | 152261103 | 53.26 | 10.2 | 22.95 |  | 20.11
DIAMOND SPRINGS 1104 | 152261104 | 18.15 | 7.56 | 4.89 |  | 5.7
DIAMOND SPRINGS 1105 | 152261105 | 131.88 | 75.04 | 48.36 |  | 8.48
DIAMOND SPRINGS 1106 | 152261106 | 120.12 |  | 109.72 |  | 10.4
DIAMOND SPRINGS 1107 | 152261107 | 57.33 | 34.14 | 17.88 |  | 5.31
DINUBA 1102 | 254091102 | 22.52 |  |  |  | 22.52
DINUBA 1104 | 254091104 | 85.42 |  |  |  | 85.42
DINUBA 1105 | 254091105 | 99.83 |  |  |  | 99.83
DINUBA 1106 | 254091106 | 10.29 |  |  |  | 10.29
DIVIDE 1101 | 182571101 | 15.49 |  |  |  | 15.49
DIVIDE 1102 | 182571102 | 47.79 |  |  |  | 47.79
DIVIDE 1103 | 182571103 | 21.03 |  | 2.38 |  | 18.65
DIXON 1102 | 62061102 | 10.84 |  |  |  | 10.84
DIXON 1103 | 62061103 | 126.63 |  |  |  | 126.63
DIXON 1104 | 62061104 | 11.67 |  |  |  | 11.67
DIXON 1105 | 62061105 | 23.75 |  |  |  | 23.75
DIXON 1106 | 62061106 | 10.06 |  |  |  | 10.06
DIXON LANDING 2101 | 14722101 | 10.74 |  |  |  | 10.74
DIXON LANDING 2102 | 14722102 | 10.86 |  |  |  | 10.86
DIXON LANDING 2103 | 14722103 | 2.81 |  |  |  | 2.81
DIXON LANDING 2105 | 14722105 | 1.68 |  |  |  | 1.68
DIXON LANDING 2109 | 14722109 | 10.59 |  |  |  | 10.59
DIXON LANDING 2111 | 14722111 | 0.13 |  |  |  | 0.13
DOBBINS 1101 | 153741101 | 81.65 | 26.57 | 54.01 |  | 1.07
DOLAN RD 1102 | 182381102 | 0.45 |  |  |  | 0.45
DOLAN ROAD 1101 | 182381101 | 69.09 |  | 2.77 |  | 66.32
DOLAN ROAD 1103 | 182381103 | 3 |  |  |  | 3
DOLAN ROAD 1104 | 182381104 | 5.06 |  |  |  | 5.06
DOS PALOS 1101 | 254041101 | 75.66 |  |  |  | 75.66
DOS PALOS 1102 | 254041102 | 0.21 |  |  |  | 0.21
DRUM 1101 | 152321101 | 18.36 | 18.32 | 0.04 |  | 0
DUMBARTON 1102 | 14471102 | 16.47 |  |  |  | 16.47
DUMBARTON 1103 | 14471103 | 1.48 |  |  |  | 1.48
DUMBARTON 1104 | 14471104 | 13.19 |  |  |  | 13.19
DUMBARTON 1106 | 14471106 | 7.25 |  |  |  | 7.25
DUMBARTON 1107 | 14471107 | 10.35 |  |  |  | 10.35
DUMBARTON 1108 | 14471108 | 3.94 |  |  |  | 3.94
DUMBARTON 1109 | 14471109 | 3.71 |  |  |  | 3.71
DUMBARTON 1110 | 14471110 | 6.95 |  |  |  | 6.95
DUMBARTON 2111 | 14472111 | 6.41 |  |  |  | 6.41
DUNBAR 1101 | 43071101 | 53.4 | 26.42 | 2.62 |  | 24.36
DUNBAR 1102 | 43071102 | 62.11 | 7.2 | 42.28 |  | 12.63
DUNBAR 1103 | 43071103 | 60.09 | 20.67 | 14.76 |  | 24.66
DUNLAP 1102 | 254061102 | 55.46 |  | 55.46 |  | 0
DUNLAP 1103 | 254061103 | 71.32 |  | 71.32 |  | 0
DUNNIGAN 1101 | 63811101 | 78.06 |  |  |  | 78.06
EAST GRAND 0401 | 22570401 | 4.71 |  |  |  | 4.71
EAST GRAND 0404 | 22570404 | 3.82 |  |  |  | 3.82
EAST GRAND 1101 | 22571101 | 7.95 |  |  |  | 7.95
EAST GRAND 1102 | 22571102 | 2.21 |  |  |  | 2.21
EAST GRAND 1103 | 22571103 | 1.51 |  |  |  | 1.51
EAST GRAND 1104 | 22571104 | 15.54 |  |  |  | 15.54
EAST GRAND 1105 | 22571105 | 5.55 |  |  |  | 5.55
EAST GRAND 1106 | 22571106 | 3.7 |  |  |  | 3.7
EAST GRAND 1107 | 22571107 | 13.53 |  |  |  | 13.53
EAST GRAND 1108 | 22571108 | 3.86 |  |  |  | 3.86
EAST GRAND 1109 | 22571109 | 2.08 |  |  |  | 2.08
EAST GRAND 1110 | 22571110 | 3.34 |  |  |  | 3.34
EAST GRAND 1111 | 22571111 | 0.88 |  |  |  | 0.88
EAST GRAND 1114 | 22571114 | 0 |  |  |  | 0
EAST GRAND 1115 | 22571115 | 0 |  |  |  | 0
EAST MARYSVILLE 1105 | 152331105 | 39.25 |  |  |  | 39.25
EAST MARYSVILLE 1107 | 152331107 | 8.01 |  |  |  | 8.01
EAST MARYSVILLE 1108 | 152331108 | 67.82 |  |  |  | 67.82
EAST NICOLAUS 1101 | 152151101 | 68.88 |  |  |  | 68.88
EAST NICOLAUS 1102 | 152151102 | 58.28 |  |  |  | 58.28
EAST NICOLAUS 1103 | 152151103 | 93.3 |  |  |  | 93.3
EAST QUINCY 1101 | 102551101 | 17.43 | 1.69 | 2.06 |  | 13.68
EAST STOCKTON 0401 | 163130401 | 8.35 |  |  |  | 8.35
EAST STOCKTON 0402 | 163130402 | 9.76 |  |  |  | 9.76
EAST STOCKTON 1101 | 163131101 | 14.59 |  |  |  | 14.59
EAST STOCKTON 1102 | 163131102 | 16.09 |  |  |  | 16.09
ECHO SUMMIT 1101 | 158031101 | 14.7 |  | 5.9 | 0.04 | 8.76
EDENVALE 1101 | 82951101 | 9.68 |  |  |  | 9.68
EDENVALE 1102 | 82951102 | 5.72 |  | 0.52 |  | 5.2
EDENVALE 1103 | 82951103 | 0.31 |  |  |  | 0.31
EDENVALE 2105 | 82952105 | 37.05 |  | 2.32 |  | 34.73
EDENVALE 2106 | 82952106 | 16.89 |  |  |  | 16.89
EDENVALE 2107 | 82952107 | 0.07 |  |  |  | 0.07
EDENVALE 2108 | 82952108 | 2.87 |  |  |  | 2.87
EDENVALE 2109 | 82952109 | 2.47 |  |  |  | 2.47
EDENVALE 2110 | 82952110 | 0 |  |  |  | 0
EDENVALE 2112 | 82952112 | 1.33 |  |  |  | 1.33
EDENVALE 2113 | 82952113 | 2.42 |  | 0.02 |  | 2.4
EDES 1101 | 13681101 | 8.54 |  |  |  | 8.54
EDES 1103 | 13681103 | 12.44 |  |  |  | 12.44
EDES 1105 | 13681105 | 3.78 |  |  |  | 3.78
EDES 1110 | 13681110 | 7.49 |  |  |  | 7.49
EDES 1111 | 13681111 | 4.22 |  |  |  | 4.22
EDES 1112 | 13681112 | 17.11 | 0.58 | 14.67 |  | 1.86
EDES 1113 | 13681113 | 4.47 |  |  |  | 4.47
EDES 1114 | 13681114 | 10.4 |  |  |  | 10.4
EEL RIVER 1102 | 192381102 | 144.59 |  | 40.02 |  | 104.57
EEL RIVER 1103 | 192381103 | 59.35 |  | 3.2 |  | 56.15
EIGHT MILE 2101 | 163912101 | 72.61 |  |  |  | 72.61
EIGHT MILE 2102 | 163912102 | 29.37 |  |  |  | 29.37
EIGHT MILE 2103 | 163912103 | 0 |  |  |  | 0
EIGHT MILE 2104 | 163912104 | 1.36 |  |  |  | 1.36
EIGHT MILE 2105 | 163912105 | 0.49 |  |  |  | 0.49
EIGHT MILE 2106 | 163912106 | 30.16 |  |  |  | 30.16
EL CAPITAN 0004 | 253880004 | 0.01 |  |  |  | 0.01
EL CAPITAN 1102 | 253881102 | 16.59 |  |  |  | 16.59
EL CAPITAN 1103 | 253881103 | 69.97 |  |  |  | 69.97
EL CAPITAN 1104 | 253881104 | 47.15 |  |  |  | 47.15
EL CAPITAN 1105 | 253881105 | 4.84 |  |  |  | 4.84
EL CAPITAN 1106 | 253881106 | 14.32 |  |  |  | 14.32
EL CAPITAN 2109 | 253882109 | 4.48 |  |  |  | 4.48
EL CAPITAN 2110 | 253882110 | 14.69 |  |  |  | 14.69
EL CERRITO G 1101 | 12501101 | 10.12 |  |  |  | 10.12
EL CERRITO G 1102 | 12501102 | 7.8 |  |  |  | 7.8
EL CERRITO G 1103 | 12501103 | 9.05 |  |  |  | 9.05
EL CERRITO G 1104 | 12501104 | 7.85 |  |  |  | 7.85
EL CERRITO G 1105 | 12501105 | 31.68 | 5.58 | 18.89 |  | 7.21
EL CERRITO G 1106 | 12501106 | 4.65 |  |  |  | 4.65
EL CERRITO G 1107 | 12501107 | 3.59 |  |  |  | 3.59
EL CERRITO G 1108 | 12501108 | 14.41 |  | 0 |  | 14.41
EL CERRITO G 1109 | 12501109 | 8 |  |  |  | 8
EL CERRITO G 1110 | 12501110 | 10.16 |  | 0.69 |  | 9.47
EL CERRITO G 1111 | 12501111 | 12.63 |  | 0.2 |  | 12.43
EL CERRITO G 1112 | 12501112 | 24.55 | 1.65 | 0.35 |  | 22.55
EL CERRITO G 1113 | 12501113 | 11.39 |  | 0.1 |  | 11.29
EL CERRITO G 1114 | 12501114 | 6.77 |  |  |  | 6.77
EL DORADO PH 2101 | 152762101 | 138.06 | 102.15 | 25.45 | 0.73 | 9.73
EL DORADO PH 2102 | 152762102 | 33.96 | 33.96 |  |  | 0
EL NIDO 1101 | 252451101 | 57.51 |  |  |  | 57.51
EL NIDO 1102 | 252451102 | 59.45 |  |  |  | 59.45
EL NIDO 1103 | 252451103 | 59.98 |  |  |  | 59.98
EL NIDO 1104 | 252451104 | 86.58 |  |  |  | 86.58
EL PATIO 1101 | 82921101 | 0 |  |  |  | 0
EL PATIO 1102 | 82921102 | 0.98 |  |  |  | 0.98
EL PATIO 1103 | 82921103 | 13.12 |  |  |  | 13.12
EL PATIO 1104 | 82921104 | 11.87 |  |  |  | 11.87
EL PATIO 1105 | 82921105 | 6.94 |  |  |  | 6.94
EL PATIO 1107 | 82921107 | 15.62 |  |  |  | 15.62
EL PATIO 1108 | 82921108 | 6.72 |  |  |  | 6.72
EL PATIO 1109 | 82921109 | 10.55 |  |  |  | 10.55
EL PATIO 1111 | 82921111 | 0.77 |  |  |  | 0.77
EL PATIO 1112 | 82921112 | 19.44 |  |  |  | 19.44
EL PATIO 1113 | 82921113 | 4.75 |  |  |  | 4.75
EL PATIO 1114 | 82921114 | 0.6 |  |  |  | 0.6
EL PATIO 1116 | 82921116 | 8.73 |  |  |  | 8.73
EL PATIO 1117 | 82921117 | 4.17 |  |  |  | 4.17
EL PATIO 1118 | 82921118 | 10.88 |  |  |  | 10.88
EL PATIO 1119 | 82921119 | 8.25 |  |  |  | 8.25
EL PECO 1102 | 253981102 | 52.17 |  |  |  | 52.17
EL PECO 1105 | 253981105 | 101.89 |  |  |  | 101.89
EL PECO 1106 | 253981106 | 38.58 |  |  |  | 38.58
ELECTRA 1101 | 162161101 | 85.08 |  | 81.56 |  | 3.52
ELECTRA 1102 | 162161102 | 19.54 |  | 16.97 |  | 2.57
ELK 1101 | 42981101 | 106.63 |  | 73.18 |  | 33.45
ELK CREEK 1101 | 102781101 | 172.65 |  | 79.1 |  | 93.55
ELK HILLS 1104 | 252441104 | 57.39 |  |  |  | 57.39
ELK HILLS 1106 | 252441106 | 21.37 |  |  |  | 21.37
EMBARCADERO (Z) 1112 | 22871112 | 0 |  |  |  | 0
EMBARCADERO (Z) 1113 | 22871113 | 0.32 |  |  |  | 0.32
EMBARCADERO (Z) 1114 | 22871114 | 0 |  |  |  | 0
EMBARCADERO (Z) 1115 | 22871115 | 0.24 |  |  |  | 0.24
EMBARCADERO (Z) 1116 | 22871116 | 1.05 |  |  |  | 1.05
EMBARCADERO (Z) 1118 | 22871118 | 0.08 |  |  |  | 0.08
EMBARCADERO (Z) 1120 | 22871120 | 0.32 |  |  |  | 0.32
EMBARCADERO (Z) 1122 | 22871122 | 0.01 |  |  |  | 0.01
EMBARCADERO (Z) 1123 | 22871123 | 0.36 |  |  |  | 0.36
EMERALD LAKE 0401 | 24080401 | 13.09 | 2.09 | 6.87 |  | 4.13
EMERALD LAKE 0402 | 24080402 | 6.56 |  | 6.56 |  | 0
ERTA 0403 | 83510403 | 2.98 |  |  |  | 2.98
ERTA 0404 | 83510404 | 6.52 |  |  |  | 6.52
ESQUON 1101 | 102171101 | 69.97 |  |  |  | 69.97
ESQUON 1102 | 102171102 | 50.49 |  |  |  | 50.49
ESQUON 1103 | 102171103 | 20.35 |  |  |  | 20.35
ESTUDILLO 0401 | 13480401 | 4.74 |  | 0.79 |  | 3.95
EUREKA A 1103 | 192121103 | 10.42 |  |  |  | 10.42
EUREKA A 1106 | 192121106 | 1.81 |  |  |  | 1.81
EUREKA A 1107 | 192121107 | 4.5 |  |  |  | 4.5
EUREKA E 1101 | 192331101 | 13.29 |  |  |  | 13.29
EUREKA E 1104 | 192331104 | 26.88 |  | 0.03 |  | 26.85
EUREKA E 1105 | 192331105 | 7.24 |  |  |  | 7.24
EVERGREEN 2101 | 82012101 | 2.53 |  |  |  | 2.53
EVERGREEN 2102 | 82012102 | 10.73 |  |  |  | 10.73
EVERGREEN 2103 | 82012103 | 19.17 |  |  |  | 19.17
EVERGREEN 2104 | 82012104 | 3.54 |  |  |  | 3.54
EVERGREEN 2105 | 82012105 | 4.63 |  |  |  | 4.63
FAIRHAVEN 1103 | 192451103 | 9.43 |  |  |  | 9.43
FAIRHAVEN 1104 | 192451104 | 3.32 |  |  |  | 3.32
FAIRMOUNT 0401 | 12650401 | 5.6 |  | 1.33 |  | 4.27
FAIRMOUNT 0402 | 12650402 | 5.07 |  |  |  | 5.07
FAIRVIEW 2206 | 13432206 | 14.25 |  |  |  | 14.25
FAIRVIEW 2207 | 13432207 | 50.47 |  | 20.92 |  | 29.55
FAIRVIEW 2208 | 13432208 | 10 |  |  |  | 10
FAIRWAY 1103 | 182061103 | 6.79 |  |  |  | 6.79
FAIRWAY 1104 | 182061104 | 22.91 |  |  |  | 22.91
FAIRWAY 1106 | 182061106 | 5.5 |  |  |  | 5.5
FAIRWAY 1107 | 182061107 | 19 |  |  |  | 19
FAIRWAY 1108 | 182061108 | 11.41 |  |  |  | 11.41
FAMOSO 1101 | 252461101 | 39.07 |  |  |  | 39.07
FAMOSO 1102 | 252461102 | 27.37 |  |  |  | 27.37
FAMOSO 1103 | 252461103 | 32.96 |  |  |  | 32.96
FAMOSO 1105 | 252461105 | 10.04 |  |  |  | 10.04
FAMOSO 1107 | 252461107 | 18.81 |  |  |  | 18.81
FELLOWS 2103 | 254242103 | 26.76 |  |  |  | 26.76
FELLOWS 2104 | 254242104 | 77.9 |  |  |  | 77.9
FIGARDEN 2102 | 254552102 | 23.69 |  |  |  | 23.69
FIGARDEN 2103 | 254552103 | 5.48 |  |  |  | 5.48
FIGARDEN 2104 | 254552104 | 1.81 |  |  |  | 1.81
FIGARDEN 2105 | 254552105 | 12.63 |  |  |  | 12.63
FIGARDEN 2107 | 254552107 | 5.43 |  |  |  | 5.43
FIGARDEN 2108 | 254552108 | 4.96 |  |  |  | 4.96
FIGARDEN 2109 | 254552109 | 3.9 |  |  |  | 3.9
FIGARDEN 2110 | 254552110 | 15.8 |  |  |  | 15.8
FIGARDEN 2111 | 254552111 | 4.81 |  |  |  | 4.81
FIGARDEN 2112 | 254552112 | 31.03 |  |  |  | 31.03
FIGARDEN 2113 | 254552113 | 11.42 |  |  |  | 11.42
FIREBAUGH 1101 | 253471101 | 92.25 |  |  |  | 92.25
FIREBAUGH 1102 | 253471102 | 52.69 |  |  |  | 52.69
FIREBAUGH 1103 | 253471103 | 75.36 |  |  |  | 75.36
FITCH MOUNTAIN 1111 | 42751111 | 30.49 |  | 0.29 |  | 30.2
FITCH MOUNTAIN 1112 | 42751112 | 0.01 |  |  |  | 0.01
FITCH MOUNTAIN 1113 | 42751113 | 145.6 | 30.76 | 46.39 |  | 68.45
FLINT 1101 | 152531101 | 18.33 |  | 6.33 |  | 12
FLINT 1102 | 152531102 | 0.12 |  | 0.12 |  | 0
FLORENCE 0401 | 12690401 | 4.28 |  | 0.82 |  | 3.46
FMC 1105 | 83871105 | 16.57 |  |  |  | 16.57
FMC 1108 | 83871108 | 1.35 |  |  |  | 1.35
FMC 1109 | 83871109 | 1.02 |  |  |  | 1.02
FMC 1111 | 83871111 | 1.56 |  |  |  | 1.56
FOOTHILL 1101 | 182951101 | 39.49 |  | 18.83 |  | 20.66
FOOTHILL 1102 | 182951102 | 18.11 |  | 8.48 |  | 9.63
FORESTHILL 1101 | 152181101 | 64.53 | 64.48 | 0.05 |  | 0
FORESTHILL 1102 | 152181102 | 29.48 | 21.71 | 7.77 |  | 0
FORT BRAGG A 1101 | 42761101 | 81.06 |  | 70.39 |  | 10.67
FORT BRAGG A 1102 | 42761102 | 81.62 |  | 66.03 |  | 15.59
FORT BRAGG A 1103 | 42761103 | 2.71 |  | 0.07 |  | 2.64
FORT BRAGG A 1104 | 42761104 | 38.88 |  | 24.89 |  | 13.99
FORT ORD 1101 | 182401101 | 16.86 |  |  |  | 16.86
FORT ORD 2105 | 182402105 | 7.39 |  |  |  | 7.39
FORT ORD 2106 | 182402106 | 24.22 |  | 2.2 |  | 22.02
FORT ORD 2107 | 182402107 | 19.41 |  | 3.78 |  | 15.63
FORT ORD 2108 | 182402108 | 0.9 |  |  |  | 0.9
FORT ROSS 1121 | 42851121 | 93.69 | 21.97 | 70.01 |  | 1.71
FORT SEWARD 1121 | 192321121 | 48.08 |  | 36.14 |  | 11.94
FORT SEWARD 1122 | 192321122 | 21.83 |  | 17.43 |  | 4.4
FRANKLIN 1101 | 13921101 | 9.2 |  | 1.27 |  | 7.93
FRANKLIN 1102 | 13921102 | 4.41 |  |  |  | 4.41
FRANKLIN 1103 | 13921103 | 12.4 |  |  |  | 12.4
FRANKLIN 1104 | 13921104 | 14.67 |  | 7.41 |  | 7.26
FREMONT 1103 | 14351103 | 4.37 |  |  |  | 4.37
FREMONT 1104 | 14351104 | 21.61 |  | 1.08 |  | 20.53
FREMONT 1107 | 14351107 | 15.13 |  |  |  | 15.13
FREMONT 1108 | 14351108 | 4.88 |  |  |  | 4.88
FREMONT 1109 | 14351109 | 13.63 |  |  |  | 13.63
FREMONT 1110 | 14351110 | 10.36 |  |  |  | 10.36
FREMONT 1112 | 14351112 | 0.18 |  |  |  | 0.18
FRENCH CAMP 1101 | 163291101 | 15.5 |  |  |  | 15.5
FRENCH CAMP 1102 | 163291102 | 87 |  |  |  | 87
FRENCH CAMP 1103 | 163291103 | 1.23 |  |  |  | 1.23
FRENCH CAMP 1104 | 163291104 | 5.61 |  |  |  | 5.61
FRENCH GULCH 1101 | 103381101 | 15.98 |  | 15.98 |  | 0
FRENCH GULCH 1102 | 103381102 | 18.73 |  | 18.63 |  | 0.1
FROGTOWN 1701 | 163451701 | 71.73 | 6.65 | 63.84 |  | 1.24
FROGTOWN 1702 | 163451702 | 230.42 |  | 205 |  | 25.42
FRUITLAND 1141 | 192311141 | 26.4 |  | 23.43 |  | 2.97
FRUITLAND 1142 | 192311142 | 67.15 |  | 57.05 | 0.03 | 10.07
FRUITVALE 1101 | 253391101 | 3.34 |  |  |  | 3.34
FRUITVALE 1103 | 253391103 | 12.63 |  |  |  | 12.63
FRUITVALE 1104 | 253391104 | 11.22 |  |  |  | 11.22
FRUITVALE 1105 | 253391105 | 3.41 |  |  |  | 3.41
FRUITVALE 1106 | 253391106 | 9.5 |  |  |  | 9.5
FRUITVALE 1108 | 253391108 | 9.13 |  |  |  | 9.13
FULTON 1101 | 42561101 | 6.7 |  |  |  | 6.7
FULTON 1102 | 42561102 | 61.63 | 1.64 | 26.31 |  | 33.68
FULTON 1103 | 42561103 | 0.01 |  |  |  | 0.01
FULTON 1104 | 42561104 | 8.47 |  | 0.41 |  | 8.06
FULTON 1105 | 42561105 | 41.6 |  |  |  | 41.6
FULTON 1106 | 42561106 | 4.89 |  |  |  | 4.89
FULTON 1107 | 42561107 | 48.31 | 35.17 | 0.01 |  | 13.13
GABILAN 1101 | 182331101 | 72.7 |  | 4.55 |  | 68.15
GABILAN 1102 | 182331102 | 9.77 |  |  |  | 9.77
GALLO 1101 | 254901101 | 0.72 |  |  |  | 0.72
GALLO 1102 | 254901102 | 0.08 |  |  |  | 0.08
GANSNER 1101 | 103021101 | 44.06 | 3 | 30.42 |  | 10.64
GANSO 1103 | 254541103 | 39.42 |  |  |  | 39.42
GANSO 1104 | 254541104 | 37.38 |  |  |  | 37.38
GARBERVILLE 1101 | 192221101 | 161.52 |  | 82.19 |  | 79.33
GARBERVILLE 1102 | 192221102 | 136.61 |  | 122.01 |  | 14.6
GARBERVILLE 1103 | 192221103 | 2.24 |  | 0.48 |  | 1.76
GARCIA 0401 | 43040401 | 2.46 |  | 2.46 |  | 0
GARDNER 0401 | 254930401 | 0.02 |  |  |  | 0.02
GATES 1101 | 253931101 | 15.24 |  |  |  | 15.24
GATES 1102 | 253931102 | 41.79 |  |  |  | 41.79
GATES 1104 | 253931104 | 25.54 |  |  |  | 25.54
GATES 1105 | 253931105 | 39.31 |  |  |  | 39.31
GATES 1106 | 253931106 | 44.6 |  |  |  | 44.6
GATES 1107 | 253931107 | 2.52 |  |  |  | 2.52
GATES 1108 | 253931108 | 2.57 |  |  |  | 2.57
GATES 1109 | 253931109 | 0.3 |  |  |  | 0.3
GATES 1110 | 253931110 | 43.24 |  |  |  | 43.24
GERBER 1101 | 103391101 | 40 |  |  |  | 40
GERBER 1102 | 103391102 | 85.04 |  |  |  | 85.04
GEYSERVILLE 1101 | 42891101 | 138.39 |  | 70.28 |  | 68.11
GEYSERVILLE 1102 | 42891102 | 118.66 | 20.31 | 33.86 |  | 64.49
GIFFEN 1102 | 253151102 | 41.33 |  |  |  | 41.33
GIFFEN 1103 | 253151103 | 50.44 |  |  |  | 50.44
GIFFEN 1106 | 253151106 | 2.17 |  |  |  | 2.17
GIFFEN 1107 | 253151107 | 2.65 |  |  |  | 2.65
GILL 0401 | 13550401 | 3.25 |  |  |  | 3.25
GILL 0402 | 13550402 | 3.92 |  |  |  | 3.92
GIRVAN 1101 | 103401101 | 106.5 | 42.25 | 58.87 |  | 5.38
GIRVAN 1102 | 103401102 | 76.13 | 33.58 | 10.82 |  | 31.73
GLENN 1101 | 102601101 | 137.02 |  | 0.26 |  | 136.76
GLENWOOD 0404 | 24090404 | 6.06 |  |  |  | 6.06
GLENWOOD 0405 | 24090405 | 5.74 |  |  |  | 5.74
GLENWOOD 0406 | 24090406 | 2.31 |  |  |  | 2.31
GLENWOOD 1101 | 24091101 | 5.42 |  |  |  | 5.42
GLENWOOD 1102 | 24091102 | 7.17 |  |  |  | 7.17
GOLDTREE 1105 | 182581105 | 14.64 |  | 6.84 |  | 7.8
GOLDTREE 1107 | 182581107 | 3.53 |  | 0.94 |  | 2.59
GOLDTREE 1108 | 182581108 | 21.57 |  | 3.45 |  | 18.12
GONZALES 1101 | 182131101 | 25.94 |  | 3.89 |  | 22.05
GONZALES 1102 | 182131102 | 0.72 |  |  |  | 0.72
GONZALES 1103 | 182131103 | 6.69 |  |  |  | 6.69
GONZALES 1104 | 182131104 | 54.29 |  | 0.74 |  | 53.55
GOOSE LAKE 1101 | 254201101 | 0.54 |  |  |  | 0.54
GOOSE LAKE 1103 | 254201103 | 74.16 |  |  |  | 74.16
GOOSE LAKE 1106 | 254201106 | 66.48 |  |  |  | 66.48
GOOSE LAKE 2104 | 254202104 | 47.72 |  |  |  | 47.72
GRAND ISLAND 2223 | 62462223 | 96.76 |  |  |  | 96.76
GRAND ISLAND 2224 | 62462224 | 63.62 |  |  |  | 63.62
GRAND ISLAND 2225 | 62462225 | 65.18 |  |  |  | 65.18
GRAND ISLAND 2226 | 62462226 | 20.89 |  |  |  | 20.89
GRAND ISLAND 2227 | 62462227 | 157.79 |  |  |  | 157.79
GRANT 1102 | 14381102 | 4.42 |  |  |  | 4.42
GRANT 1103 | 14381103 | 4.19 |  |  |  | 4.19
GRANT 1104 | 14381104 | 19.29 |  |  |  | 19.29
GRANT 1105 | 14381105 | 13.96 |  |  |  | 13.96
GRANT 1106 | 14381106 | 17.02 |  |  |  | 17.02
GRANT 1107 | 14381107 | 5.37 |  |  |  | 5.37
GRANT 1108 | 14381108 | 22.69 |  |  |  | 22.69
GRASS VALLEY 1101 | 152031101 | 18.82 | 2.31 | 13.78 |  | 2.73
GRASS VALLEY 1102 | 152031102 | 5.79 |  | 0.06 |  | 5.73
GRASS VALLEY 1103 | 152031103 | 87.67 |  | 86.04 |  | 1.63
GRAYS FLAT 0401 | 102530401 | 10.63 |  | 10.63 |  | 0
GREEN VALLEY 2101 | 83192101 | 155.9 | 32.68 | 7.64 |  | 115.58
GREEN VALLEY 2102 | 83192102 | 45.84 |  |  |  | 45.84
GREEN VALLEY 2103 | 83192103 | 68.74 |  |  |  | 68.74
GREEN VALLEY 2104 | 83192104 | 30.18 |  |  |  | 30.18
GREENBRAE 1101 | 43091101 | 1.82 |  |  |  | 1.82
GREENBRAE 1102 | 43091102 | 13.42 | 5.73 |  |  | 7.69
GREENBRAE 1103 | 43091103 | 7.41 |  | 0.75 |  | 6.66
GREENBRAE 1104 | 43091104 | 18.38 |  | 0.18 |  | 18.2
GUALALA 1111 | 42841111 | 37.83 |  | 33.18 |  | 4.65
GUALALA 1112 | 42841112 | 47.39 |  | 42.92 |  | 4.47
GUERNSEY 1101 | 252661101 | 43.38 |  |  |  | 43.38
GUERNSEY 1102 | 252661102 | 41.59 |  |  |  | 41.59
GUERNSEY 1103 | 252661103 | 31.65 |  |  |  | 31.65
GUERNSEY 1104 | 252661104 | 29.96 |  |  |  | 29.96
GUERNSEY 1105 | 252661105 | 2.17 |  |  |  | 2.17
GUERNSEY 1106 | 252661106 | 36.97 |  |  |  | 36.97
GUERNSEY 1108 | 252661108 | 2.17 |  |  |  | 2.17
GUSTINE 1101 | 163111101 | 79.66 |  |  |  | 79.66
GUSTINE 1102 | 163111102 | 137.4 |  |  |  | 137.4
HALF MOON BAY 1101 | 24101101 | 47.06 | 12.56 | 12.37 |  | 22.13
HALF MOON BAY 1102 | 24101102 | 48.04 | 5.57 | 2.86 |  | 39.61
HALF MOON BAY 1103 | 24101103 | 166.4 | 1.42 | 122.3 |  | 42.68
HALSEY 1101 | 152241101 | 68.69 |  | 68.69 |  | 0
HALSEY 1102 | 152241102 | 59.63 |  | 49.36 |  | 10.27
HAMILTON A 1101 | 102121101 | 37.39 |  |  |  | 37.39
HAMILTON A 1102 | 102121102 | 43.6 |  |  |  | 43.6
HAMILTON BRANCH 1101 | 102361101 | 34.47 |  | 24.32 |  | 10.15
HAMMER 1101 | 163301101 | 5.5 |  |  |  | 5.5
HAMMER 1102 | 163301102 | 2.76 |  |  |  | 2.76
HAMMER 1103 | 163301103 | 3.75 |  |  |  | 3.75
HAMMER 1104 | 163301104 | 10.64 |  |  |  | 10.64
HAMMER 1105 | 163301105 | 10.83 |  |  |  | 10.83
HAMMER 1106 | 163301106 | 7.23 |  |  |  | 7.23
HAMMER 1108 | 163301108 | 6.01 |  |  |  | 6.01
HAMMER 1109 | 163301109 | 3.85 |  |  |  | 3.85
HAMMONDS 1101 | 253401101 | 35.11 |  |  |  | 35.11
HAMMONDS 1102 | 253401102 | 44.27 |  |  |  | 44.27
HAMMONDS 1104 | 253401104 | 66.3 |  |  |  | 66.3
HARDING 0401 | 163310401 | 1.01 |  |  |  | 1.01
HARDING 0402 | 163310402 | 3.86 |  |  |  | 3.86
HARDING 0403 | 163310403 | 1.54 |  |  |  | 1.54
HARDING 0404 | 163310404 | 2.7 |  |  |  | 2.7
HARDING 0405 | 163310405 | 2.9 |  |  |  | 2.9
HARDING 0406 | 163310406 | 3.16 |  |  |  | 3.16
HARDWICK 1101 | 253711101 | 71.93 |  |  |  | 71.93
HARDWICK 1102 | 253711102 | 97.84 |  |  |  | 97.84
HARRIS 1108 | 192431108 | 32.62 |  | 1.71 |  | 30.91
HARRIS 1109 | 192431109 | 49.85 |  | 14.29 |  | 35.56
HARTER 1102 | 152851102 | 4.39 |  |  |  | 4.39
HARTER 1104 | 152851104 | 7.24 |  |  |  | 7.24
HARTER 1105 | 152851105 | 23.51 |  |  |  | 23.51
HARTER 1106 | 152851106 | 2.12 |  |  |  | 2.12
HARTER 1107 | 152851107 | 10.23 |  |  |  | 10.23
HARTLEY 1101 | 43211101 | 72.18 |  | 34.7 |  | 37.48
HARTLEY 1102 | 43211102 | 27.56 |  | 4.06 |  | 23.5
HATTON 1101 | 182291101 | 32.97 | 2.67 | 17.71 |  | 12.59
HATTON 1102 | 182291102 | 22.45 |  | 11.39 |  | 11.06
HAYWARD O 0401 | 12240401 | 3.3 |  |  |  | 3.3
HAYWARD O 0402 | 12240402 | 3.71 |  |  |  | 3.71
HENRIETTA 1104 | 252681104 | 36 |  |  |  | 36
HENRIETTA 1106 | 252681106 | 45.91 |  |  |  | 45.91
HENRIETTA 1108 | 252681108 | 22.66 |  |  |  | 22.66
HENRIETTA 1110 | 252681110 | 86.11 |  |  |  | 86.11
HERDLYN 1102 | 163741102 | 76.17 |  |  |  | 76.17
HERDLYN 1103 | 163741103 | 99.21 |  |  |  | 99.21
HICKS 1108 | 83431108 | 12.13 |  |  |  | 12.13
HICKS 1109 | 83431109 | 14.97 |  |  |  | 14.97
HICKS 1110 | 83431110 | 8 |  |  |  | 8
HICKS 1111 | 83431111 | 21.87 |  |  |  | 21.87
HICKS 1112 | 83431112 | 4.43 |  |  |  | 4.43
HICKS 1113 | 83431113 | 19.24 |  |  |  | 19.24
HICKS 1114 | 83431114 | 9.51 |  |  |  | 9.51
HICKS 1115 | 83431115 | 15.41 |  | 0.05 |  | 15.36
HICKS 1116 | 83431116 | 34.25 |  | 13.95 |  | 20.3
HICKS 2101 | 83432101 | 42.38 | 2.24 | 10.16 |  | 29.98
HICKS 2102 | 83432102 | 3.9 |  |  |  | 3.9
HICKS 2103 | 83432103 | 21.55 | 5.28 | 2.09 |  | 14.18
HICKS 2105 | 83432105 | 9.68 |  |  |  | 9.68
HICKS 2111 | 83432111 | 4.57 |  |  |  | 4.57
HIGGINS 1103 | 152691103 | 148.33 |  | 143.51 |  | 4.82
HIGGINS 1104 | 152691104 | 87.96 |  | 72.5 |  | 15.46
HIGGINS 1107 | 152691107 | 32.53 |  | 17.87 |  | 14.66
HIGGINS 1108 | 152691108 | 0.02 |  |  |  | 0.02
HIGGINS 1109 | 152691109 | 86.65 |  | 82.85 |  | 3.8
HIGGINS 1110 | 152691110 | 57.25 |  | 48.9 |  | 8.35
HIGHLANDS 1101 | 43361101 | 0.03 |  | 0.03 |  | 0
HIGHLANDS 1102 | 43361102 | 64.29 | 10.7 | 29.29 |  | 24.3
HIGHLANDS 1103 | 43361103 | 123.89 |  | 110.34 |  | 13.55
HIGHLANDS 1104 | 43361104 | 29.23 |  | 11.91 |  | 17.32
HIGHWAY 1101 | 42651101 | 11.19 |  |  |  | 11.19
HIGHWAY 1102 | 42651102 | 19.88 |  |  |  | 19.88
HIGHWAY 1103 | 42651103 | 6.3 |  |  |  | 6.3
HIGHWAY 1104 | 42651104 | 9.56 |  |  |  | 9.56
HIGHWAY 1105 | 42651105 | 1.04 |  |  |  | 1.04
HIGHWAY 1106 | 42651106 | 15.26 |  |  |  | 15.26
HILLSDALE 0401 | 24110401 | 7.46 |  |  |  | 7.46
HILLSDALE 0402 | 24110402 | 8.02 |  |  |  | 8.02
HILLSDALE 0403 | 24110403 | 3.27 |  |  |  | 3.27
HILLSDALE 0404 | 24110404 | 5.69 |  |  |  | 5.69
HILLSDALE 0405 | 24110405 | 5.9 |  |  |  | 5.9
HOLLISTER 2101 | 182492101 | 25.56 |  |  |  | 25.56
HOLLISTER 2102 | 182492102 | 108.31 |  | 27.73 |  | 80.58
HOLLISTER 2103 | 182492103 | 13.55 |  |  |  | 13.55
HOLLISTER 2104 | 182492104 | 122.85 |  | 6.34 |  | 116.51
HOLLISTER 2105 | 182492105 | 164.92 |  | 64.36 |  | 100.56
HOLLISTER 2106 | 182492106 | 39.29 |  | 8.09 |  | 31.2
HOLLYWOOD 0401 | 13170401 | 5.36 |  | 2.78 |  | 2.58
HONCUT 1101 | 103211101 | 115.13 |  |  |  | 115.13
HONCUT 1102 | 103211102 | 149.07 |  | 2.57 |  | 146.5
HOOPA 1101 | 192401101 | 136.98 | 4.88 | 99.7 |  | 32.4
HOPLAND 1101 | 42251101 | 130.72 |  | 81.59 |  | 49.13
HORSESHOE 1101 | 152571101 | 36.25 |  | 4.93 |  | 31.32
HORSESHOE 1102 | 152571102 | 14.83 |  |  |  | 14.83
HORSESHOE 1103 | 152571103 | 5.24 |  |  |  | 5.24
HORSESHOE 1104 | 152571104 | 11.65 |  | 1.97 |  | 9.68
HORSESHOE 1105 | 152571105 | 2.27 |  |  |  | 2.27
HORSESHOE 1106 | 152571106 | 15.3 |  |  |  | 15.3
HUMBOLDT BAY 1101 | 192341101 | 12.9 |  |  |  | 12.9
HUMBOLDT BAY 1102 | 192341102 | 41.57 |  | 6.33 |  | 35.24
HUNTERS POINT (P) 1101 | 22331101 | 3.73 |  |  |  | 3.73
HUNTERS POINT (P) 1102 | 22331102 | 8.28 |  |  |  | 8.28
HUNTERS POINT (P) 1103 | 22331103 | 5.78 |  |  |  | 5.78
HUNTERS POINT (P) 1104 | 22331104 | 3.62 |  |  |  | 3.62
HUNTERS POINT (P) 1105 | 22331105 | 10.4 |  |  |  | 10.4
HUNTERS POINT (P) 1106 | 22331106 | 1.53 |  |  |  | 1.53
HUNTERS POINT (P) 1107 | 22331107 | 5.26 |  |  |  | 5.26
HUNTERS POINT (P) 1108 | 22331108 | 5.72 |  |  |  | 5.72
HUNTERS POINT (P) 1109 | 22331109 | 1.61 |  |  |  | 1.61
HURON 1106 | 253161106 | 17.05 |  |  |  | 17.05
HURON 1107 | 253161107 | 0.34 |  |  |  | 0.34
HURON 1108 | 253161108 | 10.15 |  |  |  | 10.15
HURON 1109 | 253161109 | 0.34 |  |  |  | 0.34
HURON 1112 | 253161112 | 13.8 |  |  |  | 13.8
HURON 1116 | 253161116 | 19.73 |  |  |  | 19.73
IGNACIO 1101 | 42481101 | 11.63 | 0.5 | 5.72 |  | 5.41
IGNACIO 1102 | 42481102 | 8.52 |  |  |  | 8.52
IGNACIO 1103 | 42481103 | 2.77 |  | 0.62 |  | 2.15
IGNACIO 1104 | 42481104 | 57.17 |  | 6.33 |  | 50.84
IGNACIO 1105 | 42481105 | 20.2 |  | 4.75 |  | 15.45
INDIAN FLAT 1104 | 252691104 | 16.12 |  | 16.12 |  | 0
INDUSTRIAL ACRES 0411 | 182300411 | 2.02 |  |  |  | 2.02
INDUSTRIAL ACRES 0412 | 182300412 | 9.79 |  |  |  | 9.79
INDUSTRIAL ACRES 0413 | 182300413 | 3.71 |  |  |  | 3.71
INDUSTRIAL ACRES 0415 | 182300415 | 1.43 |  |  |  | 1.43
IONE 1101 | 163881101 | 28.99 |  | 14.89 |  | 14.1
JACINTO 1101 | 102851101 | 77.3 |  |  |  | 77.3
JACINTO 1102 | 102851102 | 80.77 |  |  |  | 80.77
JACOBS CORNER 1101 | 254771101 | 62.36 |  |  |  | 62.36
JACOBS CORNER 1102 | 254771102 | 51.45 |  |  |  | 51.45
JAMESON 1101 | 63801101 | 0.01 |  |  |  | 0.01
JAMESON 1102 | 63801102 | 20.16 |  | 8 |  | 12.16
JAMESON 1103 | 63801103 | 10.84 |  | 2.19 |  | 8.65
JAMESON 1104 | 63801104 | 0.08 |  |  |  | 0.08
JAMESON 1105 | 63801105 | 63.85 |  | 16.19 |  | 47.66
JANES CREEK 1101 | 192391101 | 29.32 |  |  |  | 29.32
JANES CREEK 1102 | 192391102 | 6.26 |  |  |  | 6.26
JANES CREEK 1103 | 192391103 | 42.51 |  |  |  | 42.51
JANES CREEK 1104 | 192391104 | 2.57 |  |  |  | 2.57
JARVIS 1101 | 13501101 | 13.72 |  | 0.58 |  | 13.14
JARVIS 1103 | 13501103 | 3.42 |  |  |  | 3.42
JARVIS 1104 | 13501104 | 4.42 |  |  |  | 4.42
JARVIS 1105 | 13501105 | 6.84 |  |  |  | 6.84
JARVIS 1106 | 13501106 | 4.78 |  |  |  | 4.78
JARVIS 1108 | 13501108 | 17.68 |  | 0.7 |  | 16.98
JARVIS 1109 | 13501109 | 4.15 |  |  |  | 4.15
JARVIS 1110 | 13501110 | 5.96 |  |  |  | 5.96
JARVIS 1111 | 13501111 | 18.99 | 0.91 | 0.03 |  | 18.05
JARVIS 1112 | 13501112 | 7.24 |  |  |  | 7.24
JERSEY ISLAND 0401 | 18320401 | 2.88 |  |  |  | 2.88
JESSUP 1101 | 103441101 | 79.63 | 0.2 | 63.69 |  | 15.74
JESSUP 1102 | 103441102 | 86.62 |  | 53.34 |  | 33.28
JESSUP 1103 | 103441103 | 38.12 |  | 3.92 |  | 34.2
JOLON 1102 | 182981102 | 105.89 |  | 65.47 |  | 40.42
JOLON 1103 | 182981103 | 18.57 |  | 12.51 |  | 6.06
JUDAH 0401 | 22400401 | 3.69 |  |  |  | 3.69
JUDAH 0402 | 22400402 | 2.14 |  |  |  | 2.14
KANAKA 1101 | 103221101 | 72.46 | 45.63 | 26.47 |  | 0.36
KEARNEY 1104 | 252701104 | 73.13 |  |  |  | 73.13
KEARNEY 1106 | 252701106 | 39.27 |  |  |  | 39.27
KEARNEY 1110 | 252701110 | 50.46 |  |  |  | 50.46
KEARNEY 1113 | 252701113 | 0.63 |  |  |  | 0.63
KEARNEY 1114 | 252701114 | 13.36 |  |  |  | 13.36
KERCKHOFF 1101 | 252561101 | 34.21 |  | 34.21 |  | 0
KERMAN 1101 | 252711101 | 145.36 |  |  |  | 145.36
KERMAN 1102 | 252711102 | 58.45 |  |  |  | 58.45
KERMAN 1103 | 252711103 | 56.38 |  |  |  | 56.38
KERMAN 1104 | 252711104 | 65.97 |  |  |  | 65.97
KERMAN 1106 | 252711106 | 75.66 |  |  |  | 75.66
KERMAN 1108 | 252711108 | 28.11 |  |  |  | 28.11
KERN OIL 1103 | 252721103 | 11.39 |  |  |  | 11.39
KERN OIL 1104 | 252721104 | 39.14 |  |  |  | 39.14
KERN OIL 1106 | 252721106 | 44.03 |  | 1.31 |  | 42.72
KERN OIL 1107 | 252721107 | 21.16 |  |  |  | 21.16
KERN OIL 1108 | 252721108 | 7.69 |  |  |  | 7.69
KERN OIL 1109 | 252721109 | 11.24 |  |  |  | 11.24
KERN OIL 1110 | 252721110 | 8.55 |  |  |  | 8.55
KERN OIL 1112 | 252721112 | 0.07 |  |  |  | 0.07
KERN OIL 1114 | 252721114 | 21.52 |  |  |  | 21.52
KERN OIL 1116 | 252721116 | 4.59 |  |  |  | 4.59
KERN POWER 2101 | 255262101 | 1.99 |  |  |  | 1.99
KERN POWER 2102 | 255262102 | 4.35 |  |  |  | 4.35
KERN POWER 2103 | 255262103 | 12.51 |  |  |  | 12.51
KERN POWER 2104 | 255262104 | 5.06 |  |  |  | 5.06
KERN POWER 2105 | 255262105 | 12.54 |  |  |  | 12.54
KESWICK 1101 | 103451101 | 51.27 | 47.91 | 3.31 |  | 0.05
KETTLEMAN HILLS 1101 | 252731101 | 38.7 |  |  |  | 38.7
KETTLEMAN HILLS 2104 | 252732104 | 34.6 |  |  |  | 34.6
KING CITY 1101 | 182031101 | 6.91 |  |  |  | 6.91
KING CITY 1102 | 182031102 | 21.54 |  |  |  | 21.54
KING CITY 1103 | 182031103 | 27.78 |  | 17.75 |  | 10.03
KING CITY 1104 | 182031104 | 14.02 |  |  |  | 14.02
KING CITY 1105 | 182031105 | 3.09 |  |  |  | 3.09
KING CITY 1106 | 182031106 | 71.72 |  |  |  | 71.72
KING CITY 1107 | 182031107 | 0.02 |  |  |  | 0.02
KING CITY 1108 | 182031108 | 0.02 |  |  |  | 0.02
KINGSBURG 1102 | 252241102 | 15.54 |  |  |  | 15.54
KINGSBURG 1108 | 252241108 | 41.31 |  |  |  | 41.31
KINGSBURG 1110 | 252241110 | 86.22 |  |  |  | 86.22
KINGSBURG 1111 | 252241111 | 81.82 |  |  |  | 81.82
KINGSBURG 1112 | 252241112 | 14.15 |  |  |  | 14.15
KINGSBURG 1113 | 252241113 | 51.34 |  |  |  | 51.34
KINGSBURG 1114 | 252241114 | 18.59 |  |  |  | 18.59
KINGSBURG 1116 | 252241116 | 113.79 |  |  |  | 113.79
KIRKER 2103 | 14452103 | 8.01 |  |  |  | 8.01
KIRKER 2104 | 14452104 | 17.21 |  | 4.01 |  | 13.2
KIRKER 2105 | 14452105 | 9.31 |  |  |  | 9.31
KIRKER 2106 | 14452106 | 16.23 |  |  |  | 16.23
KIRKER 2107 | 14452107 | 8.05 |  |  |  | 8.05
KIRKER 2108 | 14452108 | 9.57 |  |  |  | 9.57
KIRKER 2109 | 14452109 | 8.62 |  |  |  | 8.62
KNIGHTS LANDING 1101 | 62721101 | 45.1 |  |  |  | 45.1
KNIGHTS LANDING 1102 | 62721102 | 118.89 |  |  |  | 118.89
KONOCTI 1102 | 43311102 | 145.87 | 64.06 | 61.13 |  | 20.68
KONOCTI 1108 | 43311108 | 33.04 |  | 20.4 |  | 12.64
LAKEVIEW 1102 | 253411102 | 52.33 |  |  |  | 52.33
LAKEVIEW 1103 | 253411103 | 22.68 |  |  |  | 22.68
LAKEVIEW 1106 | 253411106 | 36.9 |  |  |  | 36.9
LAKEVIEW 1107 | 253411107 | 26.06 |  |  |  | 26.06
LAKEVILLE 1101 | 43371101 | 19.67 |  |  |  | 19.67
LAKEVILLE 1102 | 43371102 | 50.36 | 0.07 | 18.06 |  | 32.23
LAKEVILLE 1105 | 43371105 | 4.22 |  |  |  | 4.22
LAKEWOOD 1101 | 13531101 | 0.72 |  |  |  | 0.72
LAKEWOOD 1102 | 13531102 | 9.57 |  | 0.1 |  | 9.47
LAKEWOOD 1103 | 13531103 | 2.57 |  |  |  | 2.57
LAKEWOOD 1104 | 13531104 | 11.74 |  |  |  | 11.74
LAKEWOOD 2107 | 13532107 | 33.31 |  | 7.77 |  | 25.54
LAKEWOOD 2108 | 13532108 | 0.53 |  |  |  | 0.53
LAKEWOOD 2109 | 13532109 | 7.27 | 0.42 |  |  | 6.85
LAKEWOOD 2110 | 13532110 | 22.68 |  |  |  | 22.68
LAKEWOOD 2111 | 13532111 | 2.29 |  |  |  | 2.29
LAKEWOOD 2112 | 13532112 | 8.9 |  |  |  | 8.9
LAKEWOOD 2223 | 13532223 | 9.13 |  |  |  | 9.13
LAKEWOOD 2224 | 13532224 | 31.47 | 0.82 |  |  | 30.65
LAKEWOOD 2225 | 13532225 | 3.34 |  |  |  | 3.34
LAKEWOOD 2226 | 13532226 | 8 |  |  |  | 8
LAKEWOOD 2227 | 13532227 | 7.89 | 0.03 |  |  | 7.86
LAMMERS 1101 | 162771101 | 9.67 |  |  |  | 9.67
LAMMERS 1102 | 162771102 | 3.55 |  |  |  | 3.55
LAMMERS 1103 | 162771103 | 9.36 |  |  |  | 9.36
LAMMERS 1105 | 162771105 | 1.79 |  |  |  | 1.79
LAMMERS 1106 | 162771106 | 2.29 |  |  |  | 2.29
LAMMERS 1107 | 162771107 | 9.14 |  |  |  | 9.14
LAMMERS 1108 | 162771108 | 1.11 |  |  |  | 1.11
LAMONT 1102 | 253911102 | 69.13 |  | 3.49 |  | 65.64
LAMONT 1103 | 253911103 | 26.85 |  |  |  | 26.85
LAMONT 1104 | 253911104 | 53.32 |  | 1.43 |  | 51.89
LAMONT 1105 | 253911105 | 37.1 |  |  |  | 37.1
LAMONT 1106 | 253911106 | 22.49 |  |  |  | 22.49
LAMONT 1107 | 253911107 | 46.12 |  |  |  | 46.12
LARKIN (Y) 1107 | 22801107 | 2.36 |  |  |  | 2.36
LARKIN (Y) 1108 | 22801108 | 0.11 |  |  |  | 0.11
LARKIN (Y) 1109 | 22801109 | 0.3 |  |  |  | 0.3
LARKIN (Y) 1110 | 22801110 | 0.99 |  |  |  | 0.99
LARKIN (Y) 1111 | 22801111 | 0.12 |  |  |  | 0.12
LARKIN (Y) 1119 | 22801119 | 1.72 |  |  |  | 1.72
LARKIN (Y) 1120 | 22801120 | 2.1 |  |  |  | 2.1
LARKIN (Y) 1127 | 22801127 | 1.53 |  |  |  | 1.53
LARKIN (Y) 1128 | 22801128 | 0.11 |  |  |  | 0.11
LARKIN (Y) 1135 | 22801135 | 1.65 |  |  |  | 1.65
LARKIN (Y) 1136 | 22801136 | 1.29 |  |  |  | 1.29
LARKIN (Y) 1137 | 22801137 | 0.01 |  |  |  | 0.01
LARKIN (Y) 1138 | 22801138 | 1.48 |  |  |  | 1.48
LARKIN (Y) 1140 | 22801140 | 0.08 |  |  |  | 0.08
LARKIN (Y) 1141 | 22801141 | 0.03 |  |  |  | 0.03
LAS GALLINAS A 1103 | 42991103 | 5.28 |  |  |  | 5.28
LAS GALLINAS A 1104 | 42991104 | 12.95 |  | 0.28 |  | 12.67
LAS GALLINAS A 1105 | 42991105 | 21.48 | 8.41 | 2.85 |  | 10.22
LAS GALLINAS A 1106 | 42991106 | 15.83 | 0.02 | 1.16 |  | 14.65
LAS GALLINAS A 1107 | 42991107 | 8.05 |  | 0.02 |  | 8.03
LAS PALMAS 1101 | 254921101 | 0.27 |  |  |  | 0.27
LAS POSITAS 2103 | 14402103 | 2.99 |  |  |  | 2.99
LAS POSITAS 2104 | 14402104 | 11.37 |  |  |  | 11.37
LAS POSITAS 2105 | 14402105 | 3.76 |  |  |  | 3.76
LAS POSITAS 2106 | 14402106 | 16.19 |  |  |  | 16.19
LAS POSITAS 2107 | 14402107 | 11.24 |  |  |  | 11.24
LAS POSITAS 2108 | 14402108 | 19.96 |  | 6.85 |  | 13.11
LAS POSITAS 2109 | 14402109 | 13.26 |  |  |  | 13.26
LAS POSITAS 2110 | 14402110 | 19.65 |  |  |  | 19.65
LAS PULGAS 0401 | 24120401 | 8.88 |  | 1.97 |  | 6.91
LAS PULGAS 0402 | 24120402 | 2.57 |  |  |  | 2.57
LAS PULGAS 0403 | 24120403 | 7.84 |  |  |  | 7.84
LAS PULGAS 0404 | 24120404 | 4.05 |  |  |  | 4.05
LATHROP 0402 | 163030402 | 0.04 |  |  |  | 0.04
LAURELES 1111 | 182371111 | 106.2 | 5.72 | 99.39 |  | 1.09
LAURELES 1112 | 182371112 | 43.16 |  | 33.05 |  | 10.11
LAWNDALE 0401 | 22440401 | 4.73 |  |  |  | 4.73
LAWNDALE 0402 | 22440402 | 4.75 |  |  |  | 4.75
LAWRENCE 1102 | 83421102 | 0.08 |  |  |  | 0.08
LAWRENCE 1103 | 83421103 | 0.23 |  |  |  | 0.23
LAWRENCE 1104 | 83421104 | 9.34 |  |  |  | 9.34
LAWRENCE 1105 | 83421105 | 1.07 |  |  |  | 1.07
LAWRENCE 1106 | 83421106 | 2.77 |  |  |  | 2.77
LAWRENCE 1107 | 83421107 | 4.63 |  |  |  | 4.63
LAWRENCE 1108 | 83421108 | 0.86 |  |  |  | 0.86
LAWRENCE 1109 | 83421109 | 1.96 |  |  |  | 1.96
LAWRENCE 1110 | 83421110 | 4.92 |  |  |  | 4.92
LAWRENCE 1111 | 83421111 | 3.71 |  |  |  | 3.71
LAWRENCE 1112 | 83421112 | 11.06 |  |  |  | 11.06
LAWRENCE 1113 | 83421113 | 5.65 |  |  |  | 5.65
LAYTONVILLE 1101 | 42681101 | 79.53 |  | 51.72 |  | 27.81
LAYTONVILLE 1102 | 42681102 | 125.38 | 3.39 | 107.15 |  | 14.84
LE GRAND 1104 | 255361104 | 56.91 |  |  |  | 56.91
LE GRAND 1106 | 255361106 | 59.89 |  |  |  | 59.89
LE GRAND 1110 | 255361110 | 91.79 |  |  |  | 91.79
LE GRAND 1112 | 255361112 | 68.74 |  |  |  | 68.74
LEMOORE 1101 | 253601101 | 41.55 |  |  |  | 41.55
LEMOORE 1102 | 253601102 | 11.54 |  |  |  | 11.54
LEMOORE 1103 | 253601103 | 14.43 |  |  |  | 14.43
LEMOORE 1104 | 253601104 | 49.88 |  |  |  | 49.88
LEMOORE 1105 | 253601105 | 12.03 |  |  |  | 12.03
LERDO 1110 | 253491110 | 11.91 |  |  |  | 11.91
LERDO 1111 | 253491111 | 36.22 |  |  |  | 36.22
LERDO 1112 | 253491112 | 23.94 |  |  |  | 23.94
LERDO 1113 | 253491113 | 38.51 |  |  |  | 38.51
LERDO 1114 | 253491114 | 9.9 |  |  |  | 9.9
LERDO 1115 | 253491115 | 15.88 |  |  |  | 15.88
LERDO 1116 | 253491116 | 42.26 |  |  |  | 42.26
LINCOLN 1101 | 153701101 | 50.24 |  | 16.09 |  | 34.15
LINCOLN 1102 | 153701102 | 9.58 |  |  |  | 9.58
LINCOLN 1104 | 153701104 | 136.5 |  | 33.43 |  | 103.07
LINCOLN 1105 | 153701105 | 32.24 |  |  |  | 32.24
LINCOLN 2108 | 153702108 | 1.63 |  |  |  | 1.63
LINCOLN 2109 | 153702109 | 0.86 |  |  |  | 0.86
LINDEN 1101 | 162071101 | 34.75 |  |  |  | 34.75
LINDEN 1103 | 162071103 | 60.06 |  |  |  | 60.06
LINDEN 1104 | 162071104 | 56 |  |  |  | 56
LIVE OAK 1101 | 153771101 | 28.43 |  |  |  | 28.43
LIVE OAK 1102 | 153771102 | 25.68 |  |  |  | 25.68
LIVE OAK 1104 | 153771104 | 112.27 |  |  |  | 112.27
LIVERMORE 1101 | 12141101 | 6.04 |  |  |  | 6.04
LIVERMORE 1102 | 12141102 | 4.22 |  |  |  | 4.22
LIVERMORE 1103 | 12141103 | 4.61 |  |  |  | 4.61
LIVERMORE 1104 | 12141104 | 8.63 |  |  |  | 8.63
LIVINGSTON 1101 | 252261101 | 103.25 |  |  |  | 103.25
LIVINGSTON 1102 | 252261102 | 13.62 |  |  |  | 13.62
LIVINGSTON 1104 | 252261104 | 50.61 |  |  |  | 50.61
LIVINGSTON 1105 | 252261105 | 88.76 |  |  |  | 88.76
LIVINGSTON 1106 | 252261106 | 55.35 |  |  |  | 55.35
LLAGAS 2101 | 83182101 | 101.98 |  | 21.37 |  | 80.61
LLAGAS 2102 | 83182102 | 12.63 |  |  |  | 12.63
LLAGAS 2103 | 83182103 | 16.71 |  |  |  | 16.71
LLAGAS 2104 | 83182104 | 30.02 |  | 2.68 |  | 27.34
LLAGAS 2105 | 83182105 | 17.55 | 0.12 | 0.46 |  | 16.97
LLAGAS 2106 | 83182106 | 32.26 |  | 1.18 |  | 31.08
LLAGAS 2107 | 83182107 | 22.28 | 3.63 | 2.64 |  | 16.01
LOCKEFORD 2101 | 163682101 | 90.85 |  |  |  | 90.85
LOCKEFORD 2102 | 163682102 | 242.45 |  |  |  | 242.45
LOCKHEED NO 2 1103 | 83001103 | 0.52 |  |  |  | 0.52
LOCKHEED NO 2 1106 | 83001106 | 0.37 |  |  |  | 0.37
LOCKHEED NO 2 1107 | 83001107 | 0.77 |  |  |  | 0.77
LOCKHEED NO 2 1108 | 83001108 | 1.25 |  |  |  | 1.25
LODI 1101 | 162111101 | 44.39 |  |  |  | 44.39
LODI 1102 | 162111102 | 97.07 |  |  |  | 97.07
LOGAN CREEK 2101 | 103142101 | 163.28 |  |  |  | 163.28
LOGAN CREEK 2102 | 103142102 | 240.91 |  | 3.48 |  | 237.43
LOGAN CREEK 2103 | 103142103 | 3.17 |  |  |  | 3.17
LOGAN CREEK 2199 | 103142199 | 0.03 |  |  |  | 0.03
LONE TREE 2101 | 13232101 | 1.15 |  |  |  | 1.15
LONE TREE 2102 | 13232102 | 16.62 |  |  |  | 16.62
LONE TREE 2105 | 13232105 | 21.8 |  | 10.71 |  | 11.09
LOS ALTOS 1103 | 82241103 | 6.79 |  |  |  | 6.79
LOS ALTOS 1104 | 82241104 | 12.93 |  |  |  | 12.93
LOS ALTOS 1105 | 82241105 | 1.81 |  |  |  | 1.81
LOS ALTOS 1106 | 82241106 | 9.93 |  |  |  | 9.93
LOS ALTOS 1107 | 82241107 | 2.96 |  |  |  | 2.96
LOS COCHES 1101 | 182151101 | 24.47 |  | 2.29 |  | 22.18
LOS COCHES 1102 | 182151102 | 28.95 |  |  |  | 28.95
LOS GATOS 1101 | 82021101 | 20.95 |  | 11.8 |  | 9.15
LOS GATOS 1102 | 82021102 | 6.1 |  | 1.1 |  | 5
LOS GATOS 1106 | 82021106 | 70.61 | 67.35 | 2.43 |  | 0.83
LOS GATOS 1107 | 82021107 | 93.96 | 80.52 | 12.66 |  | 0.78
LOS GATOS 1108 | 82021108 | 6.17 | 1.13 | 3.28 |  | 1.76
LOS MOLINOS 1101 | 103481101 | 55.79 |  | 0.19 |  | 55.6
LOS MOLINOS 1102 | 103481102 | 49.36 |  |  |  | 49.36
LOS OSITOS 2101 | 182082101 | 33.71 |  |  |  | 33.71
LOS OSITOS 2102 | 182082102 | 51.57 |  | 2.48 |  | 49.09
LOS OSITOS 2103 | 182082103 | 177.64 |  | 44.31 |  | 133.33
LOST HILLS 1101 | 254281101 | 0.01 |  |  |  | 0.01
LOW GAP 1101 | 192411101 | 72.3 |  | 70.59 |  | 1.71
LOYOLA 0401 | 82160401 | 8.28 |  |  |  | 8.28
LOYOLA 0403 | 82160403 | 8.84 |  |  |  | 8.84
LOYOLA 1101 | 82161101 | 19.35 |  |  |  | 19.35
LOYOLA 1102 | 82161102 | 50.86 |  | 0.02 |  | 50.84
LUCERNE 1103 | 43351103 | 52.89 |  | 26.64 |  | 26.25
LUCERNE 1106 | 43351106 | 47.64 |  | 36.79 |  | 10.85
MABURY 1101 | 82191101 | 4.18 |  |  |  | 4.18
MABURY 1103 | 82191103 | 7.89 |  |  |  | 7.89
MABURY 1104 | 82191104 | 13.71 |  |  |  | 13.71
MABURY 1105 | 82191105 | 0.85 |  |  |  | 0.85
MABURY 1106 | 82191106 | 15.05 |  |  |  | 15.05
MADERA 1102 | 252761102 | 0.02 |  |  |  | 0.02
MADERA 1104 | 252761104 | 14.64 |  |  |  | 14.64
MADERA 1106 | 252761106 | 8.71 |  |  |  | 8.71
MADERA 1112 | 252761112 | 12.27 |  |  |  | 12.27
MADERA 1114 | 252761114 | 9.68 |  |  |  | 9.68
MADERA 1116 | 252761116 | 2.89 |  |  |  | 2.89
MADERA 1118 | 252761118 | 9.02 |  |  |  | 9.02
MADERA 1119 | 252761119 | 126.08 |  |  |  | 126.08
MADISON 1103 | 63171103 | 72.69 |  |  |  | 72.69
MADISON 1105 | 63171105 | 84.8 |  | 0.35 |  | 84.45
MADISON 2101 | 63172101 | 166.84 |  | 5.25 |  | 161.59
MAGUNDEN 1101 | 252771101 | 19.48 |  |  |  | 19.48
MAGUNDEN 1104 | 252771104 | 5.18 |  |  |  | 5.18
MAGUNDEN 1105 | 252771105 | 13.72 |  |  |  | 13.72
MAGUNDEN 1106 | 252771106 | 16.02 |  |  |  | 16.02
MAGUNDEN 1108 | 252771108 | 30.66 |  | 3.93 |  | 26.73
MAGUNDEN 2108 | 252772108 | 45.23 |  |  |  | 45.23
MAGUNDEN 2109 | 252772109 | 14.41 |  |  |  | 14.41
MAINE PRAIRIE 0401 | 68670401 | 0.06 |  |  |  | 0.06
MALAGA 1101 | 254251101 | 3.55 |  |  |  | 3.55
MALAGA 1102 | 254251102 | 55.39 |  |  |  | 55.39
MALAGA 1103 | 254251103 | 20.18 |  |  |  | 20.18
MALAGA 1104 | 254251104 | 15.37 |  |  |  | 15.37
MALAGA 1105 | 254251105 | 0.64 |  |  |  | 0.64
MALAGA 1106 | 254251106 | 9.25 |  |  |  | 9.25
MALAGA 1107 | 254251107 | 2.65 |  |  |  | 2.65
MALAGA 1108 | 254251108 | 20.04 |  |  |  | 20.04
MALAGA 1109 | 254251109 | 3.31 |  |  |  | 3.31
MALAGA 1110 | 254251110 | 15.38 |  |  |  | 15.38
MALAGA 1111 | 254251111 | 8.89 |  |  |  | 8.89
MANCHESTER 1101 | 253921101 | 11.83 |  |  |  | 11.83
MANCHESTER 1102 | 253921102 | 13.62 |  |  |  | 13.62
MANCHESTER 1103 | 253921103 | 7.17 |  |  |  | 7.17
MANCHESTER 1104 | 253921104 | 3.97 |  |  |  | 3.97
MANCHESTER 1105 | 253921105 | 9.04 |  |  |  | 9.04
MANCHESTER 1106 | 253921106 | 14.91 |  |  |  | 14.91
MANCHESTER 1107 | 253921107 | 8.68 |  |  |  | 8.68
MANCHESTER 1108 | 253921108 | 14.64 |  |  |  | 14.64
MANCHESTER 1109 | 253921109 | 15.79 |  |  |  | 15.79
MANCHESTER 1110 | 253921110 | 14.46 |  |  |  | 14.46
MANCHESTER 1111 | 253921111 | 14.44 |  |  |  | 14.44
MANCHESTER 1112 | 253921112 | 15.95 |  |  |  | 15.95
MANTECA 1701 | 162611701 | 6.15 |  |  |  | 6.15
MANTECA 1702 | 162611702 | 14.06 |  |  |  | 14.06
MANTECA 1703 | 162611703 | 15.7 |  |  |  | 15.7
MANTECA 1704 | 162611704 | 7.55 |  |  |  | 7.55
MANTECA 1705 | 162611705 | 34.85 |  |  |  | 34.85
MANTECA 1706 | 162611706 | 7.49 |  |  |  | 7.49
MANTECA 1707 | 162611707 | 7.94 |  |  |  | 7.94
MANTECA 1708 | 162611708 | 9.7 |  |  |  | 9.7
MAPLE 0401 | 13520401 | 3.66 |  |  |  | 3.66
MAPLE CREEK 1101 | 192101101 | 32.8 |  | 9.28 |  | 23.52
MARICOPA 1101 | 254211101 | 38.36 |  |  |  | 38.36
MARICOPA 1102 | 254211102 | 37.75 |  |  |  | 37.75
MARINA (F) 0401 | 22780401 | 0.53 |  |  |  | 0.53
MARINA (F) 0402 | 22780402 | 0.48 |  |  |  | 0.48
MARINA (F) 0403 | 22780403 | 0.04 |  |  |  | 0.04
MARINA (F) 0404 | 22780404 | 0.37 |  |  |  | 0.37
MARINA (F) 0405 | 22780405 | 0.14 |  |  |  | 0.14
MARINA (F) 0407 | 22780407 | 1.42 |  |  |  | 1.42
MARINA (F) 0408 | 22780408 | 0.52 |  |  |  | 0.52
MARINA (F) 1101 | 22781101 | 0 |  |  |  | 0
MARINA (F) 1102 | 22781102 | 0 |  |  |  | 0
MARINA (F) 1103 | 22781103 | 0.2 |  |  |  | 0.2
MARIPOSA 2101 | 254452101 | 257.85 | 75.47 | 177.45 |  | 4.93
MARIPOSA 2102 | 254452102 | 257.9 | 56.8 | 188.16 |  | 12.94
MARIPOSA REMOTE 0001 | 257010001 | 0.01 |  | 0.01 |  | 0
MARTELL 1101 | 163011101 | 82.53 |  | 70.23 |  | 12.3
MARTELL 1102 | 163011102 | 12.11 |  | 6.88 |  | 5.23
MARTELL 1103 | 163011103 | 29.39 |  | 20.31 |  | 9.08
MARYSVILLE 1102 | 152011102 | 7.44 |  |  |  | 7.44
MARYSVILLE 1103 | 152011103 | 12.03 |  |  |  | 12.03
MARYSVILLE 1104 | 152011104 | 5.54 |  |  |  | 5.54
MARYSVILLE 1105 | 152011105 | 8.6 |  |  |  | 8.6
MARYSVILLE 1106 | 152011106 | 3.53 |  |  |  | 3.53
MARYSVILLE 1107 | 152011107 | 8.52 |  |  |  | 8.52
MARYSVILLE 1108 | 152011108 | 51.56 |  |  |  | 51.56
MAXWELL 1102 | 62881102 | 60.09 |  |  |  | 60.09
MAXWELL 1105 | 62881105 | 88.64 |  | 3.9 |  | 84.74
MAXWELL 1106 | 62881106 | 29.6 |  |  |  | 29.6
MC ARTHUR 1101 | 103491101 | 178.95 |  | 64.9 |  | 114.05
MC ARTHUR 1102 | 103491102 | 30.19 |  | 1.08 |  | 29.11
MC CALL 1101 | 254121101 | 95.02 |  |  |  | 95.02
MC CALL 1102 | 254121102 | 25.11 |  |  |  | 25.11
MC CALL 1103 | 254121103 | 17.18 |  |  |  | 17.18
MC CALL 1104 | 254121104 | 16.64 |  |  |  | 16.64
MC CALL 1105 | 254121105 | 15.14 |  |  |  | 15.14
MC CALL 1106 | 254121106 | 76.93 |  |  |  | 76.93
MC CALL 1107 | 254121107 | 100.02 |  |  |  | 100.02
MC CALL 1108 | 254121108 | 56.04 |  |  |  | 56.04
MC FARLAND 1101 | 253181101 | 14.15 |  |  |  | 14.15
MC FARLAND 1102 | 253181102 | 42.12 |  |  |  | 42.12
MC FARLAND 1104 | 253181104 | 37.95 |  |  |  | 37.95
MC FARLAND 1105 | 253181105 | 19.83 |  |  |  | 19.83
MC KEE 1103 | 83531103 | 21.98 |  | 0.58 |  | 21.4
MC KEE 1104 | 83531104 | 15.57 |  |  |  | 15.57
MC KEE 1105 | 83531105 | 8.32 |  |  |  | 8.32
MC KEE 1106 | 83531106 | 15.19 |  |  |  | 15.19
MC KEE 1107 | 83531107 | 38.03 |  | 2.68 |  | 35.35
MC KEE 1108 | 83531108 | 10.44 |  | 0.66 |  | 9.78
MC KEE 1109 | 83531109 | 1.77 |  |  |  | 1.77
MC KEE 1110 | 83531110 | 1.67 |  |  |  | 1.67
MC KEE 1111 | 83531111 | 26.63 |  | 8.7 |  | 17.93
MC KEE 1112 | 83531112 | 16.68 |  |  |  | 16.68
MC MULLIN 1104 | 254411104 | 62.11 |  |  |  | 62.11
MC MULLIN 1105 | 254411105 | 57.86 |  |  |  | 57.86
MC MULLIN 1106 | 254411106 | 93.72 |  |  |  | 93.72
MCKITTRICK 1101 | 252781101 | 52.72 |  |  |  | 52.72
MEADOW LANE 2102 | 14302102 | 0.01 |  |  |  | 0.01
MEADOW LANE 2103 | 14302103 | 21.46 |  |  |  | 21.46
MEADOW LANE 2104 | 14302104 | 4.17 |  |  |  | 4.17
MEADOW LANE 2105 | 14302105 | 14.37 |  |  |  | 14.37
MEADOW LANE 2106 | 14302106 | 23.43 | 0.74 | 0.11 |  | 22.58
MEADOW LANE 2107 | 14302107 | 8.44 |  |  |  | 8.44
MEADOW LANE 2108 | 14302108 | 23.89 |  |  |  | 23.89
MEADOW LANE 2109 | 14302109 | 0.58 |  |  |  | 0.58
MEADOW LANE 2110 | 14302110 | 6.57 |  |  |  | 6.57
MENDOCINO 1101 | 42951101 | 74.59 | 13.37 | 18.76 |  | 42.46
MENDOCINO 1102 | 42951102 | 0.05 |  |  |  | 0.05
MENDOTA 1101 | 252311101 | 1.61 |  |  |  | 1.61
MENDOTA 1102 | 252311102 | 103.48 |  |  |  | 103.48
MENDOTA 1103 | 252311103 | 15.79 |  |  |  | 15.79
MENDOTA 1104 | 252311104 | 62.33 |  |  |  | 62.33
MENLO 0401 | 24130401 | 6.41 |  |  |  | 6.41
MENLO 0402 | 24130402 | 7.55 |  |  |  | 7.55
MENLO 0403 | 24130403 | 8.26 |  |  |  | 8.26
MENLO 0404 | 24130404 | 8.17 |  |  |  | 8.17
MENLO 1101 | 24131101 | 1.51 |  |  |  | 1.51
MENLO 1102 | 24131102 | 63.69 | 0.01 | 28.25 |  | 35.43
MENLO 1103 | 24131103 | 56.98 |  | 39.73 |  | 17.25
MENLO 1104 | 24131104 | 16.79 |  |  |  | 16.79
MERCED 1108 | 252801108 | 69.46 |  |  |  | 69.46
MERCED 1114 | 252801114 | 58.04 |  |  |  | 58.04
MERCED 1116 | 252801116 | 77.62 |  |  |  | 77.62
MERCED 2101 | 252802101 | 29.94 |  |  |  | 29.94
MERCED 2102 | 252802102 | 25.96 |  |  |  | 25.96
MERCED FALLS 1102 | 252811102 | 153.29 |  | 93.43 |  | 59.86
MERIDIAN 1101 | 62541101 | 57.74 |  |  |  | 57.74
MERIDIAN 1102 | 62541102 | 71.9 |  |  |  | 71.9
MESA 1101 | 182821101 | 81.81 | 11.14 | 37.25 |  | 33.42
MESA 1102 | 182821102 | 3.69 |  |  |  | 3.69
MESA 1103 | 182821103 | 75.79 |  | 9.98 |  | 65.81
MESA 1104 | 182821104 | 41.29 |  |  |  | 41.29
METTLER 1109 | 163701109 | 20.37 |  |  |  | 20.37
METTLER 1110 | 163701110 | 38.04 |  |  |  | 38.04
MIDDLE RIVER 1101 | 162091101 | 31.34 |  |  |  | 31.34
MIDDLE RIVER 1102 | 162091102 | 32.09 |  |  |  | 32.09
MIDDLE RIVER 1103 | 162091103 | 28.53 |  |  |  | 28.53
MIDDLETOWN 1101 | 43141101 | 105.9 | 80.67 | 9.22 |  | 16.01
MIDDLETOWN 1102 | 43141102 | 56.08 | 0.04 | 38.32 |  | 17.72
MIDDLETOWN 1103 | 43141103 | 35.5 | 6.14 | 13.98 |  | 15.38
MIDWAY 1101 | 252611101 | 60.33 |  |  |  | 60.33
MIDWAY 1102 | 252611102 | 52.66 |  |  |  | 52.66
MIDWAY 1103 | 252611103 | 30.61 |  |  |  | 30.61
MIDWAY 1104 | 252611104 | 36.82 |  |  |  | 36.82
MILLBRAE 0401 | 22690401 | 2.82 |  |  |  | 2.82
MILLBRAE 0403 | 22690403 | 4.9 |  |  |  | 4.9
MILLBRAE 0404 | 22690404 | 7.08 |  |  |  | 7.08
MILLBRAE 1101 | 22691101 | 3.98 |  |  |  | 3.98
MILLBRAE 1102 | 22691102 | 4.76 |  |  |  | 4.76
MILLBRAE 1103 | 22691103 | 0.18 |  |  |  | 0.18
MILLBRAE 1104 | 22691104 | 15.9 |  |  |  | 15.9
MILLBRAE 1105 | 22691105 | 0.26 |  |  |  | 0.26
MILLBRAE 1106 | 22691106 | 3.71 |  |  |  | 3.71
MILLBRAE 1107 | 22691107 | 4.77 |  |  |  | 4.77
MILLBRAE 1108 | 22691108 | 14.15 |  |  |  | 14.15
MILPITAS 1101 | 82831101 | 4.1 |  |  |  | 4.1
MILPITAS 1103 | 82831103 | 0.07 |  |  |  | 0.07
MILPITAS 1104 | 82831104 | 1.04 |  |  |  | 1.04
MILPITAS 1105 | 82831105 | 4.73 |  | 0.07 |  | 4.66
MILPITAS 1106 | 82831106 | 3.14 |  |  |  | 3.14
MILPITAS 1108 | 82831108 | 13.3 |  | 0.02 |  | 13.28
MILPITAS 1109 | 82831109 | 49.48 |  | 29.94 |  | 19.54
MILPITAS 2110 | 82832110 | 10.37 |  |  |  | 10.37
MILPITAS 2111 | 82832111 | 1.8 |  |  |  | 1.8
MILPITAS 2112 | 82832112 | 0.87 |  |  |  | 0.87
MILPITAS 2113 | 82832113 | 0.12 |  |  |  | 0.12
MILPITAS 2114 | 82832114 | 0.17 |  |  |  | 0.17
MIRA VISTA 0401 | 12330401 | 8.69 |  |  |  | 8.69
MIRA VISTA 0403 | 12330403 | 7.1 |  |  |  | 7.1
MIRABEL 1101 | 42091101 | 51.35 | 19.95 | 8.95 |  | 22.45
MIRABEL 1102 | 42091102 | 57.6 | 31.89 | 4.82 |  | 20.89
MISSION (X) 0401 | 22010401 | 1.63 |  |  |  | 1.63
MISSION (X) 1102 | 22011102 | 0.17 |  |  |  | 0.17
MISSION (X) 1108 | 22011108 | 5.24 |  |  |  | 5.24
MISSION (X) 1109 | 22011109 | 1.13 |  |  |  | 1.13
MISSION (X) 1110 | 22011110 | 5.72 |  |  |  | 5.72
MISSION (X) 1113 | 22011113 | 2.63 |  |  |  | 2.63
MISSION (X) 1116 | 22011116 | 3.02 |  |  |  | 3.02
MISSION (X) 1118 | 22011118 | 0.6 |  |  |  | 0.6
MISSION (X) 1124 | 22011124 | 0.71 |  |  |  | 0.71
MISSION (X) 1125 | 22011125 | 0.97 |  |  |  | 0.97
MISSION (X) 1127 | 22011127 | 0.47 |  |  |  | 0.47
MISSION (X) 1128 | 22011128 | 0.77 |  |  |  | 0.77
MIWUK 1701 | 163661701 | 76.12 | 74.58 | 1.54 |  | 0
MIWUK 1702 | 163661702 | 74.53 | 71.89 | 2.64 |  | 0
MOLINO 1101 | 42571101 | 90.26 | 7.16 | 26.47 |  | 56.63
MOLINO 1102 | 42571102 | 161.09 | 90.1 | 19.53 |  | 51.46
MOLINO 1103 | 42571103 | 77.75 |  |  |  | 77.75
MOLINO 1104 | 42571104 | 61.22 |  | 2.38 |  | 58.84
MONARCH 0401 | 162300401 | 3.2 |  |  |  | 3.2
MONARCH 0402 | 162300402 | 2.84 |  |  |  | 2.84
MONARCH 0403 | 162300403 | 4.61 |  |  |  | 4.61
MONROE 1104 | 43301104 | 5.21 |  |  |  | 5.21
MONROE 1105 | 43301105 | 10.67 |  |  |  | 10.67
MONROE 1106 | 43301106 | 13.49 |  |  |  | 13.49
MONROE 2102 | 43302102 | 4.86 |  |  |  | 4.86
MONROE 2103 | 43302103 | 11.52 | 0.45 |  |  | 11.07
MONROE 2107 | 43302107 | 10.36 | 0.61 |  |  | 9.75
MONTAGUE 2101 | 83892101 | 0.87 |  |  |  | 0.87
MONTAGUE 2102 | 83892102 | 0.81 |  |  |  | 0.81
MONTAGUE 2103 | 83892103 | 0.94 |  |  |  | 0.94
MONTAGUE 2104 | 83892104 | 0.84 |  |  |  | 0.84
MONTAGUE 2105 | 83892105 | 0.78 |  |  |  | 0.78
MONTAGUE 2106 | 83892106 | 0 |  |  |  | 0
MONTAGUE 2108 | 83892108 | 0.93 |  |  |  | 0.93
MONTAGUE 2109 | 83892109 | 0.81 |  |  |  | 0.81
MONTE RIO 1111 | 42811111 | 63.88 | 43.76 | 13.32 |  | 6.8
MONTE RIO 1112 | 42811112 | 19.68 | 19.68 |  |  | 0
MONTE RIO 1113 | 42811113 | 61.04 | 61.04 |  |  | 0
MONTICELLO 1101 | 43051101 | 123.11 |  | 107.78 |  | 15.33
MORAGA 1101 | 13801101 | 25.72 | 16.41 | 4.79 |  | 4.52
MORAGA 1102 | 13801102 | 13.3 | 2.91 | 2.1 |  | 8.29
MORAGA 1103 | 13801103 | 17.44 | 0.12 | 2 |  | 15.32
MORAGA 1104 | 13801104 | 21.15 | 0.01 | 13.63 |  | 7.51
MORAGA 1105 | 13801105 | 19.72 | 6.87 | 0.81 |  | 12.04
MORGAN HILL 2104 | 83242104 | 20.9 |  | 5.74 |  | 15.16
MORGAN HILL 2105 | 83242105 | 82.09 | 14.1 | 35.87 |  | 32.12
MORGAN HILL 2106 | 83242106 | 39.06 |  | 0.12 |  | 38.94
MORGAN HILL 2108 | 83242108 | 13.09 |  |  |  | 13.09
MORGAN HILL 2109 | 83242109 | 26.36 |  | 2.45 |  | 23.91
MORGAN HILL 2110 | 83242110 | 32.65 |  | 2.22 |  | 30.43
MORGAN HILL 2111 | 83242111 | 72.48 | 16.46 | 35 |  | 21.02
MORMON 1101 | 163211101 | 62.42 |  |  |  | 62.42
MORMON 1102 | 163211102 | 87.99 |  |  |  | 87.99
MORMON 1103 | 163211103 | 23.44 |  |  |  | 23.44
MORRO BAY 1101 | 183011101 | 46.06 | 0.49 | 4.88 |  | 40.69
MORRO BAY 1102 | 183011102 | 57.81 | 4.03 | 17.91 |  | 35.87
MOSHER 2104 | 163722104 | 0.01 |  |  |  | 0.01
MOSHER 2107 | 163722107 | 3.13 |  |  |  | 3.13
MOSHER 2108 | 163722108 | 1.88 |  |  |  | 1.88
MOSHER 2110 | 163722110 | 2.21 |  |  |  | 2.21
MOSHER 2111 | 163722111 | 17.44 |  |  |  | 17.44
MOUNTAIN QUARRIES 2101 | 152282101 | 223.64 | 22.68 | 200 |  | 0.96
MOUNTAIN VIEW 1102 | 82031102 | 14.28 |  |  |  | 14.28
MOUNTAIN VIEW 1103 | 82031103 | 2.86 |  |  |  | 2.86
MOUNTAIN VIEW 1104 | 82031104 | 7.76 |  |  |  | 7.76
MOUNTAIN VIEW 1105 | 82031105 | 9.51 |  |  |  | 9.51
MOUNTAIN VIEW 1106 | 82031106 | 7.34 |  |  |  | 7.34
MOUNTAIN VIEW 1107 | 82031107 | 19.28 |  |  |  | 19.28
MOUNTAIN VIEW 1108 | 82031108 | 14.67 |  |  |  | 14.67
MOUNTAIN VIEW 1109 | 82031109 | 9.97 |  |  |  | 9.97
MOUNTAIN VIEW 1110 | 82031110 | 9.36 |  |  |  | 9.36
MOUNTAIN VIEW 1111 | 82031111 | 1.74 |  |  |  | 1.74
MOUNTAIN VIEW 1112 | 82031112 | 0.97 |  |  |  | 0.97
MOUNTAIN VIEW 1113 | 82031113 | 3.99 |  |  |  | 3.99
MOUNTAIN VIEW 1114 | 82031114 | 6.63 |  |  |  | 6.63
MT EDEN 1101 | 13761101 | 6.7 |  |  |  | 6.7
MT EDEN 1102 | 13761102 | 6.58 |  |  |  | 6.58
MT EDEN 1103 | 13761103 | 13.07 |  |  |  | 13.07
MT EDEN 1104 | 13761104 | 14 |  |  |  | 14
MT EDEN 1105 | 13761105 | 7.04 |  |  |  | 7.04
MT EDEN 1106 | 13761106 | 6.73 |  |  |  | 6.73
MT EDEN 1107 | 13761107 | 6.07 |  |  |  | 6.07
MT EDEN 1108 | 13761108 | 23.46 |  |  |  | 23.46
MT EDEN 1109 | 13761109 | 16.98 |  |  |  | 16.98
MT EDEN 1110 | 13761110 | 3.22 |  |  |  | 3.22
MT EDEN 1111 | 13761111 | 3.24 |  |  |  | 3.24
MT EDEN 1112 | 13761112 | 16.45 |  |  |  | 16.45
MT EDEN 1113 | 13761113 | 2.64 |  |  |  | 2.64
MT EDEN 1114 | 13761114 | 3.58 |  |  |  | 3.58
NAPA 1102 | 42021102 | 32.45 |  | 0.27 |  | 32.18
NAPA 1103 | 42021103 | 14.85 |  |  |  | 14.85
NAPA 1105 | 42021105 | 15.53 |  |  |  | 15.53
NAPA 1106 | 42021106 | 1.24 |  |  |  | 1.24
NAPA 1109 | 42021109 | 11.66 |  |  |  | 11.66
NAPA 1110 | 42021110 | 13.28 |  |  |  | 13.28
NAPA 1112 | 42021112 | 51.86 |  | 19.24 |  | 32.62
NARROWS 2101 | 153132101 | 61.45 |  | 61.45 |  | 0
NARROWS 2102 | 153132102 | 117.57 |  | 93.54 |  | 24.03
NARROWS 2104 | 153132104 | 0 |  | 0 |  | 0
NARROWS 2105 | 153132105 | 196.33 |  | 176.75 |  | 19.58
NARROWS PH 1151 | 153131151 | 0.2 |  | 0.2 |  | 0
NEW HOPE 1101 | 162081101 | 38.35 |  |  |  | 38.35
NEW HOPE 1102 | 162081102 | 50.59 |  |  |  | 50.59
NEWARK 12KV 1101 | 12221101 | 1.44 |  |  |  | 1.44
NEWARK 12KV 1102 | 12221102 | 8.4 |  |  |  | 8.4
NEWARK 12KV 1103 | 12221103 | 18.1 |  |  |  | 18.1
NEWARK 12KV 1104 | 12221104 | 0.37 |  |  |  | 0.37
NEWARK 12KV 1105 | 12221105 | 1.54 |  |  |  | 1.54
NEWARK 12KV 1106 | 12221106 | 18.36 |  |  |  | 18.36
NEWARK 12KV 1107 | 12221107 | 21.46 |  |  |  | 21.46
NEWARK 12KV 1108 | 12221108 | 0.95 |  |  |  | 0.95
NEWARK 21KV 2102 | 12232102 | 2.68 |  |  |  | 2.68
NEWARK 21KV 2103 | 12232103 | 17.79 |  |  |  | 17.79
NEWARK 21KV 2104 | 12232104 | 4.99 |  |  |  | 4.99
NEWARK 21KV 2105 | 12232105 | 2.51 |  |  |  | 2.51
NEWARK 21KV 2107 | 12232107 | 7.02 |  |  |  | 7.02
NEWARK 21KV 2108 | 12232108 | 4.82 |  |  |  | 4.82
NEWARK 21KV 2109 | 12232109 | 0 |  |  |  | 0
NEWARK 21KV 2110 | 12232110 | 3.19 |  |  |  | 3.19
NEWARK 21KV 2111 | 12232111 | 0 |  |  |  | 0
NEWBURG 1131 | 192151131 | 39.09 |  | 5.67 |  | 33.42
NEWBURG 1132 | 192151132 | 22.27 |  | 1.29 |  | 20.98
NEWBURG 1133 | 192151133 | 16.92 |  | 2.38 |  | 14.54
NEWHALL 1109 | 254461109 | 66.55 |  |  |  | 66.55
NEWHALL 1111 | 254461111 | 53.93 |  |  |  | 53.93
NEWMAN 1101 | 162741101 | 36.53 |  |  |  | 36.53
NEWMAN 1102 | 162741102 | 9.51 |  |  |  | 9.51
NEWMAN 1105 | 162741105 | 42.69 |  |  |  | 42.69
NEWMAN 1106 | 162741106 | 32.51 |  |  |  | 32.51
NORCO 1101 | 254691101 | 39.26 |  |  |  | 39.26
NORCO 1102 | 254691102 | 7.67 |  |  |  | 7.67
NORD 1103 | 103071103 | 18.51 |  |  |  | 18.51
NORD 1104 | 103071104 | 50.35 |  |  |  | 50.35
NORD 1105 | 103071105 | 6.99 |  |  |  | 6.99
NORD 1106 | 103071106 | 10.83 |  |  |  | 10.83
NORIEGA 0401 | 22510401 | 1.55 |  |  |  | 1.55
NORIEGA 0402 | 22510402 | 1.76 |  |  |  | 1.76
NORTECH 2107 | 82462107 | 0.11 |  |  |  | 0.11
NORTECH 2109 | 82462109 | 3.15 |  |  |  | 3.15
NORTECH 2110 | 82462110 | 9.47 |  |  |  | 9.47
NORTECH 2111 | 82462111 | 0.71 |  |  |  | 0.71
NORTH BRANCH 1101 | 163231101 | 88.31 |  | 62.34 |  | 25.97
NORTH DUBLIN 2101 | 14052101 | 1.87 |  | 1.4 |  | 0.47
NORTH DUBLIN 2103 | 14052103 | 21.69 |  | 18.65 |  | 3.04
NORTH TOWER 1102 | 42041102 | 18.7 |  |  |  | 18.7
NORTH TOWER 1103 | 42041103 | 13.04 |  |  |  | 13.04
NORTH TOWER 1104 | 42041104 | 19.71 |  |  |  | 19.71
NORTH TOWER 1108 | 42041108 | 13.3 |  |  |  | 13.3
NORTH TOWER 2101 | 42042101 | 4.42 |  | 0.52 |  | 3.9
NORTH TOWER 2104 | 42042104 | 4.21 |  |  |  | 4.21
NOTRE DAME 1101 | 102041101 | 1.6 |  |  |  | 1.6
NOTRE DAME 1102 | 102041102 | 10.61 |  |  |  | 10.61
NOTRE DAME 1103 | 102041103 | 7.85 |  | 0.57 |  | 7.28
NOTRE DAME 1104 | 102041104 | 35.86 | 17.95 | 9.74 |  | 8.17
NOVATO 1101 | 42211101 | 7.33 |  | 1.2 |  | 6.13
NOVATO 1102 | 42211102 | 0.59 |  |  |  | 0.59
NOVATO 1103 | 42211103 | 2.95 |  |  |  | 2.95
NOVATO 1104 | 42211104 | 24.36 |  | 3.45 |  | 20.91
OAK 0401 | 12600401 | 5.41 |  | 3.45 |  | 1.96
OAK PARK 0401 | 163270401 | 2.48 |  |  |  | 2.48
OAK PARK 0402 | 163270402 | 0.5 |  |  |  | 0.5
OAKHURST 1101 | 254421101 | 91.78 | 2.56 | 88.37 |  | 0.85
OAKHURST 1102 | 254421102 | 16.32 | 1.17 | 11.32 |  | 3.83
OAKHURST 1103 | 254421103 | 125.45 | 80.93 | 41.88 |  | 2.64
OAKLAND C 1108 | 12011108 | 2.04 |  |  |  | 2.04
OAKLAND C 1109 | 12011109 | 3.28 |  |  |  | 3.28
OAKLAND C 1110 | 12011110 | 1.25 |  |  |  | 1.25
OAKLAND C 1112 | 12011112 | 1.16 |  |  |  | 1.16
OAKLAND C 1113 | 12011113 | 3.36 |  |  |  | 3.36
OAKLAND C 1114 | 12011114 | 3.27 |  |  |  | 3.27
OAKLAND C 1115 | 12011115 | 1.24 |  |  |  | 1.24
OAKLAND C 1116 | 12011116 | 2.47 |  |  |  | 2.47
OAKLAND C 1117 | 12011117 | 2.97 |  |  |  | 2.97
OAKLAND C 1118 | 12011118 | 3.32 |  |  |  | 3.32
OAKLAND C 1119 | 12011119 | 0.43 |  |  |  | 0.43
OAKLAND C 1120 | 12011120 | 2.96 |  |  |  | 2.96
OAKLAND C 1121 | 12011121 | 1.91 |  |  |  | 1.91
OAKLAND C 1132 | 12011132 | 1.22 |  |  |  | 1.22
OAKLAND C 1133 | 12011133 | 0.03 |  |  |  | 0.03
OAKLAND C 1134 | 12011134 | 1.4 |  |  |  | 1.4
OAKLAND D 0406 | 12040406 | 3.19 |  |  |  | 3.19
OAKLAND D 0407 | 12040407 | 0.33 |  |  |  | 0.33
OAKLAND D 0408 | 12040408 | 4.08 |  |  |  | 4.08
OAKLAND D 0410 | 12040410 | 2.75 |  |  |  | 2.75
OAKLAND D 1101 | 12041101 | 0.16 |  |  |  | 0.16
OAKLAND D 1102 | 12041102 | 2.85 |  |  |  | 2.85
OAKLAND D 1103 | 12041103 | 0.34 |  |  |  | 0.34
OAKLAND D 1104 | 12041104 | 5.93 |  |  |  | 5.93
OAKLAND D 1105 | 12041105 | 8.27 |  |  |  | 8.27
OAKLAND D 1106 | 12041106 | 8.78 |  |  |  | 8.78
OAKLAND D 1107 | 12041107 | 2.51 |  |  |  | 2.51
OAKLAND D 1110 | 12041110 | 5.47 |  |  |  | 5.47
OAKLAND D 1111 | 12041111 | 7.81 |  |  |  | 7.81
OAKLAND D 1112 | 12041112 | 10.64 | 1.95 | 0.41 |  | 8.28
OAKLAND D 1115 | 12041115 | 2.74 |  |  |  | 2.74
OAKLAND D 1116 | 12041116 | 2.81 |  |  |  | 2.81
OAKLAND D 1117 | 12041117 | 0.5 |  |  |  | 0.5
OAKLAND D 1130 | 12041130 | 6.44 |  |  |  | 6.44
OAKLAND D 1131 | 12041131 | 7.74 |  |  |  | 7.74
OAKLAND D 1132 | 12041132 | 2.79 |  |  |  | 2.79
OAKLAND D 1133 | 12041133 | 2.97 |  |  |  | 2.97
OAKLAND D 1134 | 12041134 | 5.07 |  |  |  | 5.07
OAKLAND D 1202 | 12041202 | 0.24 |  |  |  | 0.24
OAKLAND I 0401 | 12080401 | 3.23 |  |  |  | 3.23
OAKLAND I 0402 | 12080402 | 5.11 |  |  |  | 5.11
OAKLAND J 0401 | 12090401 | 4.63 |  |  |  | 4.63
OAKLAND J 0403 | 12090403 | 6.3 |  |  |  | 6.3
OAKLAND J 0408 | 12090408 | 4.57 |  |  |  | 4.57
OAKLAND J 0409 | 12090409 | 3 |  |  |  | 3
OAKLAND J 1101 | 12091101 | 10.41 |  |  |  | 10.41
OAKLAND J 1102 | 12091102 | 18.3 |  | 6.01 |  | 12.29
OAKLAND J 1103 | 12091103 | 2.78 |  |  |  | 2.78
OAKLAND J 1104 | 12091104 | 6.84 |  |  |  | 6.84
OAKLAND J 1105 | 12091105 | 20.26 |  | 1.52 |  | 18.74
OAKLAND J 1106 | 12091106 | 18.02 |  | 1.89 |  | 16.13
OAKLAND J 1108 | 12091108 | 9.25 |  |  |  | 9.25
OAKLAND J 1109 | 12091109 | 0.04 |  |  |  | 0.04
OAKLAND J 1110 | 12091110 | 2.08 |  |  |  | 2.08
OAKLAND J 1111 | 12091111 | 4.67 |  |  |  | 4.67
OAKLAND J 1112 | 12091112 | 5.51 |  |  |  | 5.51
OAKLAND J 1114 | 12091114 | 0 |  |  |  | 0
OAKLAND J 1115 | 12091115 | 3.9 |  |  |  | 3.9
OAKLAND J 1116 | 12091116 | 23.48 |  | 0.48 |  | 23
OAKLAND J 1117 | 12091117 | 13.12 |  |  |  | 13.12
OAKLAND J 1118 | 12091118 | 13.87 |  | 0.31 |  | 13.56
OAKLAND K 1101 | 12101101 | 7.27 | 1.09 | 1.47 |  | 4.71
OAKLAND K 1102 | 12101102 | 14.94 | 14.94 |  |  | 0
OAKLAND K 1103 | 12101103 | 10.68 | 1.13 | 4.84 |  | 4.71
OAKLAND K 1104 | 12101104 | 14.89 | 9.56 | 5.33 |  | 0
OAKLAND L 1101 | 12111101 | 5.82 |  |  |  | 5.82
OAKLAND L 1102 | 12111102 | 1.28 |  |  |  | 1.28
OAKLAND L 1103 | 12111103 | 4.69 |  |  |  | 4.69
OAKLAND L 1105 | 12111105 | 2.48 |  |  |  | 2.48
OAKLAND L 1106 | 12111106 | 0.35 |  |  |  | 0.35
OAKLAND L 1107 | 12111107 | 1.47 |  |  |  | 1.47
OAKLAND L 1108 | 12111108 | 0 |  |  |  | 0
OAKLAND X 0401 | 12540401 | 5.5 |  |  |  | 5.5
OAKLAND X 0402 | 12540402 | 1.77 |  |  |  | 1.77
OAKLAND X 1101 | 12541101 | 5.29 |  | 0.5 |  | 4.79
OAKLAND X 1102 | 12541102 | 6.37 |  |  |  | 6.37
OAKLAND X 1103 | 12541103 | 7.68 |  |  |  | 7.68
OAKLAND X 1104 | 12541104 | 13.22 | 10.71 | 1.35 |  | 1.16
OAKLAND X 1105 | 12541105 | 19.38 |  | 2.51 |  | 16.87
OAKLAND X 1106 | 12541106 | 22.88 | 4.14 | 10.81 |  | 7.93
OAKLAND X 1107 | 12541107 | 12.92 |  |  |  | 12.92
OAKLAND X 1109 | 12541109 | 7.1 |  |  |  | 7.1
OAKLAND X 1110 | 12541110 | 0.43 |  |  |  | 0.43
OAKLAND X 1111 | 12541111 | 1.03 |  |  |  | 1.03
OAKLAND X 1112 | 12541112 | 3.93 |  |  |  | 3.93
OAKLAND X 1114 | 12541114 | 5.08 |  |  |  | 5.08
OAKLAND X 1115 | 12541115 | 12.61 |  |  |  | 12.61
OCEAN 0401 | 22580401 | 3.7 |  |  |  | 3.7
OCEAN 0402 | 22580402 | 2.96 |  |  |  | 2.96
OCEANO 1102 | 182601102 | 54.18 |  | 37.12 |  | 17.06
OCEANO 1103 | 182601103 | 11.37 |  | 1.11 |  | 10.26
OCEANO 1104 | 182601104 | 112.15 | 6.75 | 78.81 |  | 26.59
OCEANO 1105 | 182601105 | 23.59 |  | 0.66 |  | 22.93
OCEANO 1106 | 182601106 | 29.36 |  | 1.96 |  | 27.4
OCEANO 1108 | 182601108 | 11.07 |  |  |  | 11.07
OILFIELDS 1102 | 182391102 | 39.1 |  |  |  | 39.1
OILFIELDS 1103 | 182391103 | 144.71 |  | 116.94 |  | 27.77
OLD RIVER 1101 | 252821101 | 41.99 |  |  |  | 41.99
OLD RIVER 1102 | 252821102 | 49.41 |  |  |  | 49.41
OLD RIVER 1103 | 252821103 | 35.34 |  |  |  | 35.34
OLD RIVER 1104 | 252821104 | 58.21 |  |  |  | 58.21
OLD RIVER 1105 | 252821105 | 15.44 |  |  |  | 15.44
OLEMA 1101 | 42291101 | 123.11 | 15.44 | 55.47 |  | 52.2
OLETA 1101 | 163541101 | 116.76 | 4.66 | 84.68 |  | 27.42
OLETA 1102 | 163541102 | 98.63 |  | 56.04 |  | 42.59
OLIVEHURST 1101 | 152901101 | 21.81 |  |  |  | 21.81
OLIVEHURST 1102 | 152901102 | 6.02 |  |  |  | 6.02
OLIVEHURST 1103 | 152901103 | 47.14 |  |  |  | 47.14
OLIVEHURST 1104 | 152901104 | 11.38 |  |  |  | 11.38
OLIVEHURST 1105 | 152901105 | 53.94 |  |  |  | 53.94
OREGON TRAIL 1102 | 103521102 | 49.03 |  | 44.69 |  | 4.34
OREGON TRAIL 1103 | 103521103 | 112.31 |  | 109.37 |  | 2.94
OREGON TRAIL 1104 | 103521104 | 73.39 |  | 60.53 |  | 12.86
ORICK 1101 | 192261101 | 7.98 |  |  |  | 7.98
ORICK 1102 | 192261102 | 23.29 |  |  |  | 23.29
ORINDA 0401 | 12350401 | 5.37 | 0.1 | 3.37 |  | 1.9
ORINDA 0402 | 12350402 | 6.61 | 3.19 | 3.16 |  | 0.26
ORLAND B 1101 | 102701101 | 29.28 |  |  |  | 29.28
ORLAND B 1102 | 102701102 | 20.04 |  |  |  | 20.04
ORLAND B 1103 | 102701103 | 94.38 |  |  |  | 94.38
ORO FINO 1101 | 103031101 | 31.74 | 31.74 |  |  | 0
ORO FINO 1102 | 103031102 | 109.38 | 83.12 | 26.26 |  | 0
ORO LOMA 1102 | 255371102 | 1.07 |  |  |  | 1.07
ORO LOMA 1103 | 255371103 | 1.1 |  |  |  | 1.1
ORO LOMA 1106 | 255371106 | 72.81 |  |  |  | 72.81
ORO LOMA 1108 | 255371108 | 55.53 |  |  |  | 55.53
ORO LOMA 1115 | 255371115 | 73.78 |  |  |  | 73.78
ORO LOMA 1116 | 255371116 | 24.7 |  |  |  | 24.7
ORO LOMA 1117 | 255371117 | 50.2 |  |  |  | 50.2
ORO LOMA 1118 | 255371118 | 42.74 |  |  |  | 42.74
OROSI 1101 | 252841101 | 50.36 |  |  |  | 50.36
OROSI 1102 | 252841102 | 34.84 |  | 0.8 |  | 34.04
OROSI 1103 | 252841103 | 37.72 |  |  |  | 37.72
OROSI 1104 | 252841104 | 55.84 |  |  |  | 55.84
OROVILLE 0402 | 102520402 | 1.58 |  |  |  | 1.58
OROVILLE 0403 | 102520403 | 2.03 |  |  |  | 2.03
OROVILLE 1101 | 102521101 | 23.53 |  |  |  | 23.53
OROVILLE 1102 | 102521102 | 6.28 |  |  |  | 6.28
OROVILLE 1103 | 102521103 | 10.36 |  |  |  | 10.36
OROVILLE 1104 | 102521104 | 9.87 |  |  |  | 9.87
ORTIGA 1105 | 254311105 | 42.41 |  |  |  | 42.41
ORTIGA 1106 | 254311106 | 53.7 |  |  |  | 53.7
OTTER 1101 | 182941101 | 26.95 | 14.55 | 7.09 |  | 5.31
OTTER 1102 | 182941102 | 53.79 | 4.38 | 48.32 |  | 1.09
PACIFIC GROVE 0421 | 182440421 | 3.34 |  |  |  | 3.34
PACIFIC GROVE 0422 | 182440422 | 6.89 |  | 0.13 |  | 6.76
PACIFIC GROVE 0423 | 182440423 | 1.68 |  |  |  | 1.68
PACIFIC GROVE 0424 | 182440424 | 8.97 |  |  |  | 8.97
PACIFIC PIPE GRAPEVI 1101 | 255441101 | 0.02 |  |  |  | 0.02
PACIFICA 1101 | 22811101 | 9.23 | 0.07 | 0.74 |  | 8.42
PACIFICA 1102 | 22811102 | 20.1 | 1.34 | 1.38 |  | 17.38
PACIFICA 1103 | 22811103 | 14.13 | 0.19 | 0.77 |  | 13.17
PACIFICA 1104 | 22811104 | 7.18 |  | 0.7 |  | 6.48
PALMER 1101 | 183031101 | 62.6 |  | 39.46 |  | 23.14
PALO SECO 0401 | 13180401 | 4.73 |  | 4.71 |  | 0.02
PANAMA 2101 | 253422101 | 38.65 |  |  |  | 38.65
PANAMA 2102 | 253422102 | 32.89 |  |  |  | 32.89
PANOCHE 1101 | 253671101 | 24.31 |  |  |  | 24.31
PANOCHE 1102 | 253671102 | 42.59 |  |  |  | 42.59
PANOCHE 1103 | 253671103 | 122.18 |  | 44.24 |  | 77.94
PANORAMA 1101 | 103461101 | 39.18 |  | 12.98 |  | 26.2
PANORAMA 1102 | 103461102 | 84.44 |  | 29.99 |  | 54.45
PARADISE 1103 | 102831103 | 36.04 | 18.47 | 14.79 |  | 2.78
PARADISE 1104 | 102831104 | 31 | 20.97 | 1.32 |  | 8.71
PARADISE 1105 | 102831105 | 48.1 | 45.54 |  |  | 2.56
PARADISE 1106 | 102831106 | 8.84 | 8.3 |  |  | 0.54
PARKWAY 1101 | 42051101 | 7.12 |  |  |  | 7.12
PARKWAY 1102 | 42051102 | 0 |  |  |  | 0
PARKWAY 1103 | 42051103 | 6.7 |  |  |  | 6.7
PARLIER 1102 | 252291102 | 10.97 |  |  |  | 10.97
PARLIER 1103 | 252291103 | 40.84 |  |  |  | 40.84
PARLIER 1104 | 252291104 | 49.86 |  |  |  | 49.86
PARLIER 1105 | 252291105 | 21.42 |  |  |  | 21.42
PARSONS 0401 | 13660401 | 1.32 |  |  |  | 1.32
PARSONS 0402 | 13660402 | 3.43 |  |  |  | 3.43
PASO ROBLES 1101 | 182611101 | 6.57 |  |  |  | 6.57
PASO ROBLES 1102 | 182611102 | 6.41 |  |  |  | 6.41
PASO ROBLES 1103 | 182611103 | 60.48 |  | 38.53 |  | 21.95
PASO ROBLES 1104 | 182611104 | 65.55 |  | 37.15 |  | 28.4
PASO ROBLES 1106 | 182611106 | 11.46 |  |  |  | 11.46
PASO ROBLES 1107 | 182611107 | 37.7 |  | 0.26 |  | 37.44
PASO ROBLES 1108 | 182611108 | 12.43 |  |  |  | 12.43
PAUL SWEET 2101 | 83252101 | 28.44 |  |  |  | 28.44
PAUL SWEET 2102 | 83252102 | 18 | 3.7 | 0.73 |  | 13.57
PAUL SWEET 2103 | 83252103 | 16.87 |  |  |  | 16.87
PAUL SWEET 2104 | 83252104 | 38.37 | 17.2 |  |  | 21.17
PAUL SWEET 2105 | 83252105 | 40.87 | 6.8 | 0.8 |  | 33.27
PAUL SWEET 2106 | 83252106 | 51.86 | 30.65 | 5.23 |  | 15.98
PAUL SWEET 2107 | 83252107 | 49.49 | 4.04 | 4.24 |  | 41.21
PAUL SWEET 2108 | 83252108 | 20.72 |  |  |  | 20.72
PAUL SWEET 2109 | 83252109 | 23.6 | 0.85 | 2.02 |  | 20.73
PEABODY 2102 | 63642102 | 7.01 |  |  |  | 7.01
PEABODY 2104 | 63642104 | 6.76 |  |  |  | 6.76
PEABODY 2105 | 63642105 | 61.12 |  |  |  | 61.12
PEABODY 2106 | 63642106 | 1.08 |  | 0.39 |  | 0.69
PEABODY 2107 | 63642107 | 194.05 |  |  |  | 194.05
PEABODY 2108 | 63642108 | 3.02 |  | 0.34 |  | 2.68
PEABODY 2109 | 63642109 | 3.63 |  |  |  | 3.63
PEABODY 2112 | 63642112 | 3.45 |  |  |  | 3.45
PEABODY 2113 | 63642113 | 9.73 |  | 1.02 |  | 8.71
PEACHTON 1101 | 103241101 | 68.89 |  |  |  | 68.89
PEACHTON 1102 | 103241102 | 67.67 |  |  |  | 67.67
PEACHTON 1103 | 103241103 | 60.88 |  |  |  | 60.88
PEASE 1101 | 153751101 | 6.84 |  |  |  | 6.84
PEASE 1102 | 153751102 | 3.98 |  |  |  | 3.98
PEASE 1103 | 153751103 | 97.44 |  |  |  | 97.44
PEASE 1104 | 153751104 | 62.57 |  |  |  | 62.57
PEASE 1105 | 153751105 | 8.24 |  |  |  | 8.24
PENNGROVE 1101 | 43471101 | 41.73 |  | 20.09 |  | 21.64
PENRYN 1103 | 152561103 | 80.22 |  | 67.15 |  | 13.07
PENRYN 1105 | 152561105 | 91.41 |  | 33.91 |  | 57.5
PENRYN 1106 | 152561106 | 25.83 |  | 0.81 |  | 25.02
PENRYN 1107 | 152561107 | 83.96 |  | 35.97 |  | 47.99
PENTLAND 1101 | 255311101 | 0.02 |  |  |  | 0.02
PEORIA 1701 | 163781701 | 84.58 |  | 77.43 |  | 7.15
PEORIA 1704 | 163781704 | 118.03 |  | 58.71 |  | 59.32
PEORIA 1705 | 163781705 | 70.02 |  | 57.46 |  | 12.56
PERRY 1101 | 183071101 | 83.71 | 7.18 | 58.34 |  | 18.19
PETALUMA A 0411 | 42120411 | 3.06 |  |  |  | 3.06
PETALUMA A 0413 | 42120413 | 2.37 |  |  |  | 2.37
PETALUMA C 1101 | 42631101 | 0.51 |  |  |  | 0.51
PETALUMA C 1102 | 42631102 | 4.21 |  |  |  | 4.21
PETALUMA C 1105 | 42631105 | 10.67 |  |  |  | 10.67
PETALUMA C 1106 | 42631106 | 9 |  |  |  | 9
PETALUMA C 1108 | 42631108 | 118.47 |  | 75.79 |  | 42.68
PETALUMA C 1109 | 42631109 | 66.6 |  | 48.74 |  | 17.86
PETALUMA C 1110 | 42631110 | 0.25 |  |  |  | 0.25
PETROL 1101 | 252541101 | 0.03 |  |  |  | 0.03
PHILO 1101 | 42601101 | 96.11 |  | 76.49 |  | 19.62
PHILO 1102 | 42601102 | 105.92 |  | 88.3 |  | 17.62
PIERCY 2109 | 83912109 | 19.9 |  |  |  | 19.9
PIERCY 2110 | 83912110 | 27.42 |  | 19.66 |  | 7.76
PIERCY 2111 | 83912111 | 0.91 |  |  |  | 0.91
PIKE CITY 1101 | 152201101 | 34.03 | 34.03 |  |  | 0
PIKE CITY 1102 | 152201102 | 9.52 | 9.52 |  |  | 0
PINE GROVE 1101 | 163751101 | 71.79 |  | 71.79 |  | 0
PINE GROVE 1102 | 163751102 | 176.13 | 85.35 | 90.78 |  | 0
PINECREST 0401 | 163160401 | 3.15 | 1.12 | 1.95 |  | 0.08
PINEDALE 2101 | 252852101 | 1.43 |  |  |  | 1.43
PINEDALE 2102 | 252852102 | 2.76 |  |  |  | 2.76
PINEDALE 2103 | 252852103 | 1.98 |  |  |  | 1.98
PINEDALE 2105 | 252852105 | 1.76 |  |  |  | 1.76
PINEDALE 2106 | 252852106 | 5.43 |  |  |  | 5.43
PINEDALE 2107 | 252852107 | 1.59 |  |  |  | 1.59
PINEDALE 2109 | 252852109 | 7.14 |  |  |  | 7.14
PINEDALE 2110 | 252852110 | 0.19 |  |  |  | 0.19
PINEDALE 2111 | 252852111 | 0.75 |  |  |  | 0.75
PIPER BANK 0401 | 18120401 | 1.56 |  |  |  | 1.56
PIT NO 1 1101 | 103721101 | 52.88 |  | 29.54 |  | 23.34
PIT NO 3 2101 | 103732101 | 48.49 |  | 47.46 |  | 1.03
PIT NO 5 1101 | 101321101 | 23.62 |  | 23.62 |  | 0
PIT NO 7 1101 | 103501101 | 2.84 |  | 2.84 |  | 0
PITTSBURG 0401 | 12160401 | 1.04 |  |  |  | 1.04
PITTSBURG 0402 | 12160402 | 1.87 |  |  |  | 1.87
PLACER 1101 | 152461101 | 7.71 |  | 1.26 |  | 6.45
PLACER 1102 | 152461102 | 2.12 |  | 1.86 |  | 0.26
PLACER 1103 | 152461103 | 29.53 |  | 12.08 |  | 17.45
PLACER 1104 | 152461104 | 13.39 |  | 0.52 |  | 12.87
PLACERVILLE 1109 | 153081109 | 11.05 |  | 10.76 |  | 0.29
PLACERVILLE 1110 | 153081110 | 34.41 | 0.73 | 32.66 |  | 1.02
PLACERVILLE 1111 | 153081111 | 16.69 |  | 14.73 |  | 1.96
PLACERVILLE 1112 | 153081112 | 29.78 |  | 27.54 |  | 2.24
PLACERVILLE 2106 | 153082106 | 273.51 | 179.49 | 93.76 |  | 0.26
PLAINFIELD 1101 | 63441101 | 33.73 |  |  |  | 33.73
PLAINFIELD 1105 | 63441105 | 51.66 |  |  |  | 51.66
PLAINFIELD 1106 | 63441106 | 32.79 |  |  |  | 32.79
PLEASANT GROVE 2103 | 152442103 | 1.88 |  |  |  | 1.88
PLEASANT GROVE 2104 | 152442104 | 2.42 |  |  |  | 2.42
PLEASANT GROVE 2107 | 152442107 | 0.02 |  |  |  | 0.02
PLEASANT GROVE 2108 | 152442108 | 2.1 |  |  |  | 2.1
PLEASANT GROVE 2110 | 152442110 | 34.64 |  |  |  | 34.64
PLUMAS 1101 | 153731101 | 32.33 |  |  |  | 32.33
PLUMAS 1102 | 153731102 | 5.63 |  |  |  | 5.63
PLUMAS 2106 | 153732106 | 31.95 |  |  |  | 31.95
PLUMAS 2107 | 153732107 | 39.77 |  |  |  | 39.77
PLYMOUTH 0401 | 22680401 | 4.7 |  |  |  | 4.7
POINT ARENA 1101 | 43381101 | 66.15 |  | 44.25 |  | 21.9
POINT MORETTI 1101 | 82931101 | 53.94 | 29.9 | 17.32 |  | 6.72
POINT PINOLE 1101 | 14261101 | 20.99 |  |  |  | 20.99
POINT PINOLE 1102 | 14261102 | 14.06 |  |  |  | 14.06
POINT PINOLE 1103 | 14261103 | 0.01 |  |  |  | 0.01
PORTOLA 0401 | 22610401 | 2.45 |  |  |  | 2.45
PORTOLA 0402 | 22610402 | 3.5 |  |  |  | 3.5
POSO MOUNTAIN 2101 | 253642101 | 59.33 |  | 48.76 |  | 10.57
POSO MOUNTAIN 2103 | 253642103 | 20.45 |  | 18.43 |  | 2.02
POSO MOUNTAIN 2104 | 253642104 | 12.55 |  | 8.03 |  | 4.52
POTRERO PP (A) 1101 | 22031101 | 7.2 |  |  |  | 7.2
POTRERO PP (A) 1102 | 22031102 | 0.48 |  |  |  | 0.48
POTRERO PP (A) 1103 | 22031103 | 1.8 |  |  |  | 1.8
POTRERO PP (A) 1104 | 22031104 | 0.3 |  |  |  | 0.3
POTRERO PP (A) 1105 | 22031105 | 1.52 |  |  |  | 1.52
POTRERO PP (A) 1107 | 22031107 | 0.9 |  |  |  | 0.9
POTRERO PP (A) 1108 | 22031108 | 3.5 |  |  |  | 3.5
POTRERO PP (A) 1109 | 22031109 | 5.2 |  |  |  | 5.2
POTRERO PP (A) 1110 | 22031110 | 6.49 |  |  |  | 6.49
POTRERO PP (A) 1112 | 22031112 | 0.93 |  |  |  | 0.93
POTRERO PP (A) 1113 | 22031113 | 1.74 |  |  |  | 1.74
POTRERO PP (A) 1114 | 22031114 | 0.07 |  |  |  | 0.07
POTRERO PP (A) 1115 | 22031115 | 0.84 |  |  |  | 0.84
POTRERO PP (A) 1116 | 22031116 | 2.21 |  |  |  | 2.21
POTRERO PP (A) 1117 | 22031117 | 4.93 |  |  |  | 4.93
POTRERO PP (A) 1118 | 22031118 | 4.29 |  |  |  | 4.29
POTRERO PP (A) 1119 | 22031119 | 2.51 |  |  |  | 2.51
POTRERO PP (A) 1121 | 22031121 | 0.17 |  |  |  | 0.17
POTTER VALLEY P H 1104 | 42281104 | 18.84 | 0.11 | 4.57 |  | 14.16
POTTER VALLEY P H 1105 | 42281105 | 73.4 | 4.64 | 43.35 |  | 25.41
PRUNEDALE 1107 | 182961107 | 46.88 |  |  |  | 46.88
PRUNEDALE 1110 | 182961110 | 79.81 |  | 0.24 |  | 79.57
PUEBLO 1102 | 43291102 | 8.99 |  |  | 0.09 | 8.9
PUEBLO 1103 | 43291103 | 8.1 |  |  |  | 8.1
PUEBLO 1104 | 43291104 | 50.91 |  | 28.41 | 0.05 | 22.45
PUEBLO 1105 | 43291105 | 70.1 |  | 20.73 | 0.05 | 49.32
PUEBLO 2101 | 43292101 | 11.6 |  |  |  | 11.6
PUEBLO 2102 | 43292102 | 98.08 | 21.14 | 0.74 |  | 76.2
PUEBLO 2103 | 43292103 | 77.46 | 37.61 | 8.1 |  | 31.75
PURISIMA 1101 | 182971101 | 58.3 |  | 17.62 |  | 40.68
PUTAH CREEK 1102 | 63681102 | 50.82 |  | 26.6 |  | 24.22
PUTAH CREEK 1103 | 63681103 | 36.51 |  | 3.76 |  | 32.75
PUTAH CREEK 1105 | 63681105 | 83.61 |  | 1.78 |  | 81.83
RACETRACK 1703 | 163761703 | 62.12 | 1.46 | 54.53 |  | 6.13
RACETRACK 1704 | 163761704 | 45.38 |  | 45.38 |  | 0
RADUM 1101 | 13151101 | 1.62 |  |  |  | 1.62
RADUM 1102 | 13151102 | 1.15 |  |  |  | 1.15
RADUM 1105 | 13151105 | 11.8 | 1.14 | 1.9 |  | 8.76
RAINBOW 1103 | 254441103 | 16.9 |  |  |  | 16.9
RAINBOW 1105 | 254441105 | 23.72 |  |  |  | 23.72
RAINBOW 1106 | 254441106 | 122.11 |  |  |  | 122.11
RALSTON 1101 | 24141101 | 14.47 | 0.41 | 8.52 |  | 5.54
RALSTON 1102 | 24141102 | 10.74 |  | 3.77 |  | 6.97
RANCHERS COTTON 1000 | 254801000 | 0.01 |  |  |  | 0.01
RANCHERS COTTON 1101 | 254801101 | 14.12 |  |  |  | 14.12
RANDOLPH 0401 | 22590401 | 0 |  |  |  | 0
RANDOLPH 0402 | 22590402 | 1.27 |  |  |  | 1.27
RANDOLPH 0403 | 22590403 | 3.12 |  |  |  | 3.12
RAWSON 1103 | 103531103 | 39.98 |  | 2.75 |  | 37.23
RED BLUFF 1101 | 103541101 | 74.44 |  | 47.63 |  | 26.81
RED BLUFF 1102 | 103541102 | 1.48 |  |  |  | 1.48
RED BLUFF 1103 | 103541103 | 37.99 |  | 16.8 |  | 21.19
RED BLUFF 1104 | 103541104 | 93.4 |  | 66.12 |  | 27.28
RED BLUFF 1105 | 103541105 | 37.7 |  | 13.6 |  | 24.1
REDBUD 1101 | 43191101 | 66.17 | 19.24 | 21.65 |  | 25.28
REDBUD 1102 | 43191102 | 58.39 | 0.65 | 27.84 |  | 29.9
REDWOOD CITY 0402 | 24160402 | 1.25 |  |  |  | 1.25
REDWOOD CITY 0403 | 24160403 | 2.15 |  |  |  | 2.15
REDWOOD CITY 0404 | 24160404 | 1.61 |  |  |  | 1.61
REDWOOD CITY 0405 | 24160405 | 3.35 |  |  |  | 3.35
REDWOOD CITY 0406 | 24160406 | 6.58 |  |  |  | 6.58
REDWOOD CITY 0408 | 24160408 | 5.6 |  |  |  | 5.6
REDWOOD CITY 0409 | 24160409 | 4.91 |  |  |  | 4.91
REDWOOD CITY 0410 | 24160410 | 5.42 |  |  |  | 5.42
REDWOOD CITY 1101 | 24161101 | 1.94 |  |  |  | 1.94
REDWOOD CITY 1102 | 24161102 | 1.63 |  |  |  | 1.63
REDWOOD CITY 1103 | 24161103 | 1.59 |  |  |  | 1.59
REDWOOD CITY 1104 | 24161104 | 0.98 |  |  |  | 0.98
REDWOOD CITY 1105 | 24161105 | 7.26 |  |  |  | 7.26
REEDLEY 1101 | 252341101 | 26.41 |  |  |  | 26.41
REEDLEY 1104 | 252341104 | 82.43 |  | 1.69 |  | 80.74
REEDLEY 1106 | 252341106 | 123.19 |  |  |  | 123.19
REEDLEY 1110 | 252341110 | 42.16 |  |  |  | 42.16
REEDLEY 1112 | 252341112 | 89.86 |  | 0.78 |  | 89.08
RENFRO 2101 | 254572101 | 31.34 |  |  |  | 31.34
RENFRO 2102 | 254572102 | 4.41 |  |  |  | 4.41
RENFRO 2103 | 254572103 | 25.47 |  |  |  | 25.47
RENFRO 2105 | 254572105 | 10.08 |  |  |  | 10.08
RENFRO 2107 | 254572107 | 6.74 |  |  |  | 6.74
RESEARCH 2101 | 14692101 | 7.79 |  |  |  | 7.79
RESEARCH 2102 | 14692102 | 20.7 | 2.17 |  |  | 18.53
RESERVATION ROAD 1101 | 182731101 | 36.95 |  | 29.08 |  | 7.87
RESERVATION ROAD 1102 | 182731102 | 58.33 |  | 19.69 |  | 38.64
RESERVE OIL 1101 | 254181101 | 2.19 |  |  |  | 2.19
RICE 1101 | 62831101 | 53.25 |  |  |  | 53.25
RICE 1102 | 62831102 | 62.18 |  |  |  | 62.18
RICE 1103 | 62831103 | 77.94 |  |  |  | 77.94
RICE 1104 | 62831104 | 32.94 |  |  |  | 32.94
RICHMOND Q 0401 | 12520401 | 5.95 |  |  |  | 5.95
RICHMOND Q 0402 | 12520402 | 3.61 |  |  |  | 3.61
RICHMOND R 1118 | 13471118 | 2.97 |  |  |  | 2.97
RICHMOND R 1119 | 13471119 | 3.58 |  |  |  | 3.58
RICHMOND R 1120 | 13471120 | 2.97 |  |  |  | 2.97
RICHMOND R 1121 | 13471121 | 4.47 |  |  |  | 4.47
RICHMOND R 1122 | 13471122 | 3.86 |  |  |  | 3.86
RICHMOND R 1123 | 13471123 | 1.33 |  |  |  | 1.33
RICHMOND R 1124 | 13471124 | 6.75 |  |  |  | 6.75
RICHMOND R 1125 | 13471125 | 4.61 |  |  |  | 4.61
RICHMOND R 1126 | 13471126 | 13.05 |  |  |  | 13.05
RICHMOND R 1127 | 13471127 | 20.27 |  |  |  | 20.27
RICHMOND R 1128 | 13471128 | 7.55 |  |  |  | 7.55
RICHMOND R 1129 | 13471129 | 13.87 |  |  |  | 13.87
RICHMOND R 1130 | 13471130 | 15.96 |  |  |  | 15.96
RIDGE 0401 | 12840401 | 2.66 |  | 2.66 |  | 0
RIDGE 0402 | 12840402 | 2.4 |  | 1.75 |  | 0.65
RINCON 1101 | 43321101 | 38.12 | 16.46 | 5.75 |  | 15.91
RINCON 1102 | 43321102 | 19.26 | 0.01 | 2.61 |  | 16.64
RINCON 1103 | 43321103 | 47.95 | 40.61 | 4.37 |  | 2.97
RINCON 1104 | 43321104 | 11.53 | 1.92 |  |  | 9.61
RIO BRAVO 1101 | 252861101 | 20.93 |  |  |  | 20.93
RIO BRAVO 1102 | 252861102 | 36.79 |  |  |  | 36.79
RIO BRAVO 1103 | 252861103 | 26.97 |  |  |  | 26.97
RIO BRAVO 1104 | 252861104 | 8.61 |  |  |  | 8.61
RIO BRAVO 1106 | 252861106 | 62.94 |  |  |  | 62.94
RIO DELL 1101 | 192251101 | 19.46 |  |  |  | 19.46
RIO DELL 1102 | 192251102 | 73.38 |  | 49.2 | 0.76 | 23.42
RIPON 1701 | 163801701 | 64.88 |  |  |  | 64.88
RIPON 1702 | 163801702 | 24.67 |  |  |  | 24.67
RIPON 1703 | 163801703 | 83.43 |  |  |  | 83.43
RIPON 1704 | 163801704 | 9.74 |  |  |  | 9.74
RISING RIVER 1101 | 103551101 | 58.65 |  | 43.52 |  | 15.13
RIVER ROCK 1101 | 255251101 | 0.02 |  |  |  | 0.02
RIVERBANK 1711 | 163191711 | 36.14 |  |  |  | 36.14
RIVERBANK 1712 | 163191712 | 54.39 |  |  |  | 54.39
RIVERBANK 1713 | 163191713 | 54.12 |  |  |  | 54.12
RIVERBANK 1714 | 163191714 | 33.84 |  |  |  | 33.84
RIVERBANK 1715 | 163191715 | 92.48 |  |  |  | 92.48
RIVERBANK 1716 | 163191716 | 26.89 |  |  |  | 26.89
ROB ROY 2104 | 83692104 | 159.83 | 39.36 | 62.04 |  | 58.43
ROB ROY 2105 | 83692105 | 66.26 | 26.89 | 11.33 |  | 28.04
ROCKLIN 1101 | 152061101 | 4.72 |  |  |  | 4.72
ROCKLIN 1102 | 152061102 | 18.66 |  |  |  | 18.66
ROCKLIN 1103 | 152061103 | 5.11 |  |  |  | 5.11
ROCKLIN 1104 | 152061104 | 3.3 |  |  |  | 3.3
ROSEDALE 1101 | 254761101 | 12.1 |  |  |  | 12.1
ROSEDALE 2102 | 254762102 | 3.72 |  |  |  | 3.72
ROSSMOOR 1101 | 14161101 | 30.55 | 2.13 | 10.74 |  | 17.68
ROSSMOOR 1102 | 14161102 | 1.45 | 0.45 |  |  | 1
ROSSMOOR 1103 | 14161103 | 2.58 |  |  |  | 2.58
ROSSMOOR 1104 | 14161104 | 19.43 |  | 0.3 |  | 19.13
ROSSMOOR 1105 | 14161105 | 4.27 |  |  |  | 4.27
ROSSMOOR 1106 | 14161106 | 16.09 | 0.58 | 2.84 |  | 12.67
ROSSMOOR 1107 | 14161107 | 10.51 | 0.03 |  |  | 10.48
ROSSMOOR 1108 | 14161108 | 13.12 | 1.97 | 3.14 |  | 8.01
ROSSMOOR 1109 | 14161109 | 13.98 | 6.35 | 1.14 |  | 6.49
ROUGH AND READY ISLA 1102 | 163081102 | 54.28 |  |  |  | 54.28
ROUND MOUNTAIN 1101 | 109001101 | 0.02 |  | 0.02 |  | 0
RUSS RANCH 1101 | 192471101 | 0.22 |  |  |  | 0.22
RUSSELL (SMUD) 2101 | 63142101 | 5.14 |  |  |  | 5.14
RUSSELL 0401 | 13310401 | 3.41 |  |  |  | 3.41
RUSSELL 0402 | 13310402 | 3.34 |  |  |  | 3.34
SALINAS 1101 | 182011101 | 8.27 |  |  |  | 8.27
SALINAS 1102 | 182011102 | 21.22 |  |  |  | 21.22
SALINAS 1103 | 182011103 | 10.8 |  |  |  | 10.8
SALINAS 1104 | 182011104 | 31.51 |  |  |  | 31.51
SALINAS 1105 | 182011105 | 10.9 |  |  |  | 10.9
SALINAS 1106 | 182011106 | 18.61 |  |  |  | 18.61
SALINAS 1107 | 182011107 | 7.19 |  |  |  | 7.19
SALINAS 1108 | 182011108 | 2.73 |  |  |  | 2.73
SALINAS 1109 | 182011109 | 20.41 |  |  |  | 20.41
SALMON CREEK 1101 | 43161101 | 47.28 | 7.21 | 14.96 |  | 25.11
SALT SPRINGS 2101 | 163692101 | 21.96 |  | 17.07 | 1.36 | 3.53
SALT SPRINGS 2102 | 163692102 | 51.97 | 42.09 | 9.81 |  | 0.07
SAN ARDO 1101 | 182191101 | 56.61 |  | 2.67 |  | 53.94
SAN ARDO 1102 | 182191102 | 124.26 |  |  |  | 124.26
SAN BENITO 2101 | 182742101 | 48.3 |  | 4.28 |  | 44.02
SAN BENITO 2102 | 182742102 | 12.95 |  |  |  | 12.95
SAN BENITO 2103 | 182742103 | 0.59 |  |  |  | 0.59
SAN BENITO 2104 | 182742104 | 51.43 |  | 26.66 |  | 24.77
SAN BERNARD 1101 | 253191101 | 41.93 |  | 1.17 |  | 40.76
SAN BERNARD 1102 | 253191102 | 11.98 |  |  |  | 11.98
SAN BERNARD 1104 | 253191104 | 9.26 |  |  |  | 9.26
SAN BRUNO 0401 | 22700401 | 3.61 |  |  |  | 3.61
SAN BRUNO 0402 | 22700402 | 3.11 |  |  |  | 3.11
SAN BRUNO 0403 | 22700403 | 5.03 |  |  |  | 5.03
SAN CARLOS 0401 | 24180401 | 1.65 |  |  |  | 1.65
SAN CARLOS 0402 | 24180402 | 4.29 |  |  |  | 4.29
SAN CARLOS 0403 | 24180403 | 6.92 |  |  |  | 6.92
SAN CARLOS 0404 | 24180404 | 8.75 |  |  |  | 8.75
SAN CARLOS 0405 | 24180405 | 8.18 |  |  |  | 8.18
SAN CARLOS 0406 | 24180406 | 6.54 |  |  |  | 6.54
SAN CARLOS 1101 | 24181101 | 1.46 |  |  |  | 1.46
SAN CARLOS 1102 | 24181102 | 0.46 |  |  |  | 0.46
SAN CARLOS 1103 | 24181103 | 16.49 |  | 3.82 |  | 12.67
SAN CARLOS 1104 | 24181104 | 22.03 |  | 10.61 |  | 11.42
SAN JOAQUIN #2 1103 | 252521103 | 79.88 | 10.31 | 69.57 |  | 0
SAN JOAQUIN #3 1101 | 252531101 | 24.33 | 22.76 | 1.57 |  | 0
SAN JOAQUIN #3 1102 | 252531102 | 11.39 | 5.46 | 5.94 |  | -0.01
SAN JOAQUIN #3 1103 | 252531103 | 56.28 | 30.39 | 25.89 |  | 0
SAN JOAQUIN 1106 | 252361106 | 52.04 |  |  |  | 52.04
SAN JOAQUIN 1108 | 252361108 | 41.1 |  |  |  | 41.1
SAN JOAQUIN 1112 | 252361112 | 42.24 |  |  |  | 42.24
SAN JOSE A 0403 | 82250403 | 3.98 |  |  |  | 3.98
SAN JOSE A 0404 | 82250404 | 1.66 |  |  |  | 1.66
SAN JOSE A 0405 | 82250405 | 1.83 |  |  |  | 1.83
SAN JOSE A 0407 | 82250407 | 1.83 |  |  |  | 1.83
SAN JOSE A 0408 | 82250408 | 2.39 |  |  |  | 2.39
SAN JOSE A 0410 | 82250410 | 4.56 |  |  |  | 4.56
SAN JOSE A 1109 | 82251109 | 0.62 |  |  |  | 0.62
SAN JOSE A 1110 | 82251110 | 9.02 |  |  |  | 9.02
SAN JOSE A 1111 | 82251111 | 0.12 |  |  |  | 0.12
SAN JOSE A 1112 | 82251112 | 10.55 |  |  |  | 10.55
SAN JOSE B 1101 | 82261101 | 0.16 |  |  |  | 0.16
SAN JOSE B 1102 | 82261102 | 0.26 |  |  |  | 0.26
SAN JOSE B 1104 | 82261104 | 0.48 |  |  |  | 0.48
SAN JOSE B 1105 | 82261105 | 8.63 |  |  |  | 8.63
SAN JOSE B 1106 | 82261106 | 0.7 |  |  |  | 0.7
SAN JOSE B 1107 | 82261107 | 9.06 |  |  |  | 9.06
SAN JOSE B 1108 | 82261108 | 8.07 |  |  |  | 8.07
SAN JOSE B 1109 | 82261109 | 0.38 |  |  |  | 0.38
SAN JOSE B 1110 | 82261110 | 13.27 |  |  |  | 13.27
SAN JOSE B 1111 | 82261111 | 0.08 |  |  |  | 0.08
SAN JOSE B 1112 | 82261112 | 12.52 |  |  |  | 12.52
SAN JOSE B 1113 | 82261113 | 0.1 |  |  |  | 0.1
SAN JOSE B 1114 | 82261114 | 0.68 |  |  |  | 0.68
SAN JOSE B 1115 | 82261115 | 0.78 |  |  |  | 0.78
SAN JOSE B 1116 | 82261116 | 5 |  |  |  | 5
SAN JOSE B 1117 | 82261117 | 3.63 |  |  |  | 3.63
SAN JUSTO 1101 | 183181101 | 55.93 |  | 37.23 |  | 18.7
SAN LEANDRO U 1101 | 13111101 | 3.89 |  |  |  | 3.89
SAN LEANDRO U 1102 | 13111102 | 12.39 |  |  |  | 12.39
SAN LEANDRO U 1103 | 13111103 | 1.93 |  |  |  | 1.93
SAN LEANDRO U 1104 | 13111104 | 6.25 |  |  |  | 6.25
SAN LEANDRO U 1105 | 13111105 | 7.75 |  |  |  | 7.75
SAN LEANDRO U 1106 | 13111106 | 12.37 |  |  |  | 12.37
SAN LEANDRO U 1107 | 13111107 | 15.01 |  |  |  | 15.01
SAN LEANDRO U 1108 | 13111108 | 8.49 |  |  |  | 8.49
SAN LEANDRO U 1109 | 13111109 | 19.8 | 0.86 | 11.57 |  | 7.37
SAN LEANDRO U 1110 | 13111110 | 18.9 |  |  |  | 18.9
SAN LEANDRO U 1111 | 13111111 | 2.29 |  |  |  | 2.29
SAN LEANDRO U 1112 | 13111112 | 3.96 |  |  |  | 3.96
SAN LEANDRO U 1113 | 13111113 | 7.11 |  |  |  | 7.11
SAN LEANDRO U 1114 | 13111114 | 29.07 |  | 9.53 |  | 19.54
SAN LEANDRO U 1115 | 13111115 | 1.47 |  |  |  | 1.47
SAN LEANDRO U 1116 | 13111116 | 3.8 |  |  |  | 3.8
SAN LEANDRO U 1151 | 13111151 | 5.95 |  |  |  | 5.95
SAN LORENZO 0401 | 13460401 | 4.37 |  |  |  | 4.37
SAN LUIS OBISPO 1101 | 182631101 | 36.78 | 10.18 | 15.4 |  | 11.2
SAN LUIS OBISPO 1102 | 182631102 | 13.44 |  | 0.58 |  | 12.86
SAN LUIS OBISPO 1103 | 182631103 | 38.96 |  | 20.21 |  | 18.75
SAN LUIS OBISPO 1104 | 182631104 | 82.39 | 21.32 | 36.56 |  | 24.51
SAN LUIS OBISPO 1105 | 182631105 | 11.79 |  | 1.43 |  | 10.36
SAN LUIS OBISPO 1107 | 182631107 | 50.34 | 24.62 | 21.75 |  | 3.97
SAN LUIS OBISPO 1108 | 182631108 | 10.03 |  | 1.61 |  | 8.42
SAN MATEO 0404 | 24190404 | 5.08 |  |  |  | 5.08
SAN MATEO 0407 | 24190407 | 3.59 |  |  |  | 3.59
SAN MATEO 0408 | 24190408 | 5.63 |  |  |  | 5.63
SAN MATEO 0409 | 24190409 | 3.13 |  |  |  | 3.13
SAN MATEO 0410 | 24190410 | 5.15 |  |  |  | 5.15
SAN MATEO 2101 | 24192101 | 7.25 |  |  |  | 7.25
SAN MATEO 2102 | 24192102 | 13.01 |  |  |  | 13.01
SAN MIGUEL 1104 | 182661104 | 144.71 |  | 23.74 |  | 120.97
SAN MIGUEL 1105 | 182661105 | 20.16 |  | 1.39 |  | 18.77
SAN MIGUEL 1106 | 182661106 | 74.23 |  | 37.82 |  | 36.41
SAN MIGUEL 1107 | 182661107 | 5.74 |  |  |  | 5.74
SAN PABLO 1105 | 14371105 | 19.47 |  |  |  | 19.47
SAN PABLO 1106 | 14371106 | 0.65 |  |  |  | 0.65
SAN RAFAEL 1101 | 42011101 | 27.43 | 12.24 | 1.2 |  | 13.99
SAN RAFAEL 1102 | 42011102 | 4.85 |  |  |  | 4.85
SAN RAFAEL 1103 | 42011103 | 5.9 |  |  |  | 5.9
SAN RAFAEL 1104 | 42011104 | 24.9 | 1.88 | 9.71 |  | 13.31
SAN RAFAEL 1105 | 42011105 | 23.01 |  | 1.62 |  | 21.39
SAN RAFAEL 1106 | 42011106 | 21.1 |  | 2.8 |  | 18.3
SAN RAFAEL 1107 | 42011107 | 29.14 | 18.24 | 2.98 |  | 7.92
SAN RAFAEL 1108 | 42011108 | 29.46 | 26.37 | 0.44 |  | 2.65
SAN RAFAEL 1109 | 42011109 | 26.32 |  | 9.79 |  | 16.53
SAN RAFAEL 1110 | 42011110 | 13.14 | 7.93 |  |  | 5.21
SAN RAMON 2101 | 14232101 | 1.08 |  | 0.61 |  | 0.47
SAN RAMON 2102 | 14232102 | 2.33 |  | 1.52 |  | 0.81
SAN RAMON 2103 | 14232103 | 2.76 | 0 |  |  | 2.76
SAN RAMON 2104 | 14232104 | 20.65 |  |  |  | 20.65
SAN RAMON 2105 | 14232105 | 3.44 |  |  |  | 3.44
SAN RAMON 2106 | 14232106 | 5.09 | 0.45 |  |  | 4.64
SAN RAMON 2107 | 14232107 | 27.43 | 14.33 | 0.17 |  | 12.93
SAN RAMON 2108 | 14232108 | 17.31 | 16.38 |  |  | 0.93
SAN RAMON 2110 | 14232110 | 0.1 |  |  |  | 0.1
SAN RAMON 2111 | 14232111 | 9.43 |  |  |  | 9.43
SAN RAMON 2114 | 14232114 | 1.61 |  |  |  | 1.61
SAN RAMON 2116 | 14232116 | 0 |  |  |  | 0
SAN RAMON 2117 | 14232117 | 1.67 |  | 0.56 |  | 1.11
SAN RAMON 2118 | 14232118 | 0.82 |  |  |  | 0.82
SAN RAMON 2119 | 14232119 | 3.02 |  | 0.59 |  | 2.43
SAND CREEK 1103 | 254601103 | 150.17 |  | 148.46 |  | 1.71
SANGER 1104 | 252351104 | 9.61 |  |  |  | 9.61
SANGER 1106 | 252351106 | 8.57 |  |  |  | 8.57
SANGER 1108 | 252351108 | 81.22 |  |  |  | 81.22
SANGER 1110 | 252351110 | 29.33 |  |  |  | 29.33
SANGER 1112 | 252351112 | 11.54 |  |  |  | 11.54
SANGER 1114 | 252351114 | 63.07 |  |  |  | 63.07
SANGER 1116 | 252351116 | 6.36 |  |  |  | 6.36
SANGER 1118 | 252351118 | 29.51 |  |  |  | 29.51
SANTA MARIA 1105 | 182671105 | 28.85 |  |  |  | 28.85
SANTA MARIA 1106 | 182671106 | 18.94 |  |  |  | 18.94
SANTA MARIA 1107 | 182671107 | 4.93 |  |  |  | 4.93
SANTA MARIA 1108 | 182671108 | 93.89 | 43.73 | 28.52 |  | 21.64
SANTA MARIA 1109 | 182671109 | 46.46 |  |  |  | 46.46
SANTA MARIA 1110 | 182671110 | 52.56 |  |  |  | 52.56
SANTA MARIA 1111 | 182671111 | 15.6 |  |  |  | 15.6
SANTA MARIA 1112 | 182671112 | 10.45 |  |  |  | 10.45
SANTA NELLA 1101 | 254051101 | 38.53 |  |  |  | 38.53
SANTA NELLA 1104 | 254051104 | 52.32 |  |  |  | 52.32
SANTA RITA 1102 | 253541102 | 89.22 |  |  |  | 89.22
SANTA RITA 1105 | 253541105 | 61.38 |  |  |  | 61.38
SANTA ROSA A 1101 | 42151101 | 4.52 |  |  |  | 4.52
SANTA ROSA A 1102 | 42151102 | 12.08 |  |  |  | 12.08
SANTA ROSA A 1103 | 42151103 | 10.95 |  |  |  | 10.95
SANTA ROSA A 1104 | 42151104 | 56.15 | 37.51 | 5.24 |  | 13.4
SANTA ROSA A 1105 | 42151105 | 9.38 |  |  |  | 9.38
SANTA ROSA A 1106 | 42151106 | 10 |  |  |  | 10
SANTA ROSA A 1107 | 42151107 | 8.43 | 2.88 |  |  | 5.55
SANTA ROSA A 1108 | 42151108 | 6.81 |  | 0.14 |  | 6.67
SANTA ROSA A 1109 | 42151109 | 5.92 |  |  |  | 5.92
SANTA ROSA A 1110 | 42151110 | 22.39 |  |  |  | 22.39
SANTA ROSA A 1111 | 42151111 | 26.1 |  | 5.67 |  | 20.43
SANTA ROSA A 1112 | 42151112 | 12.64 |  |  |  | 12.64
SANTA TERESA 2101 | 82962101 | 0.43 |  |  |  | 0.43
SANTA YNEZ 1101 | 182721101 | 58.86 | 14.55 | 14.07 |  | 30.24
SANTA YNEZ 1102 | 182721102 | 33.83 | 4.99 | 9.01 |  | 19.83
SANTA YNEZ 1104 | 182721104 | 84.8 | 4.59 | 37.72 |  | 42.49
SARANAP 0401 | 13560401 | 2.46 |  |  |  | 2.46
SARATOGA 1103 | 83371103 | 10.48 |  | 4.59 |  | 5.89
SARATOGA 1104 | 83371104 | 18.12 |  | 2.92 |  | 15.2
SARATOGA 1105 | 83371105 | 16.72 |  | 10.1 |  | 6.62
SARATOGA 1106 | 83371106 | 26.76 | 1.38 | 14.05 |  | 11.33
SARATOGA 1107 | 83371107 | 45.44 | 20.53 | 13.94 |  | 10.97
SARATOGA 1108 | 83371108 | 18.57 |  |  |  | 18.57
SARATOGA 1109 | 83371109 | 25.33 |  |  |  | 25.33
SARATOGA 1110 | 83371110 | 19.99 |  |  |  | 19.99
SARATOGA 1111 | 83371111 | 23.93 |  |  |  | 23.93
SARATOGA 1112 | 83371112 | 8.44 |  |  |  | 8.44
SARATOGA 1113 | 83371113 | 25.66 |  |  |  | 25.66
SARATOGA 1114 | 83371114 | 21.11 |  |  |  | 21.11
SARATOGA 1115 | 83371115 | 13.81 |  | 2.82 |  | 10.99
SAUSALITO 0401 | 42490401 | 2.01 |  |  |  | 2.01
SAUSALITO 0402 | 42490402 | 2.94 |  |  |  | 2.94
SAUSALITO 1101 | 42491101 | 6.74 |  | 1.25 |  | 5.49
SAUSALITO 1102 | 42491102 | 17.99 |  | 9.11 |  | 8.88
SCE MCFARLAND 1101 | 258111101 | 0.5 |  |  |  | 0.5
SCE REFUGIO 1701 | 188071701 | 0.08 | 0.08 |  |  | 0
SCE TEHACHAPI 1101 | 258131101 | 1.44 |  | 1.44 |  | 0
SCE TEJON TIE 1101 | 258191101 | 0.06 |  | 0.06 |  | 0
SCE VEGAS 1701 | 188881701 | 0.17 | 0.17 |  |  | 0
SCHINDLER 1104 | 252891104 | 0.01 |  |  |  | 0.01
SCHINDLER 1105 | 252891105 | 41.86 |  |  |  | 41.86
SCHINDLER 1107 | 252891107 | 1.43 |  |  |  | 1.43
SCHINDLER 1108 | 252891108 | 2.31 |  |  |  | 2.31
SCHINDLER 1109 | 252891109 | 1.67 |  |  |  | 1.67
SCHINDLER 1110 | 252891110 | 48.18 |  |  |  | 48.18
SCHINDLER 1111 | 252891111 | 41.63 |  |  |  | 41.63
SCHINDLER 1112 | 252891112 | 49.22 |  |  |  | 49.22
SCHINDLER 1114 | 252891114 | 58.36 |  |  |  | 58.36
SCHINDLER 1116 | 252891116 | 25.73 |  |  |  | 25.73
SEACLIFF 0401 | 83500401 | 9.16 | 6.52 | 1.23 |  | 1.41
SEACLIFF 0402 | 83500402 | 1.57 | 0.07 | 0.01 |  | 1.49
SEMITROPIC 1104 | 252901104 | 15.83 |  |  |  | 15.83
SEMITROPIC 1106 | 252901106 | 27.34 |  |  |  | 27.34
SEMITROPIC 1108 | 252901108 | 11.78 |  |  |  | 11.78
SEMITROPIC 1110 | 252901110 | 50.12 |  |  |  | 50.12
SEMITROPIC 1112 | 252901112 | 26.73 |  |  |  | 26.73
SERRAMONTE 1103 | 22861103 | 13.16 |  |  |  | 13.16
SERRAMONTE 1104 | 22861104 | 12.65 |  |  |  | 12.65
SF E 0401 | 22070401 | 3.52 |  |  |  | 3.52
SF E 0405 | 22070405 | 2.2 |  |  |  | 2.2
SF E 0406 | 22070406 | 1.47 |  |  |  | 1.47
SF E 0407 | 22070407 | 0.94 |  |  |  | 0.94
SF E 0408 | 22070408 | 2.68 |  |  |  | 2.68
SF E 0409 | 22070409 | 1.8 |  |  |  | 1.8
SF E 0410 | 22070410 | 1.87 |  |  |  | 1.87
SF E 1101 | 22071101 | 1.12 |  |  |  | 1.12
SF E 1103 | 22071103 | 3.14 |  |  |  | 3.14
SF E 1105 | 22071105 | 2.42 |  |  |  | 2.42
SF E 1107 | 22071107 | 3.75 |  |  |  | 3.75
SF G 0401 | 22090401 | 0.67 |  |  |  | 0.67
SF G 0402 | 22090402 | 1.56 |  |  |  | 1.56
SF G 0403 | 22090403 | 0.71 |  |  |  | 0.71
SF G 0404 | 22090404 | 0.96 |  |  |  | 0.96
SF G 0405 | 22090405 | 1.47 |  |  |  | 1.47
SF G 0406 | 22090406 | 1.28 |  |  |  | 1.28
SF G 0407 | 22090407 | 1.36 |  |  |  | 1.36
SF G 0408 | 22090408 | 1.28 |  |  |  | 1.28
SF G 0409 | 22090409 | 0.91 |  |  |  | 0.91
SF G 0410 | 22090410 | 0.58 |  |  |  | 0.58
SF G 0412 | 22090412 | 1.1 |  |  |  | 1.1
SF G 0413 | 22090413 | 0.98 |  |  |  | 0.98
SF G 0414 | 22090414 | 0.89 |  |  |  | 0.89
SF G 1101 | 22091101 | 1.02 |  |  |  | 1.02
SF G 1102 | 22091102 | 0.56 |  |  |  | 0.56
SF H 0401 | 22100401 | 4.61 |  |  |  | 4.61
SF H 0402 | 22100402 | 4.08 |  |  |  | 4.08
SF H 0403 | 22100403 | 1.06 |  |  |  | 1.06
SF H 0404 | 22100404 | 2.72 |  |  |  | 2.72
SF H 0405 | 22100405 | 2.46 |  |  |  | 2.46
SF H 1101 | 22101101 | 6.42 |  |  |  | 6.42
SF H 1102 | 22101102 | 6.91 |  |  |  | 6.91
SF H 1103 | 22101103 | 8.63 |  |  |  | 8.63
SF H 1104 | 22101104 | 0.65 |  |  |  | 0.65
SF H 1105 | 22101105 | 14.84 |  |  |  | 14.84
SF H 1106 | 22101106 | 7.93 |  |  |  | 7.93
SF H 1107 | 22101107 | 3.78 |  |  |  | 3.78
SF H 1108 | 22101108 | 13.42 |  |  |  | 13.42
SF H 1109 | 22101109 | 4.69 |  |  |  | 4.69
SF H 1110 | 22101110 | 13.13 |  |  |  | 13.13
SF H 1111 | 22101111 | 3.9 |  |  |  | 3.9
SF J 0402 | 22220402 | 0.87 |  |  |  | 0.87
SF J 0404 | 22220404 | 0.52 |  |  |  | 0.52
SF J 0406 | 22220406 | 0.52 |  |  |  | 0.52
SF J 0407 | 22220407 | 0 |  |  |  | 0
SF J 0409 | 22220409 | 0.15 |  |  |  | 0.15
SF J 1108 | 22221108 | 0 |  |  |  | 0
SF K 0401 | 22130401 | 2.48 |  |  |  | 2.48
SF K 0402 | 22130402 | 3.31 |  |  |  | 3.31
SF K 0403 | 22130403 | 2.49 |  |  |  | 2.49
SF K 0404 | 22130404 | 0.97 |  |  |  | 0.97
SF K 0405 | 22130405 | 2.81 |  |  |  | 2.81
SF K 0406 | 22130406 | 1.73 |  |  |  | 1.73
SF K 0407 | 22130407 | 1.28 |  |  |  | 1.28
SF K 0408 | 22130408 | 1.35 |  |  |  | 1.35
SF K 0409 | 22130409 | 2.39 |  |  |  | 2.39
SF K 0410 | 22130410 | 2.03 |  |  |  | 2.03
SF K 0411 | 22130411 | 2.27 |  |  |  | 2.27
SF K 1101 | 22131101 | 6.74 |  |  |  | 6.74
SF L 0401 | 22260401 | 2.47 |  |  |  | 2.47
SF L 0402 | 22260402 | 0 |  |  |  | 0
SF L 0403 | 22260403 | 0.25 |  |  |  | 0.25
SF L 0404 | 22260404 | 0.81 |  |  |  | 0.81
SF L 0405 | 22260405 | 2.3 |  |  |  | 2.3
SF L 0406 | 22260406 | 2.14 |  |  |  | 2.14
SF L 0407 | 22260407 | 0.55 |  |  |  | 0.55
SF L 0408 | 22260408 | 2.4 |  |  |  | 2.4
SF L 0409 | 22260409 | 0.15 |  |  |  | 0.15
SF L 1101 | 22261101 | 2.38 |  |  |  | 2.38
SF L 1102 | 22261102 | 7.95 |  |  |  | 7.95
SF L 1103 | 22261103 | 1.97 |  |  |  | 1.97
SF M 0401 | 22270401 | 3.73 |  |  |  | 3.73
SF M 0402 | 22270402 | 1.97 |  |  |  | 1.97
SF M 0403 | 22270403 | 3.69 |  |  |  | 3.69
SF M 0404 | 22270404 | 3.57 |  |  |  | 3.57
SF M 0405 | 22270405 | 2.35 |  |  |  | 2.35
SF M 0406 | 22270406 | 2.91 |  |  |  | 2.91
SF N 0401 | 22280401 | 3.13 |  |  |  | 3.13
SF N 0402 | 22280402 | 1.01 |  |  |  | 1.01
SF N 0403 | 22280403 | 2.47 |  |  |  | 2.47
SF N 0405 | 22280405 | 1.07 |  |  |  | 1.07
SF N 0406 | 22280406 | 0.8 |  |  |  | 0.8
SF N 0408 | 22280408 | 3.12 |  |  |  | 3.12
SF N 1101 | 22281101 | 0.27 |  |  |  | 0.27
SF N 1102 | 22281102 | 6.09 |  |  |  | 6.09
SHADY GLEN 1101 | 152431101 | 41.09 |  | 34.74 |  | 6.35
SHADY GLEN 1102 | 152431102 | 51.78 | 24.1 | 25.89 |  | 1.79
SHAFTER 1101 | 253651101 | 0.03 |  |  |  | 0.03
SHAFTER 1102 | 253651102 | 27.52 |  |  |  | 27.52
SHAFTER 1103 | 253651103 | 39.63 |  |  |  | 39.63
SHAFTER 1104 | 253651104 | 9.62 |  |  |  | 9.62
SHAFTER 1111 | 253651111 | 24.34 |  |  |  | 24.34
SHAFTER 1112 | 253651112 | 47.89 |  |  |  | 47.89
SHARON 1101 | 255331101 | 1.54 |  |  |  | 1.54
SHEPHERD 2109 | 252062109 | 4.35 |  |  |  | 4.35
SHEPHERD 2110 | 252062110 | 8.38 |  |  |  | 8.38
SHEPHERD 2111 | 252062111 | 69.07 |  | 29.52 |  | 39.55
SHEPHERD 2112 | 252062112 | 7.75 |  |  |  | 7.75
SHINGLE SPRINGS 1103 | 153651103 | 13.67 | 4.6 | 3.1 |  | 5.97
SHINGLE SPRINGS 1104 | 153651104 | 59.85 | 37.11 | 6.66 |  | 16.08
SHINGLE SPRINGS 2105 | 153652105 | 32.74 | 26.05 | 4.37 |  | 2.32
SHINGLE SPRINGS 2108 | 153652108 | 29.67 | 7.21 | 7.76 |  | 14.7
SHINGLE SPRINGS 2109 | 153652109 | 209.66 | 107.69 | 101.33 |  | 0.64
SHINGLE SPRINGS 2110 | 153652110 | 65.17 | 55.44 | 7.37 |  | 2.36
SILVER 0401 | 22670401 | 5.04 |  |  |  | 5.04
SILVERADO 2102 | 43432102 | 108.6 | 32.79 | 24.65 |  | 51.16
SILVERADO 2103 | 43432103 | 32.58 | 10.77 | 0.03 |  | 21.78
SILVERADO 2104 | 43432104 | 139.18 | 75.02 | 36.32 |  | 27.84
SILVERADO 2105 | 43432105 | 63.59 | 34.9 | 1.72 |  | 26.97
SISQUOC 1101 | 182811101 | 26.81 |  |  |  | 26.81
SISQUOC 1102 | 182811102 | 115.23 | 31.2 | 19.57 |  | 64.46
SISQUOC 1103 | 182811103 | 50.1 | 22.64 | 2.79 |  | 24.67
SISQUOC 1104 | 182811104 | 32.55 |  |  |  | 32.55
SKAGGS ISLAND 1101 | 43341101 | 0.05 |  |  |  | 0.05
SMARTVILLE 1101 | 153791101 | 16.07 |  | 15.75 |  | 0.32
SMUD 0401 | 158050401 | 0.01 |  | 0.01 |  | 0
SMYRNA 1101 | 253551101 | 43.48 |  |  |  | 43.48
SMYRNA 1102 | 253551102 | 66.66 |  |  |  | 66.66
SMYRNA 1104 | 253551104 | 44.55 |  |  |  | 44.55
SMYRNA 1105 | 253551105 | 51.92 |  |  |  | 51.92
SMYRNA 1106 | 253551106 | 46.54 |  |  |  | 46.54
SNEATH LANE 1101 | 22721101 | 9.42 |  | 2.26 |  | 7.16
SNEATH LANE 1102 | 22721102 | 10.53 |  | 1.24 |  | 9.29
SNEATH LANE 1106 | 22721106 | 11.62 |  | 2.62 |  | 9
SNEATH LANE 1107 | 22721107 | 10.47 |  | 0.91 |  | 9.56
SO. CAL. EDISON #3 1101 | 258861101 | 9.49 | 6.73 | 2.6 |  | 0.16
SO. CAL. EDISON 1001 | 258881001 | 2.02 |  |  |  | 2.02
SOBRANTE 1101 | 14671101 | 21.39 |  | 14.97 |  | 6.42
SOBRANTE 1102 | 14671102 | 27.62 | 1.26 | 26 |  | 0.36
SOBRANTE 1103 | 14671103 | 11.36 | 1.82 | 7.69 |  | 1.85
SOLANO 0402 | 13140402 | 6.32 |  |  |  | 6.32
SOLEDAD 2101 | 182052101 | 41.49 |  | 17.33 |  | 24.16
SOLEDAD 2102 | 182052102 | 48.97 |  | 11.6 |  | 37.37
SOLEDAD 2104 | 182052104 | 25.09 |  | 1.22 |  | 23.87
SOLEDAD 2105 | 182052105 | 47.73 |  | 4.47 |  | 43.26
SONOMA 1102 | 42721102 | 18.14 | 6.02 |  |  | 12.12
SONOMA 1103 | 42721103 | 25.42 | 12.68 |  |  | 12.74
SONOMA 1104 | 42721104 | 55.43 |  | 19.63 |  | 35.8
SONOMA 1105 | 42721105 | 63.43 | 3.47 | 10.14 |  | 49.82
SONOMA 1106 | 42721106 | 11.14 | 0.88 |  |  | 10.26
SONOMA 1107 | 42721107 | 51.96 |  | 3.87 |  | 48.09
SOQUEL 0402 | 83300402 | 6.58 |  |  |  | 6.58
SOTO 0402 | 13260402 | 2.04 |  |  |  | 2.04
SPAULDING 1101 | 152251101 | 23.94 | 1.19 | 19.15 | 0.37 | 3.23
SPENCE 1102 | 182201102 | 33.47 |  | 2.36 |  | 31.11
SPENCE 1103 | 182201103 | 12.37 |  |  |  | 12.37
SPENCE 1104 | 182201104 | 52.34 |  | 9.04 |  | 43.3
SPENCE 1105 | 182201105 | 7.18 |  |  |  | 7.18
SPRING GAP 1702 | 162831702 | 42.35 | 39.7 | 0.77 |  | 1.88
STAFFORD 1101 | 43201101 | 15.35 |  | 2.27 |  | 13.08
STAFFORD 1102 | 43201102 | 37.35 | 1.54 | 19.66 |  | 16.15
STAGG 1101 | 162421101 | 19.59 |  |  |  | 19.59
STAGG 1103 | 162421103 | 6.06 |  |  |  | 6.06
STAGG 1105 | 162421105 | 12.07 |  |  |  | 12.07
STAGG 1106 | 162421106 | 1.86 |  |  |  | 1.86
STAGG 2104 | 162422104 | 24.45 |  |  |  | 24.45
STAGG 2105 | 162422105 | 4.5 |  |  |  | 4.5
STAGG 2106 | 162422106 | 5.45 |  |  |  | 5.45
STAGG 2107 | 162422107 | 6.04 |  |  |  | 6.04
STAGG 2108 | 162422108 | 5.83 |  |  |  | 5.83
STANISLAUS 1701 | 162821701 | 74.89 | 22.65 | 51.99 |  | 0.25
STANISLAUS 1702 | 162821702 | 85 | 78.35 | 6.66 |  | -0.01
STELLING 1102 | 83481102 | 0.69 |  |  |  | 0.69
STELLING 1103 | 83481103 | 2.85 |  |  |  | 2.85
STELLING 1104 | 83481104 | 11.01 |  |  |  | 11.01
STELLING 1105 | 83481105 | 0.4 |  |  |  | 0.4
STELLING 1106 | 83481106 | 0 |  |  |  | 0
STELLING 1107 | 83481107 | 8.19 |  |  |  | 8.19
STELLING 1108 | 83481108 | 31.72 |  |  |  | 31.72
STELLING 1109 | 83481109 | 16.57 |  | 0.88 |  | 15.69
STELLING 1110 | 83481110 | 49.26 | 10.28 | 21.86 |  | 17.12
STELLING 1111 | 83481111 | 26.77 |  |  |  | 26.77
STELLING 1112 | 83481112 | 2.19 |  |  |  | 2.19
STELLING 1113 | 83481113 | 17.16 |  |  |  | 17.16
STILLWATER 1101 | 103561101 | 35.17 |  | 34.41 |  | 0.76
STILLWATER 1102 | 103561102 | 78.34 |  | 78.24 |  | 0.1
STOCKDALE 1105 | 254071105 | 5.05 |  |  |  | 5.05
STOCKDALE 1106 | 254071106 | 5.6 |  |  |  | 5.6
STOCKDALE 1108 | 254071108 | 3.84 |  |  |  | 3.84
STOCKDALE 1109 | 254071109 | 4.48 |  |  |  | 4.48
STOCKDALE 1110 | 254071110 | 6.31 |  |  |  | 6.31
STOCKDALE 1111 | 254071111 | 8.66 |  |  |  | 8.66
STOCKDALE 2105 | 254072105 | 5.01 |  |  |  | 5.01
STOCKDALE 2106 | 254072106 | 8.97 |  |  |  | 8.97
STOCKDALE 2107 | 254072107 | 1.84 |  |  |  | 1.84
STOCKDALE 2108 | 254072108 | 2.96 |  |  |  | 2.96
STOCKDALE 2109 | 254072109 | 8.53 |  |  |  | 8.53
STOCKDALE 2110 | 254072110 | 8.78 |  |  |  | 8.78
STOCKDALE 2111 | 254072111 | 2.87 |  |  |  | 2.87
STOCKDALE 2112 | 254072112 | 30.1 |  |  |  | 30.1
STOCKDALE 2113 | 254072113 | 15.7 |  |  |  | 15.7
STOCKDALE 2114 | 254072114 | 10.47 |  |  |  | 10.47
STOCKDALE 2115 | 254072115 | 0.45 |  |  |  | 0.45
STOCKTON A 0404 | 162370404 | 5.17 |  |  |  | 5.17
STOCKTON A 0405 | 162370405 | 0.39 |  |  |  | 0.39
STOCKTON A 0406 | 162370406 | 3.25 |  |  |  | 3.25
STOCKTON A 0410 | 162370410 | 6.31 |  |  |  | 6.31
STOCKTON A 1101 | 162371101 | 4.12 |  |  |  | 4.12
STOCKTON A 1102 | 162371102 | 6.47 |  |  |  | 6.47
STOCKTON A 1103 | 162371103 | 0.21 |  |  |  | 0.21
STOCKTON A 1104 | 162371104 | 15.88 |  |  |  | 15.88
STOCKTON A 1105 | 162371105 | 12.35 |  |  |  | 12.35
STOCKTON A 1106 | 162371106 | 16.95 |  |  |  | 16.95
STOCKTON A 1107 | 162371107 | 11.28 |  |  |  | 11.28
STOCKTON A 1108 | 162371108 | 9.3 |  |  |  | 9.3
STOCKTON A 1109 | 162371109 | 11.9 |  |  |  | 11.9
STOCKTON A 1110 | 162371110 | 10.08 |  |  |  | 10.08
STOCKTON A 1111 | 162371111 | 0.07 |  |  |  | 0.07
STOCKTON ACRES 0401 | 163220401 | 2.87 |  |  |  | 2.87
STOCKTON ACRES 0402 | 163220402 | 3.01 |  |  |  | 3.01
STONE 1101 | 83701101 | 19.95 |  |  |  | 19.95
STONE 1104 | 83701104 | 5.55 |  |  |  | 5.55
STONE 1107 | 83701107 | 11.97 |  |  |  | 11.97
STONE 1108 | 83701108 | 4.39 |  |  |  | 4.39
STONE 1109 | 83701109 | 8.25 |  |  |  | 8.25
STONE 1110 | 83701110 | 11.83 |  |  |  | 11.83
STONE CORRAL 1108 | 252921108 | 76.2 |  | 1.87 |  | 74.33
STONE CORRAL 1109 | 252921109 | 16.52 |  |  |  | 16.52
STONE CORRAL 1110 | 252921110 | 62.6 |  | 2.01 |  | 60.59
STOREY 1104 | 254611104 | 75.54 |  |  |  | 75.54
STOREY 1105 | 254611105 | 14.36 |  |  |  | 14.36
STOREY 1106 | 254611106 | 13.49 |  |  |  | 13.49
STOREY 1107 | 254611107 | 19.08 |  |  |  | 19.08
STOREY 1108 | 254611108 | 72.24 |  |  |  | 72.24
STOREY 1109 | 254611109 | 177.3 |  |  |  | 177.3
STOREY 1111 | 254611111 | 29.65 |  |  |  | 29.65
STROUD 1101 | 253661101 | 31.94 |  |  |  | 31.94
STROUD 1102 | 253661102 | 34.26 |  |  |  | 34.26
STROUD 1104 | 253661104 | 31.17 |  |  |  | 31.17
STUART 0401 | 13840401 | 2.94 |  |  |  | 2.94
STUART 0402 | 13840402 | 2.12 |  |  |  | 2.12
STUART 0403 | 13840403 | 3.12 |  |  |  | 3.12
STUART 0404 | 13840404 | 1.07 |  |  |  | 1.07
STUART 0405 | 13840405 | 2.8 |  |  |  | 2.8
STUART 0406 | 13840406 | 2.94 |  |  |  | 2.94
SUISUN 1101 | 62131101 | 6.17 |  |  |  | 6.17
SUISUN 1102 | 62131102 | 9.81 |  |  |  | 9.81
SUISUN 1103 | 62131103 | 2.73 |  |  |  | 2.73
SUISUN 1104 | 62131104 | 4.83 |  |  |  | 4.83
SUISUN 1105 | 62131105 | 5.37 |  |  |  | 5.37
SUISUN 1106 | 62131106 | 4.99 |  |  |  | 4.99
SUISUN 1107 | 62131107 | 9.67 |  |  |  | 9.67
SUISUN 1108 | 62131108 | 6.59 |  |  |  | 6.59
SUISUN 1109 | 62131109 | 8.06 |  |  |  | 8.06
SUISUN 1110 | 62131110 | 2.91 |  |  |  | 2.91
SUISUN 1111 | 62131111 | 0.63 |  |  |  | 0.63
SUISUN 1112 | 62131112 | 2.85 |  |  |  | 2.85
SULLIVAN 0402 | 22850402 | 3.2 |  |  |  | 3.2
SUMMIT 1101 | 152591101 | 15.19 |  | 7.2 | 2.05 | 5.94
SUMMIT 1102 | 152591102 | 5.04 |  | 5.04 |  | 0
SUNOL 1101 | 14241101 | 55.43 | 9.57 | 23.58 |  | 22.28
SWIFT 2102 | 83392102 | 2.95 |  | 0.35 |  | 2.6
SWIFT 2106 | 83392106 | 21.28 |  |  |  | 21.28
SWIFT 2107 | 83392107 | 11.89 |  | 1.89 |  | 10
SWIFT 2108 | 83392108 | 4.92 |  |  |  | 4.92
SWIFT 2109 | 83392109 | 5.46 |  | 0.15 |  | 5.31
SWIFT 2110 | 83392110 | 86.24 |  | 81.31 |  | 4.93
SWIFT 2111 | 83392111 | 8.58 |  |  |  | 8.58
SYCAMORE CREEK 1101 | 102971101 | 4.78 |  |  |  | 4.78
SYCAMORE CREEK 1102 | 102971102 | 7.55 |  |  |  | 7.55
SYCAMORE CREEK 1103 | 102971103 | 3.14 |  |  |  | 3.14
SYCAMORE CREEK 1104 | 102971104 | 8.13 |  |  |  | 8.13
SYCAMORE CREEK 1105 | 102971105 | 15.13 |  |  |  | 15.13
SYCAMORE CREEK 1107 | 102971107 | 6.01 |  |  |  | 6.01
SYCAMORE CREEK 1109 | 102971109 | 13.42 |  | 0.13 |  | 13.29
SYCAMORE CREEK 1110 | 102971110 | 8.42 |  |  |  | 8.42
SYCAMORE CREEK 1111 | 102971111 | 64.8 | 27.37 | 24.9 |  | 12.53
TAFT 1101 | 252081101 | 14.18 |  |  |  | 14.18
TAFT 1102 | 252081102 | 0.05 |  |  |  | 0.05
TAFT 1103 | 252081103 | 27.46 |  |  |  | 27.46
TAFT 1104 | 252081104 | 11.2 |  |  |  | 11.2
TAFT 1106 | 252081106 | 7.13 |  |  |  | 7.13
TAFT 1108 | 252081108 | 9.21 |  |  |  | 9.21
TAMARACK 1101 | 152291101 | 19.55 |  | 18.66 | 0.13 | 0.76
TAMARACK 1102 | 152291102 | 7.85 |  |  | 0.31 | 7.54
TAR FLAT 0401 | 163240401 | 3.62 | 0 | 3.15 |  | 0.47
TAR FLAT 0402 | 163240402 | 6.7 | 0.88 | 4.52 |  | 1.3
TARAVAL 0401 | 22500401 | 1.82 |  |  |  | 1.82
TARAVAL 0402 | 22500402 | 3.04 |  |  |  | 3.04
TARAVAL 0403 | 22500403 | 3.47 |  |  |  | 3.47
TASSAJARA 2103 | 14662103 | 19.56 | 0.18 | 0.3 |  | 19.08
TASSAJARA 2104 | 14662104 | 9.65 | 1.57 | 4.36 |  | 3.72
TASSAJARA 2106 | 14662106 | 2.92 |  | 0.35 |  | 2.57
TASSAJARA 2107 | 14662107 | 8.52 |  |  |  | 8.52
TASSAJARA 2108 | 14662108 | 24.1 | 1.7 |  |  | 22.4
TASSAJARA 2109 | 14662109 | 4.02 |  | 2.89 |  | 1.13
TASSAJARA 2112 | 14662112 | 18.54 | 6.79 | 3.56 |  | 8.19
TASSAJARA 2113 | 14662113 | 4.93 | 3.82 |  |  | 1.11
TECUYA 1101 | 254511101 | 0.04 |  |  |  | 0.04
TEJON 1102 | 252931102 | 60.73 |  | 36.83 |  | 23.9
TEJON 1103 | 252931103 | 32.57 |  | 2.96 |  | 29.61
TEJON 1105 | 252931105 | 31.29 |  |  |  | 31.29
TEJON 1106 | 252931106 | 36 |  |  |  | 36
TEJON 1107 | 252931107 | 0.54 |  |  |  | 0.54
TEMBLOR 1104 | 252551104 | 49.26 |  |  |  | 49.26
TEMBLOR 2103 | 252552103 | 30.3 |  |  |  | 30.3
TEMPLETON 2108 | 183052108 | 36.13 |  | 5.36 |  | 30.77
TEMPLETON 2109 | 183052109 | 211.96 |  |  |  | 211.96
TEMPLETON 2110 | 183052110 | 173.1 | 33.51 | 93.84 |  | 45.75
TEMPLETON 2111 | 183052111 | 63.83 | 0.88 | 45.94 |  | 17.01
TEMPLETON 2112 | 183052112 | 37.82 |  | 2.6 |  | 35.22
TEMPLETON 2113 | 183052113 | 323.88 | 53.34 | 143.01 |  | 127.53
TEMPORARY CARBONA 1101 | 169951101 | 0.64 |  |  |  | 0.64
TEMPORARY CARBONA 1102 | 169951102 | 3.44 |  |  |  | 3.44
TEMPORARY CARBONA 1104 | 169951104 | 31.68 |  |  |  | 31.68
TEMPORARY CARBONA 1105 | 169951105 | 1.64 |  |  |  | 1.64
TERMINOUS 1102 | 163021102 | 22.68 |  |  |  | 22.68
TERMINOUS 1103 | 163021103 | 40.02 |  |  |  | 40.02
TEVIS 2101 | 255322101 | 23.77 |  |  |  | 23.77
TEVIS 2102 | 255322102 | 2.27 |  |  |  | 2.27
TEVIS 2103 | 255322103 | 3.28 |  |  |  | 3.28
TEVIS 2104 | 255322104 | 18.2 |  |  |  | 18.2
TEVIS 2105 | 255322105 | 1.97 |  |  |  | 1.97
TEXACO EMIDIO 1101 | 255421101 | 0.02 |  |  |  | 0.02
TIDEWATER 2104 | 14652104 | 26 |  |  |  | 26
TIDEWATER 2105 | 14652105 | 14.06 |  |  |  | 14.06
TIDEWATER 2106 | 14652106 | 35.95 |  | 3.68 |  | 32.27
TIDEWATER 2107 | 14652107 | 21.72 |  |  |  | 21.72
TIDEWATER 2108 | 14652108 | 9.6 |  |  |  | 9.6
TIDEWATER 2109 | 14652109 | 30.53 |  |  |  | 30.53
TIDEWATER 2110 | 14652110 | 10.17 |  |  |  | 10.17
TIGER CREEK 0201 | 161380201 | 3.77 | 1.73 | 2.04 |  | 0
TIVY VALLEY 1106 | 252941106 | 26.82 |  |  |  | 26.82
TIVY VALLEY 1107 | 252941107 | 174.29 |  | 116.36 |  | 57.93
TOCALOMA 0241 | 43150241 | 0.05 |  | 0.05 |  | 0
TOKAY 1101 | 168881101 | 12.31 |  |  |  | 12.31
TRACY 0402 | 162880402 | 2.91 |  |  |  | 2.91
TRACY 0405 | 162880405 | 3.24 |  |  |  | 3.24
TRACY 1102 | 162881102 | 27.77 |  |  |  | 27.77
TRACY 1103 | 162881103 | 4.42 |  |  |  | 4.42
TRACY 1104 | 162881104 | 4.73 |  |  |  | 4.73
TRACY 1105 | 162881105 | 4.74 |  |  |  | 4.74
TRACY 1106 | 162881106 | 36.57 |  |  |  | 36.57
TRACY 1107 | 162881107 | 6.14 |  |  |  | 6.14
TRACY 1109 | 162881109 | 5.11 |  |  |  | 5.11
TRACY 1110 | 162881110 | 9.14 |  |  |  | 9.14
TRACY 1111 | 162881111 | 7.23 |  |  |  | 7.23
TRACY 1112 | 162881112 | 4.69 |  |  |  | 4.69
TRES PINOS 1111 | 183221111 | 32.91 |  | 0.11 |  | 32.8
TRES VIAS 1101 | 103251101 | 68.6 |  |  |  | 68.6
TRIDAM POWERHOUSE 2101 | 168152101 | 0.05 | 0.05 |  |  | 0
TRIMBLE 1103 | 83801103 | 2.73 |  |  |  | 2.73
TRIMBLE 1104 | 83801104 | 0.41 |  |  |  | 0.41
TRIMBLE 1105 | 83801105 | 1.44 |  |  |  | 1.44
TRIMBLE 1106 | 83801106 | 0.65 |  |  |  | 0.65
TRIMBLE 1107 | 83801107 | 1.05 |  |  |  | 1.05
TRIMBLE 1110 | 83801110 | 0.34 |  |  |  | 0.34
TRIMBLE 2114 | 83802114 | 0 |  |  |  | 0
TRIMBLE 2115 | 83802115 | 0.31 |  |  |  | 0.31
TRIMBLE 2116 | 83802116 | 3.38 |  |  |  | 3.38
TRIMBLE 2118 | 83802118 | 0.39 |  |  |  | 0.39
TRINIDAD 1101 | 192231101 | 26.53 |  |  |  | 26.53
TRINIDAD 1102 | 192231102 | 24.19 |  |  | 0.25 | 23.94
TUDOR 1101 | 153711101 | 31.73 |  |  |  | 31.73
TUDOR 1102 | 153711102 | 23.15 |  |  |  | 23.15
TULARE LAKE 1104 | 252951104 | 14.58 |  |  |  | 14.58
TULARE LAKE 1106 | 252951106 | 52.18 |  |  |  | 52.18
TULARE LAKE 1108 | 252951108 | 48.76 |  |  |  | 48.76
TULE POWER HOUSE 1101 | 258591101 | 4.07 |  | 4.07 |  | 0
TULUCAY 1101 | 42301101 | 19.94 |  | 3.77 |  | 16.17
TUPMAN 1103 | 254561103 | 45.02 |  |  |  | 45.02
TUPMAN 1104 | 254561104 | 53.33 |  |  |  | 53.33
TUPMAN 1105 | 254561105 | 17.69 |  |  |  | 17.69
TUPMAN 1106 | 254561106 | 36.62 |  |  |  | 36.62
TWISSELMAN 1101 | 254401101 | 0.02 |  |  |  | 0.02
TWISSELMAN 1102 | 254401102 | 49.23 |  |  |  | 49.23
TWISSELMAN 1104 | 254401104 | 0.02 |  |  |  | 0.02
TWISSELMAN 2105 | 254402105 | 88.97 |  |  |  | 88.97
TYLER 1103 | 103571103 | 6.41 |  |  |  | 6.41
TYLER 1104 | 103571104 | 25.49 |  |  |  | 25.49
TYLER 1105 | 103571105 | 111.8 |  | 60.18 |  | 51.62
UKIAH 1111 | 42771111 | 32 |  | 7.84 |  | 24.16
UKIAH 1113 | 42771113 | 15.84 |  | 7.5 |  | 8.34
UKIAH 1114 | 42771114 | 103.63 |  | 53.83 |  | 49.8
UKIAH 1115 | 42771115 | 50.62 |  | 35.13 |  | 15.49
UPPER LAKE 1101 | 42871101 | 79.83 | 1.44 | 41.6 |  | 36.79
VACA DIXON 1101 | 63591101 | 50.46 |  | 22.5 |  | 27.96
VACA DIXON 1102 | 63591102 | 1.96 |  |  |  | 1.96
VACA DIXON 1103 | 63591103 | 126.78 |  |  |  | 126.78
VACA DIXON 1104 | 63591104 | 7.49 |  |  |  | 7.49
VACA DIXON 1105 | 63591105 | 49.72 |  | 1.4 |  | 48.32
VACA DIXON 1106 | 63591106 | 11.11 |  |  |  | 11.11
VACA DIXON 1109 | 63591109 | 2.13 |  |  |  | 2.13
VACAVILLE 1102 | 63601102 | 1 |  |  |  | 1
VACAVILLE 1103 | 63601103 | 11.13 |  |  |  | 11.13
VACAVILLE 1104 | 63601104 | 15.09 |  | 12.86 |  | 2.23
VACAVILLE 1105 | 63601105 | 2.87 |  |  |  | 2.87
VACAVILLE 1106 | 63601106 | 1.76 |  |  |  | 1.76
VACAVILLE 1107 | 63601107 | 1.91 |  |  |  | 1.91
VACAVILLE 1108 | 63601108 | 51.98 |  | 29.74 |  | 22.24
VACAVILLE 1109 | 63601109 | 5.64 |  | 0.81 |  | 4.83
VACAVILLE 1110 | 63601110 | 2.36 |  |  |  | 2.36
VACAVILLE 1111 | 63601111 | 13.03 |  | 10.12 |  | 2.91
VACAVILLE 1112 | 63601112 | 3.33 |  | 0.19 |  | 3.14
VALLEJO B 0411 | 42450411 | 7.07 |  |  |  | 7.07
VALLEJO B 0413 | 42450413 | 6.46 |  |  |  | 6.46
VALLEJO B 0414 | 42450414 | 8.29 |  |  |  | 8.29
VALLEJO B 0415 | 42450415 | 7.61 |  |  |  | 7.61
VALLEJO B 1101 | 42451101 | 16.3 |  |  |  | 16.3
VALLEJO B 1102 | 42451102 | 2.49 |  |  |  | 2.49
VALLEJO C 0401 | 42550401 | 2.8 |  |  |  | 2.8
VALLEY HOME 1702 | 162981702 | 56.27 |  |  |  | 56.27
VALLEY HOME 1703 | 162981703 | 127.51 |  |  |  | 127.51
VALLEY HOME 1704 | 162981704 | 39.28 |  |  |  | 39.28
VALLEY VIEW 1103 | 14341103 | 18.13 | 0.59 |  |  | 17.54
VALLEY VIEW 1105 | 14341105 | 14.15 |  | 3.98 |  | 10.17
VALLEY VIEW 1106 | 14341106 | 21.32 | 1.97 | 6.78 |  | 12.57
VASCO 1101 | 13751101 | 2.56 |  |  |  | 2.56
VASCO 1102 | 13751102 | 88.13 |  | 45.63 |  | 42.5
VASCO 1103 | 13751103 | 14.67 |  |  |  | 14.67
VASONA 1101 | 83771101 | 9.94 |  |  |  | 9.94
VASONA 1102 | 83771102 | 15.36 |  | 0.12 |  | 15.24
VASONA 1103 | 83771103 | 15.52 |  |  |  | 15.52
VASONA 1104 | 83771104 | 3.73 |  |  |  | 3.73
VASONA 1105 | 83771105 | 11.62 |  |  |  | 11.62
VASONA 1108 | 83771108 | 10.93 |  |  |  | 10.93
VICTOR 1101 | 163281101 | 18.26 |  |  |  | 18.26
VICTOR 1102 | 163281102 | 87.15 |  |  |  | 87.15
VIEJO 2201 | 182852201 | 17.32 |  | 14.59 |  | 2.73
VIEJO 2202 | 182852202 | 46.34 |  | 14.57 |  | 31.77
VIEJO 2203 | 182852203 | 22.78 |  | 3.04 |  | 19.74
VIEJO 2204 | 182852204 | 24.57 |  | 4.39 |  | 20.18
VIERRA 1701 | 162701701 | 9.72 |  |  |  | 9.72
VIERRA 1702 | 162701702 | 6.9 |  |  |  | 6.9
VIERRA 1703 | 162701703 | 5.61 |  |  |  | 5.61
VIERRA 1706 | 162701706 | 6.88 |  |  |  | 6.88
VIERRA 1707 | 162701707 | 48.43 |  |  |  | 48.43
VINA 1101 | 103581101 | 56.34 |  |  |  | 56.34
VINEYARD 2104 | 14502104 | 3.86 |  |  |  | 3.86
VINEYARD 2105 | 14502105 | 3.93 |  |  |  | 3.93
VINEYARD 2106 | 14502106 | 5.5 |  |  |  | 5.5
VINEYARD 2107 | 14502107 | 13.89 |  | 3 |  | 10.89
VINEYARD 2108 | 14502108 | 13.41 | 5.17 |  |  | 8.24
VINEYARD 2109 | 14502109 | 4.72 |  |  |  | 4.72
VINEYARD 2110 | 14502110 | 11.21 |  | 5.91 |  | 5.3
VIRGINIA 0401 | 13780401 | 4.02 |  |  |  | 4.02
VOLTA 1101 | 102541101 | 149.13 | 6.23 | 140.75 |  | 2.15
VOLTA 1102 | 102541102 | 129.61 | 86.85 | 41.93 |  | 0.83
Valley Springs 1101 | 168891101 | 2.14 |  |  |  | 2.14
WAHTOKE 1106 | 254531106 | 13.92 |  |  |  | 13.92
WAHTOKE 1107 | 254531107 | 19.14 |  |  |  | 19.14
WAHTOKE 1108 | 254531108 | 108.42 |  |  |  | 108.42
WAHTOKE 1109 | 254531109 | 6.95 |  |  |  | 6.95
WAHTOKE 1110 | 254531110 | 16.19 |  |  |  | 16.19
WAHTOKE 1111 | 254531111 | 29.93 |  |  |  | 29.93
WALDO 0401 | 13350401 | 5.7 |  | 1.6 |  | 4.1
WALDO 0402 | 13350402 | 5.17 |  | 2.97 |  | 2.2
WALL 0401 | 13740401 | 5.38 |  |  |  | 5.38
WALNUT CREEK 0403 | 12200403 | 0.51 |  |  |  | 0.51
WALNUT CREEK 0404 | 12200404 | 6.44 |  |  |  | 6.44
WARD 0401 | 12980401 | 4.52 |  |  |  | 4.52
WASCO 1101 | 252961101 | 12.15 |  |  |  | 12.15
WASCO 1102 | 252961102 | 7.71 |  |  |  | 7.71
WASCO 1104 | 252961104 | 9.94 |  |  |  | 9.94
WATERLOO 1101 | 163151101 | 58 |  |  |  | 58
WATERLOO 1102 | 163151102 | 21.72 |  |  |  | 21.72
WATERSHED 0402 | 24240402 | 1.19 | 0.02 |  |  | 1.17
WATSONVILLE 0411 | 83330411 | 2.31 |  |  |  | 2.31
WATSONVILLE 0413 | 83330413 | 1.22 |  |  |  | 1.22
WATSONVILLE 0414 | 83330414 | 1.28 |  |  |  | 1.28
WATSONVILLE 2101 | 83332101 | 102.59 |  |  |  | 102.59
WEBER 1101 | 163481101 | 3.23 |  |  |  | 3.23
WEBER 1102 | 163481102 | 31.75 |  |  |  | 31.75
WEBER 1103 | 163481103 | 1.8 |  |  |  | 1.8
WEBER 1105 | 163481105 | 20.89 |  |  |  | 20.89
WEBER 1107 | 163481107 | 0.04 |  |  |  | 0.04
WEBER 1108 | 163481108 | 0.44 |  |  |  | 0.44
WEBER 1109 | 163481109 | 53.12 |  |  |  | 53.12
WEBER 1110 | 163481110 | 12.68 |  |  |  | 12.68
WEBER 1111 | 163481111 | 19.87 |  |  |  | 19.87
WEBER 1112 | 163481112 | 0.03 |  |  |  | 0.03
WEBER 1113 | 163481113 | 2.12 |  |  |  | 2.12
WEBER 1114 | 163481114 | 9.8 |  |  |  | 9.8
WEBER 1115 | 163481115 | 14.66 |  |  |  | 14.66
WEEDPATCH 1101 | 252971101 | 20.32 |  |  |  | 20.32
WEEDPATCH 1102 | 252971102 | 18.17 |  |  |  | 18.17
WEEDPATCH 1103 | 252971103 | 18.05 |  |  |  | 18.05
WEEDPATCH 1105 | 252971105 | 0.96 |  |  |  | 0.96
WEEDPATCH 1106 | 252971106 | 64.45 |  |  |  | 64.45
WEIMAR 1101 | 152491101 | 78.71 |  | 78.71 |  | 0
WEIMAR 1102 | 152491102 | 36.6 |  | 36.6 |  | 0
WELLFIELD 1102 | 254291102 | 37.87 |  |  |  | 37.87
WELLFIELD 1103 | 254291103 | 0.32 |  |  |  | 0.32
WELLFIELD 1104 | 254291104 | 5.27 |  |  |  | 5.27
WEST FRESNO 1101 | 253731101 | 16 |  |  |  | 16
WEST FRESNO 1102 | 253731102 | 4.16 |  |  |  | 4.16
WEST FRESNO 1103 | 253731103 | 5.9 |  |  |  | 5.9
WEST FRESNO 1104 | 253731104 | 16.63 |  |  |  | 16.63
WEST FRESNO 1105 | 253731105 | 6.02 |  |  |  | 6.02
WEST FRESNO 1106 | 253731106 | 5.92 |  |  |  | 5.92
WEST FRESNO 1107 | 253731107 | 4.32 |  |  |  | 4.32
WEST FRESNO 1108 | 253731108 | 2.48 |  |  |  | 2.48
WEST FRESNO 1109 | 253731109 | 20.28 |  |  |  | 20.28
WEST FRESNO 1110 | 253731110 | 5.25 |  |  |  | 5.25
WEST FRESNO 1111 | 253731111 | 27.95 |  |  |  | 27.95
WEST FRESNO 1112 | 253731112 | 29.37 |  |  |  | 29.37
WEST LANE 1101 | 163621101 | 10.01 |  |  |  | 10.01
WEST LANE 1102 | 163621102 | 14.57 |  |  |  | 14.57
WEST LANE 1103 | 163621103 | 4.91 |  |  |  | 4.91
WEST POINT 1101 | 163201101 | 63.13 | 63.09 | 0.04 |  | 0
WEST POINT 1102 | 163201102 | 252.39 | 184.3 | 67.58 |  | 0.51
WEST SACRAMENTO 1104 | 63131104 | 11.92 |  |  |  | 11.92
WEST SACRAMENTO 1105 | 63131105 | 6.31 |  |  |  | 6.31
WEST SACRAMENTO 1106 | 63131106 | 2.85 |  |  |  | 2.85
WEST SACRAMENTO 1107 | 63131107 | 18.71 |  |  |  | 18.71
WEST SACRAMENTO 1108 | 63131108 | 8.73 |  |  |  | 8.73
WEST SACRAMENTO 1109 | 63131109 | 39.04 |  |  |  | 39.04
WEST SACRAMENTO 1110 | 63131110 | 8.4 |  |  |  | 8.4
WEST SACRAMENTO 1111 | 63131111 | 0.01 |  |  |  | 0.01
WESTLAKE 0401 | 22600401 | 0.81 |  |  |  | 0.81
WESTLAKE 0403 | 22600403 | 1.76 |  |  |  | 1.76
WESTLEY 1101 | 162671101 | 86.69 |  |  |  | 86.69
WESTLEY 1102 | 162671102 | 0.07 |  |  |  | 0.07
WESTLEY 1103 | 162671103 | 95.97 |  | 0.43 |  | 95.54
WESTPARK 1101 | 253701101 | 11.34 |  |  |  | 11.34
WESTPARK 1102 | 253701102 | 3.75 |  |  |  | 3.75
WESTPARK 1103 | 253701103 | 16.92 |  |  |  | 16.92
WESTPARK 1104 | 253701104 | 10.4 |  |  |  | 10.4
WESTPARK 1105 | 253701105 | 2.29 |  |  |  | 2.29
WESTPARK 1106 | 253701106 | 2.76 |  |  |  | 2.76
WESTPARK 1107 | 253701107 | 5.37 |  |  |  | 5.37
WESTPARK 1108 | 253701108 | 19.8 |  |  |  | 19.8
WESTPARK 1109 | 253701109 | 9.84 |  |  |  | 9.84
WESTPARK 1110 | 253701110 | 12.99 |  |  |  | 12.99
WESTPARK 1111 | 253701111 | 5.22 |  |  |  | 5.22
WESTPARK 1112 | 253701112 | 6.91 |  |  |  | 6.91
WHEATLAND 1101 | 152811101 | 0 |  |  |  | 0
WHEATLAND 1102 | 152811102 | 30.05 |  |  |  | 30.05
WHEATLAND 1104 | 152811104 | 113.44 |  |  |  | 113.44
WHEATLAND 1105 | 152811105 | 74.76 |  | 10.65 |  | 64.11
WHEELER RIDGE 1101 | 253481101 | 73.76 |  |  |  | 73.76
WHEELER RIDGE 1102 | 253481102 | 34.37 |  |  |  | 34.37
WHEELER RIDGE 1103 | 253481103 | 38.83 |  |  |  | 38.83
WHISMAN 1101 | 83631101 | 5.09 |  |  |  | 5.09
WHISMAN 1102 | 83631102 | 1.76 |  |  |  | 1.76
WHISMAN 1103 | 83631103 | 2.67 |  |  |  | 2.67
WHISMAN 1104 | 83631104 | 0 |  |  |  | 0
WHISMAN 1105 | 83631105 | 0.96 |  |  |  | 0.96
WHISMAN 1106 | 83631106 | 7.12 |  |  |  | 7.12
WHISMAN 1107 | 83631107 | 0.13 |  |  |  | 0.13
WHISMAN 1108 | 83631108 | 7.33 |  |  |  | 7.33
WHISMAN 1110 | 83631110 | 1.99 |  |  |  | 1.99
WHISMAN 1111 | 83631111 | 2.2 |  |  |  | 2.2
WHITMORE 1101 | 103601101 | 90.96 | 31.87 | 59.09 |  | 0
WHITNEY 0402 | 13240402 | 1.85 |  |  |  | 1.85
WILDWOOD 1101 | 103611101 | 32.18 |  | 32.18 |  | 0
WILKINS SLOUGH 1101 | 62771101 | 52.44 |  |  |  | 52.44
WILKINS SLOUGH 1102 | 62771102 | 62.19 |  |  |  | 62.19
WILKINS SLOUGH 1103 | 62771103 | 34.46 |  |  |  | 34.46
WILLIAMS 1101 | 62051101 | 32.67 |  |  |  | 32.67
WILLIAMS 1102 | 62051102 | 98.73 |  |  |  | 98.73
WILLITS 1102 | 42661102 | 11.27 |  | 4.79 |  | 6.48
WILLITS 1103 | 42661103 | 154.71 | 49.97 | 91.44 |  | 13.3
WILLITS 1104 | 42661104 | 96.02 | 50.93 | 36.44 |  | 8.65
WILLOW CREEK 1101 | 192171101 | 56.6 | 25.95 | 20.11 |  | 10.54
WILLOW CREEK 1102 | 192171102 | 9.56 | 5.31 | 4.25 |  | 0
WILLOW CREEK 1103 | 192171103 | 76.19 | 0.54 | 74.5 |  | 1.15
WILLOW PASS 1101 | 13911101 | 7.07 |  | 1.12 |  | 5.95
WILLOW PASS 1102 | 13911102 | 5.1 |  |  |  | 5.1
WILLOW PASS 2107 | 13912107 | 3.08 |  | 0.66 |  | 2.42
WILLOW PASS 2108 | 13912108 | 21.22 |  | 0.23 |  | 20.99
WILLOWS A 1101 | 102741101 | 4.28 |  |  |  | 4.28
WILLOWS A 1103 | 102741103 | 9.85 |  |  |  | 9.85
WILLOWS A 1104 | 102741104 | 9.39 |  |  |  | 9.39
WILSON 1101 | 254301101 | 16.5 |  |  |  | 16.5
WILSON 1102 | 254301102 | 30.38 |  |  |  | 30.38
WILSON 1103 | 254301103 | 115.45 |  |  |  | 115.45
WINDSOR 1101 | 43501101 | 6.4 |  |  |  | 6.4
WINDSOR 1102 | 43501102 | 14.67 |  |  |  | 14.67
WINDSOR 1103 | 43501103 | 11.24 |  | 1.98 |  | 9.26
WINTERS 1101 | 63321101 | 12.9 |  |  |  | 12.9
WINTERS 1102 | 63321102 | 35.49 |  |  |  | 35.49
WISE 1101 | 152271101 | 13.61 |  | 5.77 |  | 7.84
WISE 1102 | 152271102 | 119.01 |  | 114.01 |  | 5
WISHON 1101 | 251511101 | 7.59 | 3.48 | 4.12 |  | -0.01
WOLFE 1104 | 83671104 | 6.79 |  |  |  | 6.79
WOLFE 1105 | 83671105 | 7.29 |  |  |  | 7.29
WOLFE 1106 | 83671106 | 9.13 |  |  |  | 9.13
WOLFE 1107 | 83671107 | 10.63 |  |  |  | 10.63
WOLFE 1109 | 83671109 | 8.89 |  |  |  | 8.89
WOLFE 1110 | 83671110 | 2.02 |  |  |  | 2.02
WOLFE 1113 | 83671113 | 17.29 |  |  |  | 17.29
WOLFE 1114 | 83671114 | 2.92 |  |  |  | 2.92
WOOD 0401 | 13380401 | 3.32 |  | 0.17 |  | 3.15
WOODACRE 1101 | 43021101 | 38.41 | 22.83 | 7.8 |  | 7.78
WOODACRE 1102 | 43021102 | 31.02 | 19.29 | 11.36 |  | 0.37
WOODLAND 1101 | 62031101 | 7.2 |  |  |  | 7.2
WOODLAND 1102 | 62031102 | 13.5 |  |  |  | 13.5
WOODLAND 1103 | 62031103 | 1.23 |  |  |  | 1.23
WOODLAND 1104 | 62031104 | 5.86 |  |  |  | 5.86
WOODLAND 1105 | 62031105 | 2.7 |  |  |  | 2.7
WOODLAND 1106 | 62031106 | 28.09 |  |  |  | 28.09
WOODLAND 1107 | 62031107 | 11.16 |  |  |  | 11.16
WOODLAND 1108 | 62031108 | 21.22 |  |  |  | 21.22
WOODLAND 1109 | 62031109 | 10.68 |  |  |  | 10.68
WOODLAND 1110 | 62031110 | 10.9 |  |  |  | 10.9
WOODLAND 1111 | 62031111 | 0.25 |  |  |  | 0.25
WOODLAND 1112 | 62031112 | 12.85 |  |  |  | 12.85
WOODLAND 1113 | 62031113 | 20.88 |  |  |  | 20.88
WOODSIDE 1101 | 24251101 | 61.87 | 42.65 | 0.49 |  | 18.73
WOODSIDE 1102 | 24251102 | 17.02 |  | 0.06 |  | 16.96
WOODSIDE 1104 | 24251104 | 44.13 | 7.16 | 13 |  | 23.97
WOODSIDE 1105 | 24251105 | 6.33 |  |  |  | 6.33
WOODWARD 2101 | 255292101 | 25.84 |  |  |  | 25.84
WOODWARD 2102 | 255292102 | 1.47 |  |  |  | 1.47
WOODWARD 2104 | 255292104 | 2.76 |  |  |  | 2.76
WOODWARD 2105 | 255292105 | 0.36 |  |  |  | 0.36
WOODWARD 2106 | 255292106 | 0.29 |  |  |  | 0.29
WOODWARD 2107 | 255292107 | 9.48 |  |  |  | 9.48
WOODWARD 2108 | 255292108 | 92.13 |  | 18.51 |  | 73.62
WOODWARD 2109 | 255292109 | 1.83 |  |  |  | 1.83
WRIGHT 1110 | 254641110 | 87.64 |  |  |  | 87.64
WYANDOTTE 1102 | 102911102 | 39.19 |  | 4.33 |  | 34.86
WYANDOTTE 1103 | 102911103 | 67.04 | 38.68 | 15.28 |  | 13.08
WYANDOTTE 1105 | 102911105 | 25.68 | 0.68 | 16.11 |  | 8.89
WYANDOTTE 1106 | 102911106 | 94.31 |  | 0.55 |  | 93.76
WYANDOTTE 1107 | 102911107 | 154.94 | 9.92 | 101.39 |  | 43.63
WYANDOTTE 1109 | 102911109 | 117.8 |  | 52.17 |  | 65.63
WYANDOTTE 1110 | 102911110 | 39.32 |  | 12.63 |  | 26.69
YOSEMITE 0401 | 22490401 | 3.55 |  |  |  | 3.55
YOSEMITE 0402 | 22490402 | 2.4 |  |  |  | 2.4
YOSEMITE 0403 | 22490403 | 0 |  |  |  | 0
ZACA 1101 | 182681101 | 26.18 | 1.3 | 16.63 |  | 8.25
ZACA 1102 | 182681102 | 80.28 | 22.35 | 40.6 |  | 17.33
ZAMORA 1105 | 63191105 | 45.61 |  |  |  | 45.61
ZAMORA 1106 | 63191106 | 52.81 |  |  |  | 52.81
ZAMORA 1107 | 63191107 | 76.92 |  |  |  | 76.92
|  |  | 6926.27 | 18133.67
25059.94