http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0021743&numberofmonths=24&showchangehistorylog=1 | 17-0021743 | SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 6927 | 20170216 | 1524 | 1690608 | 515 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 515 | 38.5975 | -122.9982 | 8810MILLCREEKRD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0021743 | OH | Sus | 42950216 | yes | 2017 | FEB | Yes | Line to Ground | 1258860 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023494&numberofmonths=24&showchangehistorylog=1 | 17-0023494 | SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE | 59153 | 20170219 | 1619 | 1701859 | 1161 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 5805 | 38.5424 | -123.2899 | 1PLDSIDEOF59153 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0023494 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1260480 | CSO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0023569&numberofmonths=24&showchangehistorylog=1 | 17-0023569 | SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER | 560 | 20170219 | 1927 | 1702027 | 1268 | Distribution Circuit | Vegetation | Tree - branch fell on line | 31 | 39308 | 38.5562 | -123.3034 | MM4286HWY1FISKMILLCOVEXSTKRUSERANCHRDAND9SPANSSOFMM4286 | Strong Winds-Rain-Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023569 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Multi-Fault | 1260560 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0027175&numberofmonths=24&showchangehistorylog=1 | 17-0027175 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1101 | 42091101 | SWITCH | 1007 | 20170227 | 2036 | 1715610 | 310 | Distribution Circuit | Equipment Failure/Involved | Overhead | 114 | 33180 | 38.4859 | -122.9621 | 5SPANSFROM12683TWD202 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0027175 | OH | Sus | 0 | No | 2017 | FEB | Yes | Line to Ground | 1263799 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0027156&numberofmonths=24&showchangehistorylog=1 | 17-0027156 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | RECLOSER | 3970 | 20170227 | 1719 | 1715476 | 279 | Distribution Circuit | Vegetation | Tree - fell into line | 2573 | 251745 | 38.4997 | -123.0054 | 15999RIVERRDGURNEVILLE1SPANLDOF524 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0027156 | OH | Sus | 42954995 | No | 2017 | FEB | Yes | Three Phase Fault | 1263785 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0027279&numberofmonths=24&showchangehistorylog=1 | 17-0027279 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 1043 | 20170228 | 807 | 1715857 | 366 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 732 | 38.5068 | -122.915 | 1SPANLOADSIDEOF1043 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0027279 | OH | Sus | 31308166 | No | 2017 | FEB | Yes | Line to Ground | 1263905 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0028788&numberofmonths=24&showchangehistorylog=1 | 17-0028788 | SONOMA | FIELD OPS NORTH | Tier 2 | CLOVERDALE-1102 | 42821102 | FUSE | 17149 | 20170306 | 1058 | 1720987 | 315 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 9135 | 38.7853 | -123.0227 | 1POLELDSIDEOFFUCO17149 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0028788 | OH | Sus | 42959645 | yes | 2017 | MAR | Yes | Line to Ground | 1265083 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0029563&numberofmonths=24&showchangehistorylog=1 | 17-0029563 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 17225 | 20170309 | 211 | 1722972 | 685 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 24660 | 38.5094 | -122.9225 | 10661RIVERDR | Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0029563 | OH | Sus | 0 | No | 2017 | MAR | Yes | Line to Line | 1265657 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0033347&numberofmonths=24&showchangehistorylog=1 | 17-0033347 | SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1101 | 42571101 | FUSE | 1761 | 20170324 | 712 | 1734352 | 507 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 16525 | 38.3789 | -122.8977 | MTR1004759381 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0033347 | OH | Sus | 42976279 | yes | 2017 | MAR | Yes | Line to Ground | 1268421 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0034498&numberofmonths=24&showchangehistorylog=1 | 17-0034498 | SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | FUSE | 5799 | 20170328 | 1339 | 1737644 | 386 | Distribution Circuit | Vegetation | Tree - branch fell on line | 41 | 15826 | 38.519 | -122.601 | MTR128545 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0034498 | OH | Sus | 42978867 | yes | 2017 | MAR | Yes | Line to Ground | 1269301 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0035085&numberofmonths=24&showchangehistorylog=1 | 17-0035085 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | FUSE | 4673 | 20170330 | 1239 | 1739267 | 123 | Distribution Circuit | Vegetation | Tree - branch fell on line | 22 | 2706 | 38.284 | -122.7332 | 1SPANLDSIDEOF4673 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0035085 | OH | Sus | 42980372 | yes | 2017 | MAR | Yes | Line to Ground | 1269782 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0035109&numberofmonths=24&showchangehistorylog=1 | 17-0035109 | SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 6751 | 20170330 | 1157 | 1739360 | 868 | Distribution Circuit | Vegetation | Tree - fell into line | 134 | 111461 | 38.592 | -122.9622 | 7505MILLCREEK | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0035109 | OH | Sus | 0 | yes | 2017 | MAR | Yes | Line to Ground | 1269800 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0035122&numberofmonths=24&showchangehistorylog=1 | 17-0035122 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 6591 | 20170330 | 1254 | 1739454 | 308 | Distribution Circuit | Vegetation | Tree - branch fell on line | 79 | 24332 | 38.5235 | -122.9786 | 17137MTJACKSONTRAIL | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0035122 | OH | Sus | 0 | yes | 2017 | MAR | Yes | Line to Ground | 1269803 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0035171&numberofmonths=24&showchangehistorylog=1 | 17-0035171 | SONOMA | FIELD OPS NORTH | Tier 2 | RINCON-1104 | 43321104 | OCB | 11042 | 20170330 | 1514 | 1739694 | 606 | Distribution Circuit | Vegetation | Tree - fell into line | 4004 | 245566 | 38.4901 | -122.6661 | MooreDave36121755BRUSHCREEKRD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0035171 | OH | Sus | 0 | yes | 2017 | MAR | Yes | Line to Ground | 1269822 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0035647&numberofmonths=24&showchangehistorylog=1 | 17-0035647 | SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | FUSE | 6113 | 20170331 | 1422 | 1741480 | 602 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 17978 | 38.5381 | -122.6468 | 1SPANLDSIDEOF6121TAP | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0035647 | OH | Sus | 0 | yes | 2017 | MAR | Yes | Line to Line | 1270198 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0036218&numberofmonths=24&showchangehistorylog=1 | 17-0036218 | SONOMA | FIELD OPS NORTH | Tier 3 | FULTON-1107 | 42561107 | OTHER | WIREDOWN1SPANSOURCESIDEOF14555 | 20170403 | 1815 | 1743304 | 557 | Distribution Circuit | Vegetation | Tree - fell into line | 298 | 73252 | 38.5438 | -122.7205 | MAINLINEATFUCO14555 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0036218 | OH | Sus | 42983131 | No | 2017 | APR | Yes | Line to Ground | 1270706 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0038349&numberofmonths=24&showchangehistorylog=1 | 17-0038349 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | FUSE | 3183 | 20170408 | 1853 | 1753122 | 1107 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 3321 | 38.2422 | -122.8992 | 8SPANSLDSIDEOFFUCO3183 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0038349 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1272401 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0038351&numberofmonths=24&showchangehistorylog=1 | 17-0038351 | SONOMA | FIELD OPS NORTH | Tier 2 | MIRABEL-1101 | 42091101 | FUSE | 6485 | 20170408 | 1709 | 1753022 | 1091 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 8728 | 38.4668 | -122.9087 | MTR1009076873 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0038351 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Line | 1272403 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0039381&numberofmonths=24&showchangehistorylog=1 | 17-0039381 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 6233 | 20170412 | 133 | 1755775 | 512 | Distribution Circuit | Environmental/External | Flood/Erosion | 13 | 6656 | 38.4471 | -122.9241 | 2SLDSOF6233 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0039381 | OH | Sus | 31318985 | No | 2017 | APR | Yes | Line to Ground | 1273272 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0040393&numberofmonths=24&showchangehistorylog=1 | 17-0040393 | SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER | 560 | 20170414 | 1323 | 1757999 | 832 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 25792 | 38.5562 | -123.3034 | 3SPANSLOADSIDEOF560 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0040393 | OH | Sus | 42995143 | No | 2017 | APR | Yes | Multi-Fault | 1273905 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0041059&numberofmonths=24&showchangehistorylog=1 | 17-0041059 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 2373 | 20170418 | 650 | 1759946 | 820 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 4920 | 38.5096 | -122.9609 | KOTULAJON4343UPMCPEAKBEHINDKORBEL | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0041059 | OH | Sus | 31320218 | yes | 2017 | APR | Yes | Force Out | 1274469 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0041600&numberofmonths=24&showchangehistorylog=1 | 17-0041600 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 6685 | 20170420 | 811 | 1761570 | 647 | Distribution Circuit | Vegetation | Tree - fell into line | 115 | 44141 | 38.5237 | -122.9788 | 15372WILLOWRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0041600 | OH | Sus | 0 | No | 2017 | APR | Yes | Line to Ground | 1274854 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0042300&numberofmonths=24&showchangehistorylog=1 | 17-0042300 | SONOMA | FIELD OPS NORTH | Tier 3 | FORT ROSS-1121 | 42851121 | JUMPER | WIREDOWNHOT | 20170424 | 607 | 1765729 | 659 | Distribution Circuit | Vegetation | Tree - fell into line | 454 | 59061 | 38.5381 | -123.1197 | 1SSOFMTR1007687696 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0042300 | OH | Sus | 31321154 | No | 2017 | APR | Yes | Line to Line | 1275447 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0043912&numberofmonths=24&showchangehistorylog=1 | 17-0043912 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 8057 | 20170429 | 1504 | 1770500 | 406 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 406 | 38.496 | -122.9377 | ALVAREZR38858720MARTINELLIRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0043912 | OH | Sus | 43003699 | No | 2017 | APR | Yes | Line to Line | 1276533 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0044665&numberofmonths=24&showchangehistorylog=1 | 17-0044665 | SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | RECLOSER | 246 | 20170502 | 1715 | 1772714 | 253 | Distribution Circuit | Vegetation | Tree - fell into line | 549 | 92609 | 38.3657 | -122.5275 | ONMAINLINEFEEDINGTRIPSAVER1249 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0044665 | OH | Sus | 43005967 | yes | 2017 | MAY | Yes | Three Phase Fault | 1277072 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0045743&numberofmonths=24&showchangehistorylog=1 | 17-0045743 | SONOMA | FIELD OPS NORTH | Tier 2 | CLOVERDALE-1102 | 42821102 | RECLOSER | 262 | 20170506 | 527 | 1775994 | 655 | Distribution Circuit | Vegetation | Tree - branch fell on line | 363 | 61793 | 38.7977 | -122.991 | ONMAINLINE76875 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0045743 | OH | Sus | 31324252 | yes | 2017 | MAY | Yes | Line to Ground | 1277857 | CAW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0047463&numberofmonths=24&showchangehistorylog=1 | 17-0047463 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE | 15383 | 20170512 | 735 | 1780538 | 335 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 7370 | 38.4483 | -123.0005 | 1SPANLDSIDEOF153838231TYRONE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0047463 | OH | Sus | 31325426 | No | 2017 | MAY | Yes | Line to Line | 1279196 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0048665&numberofmonths=24&showchangehistorylog=1 | 17-0048665 | SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1109 | 42631109 | RECLOSER | 128 | 20170517 | 1710 | 1784315 | 381 | Distribution Circuit | Vegetation | Tree - fell into line | 229 | 28077 | 38.2201 | -122.6439 | 2SLOADSIDEOF2623ONMAINLINE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0048665 | OH | Sus | 43018994 | No | 2017 | MAY | Yes | Line to Ground | 1280150 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0050433&numberofmonths=24&showchangehistorylog=1 | 17-0050433 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | JUMPER | OJSMTR1009997686 | 20170524 | 1430 | 1789737 | 470 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 470 | 38.1963 | -122.8855 | METER1009997686ENDOFCLARKRD | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on object | 17-0050433 | OH | Sus | 43022604 | No | 2017 | MAY | Yes | None | 1281379 | CSO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0050815&numberofmonths=24&showchangehistorylog=1 | 17-0050815 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 10537 | 20170525 | 1655 | 1790693 | 661 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 2644 | 38.3985 | -122.9872 | 1SPANLDSIDEOFFUCO10537 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0050815 | OH | Sus | 43023435 | No | 2017 | MAY | Yes | Line to Ground | 1281629 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0053115&numberofmonths=24&showchangehistorylog=1 | 17-0053115 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1105 | 42271105 | FUSE | 6581 | 20170606 | 1335 | 1798194 | 281 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 1405 | 38.3405 | -122.7526 | 1LDSIDEOFFUCO6581 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0053115 | OH | Sus | 43029377 | No | 2017 | JUN | Yes | Three Phase Fault | 1283395 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0055995&numberofmonths=24&showchangehistorylog=1 | 17-0055995 | SONOMA | FIELD OPS NORTH | Tier 3 | SANTA ROSA A-1104 | 42151104 | FUSE | 3647 | 20170617 | 1953 | 1807221 | 341 | Distribution Circuit | Vegetation | Tree - branch fell on line | 37 | 12198 | 38.4675 | -122.689 | BRANCHFELLAT4070ALTAVISTAAVE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0055995 | OH | Sus | 0 | yes | 2017 | JUN | Yes | Line to Ground | 1285474 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0056943&numberofmonths=24&showchangehistorylog=1 | 17-0056943 | SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1101 | 42571101 | JUMPER | WIREDOWN9850BARNETTVALLEYRD | 20170620 | 906 | 1812274 | 344 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 4872 | 38.3668 | -122.8684 | 9850BARNETTVALLEYRD | Clear-32-90 F | Conductor, Overhead | On Ground | 17-0056943 | OH | Sus | 0 | yes | 2017 | JUN | Yes | Line to Ground | 1286377 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0057838&numberofmonths=24&showchangehistorylog=1 | 17-0057838 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1101 | 42091101 | FUSE | 3355 | 20170622 | 1656 | 1815252 | 601 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 5409 | 38.4761 | -122.9304 | 9000HWY116 | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 17-0057838 | OH | Sus | 0 | yes | 2017 | JUN | Yes | Line to Line | 1287040 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0058441&numberofmonths=24&showchangehistorylog=1 | 17-0058441 | SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1103 | 43071103 | FUSE | 13333 | 20170625 | 1155 | 1817620 | 414 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 4968 | 38.3738 | -122.5176 | Deignan357112850DUNBARRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0058441 | OH | Sus | 43044668 | No | 2017 | JUN | Yes | Line to Line | 1287541 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0059600&numberofmonths=24&showchangehistorylog=1 | 17-0059600 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 429 | 20170629 | 1812 | 1820958 | 477 | Distribution Circuit | Vegetation | Tree - fell into line | 66 | 20601 | 38.4734 | -123.0226 | 21229VILLAGRANDE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0059600 | OH | Sus | 43047266 | No | 2017 | JUN | Yes | Line to Line | 1288410 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0060713&numberofmonths=24&showchangehistorylog=1 | 17-0060713 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | FUSE | 10343 | 20170705 | 1841 | 1824172 | 274 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 274 | 38.2853 | -122.7464 | 2SPANSLDSIDEOF10343 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0060713 | OH | Sus | 43049439 | No | 2017 | JUL | Yes | Line to Line | 1289159 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0063304&numberofmonths=24&showchangehistorylog=1 | 17-0063304 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | OTHER | 3OF3HOTWIRESDOWN | 20170717 | 121 | 1833181 | 563 | Distribution Circuit | Vegetation | Tree - fell into line | 1153 | 126343 | 38.4429 | -122.9914 | 7001BOHEMIANHWY | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 17-0063304 | OH | Sus | 0 | No | 2017 | JUL | Yes | Line to Ground | 1291102 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0065437&numberofmonths=24&showchangehistorylog=1 | 17-0065437 | SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | FUSE | 5549 | 20170725 | 1547 | 1839696 | 808 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 18584 | 38.3726 | -122.5385 | 4399WARMSPRINGSRDGLENELLEN | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0065437 | OH | Sus | 43067423 | No | 2017 | JUL | Yes | Line to Ground | 1292616 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0065385&numberofmonths=24&showchangehistorylog=1 | 17-0065385 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 12637 | 20170725 | 1358 | 1839626 | 276 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 36 | 9936 | 38.5017 | -123.0046 | 13972FERNRDGUERNEVILLE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0065385 | OH | Sus | 43067348 | No | 2017 | JUL | Yes | Line to Line | 1292598 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0066767&numberofmonths=24&showchangehistorylog=1 | 17-0066767 | SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 6751 | 20170731 | 1310 | 1843215 | 885 | Distribution Circuit | Vegetation | Tree - fell into line | 134 | 118590 | 38.592 | -122.9622 | 8PPAST6751ONMAINLINE | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0066767 | OH | Sus | 0 | No | 2017 | JUL | Yes | Line to Ground | 1293511 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0067550&numberofmonths=24&showchangehistorylog=1 | 17-0067550 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 2561 | 20170802 | 2155 | 1845097 | 955 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 20055 | 38.4113 | -122.965 | MooreShon42501SPANFROMMETER1007526315 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0067550 | OH | Sus | 31340526 | yes | 2017 | AUG | Yes | Line to Ground | 1294033 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0068193&numberofmonths=24&showchangehistorylog=1 | 17-0068193 | SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | RECLOSER | 24918 | 20170805 | 1625 | 1847035 | 751 | Distribution Circuit | Vegetation | Tree - fell into line | 187 | 140437 | 38.5914 | -122.92 | 2SPANSLDSIDEOFMTR1007786111 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0068193 | OH | Sus | 31341080 | No | 2017 | AUG | Yes | Line to Ground | 1294501 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0070629&numberofmonths=24&showchangehistorylog=1 | 17-0070629 | SONOMA | FIELD OPS NORTH | Tier 2 | PENNGROVE-1101 | 43471101 | OTHER | WIREDOWN1PHSNGLPHJUSTBEFORE3793 | 20170815 | 2118 | 1853405 | 517 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 15209 | 38.3357 | -122.5918 | CONTRERAST34632955SONOMAMOUNTAINRDORCO3793 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0070629 | OH | Sus | 43085627 | No | 2017 | AUG | Yes | Line to Ground | 1296215 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0071584&numberofmonths=24&showchangehistorylog=1 | 17-0071584 | SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | RECLOSER | 448 | 20170820 | 1646 | 1855771 | 565 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1305 | 204241 | 38.3443 | -122.5145 | 15DONTIMETEO | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0071584 | OH | Sus | 31343744 | No | 2017 | AUG | Yes | Line to Line | 1296912 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0073092&numberofmonths=24&showchangehistorylog=1 | 17-0073092 | SONOMA | FIELD OPS NORTH | Tier 2 | RINCON-1103 | 43321103 | RECLOSER | 7433 | 20170826 | 2029 | 1860173 | 382 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 1383 | 361520 | 38.4722 | -122.653 | ONMAINLINE130595701DUPONTDR | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0073092 | OH | Sus | 43094540 | No | 2017 | AUG | Yes | Line to Ground | 1297973 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0073179&numberofmonths=24&showchangehistorylog=1 | 17-0073179 | SONOMA | FIELD OPS NORTH | Tier 3 | FULTON-1107 | 42561107 | RECLOSER | 77670 | 20170827 | 1509 | 1860504 | 788 | Distribution Circuit | Vegetation | Tree - fell into line | 400 | 214780 | 38.5022 | -122.737 | 5232CARRIAGELN | Clear-Above 90 | Pole-Wood | Broken, wire on ground | 17-0073179 | OH | Sus | 0 | yes | 2017 | AUG | Yes | Line to Ground | 1298051 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0073984&numberofmonths=24&showchangehistorylog=1 | 17-0073984 | SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | TRIP-SAVER | 2359 | 20170830 | 157 | 1862960 | 639 | Distribution Circuit | Vegetation | Tree - fell into line | 89 | 55715 | 38.358 | -122.5256 | NoonanTodd34691457HILLRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0073984 | OH | Sus | 43095838 | No | 2017 | AUG | Yes | Line to Ground | 1298606 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0075088&numberofmonths=24&showchangehistorylog=1 | 17-0075088 | SONOMA | FIELD OPS NORTH | Tier 3 | SANTA ROSA A-1107 | 42151107 | JUMPER | WIREDOWN | 20170902 | 724 | 1866035 | 458 | Distribution Circuit | Equipment Failure/Involved | Overhead | 330 | 64356 | 38.4505 | -122.6872 | FUCO9001 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0075088 | OH | Sus | 0 | yes | 2017 | SEP | Yes | Line to Ground | 1299385 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0075429&numberofmonths=24&showchangehistorylog=1 | 17-0075429 | SONOMA | FIELD OPS NORTH | Tier 3 | SONOMA-1103 | 42721103 | FUSE | 5543 | 20170902 | 2125 | 1867532 | 972 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 71928 | 38.303 | -122.4409 | 2SPANSLDSIDEOF5543 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0075429 | OH | Sus | 0 | yes | 2017 | SEP | Yes | Line to Ground | 1299717 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0075808&numberofmonths=24&showchangehistorylog=1 | 17-0075808 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | JUMPER | WIREDOWNHOT3170WESTWOODLN | 20170904 | 948 | 1869647 | 440 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 880 | 38.4052 | -122.9705 | 3170WESTWOODLN | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0075808 | OH | Sus | 0 | yes | 2017 | SEP | Yes | Line to Ground | 1300067 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0076120&numberofmonths=24&showchangehistorylog=1 | 17-0076120 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 61169 | 20170905 | 1243 | 1870663 | 777 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 20 | 15540 | 38.4921 | -123.0664 | 2325CAZADEROHWY | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0076120 | OH | Sus | 0 | No | 2017 | SEP | Yes | Line to Ground | 1300308 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0079789&numberofmonths=24&showchangehistorylog=1 | 17-0079789 | SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | RECLOSER | 24918 | 20170918 | 1441 | 1881109 | 448 | Distribution Circuit | Vegetation | Tree - branch fell on line | 187 | 83776 | 38.5914 | -122.92 | Nott35693721MILLCREEKRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0079789 | OH | Sus | 43113382 | No | 2017 | SEP | Yes | Line to Line | 1303050 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0079875&numberofmonths=24&showchangehistorylog=1 | 17-0079875 | SONOMA | FIELD OPS NORTH | Tier 2 | GEYSERVILLE-1101 | 42891101 | FUSE | 2473 | 20170919 | 438 | 1881482 | 772 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 21895 | 38.7106 | -122.925 | NoonanTodd3469585ROSSIRD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0079875 | OH | Sus | 0 | No | 2017 | SEP | Yes | Line to Ground | 1303119 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0081329&numberofmonths=24&showchangehistorylog=1 | 17-0081329 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 1955 | 20170924 | 1642 | 1885026 | 296 | Distribution Circuit | Vegetation | Tree - branch fell on line | 160 | 22574 | 38.3879 | -122.9715 | MTR1007570521 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0081329 | OH | Sus | 43116676 | No | 2017 | SEP | Yes | Line to Ground | 1304105 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0085994&numberofmonths=24&showchangehistorylog=1 | 17-0085994 | SONOMA | FIELD OPS NORTH | Tier 3 | CLOVERDALE-1102 | 42821102 | FUSE | 1387 | 20171010 | 1129 | 1897527 | 2996 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 37248 | 38.8409 | -122.9529 | 1.0096e+18 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085994 | OH | Sus | 0 | No | 2017 | OCT | Yes | Force Out | 1307237 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0087223&numberofmonths=24&showchangehistorylog=1 | 17-0087223 | SONOMA | FIELD OPS NORTH | Tier 2 | RINCON-1102 | 43321102 | FUSE | 15249 | 20171010 | 1418 | 1897684 | 10242 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 9 | 92178 | 38.4854 | -122.6679 | MTR1007528748 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0087223 | OH | Sus | 0 | No | 2017 | OCT | Yes | Line to Ground | 1308212 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0086005&numberofmonths=24&showchangehistorylog=1 | 17-0086005 | SONOMA | FIELD OPS NORTH | Tier 3 | SONOMA-1103 | 42721103 | FUSE | 99309 | 20171010 | 700 | 1897119 | 16076 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 353672 | 38.3269 | -122.4321 | 6POLESLDSIDEOF99309 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0086005 | OH | Sus | 0 | No | 2017 | OCT | Yes | Line to Ground | 1307247 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0086350&numberofmonths=24&showchangehistorylog=1 | 17-0086350 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | RECLOSER | 320 | 20171011 | 1245 | 1898451 | 1565 | Distribution Circuit | Vegetation | Tree - branch fell on line | 145 | 226925 | 38.4989 | -123.0211 | 15180CAZADERARD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0086350 | OH | Sus | 0 | No | 2017 | OCT | Yes | Line to Line | 1307494 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0087081&numberofmonths=24&showchangehistorylog=1 | 17-0087081 | SONOMA | FIELD OPS NORTH | Tier 2 | GEYSERVILLE-1102 | 42891102 | FUSE | 188527 | 20171013 | 753 | 1899808 | 2211 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 11055 | 38.7317 | -122.8989 | 3SPTWDCOUTFROMMETER1009959849 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0087081 | OH | Sus | 0 | No | 2017 | OCT | Yes | Line to Ground | 1308100 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0088846&numberofmonths=24&showchangehistorylog=1 | 17-0088846 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | TRIP-SAVER | 999 | 20171019 | 2335 | 1904753 | 649 | Distribution Circuit | Vegetation | Tree - branch fell on line | 79 | 51271 | 38.422 | -122.954 | 21HAMPTONRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0088846 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1309422 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0089503&numberofmonths=24&showchangehistorylog=1 | 17-0089503 | SONOMA | FIELD OPS NORTH | Tier 3 | SONOMA-1103 | 42721103 | OTHER | WIREDOWNNORRBOMRDMTR1008107017 | 20171021 | 1814 | 1907292 | 1609 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 22 | 24938 | 38.3285 | -122.4393 | MTR1008107017 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0089503 | OH | Sus | 0 | No | 2017 | OCT | Yes | Force Out | 1309967 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0090251&numberofmonths=24&showchangehistorylog=1 | 17-0090251 | SONOMA | FIELD OPS NORTH | Tier 3 | FULTON-1107 | 42561107 | JUMPER | OJS1217WIKIUPDR | 20171025 | 1011 | 1909252 | 184 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 2 | 368 | 38.5098 | -122.7435 | WO1217WIKIUP | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0090251 | OH | Sus | 0 | No | 2017 | OCT | Yes | Force Out | 1310510 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0090635&numberofmonths=24&showchangehistorylog=1 | 17-0090635 | SONOMA | FIELD OPS NORTH | Tier 2 | RINCON-1102 | 43321102 | FUSE | 15265 | 20171026 | 1442 | 1910271 | 1477 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 5124 | 38.4896 | -122.6673 | 1645BairdRdMTR1008903615 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0090635 | OH | Sus | 0 | No | 2017 | OCT | Yes | Line to Line | 1310717 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0092446&numberofmonths=24&showchangehistorylog=1 | 17-0092446 | SONOMA | FIELD OPS NORTH | Tier 2 | MIRABEL-1101 | 42091101 | FUSE | 1003 | 20171103 | 1204 | 1915139 | 146 | Distribution Circuit | Equipment Failure/Involved | Overhead | 69 | 10074 | 38.4763 | -122.9069 | 2SPANSLDSIDEOF1003 | Overcast-Fog-Rain-32-90 F | Insulator | Broken, wire on ground | 17-0092446 | OH | Sus | 0 | yes | 2017 | NOV | Yes | Line to Ground | 1312011 | INS | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0094794&numberofmonths=24&showchangehistorylog=1 | 17-0094794 | SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 779 | 20171113 | 1857 | 1921777 | 1341 | Distribution Circuit | Equipment Failure/Involved | Overhead | 45 | 50440 | 38.5971 | -122.9894 | WIREDOWN1SPANSSOF3033 | Clear-32-90 F | Conductor, Overhead | On Ground | 17-0094794 | OH | Sus | 0 | No | 2017 | NOV | Yes | Line to Line | 1313785 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0095377&numberofmonths=24&showchangehistorylog=1 | 17-0095377 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | RECLOSER | 120 | 20171115 | 2020 | 1923319 | 604 | Distribution Circuit | Vegetation | Tree - fell into line | 494 | 90969 | 38.4637 | -123.0083 | MTR1007253355 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0095377 | OH | Sus | 43215957 | yes | 2017 | NOV | Yes | Line to Line | 1314269 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0095069&numberofmonths=24&showchangehistorylog=1 | 17-0095069 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 2027 | 20171115 | 732 | 1922646 | 255 | Distribution Circuit | Vegetation | Tree - branch fell on line | 28 | 7140 | 38.5191 | -122.98 | 14724EAGLENESTLN | Clear-32-90 F | Conductor, Overhead | On Ground | 17-0095069 | OH | Sus | 43214472 | yes | 2017 | NOV | Yes | Line to Ground | 1314067 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0096607&numberofmonths=24&showchangehistorylog=1 | 17-0096607 | SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | RECLOSER | 568 | 20171120 | 1433 | 1926769 | 680 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 167 | 62410 | 38.5173 | -122.655 | 7SLSOF929 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0096607 | OH | Sus | 31366547 | No | 2017 | NOV | Yes | Line to Ground | 1315174 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0097377&numberofmonths=24&showchangehistorylog=1 | 17-0097377 | SONOMA | FIELD OPS NORTH | Tier 3 | MONROE-2103 | 43302103 | FUSE | 14615 | 20171124 | 913 | 1928588 | 275 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 62 | 17050 | 38.5175 | -122.7222 | 2SPANSLDSIDEOFFUCO146151488MICHELEWAY | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0097377 | OH | Sus | 43221245 | No | 2017 | NOV | Yes | Line to Line | 1315634 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0097707&numberofmonths=24&showchangehistorylog=1 | 17-0097707 | SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1101 | 42571101 | FUSE | 2149 | 20171127 | 541 | 1929846 | 524 | Distribution Circuit | Vegetation | Tree - fell into line | 82 | 42968 | 38.3777 | -122.8781 | SSOFFUCO18123 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0097707 | OH | Sus | 43222352 | yes | 2017 | NOV | Yes | Line to Ground | 1315927 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0098083&numberofmonths=24&showchangehistorylog=1 | 17-0098083 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE | 15383 | 20171128 | 1001 | 1930950 | 318 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 6996 | 38.4483 | -123.0005 | 8231TYRONERD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0098083 | OH | Sus | 43223484 | No | 2017 | NOV | Yes | Line to Ground | 1316292 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0098537&numberofmonths=24&showchangehistorylog=1 | 17-0098537 | SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | OTHER | WIREDOWNMTR1007662094 | 20171130 | 654 | 1932318 | 584 | Distribution Circuit | Vegetation | Tree - fell into line | 532 | 111884 | 38.3686 | -122.535 | MTR10076620944463LAKESIDEDRGLENNELLEN | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0098537 | OH | Sus | 31367702 | No | 2017 | NOV | Yes | Line to Ground | 1316669 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0100137&numberofmonths=24&showchangehistorylog=1 | 17-0100137 | SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1108 | 42631108 | RECLOSER | 636 | 20171205 | 1704 | 1936881 | 522 | Distribution Circuit | Equipment Failure/Involved | Overhead | 142 | 23869 | 38.2618 | -122.7158 | CONTRERAST34635730BODEGAAVE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0100137 | OH | Sus | 43227597 | yes | 2017 | DEC | Yes | Line to Ground | 1317806 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0100881&numberofmonths=24&showchangehistorylog=1 | 17-0100881 | SONOMA | FIELD OPS NORTH | Tier 2 | ANNAPOLIS-1101 | 42861101 | JUMPER | WIREDOWN | 20171208 | 1719 | 1939265 | 4139 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 9779 | 38.6629 | -123.2356 | 4609COUTPOLE | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 17-0100881 | OH | Sus | 43229525 | No | 2017 | DEC | Yes | Line to Ground | 1318524 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0100915&numberofmonths=24&showchangehistorylog=1 | 17-0100915 | SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | RECLOSER | 568 | 20171209 | 658 | 1939399 | 441 | Distribution Circuit | Animal | Bird found | 167 | 24035 | 38.5173 | -122.655 | 10SPANSLDSIDEOF929 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0100915 | OH | Sus | 43229436 | No | 2017 | DEC | Yes | Line to Ground | 1318558 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0101649&numberofmonths=24&showchangehistorylog=1 | 17-0101649 | SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1101 | 43321101 | JUMPER | 1251 | 20171214 | 1129 | 1942977 | 186 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 17 | 3156 | 38.4517 | -122.5744 | ATMTR1007221702 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0101649 | OH | Sus | 43235201 | No | 2017 | DEC | Yes | Line to Ground | 1319537 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0101861&numberofmonths=24&showchangehistorylog=1 | 17-0101861 | SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | OCB | 11212 | 20171215 | 1907 | 1943877 | 502 | Distribution Circuit | Vegetation | Tree - fell into line | 638 | 99293 | 38.5408 | -123.2237 | SSTO9425BENWAY | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0101861 | OH | Sus | 43236420 | No | 2017 | DEC | Yes | Line to Line | 1319753 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0003716&numberofmonths=24&showchangehistorylog=1 | 18-0003716 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | TRIP-SAVER | 1067 | 20180104 | 1749 | 2210 | 530 | Distribution Circuit | Vegetation | Tree - fell into line | 109 | 57770 | 38.4934 | -123.0059 | 2SPANSLDSIDEOF1067 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0003716 | OH | Sus | 31372271 | yes | 2018 | JAN | Yes | Line to Line | 1323221 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0004427&numberofmonths=24&showchangehistorylog=1 | 18-0004427 | SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1102 | 42571102 | FUSE | 12153 | 20180108 | 1557 | 4127 | 248 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 744 | 38.4446 | -122.9204 | FUCO12153 | Clear-32-90 F | Insulator | Broken, wire on object | 18-0004427 | OH | Sus | 43246416 | yes | 2018 | JAN | Yes | Force Out | 1323669 | INS | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0004361&numberofmonths=24&showchangehistorylog=1 | 18-0004361 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 1047 | 20180108 | 1255 | 3968 | 915 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 44835 | 38.5319 | -123.0876 | 2BROKENPOLESATMTR5000012222WIREDOWNATMTR1009769849 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0004361 | OH | Sus | 43246404 | yes | 2018 | JAN | Yes | Line to Line | 1323646 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0004489&numberofmonths=24&showchangehistorylog=1 | 18-0004489 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | OTHER | 15383 | 20180108 | 2034 | 4327 | 889 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 18277 | 38.4483 | -123.0005 | 9SPANSLDSIDEOFFUCO15383 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0004489 | OH | Sus | 43246523 | yes | 2018 | JAN | Yes | Line to Ground | 1323722 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0004797&numberofmonths=24&showchangehistorylog=1 | 18-0004797 | SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1101 | 43071101 | FUSE | 3749 | 20180109 | 1349 | 5208 | 180 | Distribution Circuit | Vegetation | Tree - branch fell on line | 21 | 3780 | 38.4006 | -122.5682 | 633VIAFERRARI | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0004797 | OH | Sus | 0 | yes | 2018 | JAN | Yes | Line to Ground | 1323913 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0013241&numberofmonths=24&showchangehistorylog=1 | 18-0013241 | SONOMA | FIELD OPS NORTH | Tier 2 | SALMON CREEK-1101 | 43161101 | FUSE | 2239 | 20180211 | 1302 | 22733 | 776 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 3880 | 38.3448 | -123.0243 | 2SPANSLDSIDEOF2239 | Partly Cloudy-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 18-0013241 | OH | Sus | 0 | No | 2018 | FEB | Yes | Three Phase Fault | 1329413 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0013860&numberofmonths=24&showchangehistorylog=1 | 18-0013860 | SONOMA | FIELD OPS NORTH | Tier 3 | FULTON-1107 | 42561107 | FUSE | 2375 | 20180213 | 1214 | 24022 | 511 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 21 | 10731 | 38.5423 | -122.7203 | LDSIDEOFFUCO2375 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0013860 | OH | Sus | 43278014 | No | 2018 | FEB | Yes | Line to Ground | 1329858 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0015259&numberofmonths=24&showchangehistorylog=1 | 18-0015259 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE | 4837 | 20180218 | 1640 | 26786 | 399 | Distribution Circuit | Vegetation | Tree - branch fell on line | 52 | 20748 | 38.4804 | -122.9967 | 2SPANSLDSIDEOF4837 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0015259 | OH | Sus | 43280611 | yes | 2018 | FEB | Yes | Force Out | 1330696 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0017109&numberofmonths=24&showchangehistorylog=1 | 18-0017109 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1105 | 42271105 | RECLOSER | 634 | 20180226 | 401 | 31369 | 380 | Distribution Circuit | Equipment Failure/Involved | Overhead | 48 | 11865 | 38.2982 | -122.8208 | 15SPANSLDSIDEOF79249 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 18-0017109 | OH | Sus | 43284506 | yes | 2018 | FEB | Yes | Line to Ground | 1332055 | CSO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0018367&numberofmonths=24&showchangehistorylog=1 | 18-0018367 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | JUMPER | WIREDOWN1SOF3409 | 20180301 | 643 | 34217 | 395 | Distribution Circuit | Vegetation | Tree - bark fell into line | 149 | 35562 | 38.2063 | -122.9202 | 1SPANSOUTHOF3409ONMAINLINE | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0018367 | OH | Sus | 43287212 | yes | 2018 | MAR | Yes | Line to Ground | 1332898 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0018930&numberofmonths=24&showchangehistorylog=1 | 18-0018930 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 2373 | 20180301 | 2148 | 35800 | 942 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 5652 | 38.5096 | -122.9609 | 12550MCPEAKRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0018930 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1333284 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0018816&numberofmonths=24&showchangehistorylog=1 | 18-0018816 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | RECLOSER | 104 | 20180301 | 1857 | 35614 | 913 | Distribution Circuit | Vegetation | Tree - fell into line | 1499 | 647323 | 38.403 | -122.9214 | 13330OCCIDENTALRD | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 18-0018816 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1333182 | CAW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0022724&numberofmonths=24&showchangehistorylog=1 | 18-0022724 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | FUSE | 3421 | 20180314 | 1055 | 44111 | 900 | Distribution Circuit | Environmental/External | Lightning | 7 | 6300 | 38.2866 | -122.8527 | MTR10101967494SPANSLDSIDEOF3421 | Partly Cloudy-Drizzle-Lightning-32-90 F | Transformer (OH) | Broken, wire on ground | 18-0022724 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1335861 | TXO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0023217&numberofmonths=24&showchangehistorylog=1 | 18-0023217 | SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | RECLOSER | 568 | 20180315 | 2209 | 45137 | 566 | Distribution Circuit | 3rd Party | Vehicle | 167 | 49045 | 38.5173 | -122.655 | 1SPANSOF1199ONMAINLINECAMPNEWMANPORTERCREEKRD | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023217 | OH | Sus | 43301931 | No | 2018 | MAR | Yes | Multi-Fault | 1336119 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0023887&numberofmonths=24&showchangehistorylog=1 | 18-0023887 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1102 | 42271102 | TRIP-SAVER | 681 | 20180318 | 1025 | 47308 | 463 | Distribution Circuit | Vegetation | Tree - fell into line | 129 | 40260 | 38.2838 | -122.7101 | MTR1009647754 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023887 | OH | Sus | 43303123 | No | 2018 | MAR | Yes | Line to Ground | 1336691 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0024677&numberofmonths=24&showchangehistorylog=1 | 18-0024677 | SONOMA | FIELD OPS NORTH | Tier 2 | MIRABEL-1101 | 42091101 | FUSE | 6485 | 20180321 | 427 | 49112 | 758 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 6064 | 38.4668 | -122.9087 | 7SPANSLDSIDEOFFUSES | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0024677 | OH | Sus | 43304152 | yes | 2018 | MAR | Yes | Multi-Fault | 1337228 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0025276&numberofmonths=24&showchangehistorylog=1 | 18-0025276 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1105 | 42271105 | FUSE | 3287 | 20180322 | 527 | 50171 | 422 | Distribution Circuit | Vegetation | Tree - fell into line | 175 | 73850 | 38.3381 | -122.7858 | 6000BLANKRD | Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0025276 | OH | Sus | 43305958 | yes | 2018 | MAR | Yes | Line to Ground | 1337490 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0025337&numberofmonths=24&showchangehistorylog=1 | 18-0025337 | SONOMA | FIELD OPS NORTH | Tier 2 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 2353 | 20180322 | 512 | 50225 | 453 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1812 | 38.6326 | -122.8307 | 2SPANSSOURCESIDEOFEOL | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0025337 | OH | Sus | 43306110 | yes | 2018 | MAR | Yes | Line to Ground | 1337521 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0025324&numberofmonths=24&showchangehistorylog=1 | 18-0025324 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 433 | 20180322 | 724 | 50280 | 509 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 16797 | 38.5091 | -122.9283 | 11955WESTSIDERD | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0025324 | OH | Sus | 43306112 | yes | 2018 | MAR | Yes | Line to Ground | 1337510 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0025348&numberofmonths=24&showchangehistorylog=1 | 18-0025348 | SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | FUSE | 2223 | 20180322 | 740 | 50309 | 378 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 15680 | 38.5471 | -122.6692 | 3480CALISTOGA | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0025348 | OH | Sus | 43306118 | yes | 2018 | MAR | Yes | Line to Line | 1337528 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0026329&numberofmonths=24&showchangehistorylog=1 | 18-0026329 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1105 | 42271105 | FUSE | 6563 | 20180324 | 1540 | 52762 | 485 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 5820 | 38.3217 | -122.7872 | 4SPANSLOADSIDEOF6563 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0026329 | OH | Sus | 0 | No | 2018 | MAR | Yes | Line to Ground | 1338166 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0026404&numberofmonths=24&showchangehistorylog=1 | 18-0026404 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1101 | 42091101 | TRIP-SAVER | 4859 | 20180325 | 720 | 52972 | 559 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 26832 | 38.4755 | -122.9527 | 14025GREENVALLEYRD | Clear-32-90 F | Conductor, Overhead | On Ground | 18-0026404 | OH | Sus | 43308453 | No | 2018 | MAR | Yes | Multi-Fault | 1338260 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0029825&numberofmonths=24&showchangehistorylog=1 | 18-0029825 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1101 | 42571101 | OTHER | WIREDOWN | 20180406 | 901 | 60702 | 423 | Distribution Circuit | Vegetation | Tree - fell into line | 1049 | 42343 | 38.3938 | -122.8951 | 920FURLONGRDSEBASTOPOL | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0029825 | OH | Sus | 43316563 | yes | 2018 | APR | Yes | Line to Ground | 1340878 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0030201&numberofmonths=24&showchangehistorylog=1 | 18-0030201 | SONOMA | FIELD OPS NORTH | Tier 2 | MIRABEL-1102 | 42091102 | FUSE | 13669 | 20180407 | 614 | 61640 | 533 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 4797 | 38.509 | -122.8869 | 6POLESLDSIDEOF13669 | Overcast-Fog-32-90 F | Pole-Wood | Broken, wire on ground | 18-0030201 | OH | Sus | 0 | yes | 2018 | APR | Yes | Three Phase Fault | 1341075 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0031475&numberofmonths=24&showchangehistorylog=1 | 18-0031475 | SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | FUSE | 12383 | 20180411 | 1933 | 65049 | 617 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 8638 | 38.3393 | -122.5289 | 1SPANLOADSIDE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0031475 | OH | Sus | 0 | yes | 2018 | APR | Yes | Line to Line | 1342113 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0031446&numberofmonths=24&showchangehistorylog=1 | 18-0031446 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 1499 | 20180411 | 1906 | 64948 | 315 | Distribution Circuit | Vegetation | Tree - branch fell on line | 129 | 28135 | 38.5089 | -122.9291 | 11091SEQUOIARD | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0031446 | OH | Sus | 0 | yes | 2018 | APR | Yes | Line to Line | 1342076 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0031458&numberofmonths=24&showchangehistorylog=1 | 18-0031458 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 1045 | 20180411 | 1759 | 64934 | 606 | Distribution Circuit | Equipment Failure/Involved | Overhead | 67 | 40602 | 38.5008 | -122.9054 | 1SPANLOADSIDE | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0031458 | OH | Sus | 0 | yes | 2018 | APR | Yes | Line to Ground | 1342091 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0031670&numberofmonths=24&showchangehistorylog=1 | 18-0031670 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 8057 | 20180412 | 833 | 65349 | 325 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 325 | 38.496 | -122.9377 | 1LDSIDEOF8057 | Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0031670 | OH | Sus | 43323320 | yes | 2018 | APR | Yes | Line to Line | 1342289 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0033253&numberofmonths=24&showchangehistorylog=1 | 18-0033253 | SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE | 8493 | 20180417 | 2308 | 69184 | 1226 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 47695 | 38.5329 | -123.2714 | 1SPANNOFMTR100789918220885HWY1 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0033253 | OH | Sus | 43326942 | No | 2018 | APR | Yes | Line to Ground | 1343431 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0034556&numberofmonths=24&showchangehistorylog=1 | 18-0034556 | SONOMA | FIELD OPS NORTH | Tier 3 | DUNBAR-1102 | 43071102 | OTHER | 7051 | 20180423 | 818 | 71891 | 418 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 4598 | 38.3666 | -122.5653 | 4SPANSLDSIDEOF7051 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0034556 | OH | Sus | 31389606 | No | 2018 | APR | Yes | Force Out | 1344370 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0035535&numberofmonths=24&showchangehistorylog=1 | 18-0035535 | SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | FUSE | 2269 | 20180425 | 1349 | 73832 | 812 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 19488 | 38.5183 | -122.6032 | MTR1003850696 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0035535 | OH | Sus | 0 | No | 2018 | APR | Yes | Multi-Fault | 1344997 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0036416&numberofmonths=24&showchangehistorylog=1 | 18-0036416 | SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1108 | 42631108 | RECLOSER | 636 | 20180427 | 2206 | 75705 | 1005 | Distribution Circuit | Equipment Failure/Involved | Overhead | 141 | 36141 | 38.2618 | -122.7158 | MTR5000011262 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0036416 | OH | Sus | 43333110 | No | 2018 | APR | Yes | Line to Ground | 1345487 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0036544&numberofmonths=24&showchangehistorylog=1 | 18-0036544 | SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | RECLOSER | 24918 | 20180428 | 2036 | 76057 | 1069 | Distribution Circuit | Vegetation | Tree - fell into line | 187 | 199903 | 38.5914 | -122.92 | 4535MILLCREEKRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0036544 | OH | Sus | 43333221 | No | 2018 | APR | Yes | Line to Ground | 1345619 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0039404&numberofmonths=24&showchangehistorylog=1 | 18-0039404 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 1499 | 20180508 | 1923 | 81953 | 365 | Distribution Circuit | Vegetation | Tree - fell into line | 129 | 47723 | 38.5089 | -122.9291 | 11055DELLAVE11091DELLAVE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0039404 | OH | Sus | 43339372 | No | 2018 | MAY | Yes | Line to Line | 1347607 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0039683&numberofmonths=24&showchangehistorylog=1 | 18-0039683 | SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER | 560 | 20180509 | 1400 | 82502 | 1018 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 29522 | 38.5562 | -123.3034 | FISKMILLCOVEMILEKARKER42 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0039683 | OH | Sus | 43339946 | No | 2018 | MAY | Yes | Line to Ground | 1347853 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0039981&numberofmonths=24&showchangehistorylog=1 | 18-0039981 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | TRIP-SAVER | 841 | 20180510 | 1647 | 83337 | 577 | Distribution Circuit | Vegetation | Tree - branch fell on line | 133 | 31753 | 38.5087 | -122.9261 | MooreS4308BETWEENCO13597ANDMETER1008019873 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0039981 | OH | Sus | 43344425 | No | 2018 | MAY | Yes | Line to Ground | 1348131 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0040240&numberofmonths=24&showchangehistorylog=1 | 18-0040240 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | TRIP-SAVER | 6917 | 20180511 | 1013 | 83837 | 242 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 5959 | 38.3873 | -122.9728 | 17450TAYLOR | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0040240 | OH | Sus | 43345988 | yes | 2018 | MAY | Yes | Line to Ground | 1348335 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0040429&numberofmonths=24&showchangehistorylog=1 | 18-0040429 | SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | FUSE | 2225 | 20180511 | 1803 | 84346 | 311 | Distribution Circuit | Vegetation | Tree - fell into line | 90 | 27990 | 38.5242 | -122.6544 | 3166CALISTOGARD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0040429 | OH | Sus | 43346461 | yes | 2018 | MAY | Yes | Line to Line | 1348435 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0042546&numberofmonths=24&showchangehistorylog=1 | 18-0042546 | SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1108 | 42631108 | RECLOSER | 636 | 20180519 | 1624 | 89814 | 236 | Distribution Circuit | Equipment Failure/Involved | Overhead | 141 | 15606 | 38.2618 | -122.7158 | 1PNOF4259 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0042546 | OH | Sus | 43351611 | No | 2018 | MAY | Yes | Line to Line | 1350129 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0043287&numberofmonths=24&showchangehistorylog=1 | 18-0043287 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | FUSE | 4133 | 20180522 | 1325 | 91919 | 1042 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 31253 | 38.1494 | -122.8233 | 5600PETALUMAMARSHALLRD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0043287 | OH | Sus | 43353725 | No | 2018 | MAY | Yes | Three Phase Fault | 1350879 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0047625&numberofmonths=24&showchangehistorylog=1 | 18-0047625 | SONOMA | FIELD OPS NORTH | Tier 3 | FULTON-1107 | 42561107 | OTHER | HOTWIREDOWN2375 | 20180605 | 1345 | 102064 | 819 | Distribution Circuit | Vegetation | Tree - fell into line | 212 | 38493 | 38.5396 | -122.7208 | 2390MARKWESTSPRINGSRD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0047625 | OH | Sus | 0 | No | 2018 | JUN | Yes | Open Circuit | 1354100 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0049445&numberofmonths=24&showchangehistorylog=1 | 18-0049445 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 737 | 20180610 | 1719 | 105889 | 411 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 2386 | 38.4084 | -122.9079 | MTR1010299830 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0049445 | OH | Sus | 43369565 | No | 2018 | JUN | Yes | Line to Ground | 1355506 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0052032&numberofmonths=24&showchangehistorylog=1 | 18-0052032 | SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1101 | 42571101 | RECLOSER | 322 | 20180618 | 1509 | 112225 | 724 | Distribution Circuit | 3rd Party | Vehicle | 375 | 94110 | 38.3868 | -122.8901 | 18689 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 18-0052032 | OH | Sus | 0 | No | 2018 | JUN | Yes | Line to Line | 1357484 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0056492&numberofmonths=24&showchangehistorylog=1 | 18-0056492 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 1043 | 20180702 | 1710 | 123301 | 630 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1260 | 38.5068 | -122.915 | 1LDSIDEOF104310140CANYONRD | Clear-32-90F | Pole-Wood | Broken, wire on ground | 18-0056492 | OH | Sus | 0 | No | 2018 | JUL | Yes | Multi-Fault | 1361163 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0059799&numberofmonths=24&showchangehistorylog=1 | 18-0059799 | SONOMA | FIELD OPS NORTH | Tier 2 | FITCH MOUNTAIN-1113 | 42751113 | RECLOSER | 24550 | 20180714 | 1240 | 131638 | 552 | Distribution Circuit | 3rd Party | Vehicle | 225 | 20804 | 38.5793 | -122.878 | 2SPANSSSOF38536 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 18-0059799 | OH | Sus | 0 | No | 2018 | JUL | Yes | Line to Ground | 1363775 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0060829&numberofmonths=24&showchangehistorylog=1 | 18-0060829 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 6877 | 20180717 | 1653 | 134079 | 555 | Distribution Circuit | Vegetation | Tree - fell into line | 64 | 12038 | 38.3942 | -122.9138 | 1SSFU7317 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0060829 | OH | Sus | 31400289 | yes | 2018 | JUL | Yes | Line to Line | 1364537 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0060883&numberofmonths=24&showchangehistorylog=1 | 18-0060883 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 6877 | 20180718 | 246 | 134376 | 524 | Distribution Circuit | Vegetation | Tree - fell into line | 64 | 6868 | 38.3942 | -122.9138 | 12430FIORILNSEBASTOPOL | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0060883 | OH | Sus | 0 | yes | 2018 | JUL | Yes | Line to Ground | 1364593 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0065221&numberofmonths=24&showchangehistorylog=1 | 18-0065221 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1105 | 42271105 | RECLOSER | 36536 | 20180731 | 634 | 145643 | 1183 | Distribution Circuit | 3rd Party | Vehicle | 792 | 162993 | 38.3142 | -122.7365 | CANFIELDROBLAR | Clear-32-90F | Pole-Wood | Broken, wire on ground | 18-0065221 | OH | Sus | 0 | No | 2018 | JUL | Yes | Three Phase Fault | 1367911 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0065479&numberofmonths=24&showchangehistorylog=1 | 18-0065479 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 6543 | 20180731 | 1545 | 146119 | 469 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 8323 | 38.3683 | -122.9641 | 16721BURLLN | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0065479 | OH | Sus | 43426906 | No | 2018 | JUL | Yes | Line to Ground | 1368112 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0066335&numberofmonths=24&showchangehistorylog=1 | 18-0066335 | SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1109 | 42631109 | FUSE | 2621 | 20180802 | 2127 | 147932 | 377 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 5655 | 38.1683 | -122.6739 | 1SPANSSOFMTR1007932553 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0066335 | OH | Sus | 43428965 | No | 2018 | AUG | Yes | Line to Line | 1368730 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0068470&numberofmonths=24&showchangehistorylog=1 | 18-0068470 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 1407 | 20180809 | 1621 | 152381 | 559 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 10062 | 38.4977 | -122.9026 | FUCO13491 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 18-0068470 | OH | Sus | 31402437 | No | 2018 | AUG | Yes | Line to Line | 1370091 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0072613&numberofmonths=24&showchangehistorylog=1 | 18-0072613 | SONOMA | FIELD OPS NORTH | Tier 2 | RINCON-1103 | 43321103 | OCB | 11032 | 20180822 | 1653 | 160482 | 487 | Distribution Circuit | Vegetation | Tree - branch fell on line | 700 | 129734 | 38.4901 | -122.6661 | 509GARFEILDPARKAVE15133TWD5197 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0072613 | OH | Sus | 31403994 | No | 2018 | AUG | Yes | Line to Line | 1372765 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0073589&numberofmonths=24&showchangehistorylog=1 | 18-0073589 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | OTHER | 6399 | 20180826 | 1337 | 162668 | 358 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 11098 | 38.5038 | -122.9115 | 10385SCENICDR | Clear-32-90F | Connector or Splice (OH) | Broken, wire on ground | 18-0073589 | OH | Sus | 43448406 | No | 2018 | AUG | Yes | Line to Ground | 1373558 | CSO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0075948&numberofmonths=24&showchangehistorylog=1 | 18-0075948 | SONOMA | FIELD OPS NORTH | Tier 2 | MIRABEL-1102 | 42091102 | FUSE | 13669 | 20180903 | 704 | 167343 | 302 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 2718 | 38.509 | -122.8869 | 7SPANSLDSIDEOF13669 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0075948 | OH | Sus | 43452904 | No | 2018 | SEP | Yes | Line to Ground | 1375322 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0084428&numberofmonths=24&showchangehistorylog=1 | 18-0084428 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 3897 | 20180928 | 556 | 183114 | 620 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 3100 | 38.5263 | -123.0906 | 2POLESLDSIDEOF38975701KRAMERRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0084428 | OH | Sus | 31410169 | No | 2018 | SEP | Yes | Line to Line | 1381334 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0086729&numberofmonths=24&showchangehistorylog=1 | 18-0086729 | SONOMA | FIELD OPS NORTH | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE | 7123 | 20181004 | 913 | 188135 | 487 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 2362 | 38.6276 | -123.319 | 4SLDSIDEOF7123 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0086729 | OH | Sus | 43496927 | yes | 2018 | OCT | Yes | Line to Line | 1383078 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0087497&numberofmonths=24&showchangehistorylog=1 | 18-0087497 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | RECLOSER | 79306 | 20181005 | 1608 | 189301 | 644 | Distribution Circuit | 3rd Party | Vehicle | 76 | 30009 | 38.3722 | -122.9117 | FUCO10135 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 18-0087497 | OH | Sus | 0 | No | 2018 | OCT | Yes | Three Phase Fault | 1383450 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0090384&numberofmonths=24&showchangehistorylog=1 | 18-0090384 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 4895 | 20181015 | 814 | 195273 | 391 | Distribution Circuit | Vegetation | Tree - fell into line | 151 | 10201 | 38.4116 | -122.9752 | 17200FITZPATRICK | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0090384 | OH | Sus | 0 | No | 2018 | OCT | Yes | Line to Ground | 1385619 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0090444&numberofmonths=24&showchangehistorylog=1 | 18-0090444 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 12035 | 20181015 | 941 | 195402 | 84 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 3948 | 38.4041 | -123.0038 | 17200FITZPATRICK | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0090444 | OH | Sus | 0 | No | 2018 | OCT | Yes | Line to Ground | 1385711 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0091127&numberofmonths=24&showchangehistorylog=1 | 18-0091127 | SONOMA | FIELD OPS NORTH | Tier 3 | CLOVERDALE-1102 | 42821102 | FUSE | 12907 | 20181016 | 1630 | 196726 | 186 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 744 | 38.7756 | -122.8984 | 1SPANLDSIDEFU12907 | Clear-32-90 F | Conductor, Overhead | On Ground | 18-0091127 | OH | Sus | 0 | No | 2018 | OCT | Yes | Line to Line | 1386174 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0096498&numberofmonths=24&showchangehistorylog=1 | 18-0096498 | SONOMA | FIELD OPS NORTH | Tier 2 | SALMON CREEK-1101 | 43161101 | FUSE | 2331 | 20181101 | 2045 | 207229 | 475 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 6650 | 38.3653 | -123.0706 | MTR1010375927 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0096498 | OH | Sus | 31414807 | No | 2018 | NOV | Yes | Line to Ground | 1389921 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0099985&numberofmonths=24&showchangehistorylog=1 | 18-0099985 | SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE | 4367 | 20181115 | 934 | 215810 | 641 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 19 | 12179 | 38.5489 | -123.2445 | Arvig3471cornerofSeaviewrdandBenWyCazadero | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0099985 | OH | Sus | 43540504 | No | 2018 | NOV | Yes | Line to Ground | 1392785 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0102605&numberofmonths=24&showchangehistorylog=1 | 18-0102605 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | OTHER | WIREDOWN | 20181123 | 1430 | 223002 | 245 | Distribution Circuit | Vegetation | Tree - branch fell on line | 133 | 15033 | 38.5055 | -122.9245 | Nott356911025TERRACEDR | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0102605 | OH | Sus | 0 | yes | 2018 | NOV | Yes | Line to Ground | 1394718 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0102580&numberofmonths=24&showchangehistorylog=1 | 18-0102580 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | OTHER | 13817 | 20181123 | 1212 | 222893 | 243 | Distribution Circuit | Vegetation | Tree - branch fell on line | 40 | 9720 | 38.4641 | -123.013 | MTR1007360020 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0102580 | OH | Sus | 0 | yes | 2018 | NOV | Yes | Line to Ground | 1394705 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0102773&numberofmonths=24&showchangehistorylog=1 | 18-0102773 | SONOMA | FIELD OPS NORTH | Tier 3 | FORT ROSS-1121 | 42851121 | FUSE | 10179 | 20181124 | 829 | 223504 | 546 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 1092 | 38.5405 | -123.1103 | 2SPANSLDSIDEOFFUCO10179 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0102773 | OH | Sus | 0 | No | 2018 | NOV | Yes | Line to Line | 1394856 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0102798&numberofmonths=24&showchangehistorylog=1 | 18-0102798 | SONOMA | FIELD OPS NORTH | Tier 3 | FORT ROSS-1121 | 42851121 | FUSE | 2989 | 20181124 | 1230 | 223686 | 495 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 1980 | 38.5324 | -123.1351 | INGRAMJOHN6SPANSLSCO2989 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0102798 | OH | Sus | 0 | No | 2018 | NOV | Yes | Line to Ground | 1394876 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0104118&numberofmonths=24&showchangehistorylog=1 | 18-0104118 | SONOMA | FIELD OPS NORTH | Tier 3 | FORT ROSS-1121 | 42851121 | OTHER | 179993 | 20181127 | 1845 | 226105 | 1186 | Distribution Circuit | Vegetation | Tree - fell into line | 96 | 32544 | 38.539 | -123.118 | 1SPANWOF14363FUSESNOCUSTAFFECTEDFROMWIREDOWN | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0104118 | OH | Sus | 43587192 | yes | 2018 | NOV | Yes | Force Out | 1395680 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0104002&numberofmonths=24&showchangehistorylog=1 | 18-0104002 | SONOMA | FIELD OPS NORTH | Tier 2 | MIRABEL-1101 | 42091101 | FUSE | 6485 | 20181127 | 1504 | 225875 | 646 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 5168 | 38.4668 | -122.9087 | 7040GIOVANETTIRD | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0104002 | OH | Sus | 31416939 | yes | 2018 | NOV | Yes | Line to Ground | 1395616 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0104624&numberofmonths=24&showchangehistorylog=1 | 18-0104624 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 74315 | 20181128 | 2142 | 226993 | 746 | Distribution Circuit | Vegetation | Tree - branch fell on line | 24 | 14076 | 38.491 | -123.063 | MTR1007661080 | Clear-32-90 F | Conductor, Overhead | On Ground | 18-0104624 | OH | Sus | 0 | yes | 2018 | NOV | Yes | Line to Ground | 1395939 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0099363&numberofmonths=24&showchangehistorylog=1 | 18-0099363 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1105 | 42271105 | OTHER | WIREDOWN2SSCGC217683022935TWD634 | 20181201 | 954 | s1397795 | 206 | Distribution Circuit | Equipment Failure/Involved | Overhead | 775 | 22166 | 38.295 | -122.8098 | 2SSOFCGC217683022935TWD634 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 18-0099363 | OH | Sus | 35027438 | yes | 2018 | DEC | Yes | Open Circuit | 1397795 | CSO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0106340&numberofmonths=24&showchangehistorylog=1 | 18-0106340 | SONOMA | FIELD OPS NORTH | Tier 2 | SONOMA-1104 | 42721104 | OTHER | WIREDOWN3SPANSLDSIDEOF16123 | 20181203 | 656 | 232256 | 351 | Distribution Circuit | Equipment Failure/Involved | Overhead | 358 | 89562 | 38.2976 | -122.5365 | 3SPANSLDSIDEOF16123 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 18-0106340 | OH | Sus | 43605110 | No | 2018 | DEC | Yes | Line to Ground | 1397239 | CSO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0107166&numberofmonths=24&showchangehistorylog=1 | 18-0107166 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | JUMPER | 1OF3HOTWIRESDOWN | 20181205 | 551 | 234007 | 708 | Distribution Circuit | Vegetation | Tree - fell into line | 281 | 72284 | 38.4763 | -122.9537 | 10135HWY116 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0107166 | OH | Sus | 43606293 | yes | 2018 | DEC | Yes | Line to Ground | 1397672 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0107951&numberofmonths=24&showchangehistorylog=1 | 18-0107951 | SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | RECLOSER | 5152 | 20181207 | 1435 | 235860 | 854 | Distribution Circuit | 3rd Party | Vehicle | 12 | 10248 | 38.5499 | -122.6678 | 4411PORTERCREEKRD6SPANSSSOF15033 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 18-0107951 | OH | Sus | 0 | No | 2018 | DEC | Yes | Line to Line | 1398296 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0109576&numberofmonths=24&showchangehistorylog=1 | 18-0109576 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 18253 | 20181216 | 2258 | 241875 | 1086 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 29887 | 38.4731 | -123.0241 | MTR1007247410 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0109576 | OH | Sus | 0 | yes | 2018 | DEC | Yes | Three Phase Fault | 1400207 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0109883&numberofmonths=24&showchangehistorylog=1 | 18-0109883 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | JUMPER | WIREDOWN1SPANLDSIDEOF7881 | 20181218 | 1320 | 243082 | 312 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 624 | 38.2759 | -122.8784 | INGRAMJOHN2400FALLONRD | Overcast-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 18-0109883 | OH | Sus | 43617664 | No | 2018 | DEC | Yes | Line to Ground | 1400636 | CSO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0110031&numberofmonths=24&showchangehistorylog=1 | 18-0110031 | SONOMA | FIELD OPS NORTH | Tier 2 | SALMON CREEK-1101 | 43161101 | FUSE | 2331 | 20181219 | 1626 | 244112 | 239 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 3346 | 38.3653 | -123.0706 | 10SPANSLDSIDEOFFUCO2331 | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | On Ground | 18-0110031 | OH | Sus | 43619367 | No | 2018 | DEC | Yes | Line to Ground | 1400882 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0110229&numberofmonths=24&showchangehistorylog=1 | 18-0110229 | SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | RECLOSER | 5152 | 20181221 | 929 | 245012 | 690 | Distribution Circuit | 3rd Party | Vehicle | 12 | 8280 | 38.5499 | -122.6678 | 2LDSIDEOF14389 | Partly Cloudy-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 18-0110229 | OH | Sus | 0 | No | 2018 | DEC | Yes | Three Phase Fault | 1401217 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0110338&numberofmonths=24&showchangehistorylog=1 | 18-0110338 | SONOMA | FIELD OPS NORTH | Tier 2 | MONTE RIO-1111 | 42811111 | FUSE | 13717 | 20181222 | 1242 | 245672 | 476 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 476 | 38.4868 | -123.1389 | 2SPANSLDSIDEOF13717 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0110338 | OH | Sus | 43621075 | No | 2018 | DEC | Yes | Line to Ground | 1401406 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0110510&numberofmonths=24&showchangehistorylog=1 | 18-0110510 | SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE | 8493 | 20181224 | 1401 | 246289 | 850 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 33150 | 38.5329 | -123.2714 | MTR5000024682MTR1005387127 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0110510 | OH | Sus | 0 | yes | 2018 | DEC | Yes | Three Phase Fault | 1401589 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0110540&numberofmonths=24&showchangehistorylog=1 | 18-0110540 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE | 64917 | 20181224 | 1747 | 246431 | 210 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 840 | 38.4682 | -123.0049 | 20791KINGSTONAVE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0110540 | OH | Sus | 0 | yes | 2018 | DEC | Yes | Line to Ground | 1401619 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0110474&numberofmonths=24&showchangehistorylog=1 | 18-0110474 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | OCB | 11132 | 20181224 | 1419 | 246354 | 748 | Distribution Circuit | Vegetation | Tree - fell into line | 4075 | 616898 | 38.4714 | -123.0117 | 16225DRAKESEXT2SPANSLSOSW1015 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0110474 | OH | Sus | 0 | yes | 2018 | DEC | Yes | Line to Line | 1401552 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0110654&numberofmonths=24&showchangehistorylog=1 | 18-0110654 | SONOMA | FIELD OPS NORTH | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE | 7123 | 20181225 | 1017 | 247092 | 1828 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 9140 | 38.6276 | -123.319 | 2SPANSLDSIDEOF7123ONTHESINGLEPHASEOH | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0110654 | OH | Sus | 43621732 | No | 2018 | DEC | Yes | Line to Line | 1401736 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0111090&numberofmonths=24&showchangehistorylog=1 | 18-0111090 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 12035 | 20181229 | 2145 | 249537 | 937 | Distribution Circuit | Equipment Failure/Involved | Overhead | 50 | 46850 | 38.4041 | -123.0038 | 12035 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 18-0111090 | OH | Sus | 43623421 | No | 2018 | DEC | Yes | Line to Ground | 1402309 | CSO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0004800&numberofmonths=24&showchangehistorylog=1 | 19-0004800 | SONOMA | FIELD OPS NORTH | Tier 3 | FORT ROSS-1121 | 42851121 | FUSE | 4523 | 20190105 | 1205 | 253950 | 1695 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 27120 | 38.536 | -123.1405 | 10SPNOFFUCO8971 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0004800 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1403347 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0004717&numberofmonths=24&showchangehistorylog=1 | 19-0004717 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 74315 | 20190105 | 1148 | 253898 | 317 | Distribution Circuit | Vegetation | Tree - branch fell on line | 20 | 6340 | 38.491 | -123.0602 | 2105CAZADEROHWY | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0004717 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1403271 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0004905&numberofmonths=24&showchangehistorylog=1 | 19-0004905 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | JUMPER | WIREDOWN | 20190105 | 1700 | 254726 | 304 | Distribution Circuit | Vegetation | Tree - branch fell on line | 23 | 6277 | 38.4877 | -123.0241 | 1LDOFMTR1010344781 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0004905 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Open Circuit | 1403436 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005630&numberofmonths=24&showchangehistorylog=1 | 19-0005630 | SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 779 | 20190107 | 553 | 258568 | 427 | Distribution Circuit | Vegetation | Tree - branch fell on line | 45 | 19215 | 38.5971 | -122.9894 | 5356PALMERCREEK | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005630 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1404080 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005658&numberofmonths=24&showchangehistorylog=1 | 19-0005658 | SONOMA | FIELD OPS NORTH | Tier 2 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 3539 | 20190107 | 817 | 258598 | 358 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 4654 | 38.6225 | -122.8282 | Nott35693215RIOLINDOAVE | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on object | 19-0005658 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Force Out | 1404097 | CSO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0007176&numberofmonths=24&showchangehistorylog=1 | 19-0007176 | SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | FUSE | 4877 | 20190109 | 2022 | 262074 | 360 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 7920 | 38.3821 | -122.555 | 9100BENNETTVALLEYRD | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0007176 | OH | Sus | 43628608 | yes | 2019 | JAN | Yes | Line to Ground | 1405010 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0006750&numberofmonths=24&showchangehistorylog=1 | 19-0006750 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1101 | 42091101 | FUSE | 1939 | 20190109 | 815 | 261351 | 1965 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 14945 | 38.4782 | -122.9384 | 7SLDSIDEOF1939 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0006750 | OH | Sus | 43628212 | yes | 2019 | JAN | Yes | Line to Ground | 1404806 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0008952&numberofmonths=24&showchangehistorylog=1 | 19-0008952 | SONOMA | FIELD OPS NORTH | Tier 3 | DUNBAR-1101 | 43071101 | FUSE | 15877 | 20190115 | 810 | 265392 | 417 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1668 | 38.4006 | -122.5129 | 1SPANSSOF17849 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0008952 | OH | Sus | 31421981 | yes | 2019 | JAN | Yes | Line to Line | 1406295 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011979&numberofmonths=24&showchangehistorylog=1 | 19-0011979 | SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1101 | 42571101 | TRIP-SAVER | 891 | 20190118 | 1924 | 276277 | 1156 | Distribution Circuit | Vegetation | Tree - branch fell on line | 94 | 16009 | 38.3901 | -122.8854 | MooreS43081175FURLONGRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011979 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1408315 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011745&numberofmonths=24&showchangehistorylog=1 | 19-0011745 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 7697 | 20190118 | 819 | 275325 | 1762 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 14096 | 38.5161 | -123.0648 | 2SPANSSSOFMTR1010252611 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011745 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Three Phase Fault | 1408189 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011674&numberofmonths=24&showchangehistorylog=1 | 19-0011674 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE | 487 | 20190118 | 816 | 275313 | 675 | Distribution Circuit | Vegetation | Tree - branch fell on line | 91 | 61425 | 38.4641 | -123.0115 | 3WAYCORNERFEEDING13839 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011674 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1408157 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0011761&numberofmonths=24&showchangehistorylog=1 | 19-0011761 | SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | FUSE | 6121 | 20190118 | 613 | 275193 | 2122 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 29708 | 38.5399 | -122.6386 | 6200GATESRD | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011761 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1408201 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0012175&numberofmonths=24&showchangehistorylog=1 | 19-0012175 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 4661 | 20190119 | 1937 | 276976 | 1478 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 65032 | 38.5078 | -122.9895 | 15480OLDRIVERRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0012175 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1408527 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0012514&numberofmonths=24&showchangehistorylog=1 | 19-0012514 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | TRIP-SAVER | 999 | 20190120 | 658 | 277101 | 307 | Distribution Circuit | Vegetation | Tree - branch fell on line | 79 | 24253 | 38.422 | -122.954 | 1SPANLOADSIDETOEAST | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0012514 | OH | Sus | 31422641 | yes | 2019 | JAN | Yes | Line to Ground | 1408863 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0016368&numberofmonths=24&showchangehistorylog=1 | 19-0016368 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | RECLOSER | 66006 | 20190131 | 1533 | 284936 | 802 | Distribution Circuit | 3rd Party | Vehicle | 2077 | 489947 | 38.4055 | -122.9478 | 1SPANFROM16575TWDS1617ONMAINLINE | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0016368 | OH | Sus | 0 | No | 2019 | JAN | Yes | Multi-Fault | 1411026 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0016752&numberofmonths=24&showchangehistorylog=1 | 19-0016752 | SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER | 560 | 20190201 | 1830 | 285643 | 1273 | Distribution Circuit | Vegetation | Tree - branch fell on line | 229 | 42451 | 38.5562 | -123.3034 | 3SPANSLDSIDEOF5605SPANSSOURCESIDEOFMTR100886302825050HWY1 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0016752 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1411213 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0017591&numberofmonths=24&showchangehistorylog=1 | 19-0017591 | SONOMA | FIELD OPS NORTH | Tier 2 | GEYSERVILLE-1101 | 42891101 | FUSE | 5531 | 20190203 | 1318 | 289087 | 1523 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 25 | 8875 | 38.6773 | -123.0625 | 1NOFCGC216848037078 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0017591 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1412003 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0026195&numberofmonths=24&showchangehistorylog=1 | 19-0026195 | SONOMA | FIELD OPS NORTH | Tier 2 | MONTE RIO-1111 | 42811111 | FUSE | 7385 | 20190219 | 1444 | 318985 | 521 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 39 | 20319 | 38.4831 | -123.1475 | 1SSOF13717 | Clear-32-90 F | Conductor, Overhead | On Ground | 19-0026195 | OH | Sus | 43682176 | yes | 2019 | FEB | Yes | Line to Ground | 1419042 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0026982&numberofmonths=24&showchangehistorylog=1 | 19-0026982 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | JUMPER | 2SPANSSSMTR1009647577 | 20190221 | 1339 | 320691 | 511 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 1022 | 38.4044 | -122.9491 | MTR1009647577 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0026982 | OH | Sus | 43683462 | yes | 2019 | FEB | Yes | Force Out | 1419474 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0027973&numberofmonths=24&showchangehistorylog=1 | 19-0027973 | SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1101 | 42571101 | TRIP-SAVER | 891 | 20190225 | 1712 | 323376 | 322 | Distribution Circuit | Vegetation | Tree - fell into line | 94 | 19320 | 38.3901 | -122.8854 | 300RYANRANCHRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0027973 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Multi-Fault | 1420084 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0027941&numberofmonths=24&showchangehistorylog=1 | 19-0027941 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 12717 | 20190225 | 1422 | 323197 | 499 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 3992 | 38.4689 | -123.0521 | LDSIDE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0027941 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Multi-Fault | 1420066 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0028045&numberofmonths=24&showchangehistorylog=1 | 19-0028045 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE | 6759 | 20190225 | 2204 | 323590 | 1100 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 25300 | 38.4634 | -123.0122 | 4SPANSLDSIDEOF6759 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028045 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1420155 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0029698&numberofmonths=24&showchangehistorylog=1 | 19-0029698 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1101 | 42091101 | FUSE | 12061 | 20190301 | 938 | 328752 | 1667 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1667 | 38.484 | -122.9147 | 2LDSIDEOFFUCO120618075MARTINELLIRD | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 19-0029698 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Line to Line | 1421270 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0030047&numberofmonths=24&showchangehistorylog=1 | 19-0030047 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 3041 | 20190302 | 943 | 329520 | 391 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 5083 | 38.3811 | -122.9885 | MTR1009712084 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0030047 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Line to Line | 1421533 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0030256&numberofmonths=24&showchangehistorylog=1 | 19-0030256 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1101 | 42091101 | JUMPER | WIREDOWN | 20190303 | 808 | 330095 | 532 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2422 | 38.4654 | -122.9213 | Nott35697220GIOVANETTIRD | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0030256 | OH | Sus | 0 | No | 2019 | MAR | Yes | Line to Ground | 1421713 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0030607&numberofmonths=24&showchangehistorylog=1 | 19-0030607 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | RECLOSER | 132 | 20190304 | 1836 | 331076 | 416 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1019 | 88845 | 38.2647 | -122.8057 | KOTULAJON43432Wof2322FallonTwoRockRD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0030607 | OH | Sus | 43690161 | No | 2019 | MAR | Yes | Multi-Fault | 1421920 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0031021&numberofmonths=24&showchangehistorylog=1 | 19-0031021 | SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER | 6693 | 20190305 | 2205 | 331991 | 1224 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 34008 | 38.5562 | -123.3034 | ATSW4535 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0031021 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Multi-Fault | 1422228 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0030957&numberofmonths=24&showchangehistorylog=1 | 19-0030957 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | JUMPER | OJSAT14520SOLARIDGERD | 20190305 | 1702 | 331716 | 1290 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2956 | 38.5012 | -123.0093 | 14520SOLARIDGERD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0030957 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Line to Ground | 1422083 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0031418&numberofmonths=24&showchangehistorylog=1 | 19-0031418 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1105 | 42271105 | RECLOSER | 634 | 20190306 | 1523 | 333052 | 298 | Distribution Circuit | Equipment Failure/Involved | Overhead | 50 | 9175 | 38.2982 | -122.8208 | INGRAM42533SPANSLSCO4021ONMAINLINE | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0031418 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Line to Ground | 1422369 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0031178&numberofmonths=24&showchangehistorylog=1 | 19-0031178 | SONOMA | FIELD OPS NORTH | Tier 3 | FORT ROSS-1121 | 42851121 | FUSE | 4523 | 20190306 | 238 | 332320 | 873 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 13968 | 38.536 | -123.1405 | 4LDSIDEOFFUSES | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0031178 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Multi-Fault | 1422239 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0031066&numberofmonths=24&showchangehistorylog=1 | 19-0031066 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | TRIP-SAVER | 7401 | 20190306 | 10 | 332044 | 655 | Distribution Circuit | Vegetation | Tree - fell into line | 66 | 43230 | 38.5037 | -122.9487 | 16115TWD12997 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0031066 | OH | Sus | 43690689 | yes | 2019 | MAR | Yes | Line to Line | 1422176 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0031043&numberofmonths=24&showchangehistorylog=1 | 19-0031043 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | RECLOSER | 320 | 20190306 | 12 | 332049 | 803 | Distribution Circuit | Vegetation | Tree - fell into line | 147 | 118041 | 38.4989 | -123.0211 | 15105OLDCAZADEROHWY | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0031043 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Line to Ground | 1422154 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0031046&numberofmonths=24&showchangehistorylog=1 | 19-0031046 | SONOMA | FIELD OPS NORTH | Tier 2 | SALMON CREEK-1101 | 43161101 | OTHER | WIREDOWNBET14079REG11047 | 20190306 | 17 | 332067 | 828 | Distribution Circuit | Equipment Failure/Involved | Overhead | 193 | 86639 | 38.3448 | -123.0184 | BETWEENFUCO14079REGS11047 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0031046 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Force Out | 1422157 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0031891&numberofmonths=24&showchangehistorylog=1 | 19-0031891 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | RECLOSER | 132 | 20190308 | 615 | 334071 | 339 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1019 | 213505 | 38.2647 | -122.8057 | Kikuchi22725488MiddleRdFallon | Partly Cloudy-Fog-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0031891 | OH | Sus | 43692407 | No | 2019 | MAR | Yes | Line to Ground | 1422702 | CSO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0033176&numberofmonths=24&showchangehistorylog=1 | 19-0033176 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1105 | 42271105 | RECLOSER | 616 | 20190312 | 1740 | 337800 | 1268 | Distribution Circuit | Vegetation | Tree - branch fell on line | 224 | 59142 | 38.3102 | -122.8518 | DeignanPat357117400VALLEYFORDRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0033176 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Line to Ground | 1423638 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0032881&numberofmonths=24&showchangehistorylog=1 | 19-0032881 | SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | RECLOSER | 861496 | 20190312 | 729 | 336788 | 666 | Distribution Circuit | Vegetation | Tree - branch fell on line | 90 | 29751 | 38.358 | -122.5256 | 2600LONDONRANCHRDJACKLONDONSTATEPARK | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0032881 | OH | Sus | 31428568 | yes | 2019 | MAR | Yes | Line to Ground | 1423455 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0033120&numberofmonths=24&showchangehistorylog=1 | 19-0033120 | SONOMA | FIELD OPS NORTH | Tier 2 | MIRABEL-1102 | 42091102 | FUSE | 13669 | 20190312 | 1414 | 337355 | 395 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 3555 | 38.509 | -122.8869 | Rendon47547SPANSLOADSIDECO13669 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0033120 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Three Phase Fault | 1423602 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0033221&numberofmonths=24&showchangehistorylog=1 | 19-0033221 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | TRIP-SAVER | 841 | 20190312 | 1858 | 337929 | 1092 | Distribution Circuit | Vegetation | Tree - fell into line | 133 | 18871 | 38.5087 | -122.9261 | MTR1007934935 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0033221 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Line to Line | 1423680 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0033188&numberofmonths=24&showchangehistorylog=1 | 19-0033188 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | JUMPER | WIREDOWN | 20190312 | 1823 | 337676 | 1185 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 13035 | 38.5423 | -123.0016 | 2SSOFMTR1009125135 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0033188 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Open Circuit | 1423650 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0035334&numberofmonths=24&showchangehistorylog=1 | 19-0035334 | SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE | 4543 | 20190320 | 620 | 343433 | 474 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 4740 | 38.5893 | -123.3034 | 34285KRUSERANCHRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0035334 | OH | Sus | 43712011 | yes | 2019 | MAR | Yes | Line to Line | 1425288 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0036204&numberofmonths=24&showchangehistorylog=1 | 19-0036204 | SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER | 134 | 20190322 | 1720 | 345501 | 1269 | Distribution Circuit | Vegetation | Tree - fell into line | 229 | 290601 | 38.5588 | -123.2702 | 22400TIMBERCOVERD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0036204 | OH | Sus | 43714490 | No | 2019 | MAR | Yes | Line to Ground | 1425755 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0036248&numberofmonths=24&showchangehistorylog=1 | 19-0036248 | SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1101 | 42571101 | RECLOSER | 322 | 20190322 | 2323 | 345622 | 982 | Distribution Circuit | Vegetation | Tree - fell into line | 375 | 27672 | 38.3868 | -122.8901 | DOEDINGD241111266BODEGAHWY | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0036248 | OH | Sus | 31430272 | No | 2019 | MAR | Yes | Line to Ground | 1425800 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0039053&numberofmonths=24&showchangehistorylog=1 | 19-0039053 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 17803 | 20190402 | 617 | 352120 | 943 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 7544 | 38.5216 | -123.0968 | MTR1009059338 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0039053 | OH | Sus | 43726355 | yes | 2019 | APR | Yes | Line to Line | 1427812 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0040219&numberofmonths=24&showchangehistorylog=1 | 19-0040219 | SONOMA | FIELD OPS NORTH | Tier 2 | CLOVERDALE-1102 | 42821102 | RECLOSER | 156 | 20190405 | 1834 | 354626 | 843 | Distribution Circuit | 3rd Party | Vehicle | 590 | 204502 | 38.7991 | -122.9913 | MTR1009945504 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0040219 | OH | Sus | 0 | No | 2019 | APR | Yes | Line to Ground | 1428509 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0041464&numberofmonths=24&showchangehistorylog=1 | 19-0041464 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 1043 | 20190410 | 2034 | 358486 | 348 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 696 | 38.5068 | -122.915 | LASTSPANONTAP | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0041464 | OH | Sus | 43736603 | yes | 2019 | APR | Yes | Line to Line | 1429522 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0042307&numberofmonths=24&showchangehistorylog=1 | 19-0042307 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 4619 | 20190414 | 1058 | 360508 | 394 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 2758 | 38.4867 | -123.015 | 1SPANLDSIDEOF4619 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0042307 | OH | Sus | 43738669 | No | 2019 | APR | Yes | Line to Ground | 1430151 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0043092&numberofmonths=24&showchangehistorylog=1 | 19-0043092 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | OTHER | WIREDOWNSS3891 | 20190417 | 626 | 362260 | 602 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 43786 | 38.5158 | -123.065 | SSOF3891 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0043092 | OH | Sus | 43742413 | No | 2019 | APR | Yes | Line to Ground | 1430638 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0044402&numberofmonths=24&showchangehistorylog=1 | 19-0044402 | SONOMA | FIELD OPS NORTH | Tier 2 | GEYSERVILLE-1102 | 42891102 | FUSE | 2273 | 20190419 | 1138 | 363815 | 1434 | Distribution Circuit | Vegetation | Tree - branch fell on line | 22 | 31548 | 38.736 | -122.8364 | 13SPANSLDSIDEOFFUSES | Partly Cloudy-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0044402 | OH | Sus | 31434962 | No | 2019 | APR | Yes | Multi-Fault | 1431587 | CAW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0046198&numberofmonths=24&showchangehistorylog=1 | 19-0046198 | SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | RECLOSER | 261774 | 20190425 | 1325 | 368152 | 1133 | Distribution Circuit | Vegetation | Tree - fell into line | 185 | 47067 | 38.3787 | -122.5531 | DOEDINGD24115761SONOMAMTNRD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0046198 | OH | Sus | 0 | No | 2019 | APR | Yes | Line to Ground | 1432849 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0048491&numberofmonths=24&showchangehistorylog=1 | 19-0048491 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | OTHER | WIREDOWN1NOFTSV999 | 20190502 | 2349 | 372747 | 1080 | Distribution Circuit | Vegetation | Tree - fell into line | 386 | 398448 | 38.4225 | -122.9543 | 1POLENOFTRIPSAVER999ONTHEMAINLINE | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0048491 | OH | Sus | 0 | No | 2019 | MAY | Yes | Line to Ground | 1434256 | PW | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0048689&numberofmonths=24&showchangehistorylog=1 | 19-0048689 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1101 | 42571101 | FUSE | 13545 | 20190503 | 1242 | 373271 | 361 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 361 | 38.3856 | -122.9033 | LDSIDEOF13545 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0048689 | OH | Sus | 0 | No | 2019 | MAY | Yes | Line to Ground | 1434421 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0052336&numberofmonths=24&showchangehistorylog=1 | 19-0052336 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | FUSE | 4571 | 20190515 | 2136 | 381338 | 1134 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2268 | 38.1681 | -122.8937 | MOOREDAVE36127SPANLOADSIDE4571 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0052336 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Line to Ground | 1436978 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0052294&numberofmonths=24&showchangehistorylog=1 | 19-0052294 | SONOMA | FIELD OPS NORTH | Tier 3 | DUNBAR-1102 | 43071102 | FUSE | 13499 | 20190515 | 1731 | 381292 | 1199 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 8393 | 38.3959 | -122.472 | 2LDSIDEOF13499 | Partly Cloudy-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0052294 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Multi-Fault | 1436935 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0052045&numberofmonths=24&showchangehistorylog=1 | 19-0052045 | SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 769 | 20190515 | 902 | 380638 | 353 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 10590 | 38.5963 | -122.9146 | 3000WALLACECREEKRD | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0052045 | OH | Sus | 31440370 | yes | 2019 | MAY | Yes | Line to Line | 1436809 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0052480&numberofmonths=24&showchangehistorylog=1 | 19-0052480 | SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | OTHER | WIREDOWN5PSSOFCGC217282033175 | 20190515 | 2131 | 381716 | 741 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 27780 | 38.5731 | -122.9595 | 5PSSOFCGC217272033175 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0052480 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Line to Ground | 1437125 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0052320&numberofmonths=24&showchangehistorylog=1 | 19-0052320 | SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER | 560 | 20190515 | 2022 | 381450 | 985 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 26595 | 38.5562 | -123.3034 | 23350HWY12SPANSLDSIDEOFLR560 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0052320 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Line to Ground | 1436963 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0052153&numberofmonths=24&showchangehistorylog=1 | 19-0052153 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 12997 | 20190515 | 1217 | 380874 | 358 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 1618 | 38.5031 | -122.9544 | 1ST3RDSPANLDSIDEOF12995 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0052153 | OH | Sus | 43781826 | yes | 2019 | MAY | Yes | Line to Line | 1436873 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0052350&numberofmonths=24&showchangehistorylog=1 | 19-0052350 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 12997 | 20190515 | 2041 | 381400 | 935 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 12155 | 38.5031 | -122.9544 | EOL | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0052350 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Multi-Fault | 1436992 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0052286&numberofmonths=24&showchangehistorylog=1 | 19-0052286 | SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1101 | 42571101 | FUSE | 18581 | 20190515 | 1716 | 381156 | 235 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 1410 | 38.3843 | -122.8765 | 1715WSEXTONRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0052286 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Line to Ground | 1436930 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0052456&numberofmonths=24&showchangehistorylog=1 | 19-0052456 | SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1101 | 42571101 | FUSE | 5831 | 20190515 | 2117 | 381504 | 1248 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 8736 | 38.3724 | -122.8716 | 4SPANSLDSIDEOFFUCO58311815SEXTONRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0052456 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Line to Line | 1437101 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0052984&numberofmonths=24&showchangehistorylog=1 | 19-0052984 | SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 6217 | 20190516 | 1451 | 382658 | 1411 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 6378 | 38.5868 | -122.9279 | 1STPOLEOFFTAPFEEDING17003 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0052984 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Line to Line | 1437383 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0053028&numberofmonths=24&showchangehistorylog=1 | 19-0053028 | SONOMA | FIELD OPS NORTH | Tier 3 | FULTON-1107 | 42561107 | FUSE | 649 | 20190516 | 2050 | 383027 | 1063 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 4252 | 38.5498 | -122.7115 | 2SLDSIDEOF649 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0053028 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Line to Ground | 1437419 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0052879&numberofmonths=24&showchangehistorylog=1 | 19-0052879 | SONOMA | FIELD OPS NORTH | Tier 2 | GEYSERVILLE-1101 | 42891101 | FUSE | 5531 | 20190516 | 1430 | 382616 | 357 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 7157 | 38.6773 | -123.0625 | Nott35699SPANSLOADSIDE12501SKAGGSSPRINGSRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0052879 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Line to Ground | 1437334 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0053682&numberofmonths=24&showchangehistorylog=1 | 19-0053682 | SONOMA | FIELD OPS NORTH | Tier 2 | MIRABEL-1101 | 42091101 | FUSE | 1003 | 20190518 | 1508 | 384343 | 742 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 46272 | 38.4763 | -122.9069 | 8350MARTINELLIRD | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0053682 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Line to Ground | 1437906 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0053638&numberofmonths=24&showchangehistorylog=1 | 19-0053638 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER | 256 | 20190518 | 1119 | 384193 | 566 | Distribution Circuit | Vegetation | Tree - fell into line | 1592 | 143726 | 38.4698 | -123.0145 | 3SPANSEOFSW7521 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0053638 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Three Phase Fault | 1437882 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0053896&numberofmonths=24&showchangehistorylog=1 | 19-0053896 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 669275 | 20190519 | 833 | 384977 | 615 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 5535 | 38.4105 | -122.9493 | 14500GRATONRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0053896 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Line to Ground | 1438107 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0054150&numberofmonths=24&showchangehistorylog=1 | 19-0054150 | SONOMA | FIELD OPS NORTH | Tier 2 | CLOVERDALE-1102 | 42821102 | RECLOSER | 262 | 20190520 | 110 | 385716 | 866 | Distribution Circuit | Equipment Failure/Involved | Overhead | 359 | 99419 | 38.7977 | -122.991 | MAINLINE1SPANNOFFUCO15675 | Clear-32-90 F | Pole-Wood | Broken, wire on object | 19-0054150 | OH | Sus | 0 | No | 2019 | MAY | Yes | Multi-Fault | 1438348 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0054664&numberofmonths=24&showchangehistorylog=1 | 19-0054664 | SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | TRIP-SAVER | 6751 | 20190521 | 6 | 386610 | 794 | Distribution Circuit | Vegetation | Tree - fell into line | 134 | 26473 | 38.592 | -122.9622 | FUCO10905 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0054664 | OH | Sus | 31443410 | yes | 2019 | MAY | Yes | Line to Ground | 1438695 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0054678&numberofmonths=24&showchangehistorylog=1 | 19-0054678 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | RECLOSER | 38514 | 20190521 | 600 | 386640 | 580 | Distribution Circuit | Vegetation | Tree - fell into line | 547 | 181630 | 38.5056 | -122.9307 | ATFUCO2103 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0054678 | OH | Sus | 43790709 | yes | 2019 | MAY | Yes | Multi-Fault | 1438704 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0062328&numberofmonths=24&showchangehistorylog=1 | 19-0062328 | SONOMA | FIELD OPS NORTH | Tier 3 | FULTON-1107 | 42561107 | RECLOSER | 214 | 20190604 | 531 | 397039 | 322 | Distribution Circuit | Equipment Failure/Involved | Overhead | 397 | 67215 | 38.5031 | -122.7355 | DOEDINGD24111990markwestspringrd | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0062328 | OH | Sus | 31450708 | yes | 2019 | JUN | Yes | Line to Line | 1445053 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0064293&numberofmonths=24&showchangehistorylog=1 | 19-0064293 | SONOMA | FIELD OPS NORTH | Tier 2 | GEYSERVILLE-1102 | 42891102 | OTHER | 732035 | 20190607 | 1310 | 400775 | 721 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 4326 | 38.693 | -122.8855 | 13SPANSLDSIDEOF732035 | Clear-32-90 F | Conductor, Overhead | On Ground | 19-0064293 | OH | Sus | 0 | yes | 2019 | JUN | Yes | Line to Ground | 1446494 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0065733&numberofmonths=24&showchangehistorylog=1 | 19-0065733 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | OTHER | WIREDOWNMAINLINE26150HWY1 | 20190611 | 606 | 405019 | 306 | Distribution Circuit | Vegetation | Tree - branch fell on line | 149 | 45571 | 38.237 | -122.9056 | MAINLINEPASTFIRSTHARDTAPLDSIDEOFLR148 | Partly Cloudy-32-90 F | Conductor, Overhead | On Ground | 19-0065733 | OH | Sus | 0 | yes | 2019 | JUN | Yes | Open Circuit | 1447875 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0072290&numberofmonths=24&showchangehistorylog=1 | 19-0072290 | SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | OCB | 11212 | 20190626 | 1301 | 429784 | 423 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 639 | 111069 | 38.5408 | -123.2237 | 2559 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0072290 | OH | Sus | 31455526 | No | 2019 | JUN | Yes | Line to Ground | 1452889 | CAW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0074656&numberofmonths=24&showchangehistorylog=1 | 19-0074656 | SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1102 | 42571102 | RECLOSER | 658 | 20190704 | 2000 | 441126 | 481 | Distribution Circuit | Vegetation | Tree - fell into line | 131 | 63011 | 38.4451 | -122.9104 | ATFUCO12153ONMAINLINE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0074656 | OH | Sus | 43867987 | No | 2019 | JUL | Yes | Line to Ground | 1454364 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0074675&numberofmonths=24&showchangehistorylog=1 | 19-0074675 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER | 64758 | 20190705 | 352 | 441198 | 622 | Distribution Circuit | Vegetation | Tree - fell into line | 282 | 72328 | 38.5089 | -123.0696 | Arvig347118595KingRidgerdCazadero | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0074675 | OH | Sus | 43867994 | No | 2019 | JUL | Yes | Multi-Fault | 1454386 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0077351&numberofmonths=24&showchangehistorylog=1 | 19-0077351 | SONOMA | FIELD OPS NORTH | Tier 2 | SONOMA-1104 | 42721104 | JUMPER | WIREDOWN1SPANSSOF950789TWDEAST | 20190715 | 749 | 450516 | 427 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2348 | 38.3266 | -122.568 | 1SPANSOURCESIDESB950789 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0077351 | OH | Sus | 43879274 | No | 2019 | JUL | Yes | Line to Ground | 1456283 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0079444&numberofmonths=24&showchangehistorylog=1 | 19-0079444 | SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | FUSE | 13193 | 20190720 | 928 | 462890 | 283 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 1698 | 38.538 | -122.6472 | 325BODMERLN | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0079444 | OH | Sus | 43890719 | No | 2019 | JUL | Yes | Line to Line | 1457563 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0081895&numberofmonths=24&showchangehistorylog=1 | 19-0081895 | SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | FUSE | 2269 | 20190728 | 49 | 473714 | 1106 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 26544 | 38.5183 | -122.6032 | KIKUCHI22728100TarwaterRdNealCreekRd | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0081895 | OH | Sus | 43899665 | No | 2019 | JUL | Yes | Line to Line | 1459187 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0086913&numberofmonths=24&showchangehistorylog=1 | 19-0086913 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE | 6759 | 20190812 | 1210 | 503677 | 296 | Distribution Circuit | Vegetation | Tree - fell into line | 150 | 8205 | 38.4634 | -123.0122 | 9725MAINST | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0086913 | OH | Sus | 43919153 | No | 2019 | AUG | Yes | Line to Line | 1462464 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0087094&numberofmonths=24&showchangehistorylog=1 | 19-0087094 | SONOMA | FIELD OPS NORTH | Tier 2 | RINCON-1103 | 43321103 | OCB | 11032 | 20190812 | 2112 | 504768 | 411 | Distribution Circuit | 3rd Party | Vehicle | 2302 | 165663 | 38.4901 | -122.6661 | FUCO14017 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0087094 | OH | Sus | 0 | No | 2019 | AUG | Yes | Three Phase Fault | 1462529 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0090865&numberofmonths=24&showchangehistorylog=1 | 19-0090865 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 433 | 20190822 | 928 | 530707 | 938 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 30954 | 38.5091 | -122.9283 | 12300WESTSIDERD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0090865 | OH | Sus | 43933640 | No | 2019 | AUG | Yes | Line to Line | 1465065 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0091633&numberofmonths=24&showchangehistorylog=1 | 19-0091633 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | TRIP-SAVER | 1991 | 20190823 | 1511 | 534716 | 603 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 30753 | 38.5445 | -122.9849 | 19000SWEETWATERMTR1009796848 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0091633 | OH | Sus | 43937498 | No | 2019 | AUG | Yes | Multi-Fault | 1465414 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0094251&numberofmonths=24&showchangehistorylog=1 | 19-0094251 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 801 | 20190830 | 1751 | 549224 | 328 | Distribution Circuit | Vegetation | Tree - fell into line | 111 | 36408 | 38.5165 | -122.9962 | 17300WATSONRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0094251 | OH | Sus | 43942854 | No | 2019 | AUG | Yes | Line to Line | 1466920 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0095841&numberofmonths=24&showchangehistorylog=1 | 19-0095841 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1101 | 42091101 | FUSE | 1593 | 20190905 | 1900 | 556913 | 804 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 3216 | 38.4742 | -122.9221 | MTR1009127372 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0095841 | OH | Sus | 0 | No | 2019 | SEP | Yes | None | 1467982 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0096476&numberofmonths=24&showchangehistorylog=1 | 19-0096476 | SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | RECLOSER | 903030 | 20190907 | 1736 | 562175 | 468 | Distribution Circuit | 3rd Party | Vehicle | 22 | 10296 | 38.382 | -122.5549 | 9050BENNETTVALLEYRD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0096476 | OH | Sus | 0 | yes | 2019 | SEP | Yes | Line to Ground | 1468388 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0096473&numberofmonths=24&showchangehistorylog=1 | 19-0096473 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 12997 | 20190907 | 1700 | 562147 | 825 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 7667 | 38.5031 | -122.9544 | 2SPANSLOADSIDE12997 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0096473 | OH | Sus | 0 | yes | 2019 | SEP | Yes | Line to Line | 1468384 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0096900&numberofmonths=24&showchangehistorylog=1 | 19-0096900 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 12029 | 20190909 | 1253 | 564574 | 457 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 5484 | 38.3943 | -122.9647 | 1009911436 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0096900 | OH | Sus | 31471181 | No | 2019 | SEP | Yes | Line to Line | 1468760 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0098493&numberofmonths=24&showchangehistorylog=1 | 19-0098493 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1101 | 42091101 | FUSE | 1595 | 20190912 | 1846 | 576529 | 469 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2345 | 38.477 | -122.9333 | 1STPOLELDSIDEOF1595 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0098493 | OH | Sus | 0 | No | 2019 | SEP | Yes | Line to Line | 1469626 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0099273&numberofmonths=24&showchangehistorylog=1 | 19-0099273 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 6175 | 20190915 | 1744 | 583416 | 1561 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 3122 | 38.5093 | -122.9878 | 3SPANSLOADSIDEOF6175 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0099273 | OH | Sus | 31471783 | No | 2019 | SEP | Yes | Line to Ground | 1470159 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0099397&numberofmonths=24&showchangehistorylog=1 | 19-0099397 | SONOMA | FIELD OPS NORTH | Tier 2 | SANTA ROSA A-1111 | 42151111 | OTHER | WIREDOWN4324MTTAYLORRD | 20190916 | 719 | 583937 | 807 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 59231 | 38.4207 | -122.6759 | ATCUTOUTS58425WIREDOWN4324MTTAYLORRD | Partly Cloudy-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0099397 | OH | Sus | 0 | yes | 2019 | SEP | Yes | Open Circuit | 1470270 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0102853&numberofmonths=24&showchangehistorylog=1 | 19-0102853 | SONOMA | FIELD OPS NORTH | Tier 2 | GEYSERVILLE-1101 | 42891101 | FUSE | 5531 | 20190924 | 627 | 608093 | 711 | Distribution Circuit | 3rd Party | Vehicle | 25 | 9853 | 38.6773 | -123.0625 | 2EOF9485 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0102853 | OH | Sus | 0 | No | 2019 | SEP | Yes | Three Phase Fault | 1472351 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0105006&numberofmonths=24&showchangehistorylog=1 | 19-0105006 | SONOMA | FIELD OPS NORTH | Tier 2 | FULTON-1102 | 42561102 | FUSE | 751 | 20190928 | 1517 | 627800 | 333 | Distribution Circuit | Vegetation | Tree - branch fell on line | 35 | 11655 | 38.6311 | -122.77 | 2LDSIDEOFCGC217831935454 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0105006 | OH | Sus | 0 | yes | 2019 | SEP | Yes | Line to Ground | 1473781 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0104964&numberofmonths=24&showchangehistorylog=1 | 19-0104964 | SONOMA | FIELD OPS NORTH | Tier 2 | MIRABEL-1101 | 42091101 | FUSE | 15423 | 20190928 | 1047 | 626035 | 581 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 581 | 38.4734 | -122.9015 | 1SPANLDSIDEOFFUCO15423 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0104964 | OH | Sus | 0 | yes | 2019 | SEP | Yes | Line to Ground | 1473748 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0105272&numberofmonths=24&showchangehistorylog=1 | 19-0105272 | SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE | 4537 | 20190929 | 2056 | 629460 | 1058 | Distribution Circuit | Equipment Failure/Involved | Overhead | 39 | 11856 | 38.5247 | -123.2648 | 1SPLDSIDEOFCOUT4537 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0105272 | OH | Sus | 43973890 | No | 2019 | SEP | Yes | Line to Line | 1474004 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0112113&numberofmonths=24&showchangehistorylog=1 | 19-0112113 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | FUSE | 14413 | 20191015 | 2152 | 659986 | 457 | Distribution Circuit | Animal | Bird found | 5 | 2285 | 38.2702 | -122.7834 | 3SPANSSOUTHFOFUCO14413 | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0112113 | OH | Sus | 0 | No | 2019 | OCT | Yes | Line to Ground | 1480298 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0118244&numberofmonths=24&showchangehistorylog=1 | 19-0118244 | SONOMA | FIELD OPS NORTH | Tier 2 | SONOMA-1104 | 42721104 | FUSE | 9667 | 20191028 | 2055 | 692622 | 1360 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 5440 | 38.2862 | -122.5456 | 7SPANSLDSIDEOF9667 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0118244 | OH | Sus | 0 | yes | 2019 | OCT | Yes | Line to Ground | 1487251 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0119903&numberofmonths=24&showchangehistorylog=1 | 19-0119903 | SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1101 | 43071101 | OTHER | WIREDOWN10453SLATTERYRD | 20191101 | 844 | 697294 | 734 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 18208 | 38.3957 | -122.5442 | 10453 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0119903 | OH | Sus | 0 | No | 2019 | NOV | Yes | Force Out | 1488674 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0125541&numberofmonths=24&showchangehistorylog=1 | 19-0125541 | SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1109 | 42631109 | FUSE | 2607 | 20191117 | 2334 | 708862 | 460 | Distribution Circuit | 3rd Party | Vehicle | 56 | 25760 | 38.1901 | -122.6621 | 4665 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0125541 | OH | Sus | 0 | No | 2019 | NOV | Yes | Line to Line | 1491988 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0131419&numberofmonths=24&showchangehistorylog=1 | 19-0131419 | SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER | 134 | 20191130 | 1338 | 724304 | 443 | Distribution Circuit | Vegetation | Tree - fell into line | 232 | 48508 | 38.5588 | -123.2702 | BETWEEN950369993 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0131419 | OH | Sus | 0 | yes | 2019 | NOV | Yes | Force Out | 1496120 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0133684&numberofmonths=24&showchangehistorylog=1 | 19-0133684 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 4663 | 20191204 | 2223 | 730171 | 893 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 7144 | 38.4983 | -122.9937 | 16455NEELYRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0133684 | OH | Sus | 44112689 | yes | 2019 | DEC | Yes | Line to Ground | 1497754 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0134854&numberofmonths=24&showchangehistorylog=1 | 19-0134854 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1101 | 42091101 | TRIP-SAVER | 4859 | 20191207 | 1320 | 732850 | 275 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 13200 | 38.4755 | -122.9527 | LDSIDEOF4859 | Rain | Conductor, Overhead | Broken, wire on ground | 19-0134854 | OH | Sus | 0 | yes | 2019 | DEC | Yes | Multi-Fault | 1498654 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0134662&numberofmonths=24&showchangehistorylog=1 | 19-0134662 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 1955 | 20191207 | 105 | 732105 | 801 | Distribution Circuit | Vegetation | Tree - fell into line | 161 | 128961 | 38.3879 | -122.9715 | RO2807JOYRD | Overcast-Fog-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0134662 | OH | Sus | 0 | yes | 2019 | DEC | Yes | Line to Ground | 1498414 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0135069&numberofmonths=24&showchangehistorylog=1 | 19-0135069 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 1997 | 20191208 | 1607 | 733944 | 424 | Distribution Circuit | Vegetation | Tree - fell into line | 112 | 47488 | 38.502 | -123.0239 | Nott356915607OLDCAZADERORD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0135069 | OH | Sus | 44115438 | No | 2019 | DEC | Yes | Line to Line | 1498874 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0136527&numberofmonths=24&showchangehistorylog=1 | 19-0136527 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 2027 | 20191214 | 36 | 738854 | 549 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 14823 | 38.5191 | -122.98 | 14734EAGLESNESTLANE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0136527 | OH | Sus | 44122670 | No | 2019 | DEC | Yes | Line to Ground | 1500529 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0004544&numberofmonths=24&showchangehistorylog=1 | 20-0004544 | SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1108 | 42631108 | OTHER | WIREDOWNSSMTR1005515502 | 20200102 | 1314 | 753833 | 247 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 757 | 38.2666 | -122.7246 | SSOFMTR1005515502 | Partly Cloudy-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 20-0004544 | OH | Sus | 44143173 | No | 2020 | JAN | Yes | Open Circuit | 1503829 | CSO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0008362&numberofmonths=24&showchangehistorylog=1 | 20-0008362 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1105 | 42271105 | OTHER | WIREDOWNLR213984 | 20200114 | 615 | 760582 | 700 | Distribution Circuit | 3rd Party | Vehicle | 799 | 219087 | 38.2986 | -122.8223 | SWPOLE1605IMMEDIATELYWOFLR213894 | Partly Cloudy-Fog-32-90 F | Pole-Wood | Broken, wire on ground | 20-0008362 | OH | Sus | 44155347 | No | 2020 | JAN | Yes | Line to Ground | 1506094 | PW | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0014789&numberofmonths=24&showchangehistorylog=1 | 20-0014789 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | OCB | 11132 | 20200129 | 641 | 772282 | 573 | Distribution Circuit | Vegetation | Tree - fell into line | 3919 | 925170 | 38.4714 | -123.0117 | DOEDINGD241117620hwy116 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0014789 | OH | Sus | 0 | No | 2020 | JAN | Yes | Line to Ground | 1509946 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0016080&numberofmonths=24&showchangehistorylog=1 | 20-0016080 | SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 3903 | 20200131 | 1830 | 774693 | 585 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1170 | 38.6019 | -123.0033 | 3RDAND5THPOLELDSIDEOFFUCO3903 | Partly Cloudy-32-90 F | Crossarm, Wood | Broken, wire on ground | 20-0016080 | OH | Sus | 31488336 | No | 2020 | JAN | Yes | Line to Ground | 1510856 | CAW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0016366&numberofmonths=24&showchangehistorylog=1 | 20-0016366 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | JUMPER | WIREDOWN1SPANSSOF6493 | 20200202 | 1602 | 775992 | 352 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2022 | 38.5194 | -122.958 | 1SPANSSOF6493 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0016366 | OH | Sus | 44175142 | yes | 2020 | FEB | Yes | Line to Ground | 1511130 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0016440&numberofmonths=24&showchangehistorylog=1 | 20-0016440 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1105 | 42271105 | RECLOSER | 616 | 20200203 | 608 | 776169 | 495 | Distribution Circuit | 3rd Party | Vehicle | 225 | 69571 | 38.3102 | -122.8518 | NOONAN346913800HWY1VALLEYFORD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0016440 | OH | Sus | 0 | No | 2020 | FEB | Yes | Line to Ground | 1511196 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0017902&numberofmonths=24&showchangehistorylog=1 | 20-0017902 | SONOMA | FIELD OPS NORTH | Tier 3 | FULTON-1107 | 42561107 | FUSE | 14593 | 20200206 | 433 | 778902 | 462 | Distribution Circuit | 3rd Party | Vehicle | 9 | 4158 | 38.5183 | -122.7205 | 1PSOF14593 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0017902 | OH | Sus | 0 | No | 2020 | FEB | Yes | Line to Line | 1512222 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0024981&numberofmonths=24&showchangehistorylog=1 | 20-0024981 | SONOMA | FIELD OPS NORTH | Tier 2 | GEYSERVILLE-1102 | 42891102 | FUSE | 523 | 20200222 | 2112 | 800864 | 302 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 8555 | 38.6573 | -122.8317 | FIRSTSPANLOADSIDEFUCO523 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 20-0024981 | OH | Sus | 44208080 | No | 2020 | FEB | Yes | Line to Ground | 1517113 | CSO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0025171&numberofmonths=24&showchangehistorylog=1 | 20-0025171 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1101 | 42091101 | OTHER | WIREDOWNONGUYWIRE | 20200224 | 936 | 802457 | 306 | Distribution Circuit | Vegetation | Tree - branch fell on line | 107 | 31962 | 38.4771 | -122.9557 | 1WOF8591 | Clear-32-90 F | Other | Broken, wire on object | 20-0025171 | OH | Sus | 0 | No | 2020 | FEB | Yes | Open Circuit | 1517314 | NON | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0036610&numberofmonths=24&showchangehistorylog=1 | 20-0036610 | SONOMA | FIELD OPS NORTH | Tier 2 | FITCH MOUNTAIN-1113 | 42751113 | RECLOSER | 24550 | 20200327 | 949 | 868253 | 419 | Distribution Circuit | 3rd Party | Vehicle | 220 | 49449 | 38.5793 | -122.878 | CGC217513332799 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on object | 20-0036610 | OH | Sus | 0 | No | 2020 | MAR | Yes | Line to Line | 1524206 | PW | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0038407&numberofmonths=24&showchangehistorylog=1 | 20-0038407 | SONOMA | FIELD OPS NORTH | Tier 3 | CLOVERDALE-1102 | 42821102 | FUSE | 6953 | 20200404 | 1123 | 882264 | 374 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 5236 | 38.772 | -122.9619 | MTR1009074665 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0038407 | OH | Sus | 44281564 | No | 2020 | APR | Yes | Line to Ground | 1525243 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0046525&numberofmonths=24&showchangehistorylog=1 | 20-0046525 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | OCB | 11032 | 20200501 | 2042 | 905621 | 802 | Distribution Circuit | Animal | Bird found | 1460 | 233968 | 38.3098 | -122.7316 | SSSPANTOSW6589 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0046525 | OH | Sus | 44308068 | No | 2020 | MAY | Yes | Line to Line | 1530297 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0046620&numberofmonths=24&showchangehistorylog=1 | 20-0046620 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | FUSE | 2439 | 20200502 | 1517 | 905875 | 400 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 800 | 38.2165 | -122.9231 | BETDILLONBEACHRDHWY1 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0046620 | OH | Sus | 31501777 | No | 2020 | MAY | Yes | Line to Ground | 1530383 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0046772&numberofmonths=24&showchangehistorylog=1 | 20-0046772 | SONOMA | FIELD OPS NORTH | Tier 3 | FORT ROSS-1121 | 42851121 | OTHER | WIREDOWNFTROSSRDEONEISTRATH | 20200503 | 2356 | 906441 | 598 | Distribution Circuit | Equipment Failure/Involved | Overhead | 189 | 96796 | 38.5294 | -123.1809 | FTROSSRDEONEISTRATH | Clear-32-90 F | Insulator | Broken, wire on ground | 20-0046772 | OH | Sus | 31501929 | No | 2020 | MAY | Yes | Open Circuit | 1530504 | INS | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0047617&numberofmonths=24&showchangehistorylog=1 | 20-0047617 | SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 6217 | 20200505 | 1537 | 907643 | 473 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 16 | 7568 | 38.5868 | -122.9279 | 17003 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0047617 | OH | Sus | 44311357 | No | 2020 | MAY | Yes | Line to Ground | 1530908 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0047688&numberofmonths=24&showchangehistorylog=1 | 20-0047688 | SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1101 | 42571101 | RECLOSER | 322 | 20200506 | 527 | 907845 | 739 | Distribution Circuit | 3rd Party | Vehicle | 725 | 116519 | 38.3868 | -122.8901 | 11371BODEGAHWY | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0047688 | OH | Sus | 0 | No | 2020 | MAY | Yes | Line to Ground | 1530955 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0049155&numberofmonths=24&showchangehistorylog=1 | 20-0049155 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER | 240 | 20200511 | 1350 | 911388 | 224 | Distribution Circuit | Vegetation | Tree - branch fell on line | 811 | 91045 | 38.4715 | -123.0471 | 2SPANSSSOF969182 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0049155 | OH | Sus | 44320983 | yes | 2020 | MAY | Yes | Line to Ground | 1531958 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0058317&numberofmonths=24&showchangehistorylog=1 | 20-0058317 | SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1101 | 42571101 | TRIP-SAVER | 891 | 20200605 | 1818 | 932236 | 587 | Distribution Circuit | Vegetation | Tree - branch fell on line | 95 | 8081 | 38.3901 | -122.8854 | ATFUCO13903 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0058317 | OH | Sus | 44344353 | yes | 2020 | JUN | Yes | Line to Line | 1537559 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0058447&numberofmonths=24&showchangehistorylog=1 | 20-0058447 | SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | RECLOSER | 24918 | 20200606 | 1440 | 932841 | 260 | Distribution Circuit | Vegetation | Tree - branch fell on line | 187 | 48620 | 38.5914 | -122.92 | 5SLSOFLR24918 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0058447 | OH | Sus | 44344548 | yes | 2020 | JUN | Yes | Line to Ground | 1537679 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0058466&numberofmonths=24&showchangehistorylog=1 | 20-0058466 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 429 | 20200606 | 1411 | 932799 | 564 | Distribution Circuit | Vegetation | Tree - branch fell on line | 66 | 12933 | 38.4734 | -123.0226 | INGRAM425321940RUSSIANRIVERAVE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0058466 | OH | Sus | 44344546 | yes | 2020 | JUN | Yes | Line to Ground | 1537696 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0058722&numberofmonths=24&showchangehistorylog=1 | 20-0058722 | SONOMA | FIELD OPS NORTH | Tier 3 | FORT ROSS-1121 | 42851121 | RECLOSER | 70288 | 20200608 | 523 | 933832 | 577 | Distribution Circuit | Vegetation | Tree - fell into line | 156 | 64601 | 38.5287 | -123.1574 | 4SPANSWESTOF4167 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0058722 | OH | Sus | 31505342 | yes | 2020 | JUN | Yes | Line to Ground | 1537937 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0060729&numberofmonths=24&showchangehistorylog=1 | 20-0060729 | SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | OTHER | WIREDOWN | 20200612 | 1603 | 938024 | 221 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 187 | 40460 | 38.5909 | -122.9588 | 10SPSSOF6751 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0060729 | OH | Sus | 0 | yes | 2020 | JUN | Yes | Open Circuit | 1539345 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0062919&numberofmonths=24&showchangehistorylog=1 | 20-0062919 | SONOMA | FIELD OPS NORTH | Tier 2 | FITCH MOUNTAIN-1113 | 42751113 | OTHER | WIREDOWN6SPANSSSOF16347 | 20200619 | 20 | 942318 | 547 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 7868 | 38.6413 | -122.92 | 6SPANSSSOF16347 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0062919 | OH | Sus | 44360218 | No | 2020 | JUN | Yes | Line to Ground | 1540854 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0065110&numberofmonths=24&showchangehistorylog=1 | 20-0065110 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 467555 | 20200625 | 1922 | 947557 | 568 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 3408 | 38.3966 | -122.9397 | 2PLDSIDEOF467555 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0065110 | OH | Sus | 0 | No | 2020 | JUN | Yes | Line to Line | 1542547 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0065628&numberofmonths=24&showchangehistorylog=1 | 20-0065628 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | OTHER | WIREDOWN1SPANSSOF17045 | 20200627 | 334 | 948545 | 545 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1463 | 147943 | 38.3007 | -122.7451 | GRACIERICHARDEP1SpanSSof17045 | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0065628 | OH | Sus | 0 | No | 2020 | JUN | Yes | Open Circuit | 1542852 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0065770&numberofmonths=24&showchangehistorylog=1 | 20-0065770 | SONOMA | FIELD OPS NORTH | Tier 3 | FULTON-1107 | 42561107 | FUSE | 2375 | 20200628 | 145 | 949173 | 689 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 11713 | 38.5423 | -122.7203 | 1SPANLOADSIDE | Clear | Conductor, Overhead | Broken, wire on ground | 20-0065770 | OH | Sus | 44368200 | No | 2020 | JUN | Yes | Line to Ground | 1542990 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0065990&numberofmonths=24&showchangehistorylog=1 | 20-0065990 | SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | RECLOSER | 24918 | 20200629 | 510 | 949651 | 643 | Distribution Circuit | 3rd Party | Vehicle | 171 | 109953 | 38.5914 | -122.92 | NOONAN34692POLESSOURCESIDEOFCOPOLE6217MILLCREEKRD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0065990 | OH | Sus | 0 | No | 2020 | JUN | Yes | Line to Line | 1543136 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0068422&numberofmonths=24&showchangehistorylog=1 | 20-0068422 | SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | RECLOSER | 24918 | 20200705 | 117 | 957989 | 561 | Distribution Circuit | Vegetation | Tree - fell into line | 187 | 104907 | 38.5914 | -122.92 | 9LDSIDEOF6217ONMAINLINE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0068422 | OH | Sus | 44377964 | No | 2020 | JUL | Yes | Line to Ground | 1544442 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0070341&numberofmonths=24&showchangehistorylog=1 | 20-0070341 | SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | RECLOSER | 861496 | 20200710 | 359 | 961366 | 549 | Distribution Circuit | Vegetation | Tree - fell into line | 89 | 28253 | 38.358 | -122.5256 | 5SPANSSSOF6215 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0070341 | OH | Sus | 31508158 | No | 2020 | JUL | Yes | Line to Ground | 1545573 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0079813&numberofmonths=24&showchangehistorylog=1 | 20-0079813 | SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1108 | 42631108 | RECLOSER | 636 | 20200805 | 719 | 978986 | 775 | Distribution Circuit | 3rd Party | Vehicle | 141 | 31185 | 38.2618 | -122.7158 | FUCO12207 | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0079813 | OH | Sus | 0 | yes | 2020 | AUG | Yes | Line to Ground | 1551763 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0079795&numberofmonths=24&showchangehistorylog=1 | 20-0079795 | SONOMA | FIELD OPS NORTH | Tier 3 | SALMON CREEK-1101 | 43161101 | FUSE | 6059 | 20200805 | 142 | 978939 | 565 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 5554 | 38.3558 | -122.9804 | 1665TANNERYCREEKRD | Overcast-Fog-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0079795 | OH | Sus | 44409889 | yes | 2020 | AUG | Yes | Line to Ground | 1551752 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0080240&numberofmonths=24&showchangehistorylog=1 | 20-0080240 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1105 | 42271105 | RECLOSER | 36536 | 20200806 | 357 | 979836 | 784 | Distribution Circuit | 3rd Party | Vehicle | 802 | 135640 | 38.3142 | -122.7365 | 1WOF2137 | Overcast-Fog-32-90 F | Pole-Wood | Broken, wire on ground | 20-0080240 | OH | Sus | 0 | No | 2020 | AUG | Yes | Line to Ground | 1552072 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0083024&numberofmonths=24&showchangehistorylog=1 | 20-0083024 | SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1101 | 43071101 | FUSE | 9719 | 20200813 | 915 | 995018 | 317 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 6974 | 38.4156 | -122.563 | 7SPANSLDSIDEOFFUSES9719 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0083024 | OH | Sus | 44434934 | yes | 2020 | AUG | Yes | Multi-Fault | 1553903 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0084014&numberofmonths=24&showchangehistorylog=1 | 20-0084014 | SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | RECLOSER | 903030 | 20200814 | 2126 | 1003269 | 406 | Distribution Circuit | 3rd Party | Vehicle | 21 | 8526 | 38.382 | -122.5549 | 9SPANSLDSIDEOF903030 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0084014 | OH | Sus | 0 | yes | 2020 | AUG | Yes | Line to Ground | 1554547 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0088250&numberofmonths=24&showchangehistorylog=1 | 20-0088250 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | TRIP-SAVER | 999 | 20200820 | 2044 | 1025942 | 321 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 25359 | 38.422 | -122.954 | 1SPANSOURCESIDEOFMTR1009708972 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0088250 | OH | Sus | 0 | yes | 2020 | AUG | Yes | Line to Line | 1557606 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0089140&numberofmonths=24&showchangehistorylog=1 | 20-0089140 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | OTHER | WIREDOWN4SPANSNOF999 | 20200824 | 45 | 1028023 | 1063 | Distribution Circuit | Vegetation | Tree - fell into line | 388 | 408384 | 38.4234 | -122.9552 | 4SPANSNOF999 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0089140 | OH | Sus | 0 | yes | 2020 | AUG | Yes | Open Circuit | 1558276 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0091325&numberofmonths=24&showchangehistorylog=1 | 20-0091325 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | JUMPER | 539938 | 20200829 | 1734 | 1040774 | 90 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 2970 | 38.5404 | -122.9849 | 13SPANSSSOF1991 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0091325 | OH | Sus | 0 | No | 2020 | AUG | Yes | Line to Ground | 1559767 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0093640&numberofmonths=24&showchangehistorylog=1 | 20-0093640 | SONOMA | FIELD OPS NORTH | Tier 2 | CLOVERDALE-1101 | 42821101 | FUSE | 7295 | 20200904 | 2142 | 1055463 | 766 | Distribution Circuit | Vegetation | Tree - branch fell on line | 34 | 26044 | 38.863 | -123.0863 | 6SPANSLDSIDEOF7295 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0093640 | OH | Sus | 44458915 | No | 2020 | SEP | Yes | Line to Line | 1560977 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0095395&numberofmonths=24&showchangehistorylog=1 | 20-0095395 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | OTHER | WIREDOWN2SPANSWOF12683 | 20200909 | 821 | 1061841 | 369 | Distribution Circuit | Vegetation | Tree - branch fell on line | 115 | 38696 | 38.499 | -122.978 | 2SPANSWOF126834SPANSLDSIDEOF1031 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0095395 | OH | Sus | 31513306 | yes | 2020 | SEP | Yes | Open Circuit | 1562524 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0099892&numberofmonths=24&showchangehistorylog=1 | 20-0099892 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | OTHER | WIREDOWN7800BOHEMIANHWY | 20200921 | 2348 | 1086259 | 549 | Distribution Circuit | Vegetation | Tree - fell into line | 494 | 78609 | 38.4439 | -122.9942 | 7800BOHEMIANHWY | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0099892 | OH | Sus | 44476575 | No | 2020 | SEP | Yes | Open Circuit | 1565171 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0101509&numberofmonths=24&showchangehistorylog=1 | 20-0101509 | SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | RECLOSER | 24918 | 20200925 | 950 | 1092320 | 421 | Distribution Circuit | Vegetation | Tree - fell into line | 171 | 61247 | 38.5911 | -122.9201 | 1SPANSOURCESIDEOF818325 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0101509 | OH | Sus | 31514646 | No | 2020 | SEP | Yes | Line to Line | 1566094 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0105814&numberofmonths=24&showchangehistorylog=1 | 20-0105814 | SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | FUSE | 2223 | 20201006 | 1256 | 1112205 | 550 | Distribution Circuit | Vegetation | Tree - branch fell on line | 46 | 25300 | 38.5467 | -122.6697 | 3615CALISTOGARD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0105814 | OH | Sus | 44488801 | No | 2020 | OCT | Yes | Line to Ground | 1568921 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0109467&numberofmonths=24&showchangehistorylog=1 | 20-0109467 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 4895 | 20201016 | 413 | 1119052 | 628 | Distribution Circuit | Vegetation | Tree - fell into line | 152 | 95456 | 38.4118 | -122.9751 | SPANBETWEEN12023AND6431 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 20-0109467 | OH | Sus | 44499205 | No | 2020 | OCT | Yes | Line to Line | 1571249 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0113280&numberofmonths=24&showchangehistorylog=1 | 20-0113280 | SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1101 | 42571101 | RECLOSER | 322 | 20201026 | 442 | 1128407 | 804 | Distribution Circuit | Vegetation | Tree - fell into line | 1021 | 385695 | 38.3868 | -122.8901 | MTR1009723336 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0113280 | OH | Sus | 0 | yes | 2020 | OCT | Yes | Line to Ground | 1574638 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0116297&numberofmonths=24&showchangehistorylog=1 | 20-0116297 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | OTHER | WIREDOWN6759 | 20201102 | 1718 | 1134808 | 387 | Distribution Circuit | Vegetation | Tree - fell into line | 106 | 38627 | 38.4634 | -123.0122 | 6759ONMAINLINE | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 20-0116297 | OH | Sus | 0 | No | 2020 | NOV | Yes | Line to Ground | 1576489 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0117609&numberofmonths=24&showchangehistorylog=1 | 20-0117609 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 1035 | 20201106 | 255 | 1137044 | 607 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 7891 | 38.4989 | -122.9929 | CONTRERAST446313752GUERNEHILLRD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 20-0117609 | OH | Sus | 0 | No | 2020 | NOV | Yes | Line to Line | 1577379 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0118481&numberofmonths=24&showchangehistorylog=1 | 20-0118481 | SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | RECLOSER | 568 | 20201108 | 1232 | 1139473 | 411 | Distribution Circuit | Equipment Failure/Involved | Overhead | 161 | 22582 | 38.5166 | -122.6547 | Nott35695000ALPINERD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 20-0118481 | OH | Sus | 0 | No | 2020 | NOV | Yes | Line to Line | 1578115 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0121894&numberofmonths=24&showchangehistorylog=1 | 20-0121894 | SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | OTHER | WIREDOWN1LDSIDEOFMTR1008107675 | 20201117 | 1149 | 1147284 | 413 | Distribution Circuit | Vegetation | Tree - fell into line | 234 | 49792 | 38.5469 | -123.2949 | 1LDSIDEOFMTR1008107675 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0121894 | OH | Sus | 44543693 | No | 2020 | NOV | Yes | Open Circuit | 1580626 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0123398&numberofmonths=24&showchangehistorylog=1 | 20-0123398 | SONOMA | FIELD OPS NORTH | Tier 3 | DUNBAR-1101 | 43071101 | OTHER | 4817 | 20201120 | 1223 | 1150260 | 332 | Distribution Circuit | Vegetation | Tree - branch fell on line | 62 | 8312 | 38.3984 | -122.5802 | 2865BRISTOLRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0123398 | OH | Sus | 44564057 | No | 2020 | NOV | Yes | Open Circuit | 1581627 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0128415&numberofmonths=24&showchangehistorylog=1 | 20-0128415 | SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | FUSE | 15707 | 20201207 | 254 | 1167366 | 667 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 18009 | 38.5447 | -122.6483 | 3430CHALFAMTRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0128415 | OH | Sus | 44578801 | No | 2020 | DEC | Yes | Line to Ground | 1584977 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0130218&numberofmonths=24&showchangehistorylog=1 | 20-0130218 | SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1109 | 42631109 | OTHER | WIREDOWN | 20201213 | 2220 | 1182892 | 876 | Distribution Circuit | 3rd Party | Vehicle | 230 | 25002 | 38.1563 | -122.6956 | 1SPANLDSIDEOFFUCO893363ONMAINLINE | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0130218 | OH | Sus | 0 | No | 2020 | DEC | Yes | Open Circuit | 1586960 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0130385&numberofmonths=24&showchangehistorylog=1 | 20-0130385 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | TRIP-SAVER | 15401 | 20201214 | 1211 | 1184755 | 430 | Distribution Circuit | Vegetation | Tree - fell into line | 104 | 44720 | 38.4246 | -122.9613 | 125RAILROADAVE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0130385 | OH | Sus | 31521768 | No | 2020 | DEC | Yes | Line to Line | 1587277 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0004543&numberofmonths=24&showchangehistorylog=1 | 21-0004543 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER | 969182 | 20210104 | 759 | 1203009 | 461 | Distribution Circuit | Vegetation | Tree - fell into line | 561 | 147152 | 38.4901 | -123.0598 | Arvig34713415AustinCreekrdCazadero | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0004543 | OH | Sus | 0 | No | 2021 | JAN | Yes | Three Phase Fault | 1590601 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0006963&numberofmonths=24&showchangehistorylog=1 | 21-0006963 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 1993 | 20210110 | 157 | 1207454 | 858 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 21450 | 38.5274 | -123.0007 | 6SPANSLDSIDEOF1993 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0006963 | OH | Sus | 44620200 | No | 2021 | JAN | Yes | Three Phase Fault | 1592062 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0007658&numberofmonths=24&showchangehistorylog=1 | 21-0007658 | SONOMA | FIELD OPS NORTH | Tier 2 | GEYSERVILLE-1101 | 42891101 | FUSE | 2913 | 20210112 | 822 | 1208712 | 454 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 1436 | 38.7033 | -122.9205 | MTR1010390519 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0007658 | OH | Sus | 0 | No | 2021 | JAN | Yes | Multi-Fault | 1592522 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0012453&numberofmonths=24&showchangehistorylog=1 | 21-0012453 | SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1109 | 42631109 | RECLOSER | 128 | 20210122 | 841 | 1220542 | 409 | Distribution Circuit | 3rd Party | Vehicle | 230 | 44553 | 38.2203 | -122.6437 | 1PNOF6671 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 21-0012453 | OH | Sus | 0 | No | 2021 | JAN | Yes | Multi-Fault | 1595681 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0023338&numberofmonths=24&showchangehistorylog=1 | 21-0023338 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | RECLOSER | 334 | 20210209 | 419 | 1251164 | 505 | Distribution Circuit | 3rd Party | Vehicle | 91 | 34205 | 38.5009 | -122.9053 | 2SPANSSSSIDEOFCAP700 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0023338 | OH | Sus | 44645102 | No | 2021 | FEB | Yes | Line to Line | 1603891 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0027102&numberofmonths=24&showchangehistorylog=1 | 21-0027102 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 8227 | 20210218 | 1607 | 1257493 | 305 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 5490 | 38.5037 | -123.0299 | 14455CAMINODELARROYO | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0027102 | OH | Sus | 44656080 | No | 2021 | FEB | Yes | Line to Ground | 1606128 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0027599&numberofmonths=24&showchangehistorylog=1 | 21-0027599 | SONOMA | FIELD OPS NORTH | Tier 3 | DUNBAR-1102 | 43071102 | FUSE | 7125 | 20210220 | 104 | 1258272 | 846 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 6768 | 38.3658 | -122.5744 | 1SPANLDSIDEOFFUCO7125 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0027599 | OH | Sus | 31530579 | No | 2021 | FEB | Yes | Line to Ground | 1606437 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0027595&numberofmonths=24&showchangehistorylog=1 | 21-0027595 | SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1109 | 42631109 | RECLOSER | 128 | 20210220 | 101 | 1258271 | 743 | Distribution Circuit | Vegetation | Tree - fell into line | 230 | 64764 | 38.2203 | -122.6437 | 3SPANSSSOFFUCO567455ONMAINLINE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0027595 | OH | Sus | 44657622 | No | 2021 | FEB | Yes | Line to Ground | 1606433 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0029630&numberofmonths=24&showchangehistorylog=1 | 21-0029630 | SONOMA | FIELD OPS NORTH | Tier 3 | DUNBAR-1103 | 43071103 | JUMPER | WIREDOWNATMTR1010493817 | 20210225 | 1205 | 1262439 | 643 | Distribution Circuit | Vegetation | Tree - branch fell on line | 99 | 26631 | 38.384 | -122.4818 | 1SPANLDSIDEOFMTR1010493817 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0029630 | OH | Sus | 44664056 | No | 2021 | FEB | Yes | Open Circuit | 1607928 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0033080&numberofmonths=24&showchangehistorylog=1 | 21-0033080 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1101 | 42091101 | FUSE | 485 | 20210306 | 1253 | 1272028 | 280 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 280 | 38.4829 | -123.0002 | WIREDOWN1SPANLDSIDEOF485 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0033080 | OH | Sus | 0 | No | 2021 | MAR | Yes | Line to Ground | 1610141 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0033049&numberofmonths=24&showchangehistorylog=1 | 21-0033049 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 15453 | 20210306 | 955 | 1271309 | 441 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 882 | 38.462 | -122.9373 | 2SPLDSIDEOF15453 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0033049 | OH | Sus | 0 | No | 2021 | MAR | Yes | Line to Ground | 1610129 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0035394&numberofmonths=24&showchangehistorylog=1 | 21-0035394 | SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | OTHER | 3069 | 20210311 | 1310 | 1278956 | 455 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 3185 | 38.6051 | -122.9833 | 1STSPANTONWLDSIDE3069 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0035394 | OH | Sus | 44680387 | No | 2021 | MAR | Yes | Open Circuit | 1611429 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0037259&numberofmonths=24&showchangehistorylog=1 | 21-0037259 | SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | JUMPER | WIREDOWN20SPANSLDSIDEOF6217FUCO | 20210316 | 1429 | 1285388 | 150 | Distribution Circuit | Equipment Failure/Involved | Overhead | 172 | 25060 | 38.5854 | -122.9439 | WIREDOWN20SPANSSWOF6217FUCO | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0037259 | OH | Sus | 0 | No | 2021 | MAR | Yes | Line to Ground | 1612670 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0038040&numberofmonths=24&showchangehistorylog=1 | 21-0038040 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | FUSE | 2439 | 20210318 | 1123 | 1287632 | 262 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 524 | 38.2162 | -122.9225 | 3SPANSLDSIDEOF2439 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0038040 | OH | Sus | 31533641 | No | 2021 | MAR | Yes | Line to Ground | 1613135 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0039623&numberofmonths=24&showchangehistorylog=1 | 21-0039623 | SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1108 | 42631108 | OTHER | WIREDOWN2SPANSNOF3443 | 20210323 | 418 | 1292762 | 370 | Distribution Circuit | Vegetation | Tree - bark fell into line | 868 | 166648 | 38.278 | -122.8 | 2SPANSNOF3443 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0039623 | OH | Sus | 31534112 | No | 2021 | MAR | Yes | Open Circuit | 1614067 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0039880&numberofmonths=24&showchangehistorylog=1 | 21-0039880 | SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1108 | 42631108 | FUSE | 67329 | 20210323 | 1221 | 1293997 | 182 | Distribution Circuit | Animal | Bird found | 1 | 182 | 38.2067 | -122.7644 | LDSIDEOFFUCO67329 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0039880 | OH | Sus | 0 | No | 2021 | MAR | Yes | Line to Ground | 1614309 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0040707&numberofmonths=24&showchangehistorylog=1 | 21-0040707 | SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | FUSE | 6215 | 20210324 | 2233 | 1296600 | 1231 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 14772 | 38.3555 | -122.545 | 2211LONDONRANCHRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0040707 | OH | Sus | 31534154 | No | 2021 | MAR | Yes | Three Phase Fault | 1614812 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0044144&numberofmonths=24&showchangehistorylog=1 | 21-0044144 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 5687 | 20210402 | 1033 | 1305763 | 251 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 1506 | 38.4072 | -122.932 | 13799OCCIDENTALRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0044144 | OH | Sus | 44720129 | No | 2021 | APR | Yes | Multi-Fault | 1617205 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0057852&numberofmonths=24&showchangehistorylog=1 | 21-0057852 | SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER | 560 | 20210506 | 1059 | 1342454 | 469 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 14070 | 38.5561 | -123.3034 | 7SPANSLOADSIDEOF6745 | Clear-32-90 F | Crossarm, Wood | Broken, wire on object | 21-0057852 | OH | Sus | 31539628 | No | 2021 | MAY | Yes | Force Out | 1626211 | CAW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0059031&numberofmonths=24&showchangehistorylog=1 | 21-0059031 | SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1108 | 42631108 | RECLOSER | 208 | 20210509 | 2051 | 1344565 | 378 | Distribution Circuit | Equipment Failure/Involved | Overhead | 181 | 19359 | 38.2261 | -122.7211 | 7SPANSLDIDEOF4383 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0059031 | OH | Sus | 44779340 | No | 2021 | MAY | Yes | Multi-Fault | 1627022 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0070672&numberofmonths=24&showchangehistorylog=1 | 21-0070672 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1101 | 42091101 | OTHER | BROKENCONDUCTOR11000VELLUTINIRD | 20210606 | 2221 | 1367135 | 730 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 19038 | 38.4887 | -122.9273 | 11000VELLUTINIRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0070672 | OH | Sus | 31542268 | No | 2021 | JUN | Yes | Open Circuit | 1634970 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0071336&numberofmonths=24&showchangehistorylog=1 | 21-0071336 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 429 | 20210608 | 723 | 1368172 | 670 | Distribution Circuit | 3rd Party | Vehicle | 66 | 44220 | 38.4735 | -123.023 | SBCO13835 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0071336 | OH | Sus | 0 | No | 2021 | JUN | Yes | Line to Ground | 1635512 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0072293&numberofmonths=24&showchangehistorylog=1 | 21-0072293 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1105 | 42271105 | FUSE | 2881 | 20210609 | 1517 | 1369559 | 433 | Distribution Circuit | Equipment Failure/Involved | Overhead | 46 | 10798 | 38.3435 | -122.7573 | WIREDOWN5050GILCHRISTRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0072293 | OH | Sus | 44845421 | No | 2021 | JUN | Yes | Line to Line | 1635996 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0073332&numberofmonths=24&showchangehistorylog=1 | 21-0073332 | SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1101 | 42571101 | OTHER | 5773 | 20210611 | 1432 | 1371077 | 503 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 6036 | 38.3731 | -122.8672 | SSOF6705 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0073332 | OH | Sus | 44853338 | No | 2021 | JUN | Yes | Line to Ground | 1636566 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0075009&numberofmonths=24&showchangehistorylog=1 | 21-0075009 | SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | RECLOSER | 5152 | 20210616 | 1115 | 1375273 | 278 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 3336 | 38.5498 | -122.6679 | 4300PORTERCREEKRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0075009 | OH | Sus | 31543750 | No | 2021 | JUN | Yes | Line to Ground | 1637829 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0078266&numberofmonths=24&showchangehistorylog=1 | 21-0078266 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE | 6759 | 20210623 | 1437 | 1383148 | 344 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 7912 | 38.4634 | -123.0122 | Arvig3471350WOF9870mainstmonterio | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0078266 | OH | Sus | 44875490 | No | 2021 | JUN | Yes | Line to Line | 1640282 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0081469&numberofmonths=24&showchangehistorylog=1 | 21-0081469 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 883 | 20210629 | 1047 | 1387967 | 291 | Distribution Circuit | Vegetation | Tree - fell into line | 250 | 12510 | 38.4074 | -122.9484 | WILLOWCREEKRDANDCOLEMANVALLEYRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0081469 | OH | Sus | 31545039 | No | 2021 | JUN | Yes | Line to Ground | 1642965 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0085615&numberofmonths=24&showchangehistorylog=1 | 21-0085615 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE | 13839 | 20210706 | 1653 | 1393129 | 401 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 7619 | 38.4637 | -123.013 | 21462BONITATERRACE | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0085615 | OH | Sus | 31545824 | No | 2021 | JUL | Yes | Line to Line | 1645758 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0086227&numberofmonths=24&showchangehistorylog=1 | 21-0086227 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 3895 | 20210707 | 2145 | 1394143 | 544 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 5984 | 38.5158 | -123.0795 | SECONDANDTHIRDSPANLDSIDEOF3895 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0086227 | OH | Sus | 31545835 | No | 2021 | JUL | Yes | Line to Ground | 1646095 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0090081&numberofmonths=24&showchangehistorylog=1 | 21-0090081 | SONOMA | FIELD OPS NORTH | Tier 2 | GEYSERVILLE-1101 | 42891101 | RECLOSER | 705777 | 20210715 | 942 | 1405269 | 371 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 45 | 16695 | 38.7102 | -122.9248 | 4SPANSLDSIDE705777 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0090081 | OH | Sus | 44908378 | No | 2021 | JUL | Yes | Line to Ground | 1648577 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0093183&numberofmonths=24&showchangehistorylog=1 | 21-0093183 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER | 64758 | 20210721 | 2138 | 1410653 | 359 | Distribution Circuit | 3rd Party | Vehicle | 282 | 67014 | 38.5087 | -123.0696 | 3SPANSOF4167 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0093183 | OH | Sus | 44916460 | No | 2021 | JUL | Yes | Line to Line | 1650436 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0097183&numberofmonths=24&showchangehistorylog=1 | 21-0097183 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | OCB | 11032 | 20210730 | 253 | 1420620 | 601 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1459 | 470318 | 38.3098 | -122.7316 | SCHILLINGJASON2778388MECHAMROAD | Clear-32-90 F | Insulator | Broken, wire on ground | 21-0097183 | OH | Sus | 31548313 | No | 2021 | JUL | Yes | Multi-Fault | 1653073 | INS | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0103361&numberofmonths=24&showchangehistorylog=1 | 21-0103361 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 2001 | 20210811 | 2010 | 1440544 | 554 | Distribution Circuit | Vegetation | Tree - fell into line | 75 | 9122 | 38.5028 | -122.9888 | TREEINLINE3SPANSLDSIDEOFFUCO1560115865EDGEHILL | Clear-32-90F | Crossarm, Wood | Broken, wire on ground | 21-0103361 | OH | Sus | 31549386 | No | 2021 | AUG | Yes | Line to Ground | 1656734 | CAW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0104236&numberofmonths=24&showchangehistorylog=1 | 21-0104236 | SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1108 | 42631108 | FUSE | 1205 | 20210813 | 1204 | 1441972 | 376 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1504 | 38.2496 | -122.7265 | WATTSCHAD6spansloadsidebetweenSAPIDs103143256103143257 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0104236 | OH | Sus | 44947169 | No | 2021 | AUG | Yes | Line to Ground | 1657369 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0104483&numberofmonths=24&showchangehistorylog=1 | 21-0104483 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER | 256 | 20210814 | 156 | 1442399 | 695 | Distribution Circuit | Vegetation | Tree - fell into line | 1259 | 436815 | 38.4901 | -123.0598 | 4SPANSLDSIDEOF4001 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0104483 | OH | Sus | 0 | No | 2021 | AUG | Yes | Line to Ground | 1657439 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0104731&numberofmonths=24&showchangehistorylog=1 | 21-0104731 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 797 | 20210815 | 55 | 1443069 | 671 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 2572 | 38.5039 | -122.9005 | 2SPANSLDSIDEOF468859 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0104731 | OH | Sus | 31549622 | No | 2021 | AUG | Yes | Line to Ground | 1657672 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0112438&numberofmonths=24&showchangehistorylog=1 | 21-0112438 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1101 | 42571101 | FUSE | 18707 | 20210901 | 2205 | 1460456 | 477 | Distribution Circuit | 3rd Party | Vehicle | 3 | 1431 | 38.3747 | -122.9078 | 1POLELDSIDEOFFUSES | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0112438 | OH | Sus | 31551032 | No | 2021 | SEP | Yes | Multi-Fault | 1662916 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0114908&numberofmonths=24&showchangehistorylog=1 | 21-0114908 | SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | FUSE | 15707 | 20210908 | 1500 | 1464763 | 493 | Distribution Circuit | Vegetation | Tree - branch fell on line | 27 | 13311 | 38.5447 | -122.6483 | 3430CHALFANT | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0114908 | OH | Sus | 44972802 | No | 2021 | SEP | Yes | Line to Line | 1664214 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0116901&numberofmonths=24&showchangehistorylog=1 | 21-0116901 | SONOMA | FIELD OPS NORTH | Tier 3 | FULTON-1107 | 42561107 | RECLOSER | 214 | 20210913 | 1317 | 1470785 | 336 | Distribution Circuit | Vegetation | Tree - fell into line | 452 | 59332 | 38.5031 | -122.7355 | 2SPANSLDSIDEOFCGC218025032582 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 21-0116901 | OH | Sus | 31552031 | No | 2021 | SEP | Yes | Multi-Fault | 1665412 | CAW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0119589&numberofmonths=24&showchangehistorylog=1 | 21-0119589 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | OTHER | WIREDOWN1SPANLDSIDE15601 | 20210919 | 1340 | 1475653 | 503 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 3904 | 38.5027 | -122.9872 | 1SPANLDSIDEOF15601 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0119589 | OH | Sus | 0 | No | 2021 | SEP | Yes | Line to Ground | 1667070 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0120752&numberofmonths=24&showchangehistorylog=1 | 21-0120752 | SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | OTHER | WIREDOWNAT1310LONDONRANCHRD | 20210922 | 603 | 1477688 | 518 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 6216 | 38.3625 | -122.5288 | 1310LONDONRANCHRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0120752 | OH | Sus | 31552475 | No | 2021 | SEP | Yes | Line to Ground | 1667785 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0123670&numberofmonths=24&showchangehistorylog=1 | 21-0123670 | SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | RECLOSER | 448 | 20210929 | 817 | 1483145 | 349 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 1304 | 79685 | 38.3443 | -122.5144 | 15655ArnoldDrSonoma | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0123670 | OH | Sus | 44993894 | No | 2021 | SEP | Yes | Line to Line | 1669557 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0133354&numberofmonths=24&showchangehistorylog=1 | 21-0133354 | SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER | 134 | 20211019 | 1929 | 1502381 | 818 | Distribution Circuit | Vegetation | Tree - fell into line | 233 | 189564 | 38.5592 | -123.2701 | 2SPANSLDSIDEOFFUCO59153 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0133354 | OH | Sus | 45016653 | No | 2021 | OCT | Yes | Line to Ground | 1675789 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0134436&numberofmonths=24&showchangehistorylog=1 | 21-0134436 | SONOMA | FIELD OPS NORTH | Tier 2 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 2371 | 20211021 | 1015 | 1504439 | 703 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 4218 | 38.5423 | -122.8717 | CGC217507932000 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0134436 | OH | Sus | 0 | No | 2021 | OCT | Yes | Three Phase Fault | 1676407 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0134157&numberofmonths=24&showchangehistorylog=1 | 21-0134157 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | TRIP-SAVER | 1313 | 20211021 | 9 | 1503892 | 357 | Distribution Circuit | Vegetation | Tree - fell into line | 110 | 39270 | 38.504 | -122.9884 | MELODYAVEANDDRAKERD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0134157 | OH | Sus | 31555270 | No | 2021 | OCT | Yes | Line to Ground | 1676245 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0134819&numberofmonths=24&showchangehistorylog=1 | 21-0134819 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER | 506 | 20211022 | 353 | 1505271 | 686 | Distribution Circuit | Vegetation | Tree - fell into line | 143 | 59675 | 38.4693 | -123.0137 | CORNEROFRIVERMOSCOWRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0134819 | OH | Sus | 45019144 | No | 2021 | OCT | Yes | Line to Ground | 1676561 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0134813&numberofmonths=24&showchangehistorylog=1 | 21-0134813 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE | 6759 | 20211022 | 12 | 1505175 | 397 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 9131 | 38.4634 | -123.0122 | 9815MAINST | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0134813 | OH | Sus | 31555594 | No | 2021 | OCT | Yes | Line to Ground | 1676553 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0138513&numberofmonths=24&showchangehistorylog=1 | 21-0138513 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | RECLOSER | 318 | 20211026 | 2310 | 1522494 | 692 | Distribution Circuit | Vegetation | Tree - fell into line | 437 | 138298 | 38.4046 | -122.9485 | 2LDSIDEOF318 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0138513 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Ground | 1679464 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0139670&numberofmonths=24&showchangehistorylog=1 | 21-0139670 | SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | RECLOSER | 246 | 20211029 | 835 | 1525013 | 526 | Distribution Circuit | Vegetation | Tree - fell into line | 528 | 57764 | 38.3657 | -122.5275 | 3SPANSEOF11121 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0139670 | OH | Sus | 45024490 | No | 2021 | OCT | Yes | Line to Ground | 1680107 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0140732&numberofmonths=24&showchangehistorylog=1 | 21-0140732 | SONOMA | FIELD OPS NORTH | Tier 2 | CLOVERDALE-1101 | 42821101 | JUMPER | DOWNWIRE4SPANSSSOF6085 | 20211101 | 1322 | 1527376 | 266 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 23526 | 38.8339 | -123.0513 | 4SPANSSSOF608532725HWY128 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0140732 | OH | Sus | 45031462 | No | 2021 | NOV | Yes | None | 1680864 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0140805&numberofmonths=24&showchangehistorylog=1 | 21-0140805 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 1499 | 20211101 | 1431 | 1527384 | 536 | Distribution Circuit | Vegetation | Tree - fell into line | 131 | 70216 | 38.5089 | -122.9291 | 2SS7363 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0140805 | OH | Sus | 31573861 | No | 2021 | NOV | Yes | Line to Ground | 1680882 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0140582&numberofmonths=24&showchangehistorylog=1 | 21-0140582 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | RECLOSER | 539938 | 20211101 | 1130 | 1527204 | 529 | Distribution Circuit | Vegetation | Tree - fell into line | 84 | 44436 | 38.5277 | -123 | INGRAM388817200SWEETWATERSPRINGSRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0140582 | OH | Sus | 31573313 | No | 2021 | NOV | Yes | Multi-Fault | 1680808 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0142544&numberofmonths=24&showchangehistorylog=1 | 21-0142544 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | TRIP-SAVER | 1701 | 20211104 | 1614 | 1535109 | 675 | Distribution Circuit | Vegetation | Tree - branch fell on line | 66 | 44550 | 38.4728 | -123.0474 | 64MAGICMTNRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0142544 | OH | Sus | 31577708 | No | 2021 | NOV | Yes | Line to Ground | 1681867 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0142871&numberofmonths=24&showchangehistorylog=1 | 21-0142871 | SONOMA | FIELD OPS NORTH | Tier 2 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 6049 | 20211105 | 1322 | 1535838 | 213 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 852 | 38.5986 | -122.9118 | 6SPANSLDSIDEOF6049 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0142871 | OH | Sus | 0 | No | 2021 | NOV | Yes | Force Out | 1682121 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0145198&numberofmonths=24&showchangehistorylog=1 | 21-0145198 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1105 | 42271105 | FUSE | 3315 | 20211113 | 443 | 1542168 | 404 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 4528 | 38.3217 | -122.7592 | SCHILLINGJASON27786400PETERSONROAD | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 21-0145198 | OH | Sus | 31578330 | No | 2021 | NOV | Yes | Line to Line | 1683943 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0145461&numberofmonths=24&showchangehistorylog=1 | 21-0145461 | SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1102 | 42571102 | FUSE | 12153 | 20211114 | 1613 | 1543994 | 557 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1114 | 38.4444 | -122.9202 | 2SPANSLDSIDE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0145461 | OH | Sus | 45066176 | No | 2021 | NOV | Yes | Line to Ground | 1684240 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0147716&numberofmonths=24&showchangehistorylog=1 | 21-0147716 | SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1109 | 42631109 | FUSE | 2613 | 20211118 | 902 | 1548755 | 227 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 1816 | 38.1849 | -122.6646 | 9SPANSLDSIDEOF2613 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 21-0147716 | OH | Sus | 45070473 | No | 2021 | NOV | Yes | Line to Ground | 1686079 | CSO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0155024&numberofmonths=24&showchangehistorylog=1 | 21-0155024 | SONOMA | FIELD OPS NORTH | Tier 3 | DUNBAR-1103 | 43071103 | FUSE | 15877 | 20211205 | 810 | 1559541 | 441 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1764 | 38.3982 | -122.5127 | 1LDSIDEOFFUSES | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0155024 | OH | Sus | 45081863 | No | 2021 | DEC | Yes | Multi-Fault | 1691529 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0156049&numberofmonths=24&showchangehistorylog=1 | 21-0156049 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | JUMPER | 1OF3WIRESDOWN2SPANLDSIDEOFFUCO2443 | 20211208 | 1205 | 1562098 | 322 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 2898 | 38.1939 | -122.9104 | 2SPANSLDSIDEOF2443 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0156049 | OH | Sus | 45084752 | No | 2021 | DEC | Yes | Line to Ground | 1692654 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0159823&numberofmonths=24&showchangehistorylog=1 | 21-0159823 | SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1108 | 42631108 | RECLOSER | 208 | 20211220 | 753 | 1577776 | 457 | Distribution Circuit | Equipment Failure/Involved | Overhead | 179 | 23154 | 38.2261 | -122.7211 | HLEBAKOSFRANK1277TomalesRdArizonaAve | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0159823 | OH | Sus | 31588021 | No | 2021 | DEC | Yes | Line to Ground | 1697054 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0005783&numberofmonths=24&showchangehistorylog=1 | 22-0005783 | SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | FUSE | 17881 | 20220103 | 2144 | 1594346 | 1236 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 9888 | 38.3646 | -122.5447 | 7920EMERY | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0005783 | OH | Sus | 45106902 | No | 2022 | JAN | Yes | Line to Ground | 1700830 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0005812&numberofmonths=24&showchangehistorylog=1 | 22-0005812 | SONOMA | FIELD OPS NORTH | Tier 2 | GEYSERVILLE-1101 | 42891101 | FUSE | 5531 | 20220104 | 606 | 1594571 | 723 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 8025 | 38.6773 | -123.0625 | 12000SKAGGSSPRINGSRD | Clear-32-90F | Pole-Wood | Broken, wire on ground | 22-0005812 | OH | Sus | 0 | No | 2022 | JAN | Yes | Three Phase Fault | 1700850 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0011312&numberofmonths=24&showchangehistorylog=1 | 22-0011312 | SONOMA | FIELD OPS NORTH | Tier 3 | SANTA ROSA A-1104 | 42151104 | RECLOSER | 32180 | 20220119 | 1240 | 1605245 | 401 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 759 | 98914 | 38.4782 | -122.679 | HESSONG3884LDSD7162SPANSFROMEOLWALLACERD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0011312 | OH | Sus | 45128169 | No | 2022 | JAN | Yes | Line to Ground | 1703495 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0012806&numberofmonths=24&showchangehistorylog=1 | 22-0012806 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 1181 | 20220121 | 2308 | 1608054 | 805 | Distribution Circuit | Vegetation | Tree - fell into line | 111 | 89355 | 38.4027 | -122.9163 | 3SPANSLDSIDEOF1181 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0012806 | OH | Sus | 0 | No | 2022 | JAN | Yes | Force Out | 1704129 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0013040&numberofmonths=24&showchangehistorylog=1 | 22-0013040 | SONOMA | FIELD OPS NORTH | Tier 3 | GEYSERVILLE-1102 | 42891102 | JUMPER | SBCO1SPSOURCESIDECGC217578640034 | 20220122 | 16 | 1609381 | 770 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 770 | 38.765 | -122.8444 | CGC217578640034 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0013040 | OH | Sus | 0 | No | 2022 | JAN | Yes | Line to Ground | 1704379 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0013001&numberofmonths=24&showchangehistorylog=1 | 22-0013001 | SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | FUSE | 3447 | 20220122 | 10 | 1608070 | 1010 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 17170 | 38.5152 | -122.6288 | 2SPANSLDSIDE | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0013001 | OH | Sus | 0 | No | 2022 | JAN | Yes | Multi-Fault | 1704343 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0016818&numberofmonths=24&showchangehistorylog=1 | 22-0016818 | SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | RECLOSER | 655192 | 20220201 | 945 | 1617856 | 398 | Distribution Circuit | Vegetation | Tree - branch fell on line | 44 | 17512 | 38.5467 | -122.6696 | 3609CALISTOGARD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0016818 | OH | Sus | 31591620 | No | 2022 | FEB | Yes | Line to Line | 1706605 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0019061&numberofmonths=24&showchangehistorylog=1 | 22-0019061 | SONOMA | FIELD OPS NORTH | Tier 2 | CLOVERDALE-1102 | 42821102 | JUMPER | WIREDOWN1SPANFROMEOL | 20220206 | 422 | 1622114 | 616 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 934 | 38.7674 | -123.0521 | 1SPANFROMEOL | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0019061 | OH | Sus | 45166041 | No | 2022 | FEB | Yes | Line to Ground | 1707906 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0022015&numberofmonths=24&showchangehistorylog=1 | 22-0022015 | SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1101 | 42571101 | FUSE | 1709 | 20220214 | 937 | 1626911 | 237 | Distribution Circuit | Vegetation | Tree - branch fell on line | 171 | 24819 | 38.3737 | -122.8687 | 3696BURNSIDERDSANTAROSA | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0022015 | OH | Sus | 45177208 | No | 2022 | FEB | Yes | Line to Ground | 1709892 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0029957&numberofmonths=24&showchangehistorylog=1 | 22-0029957 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 1525 | 20220304 | 1245 | 1642229 | 278 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 15290 | 38.4106 | -122.9828 | Galea3472ATRISERPOLE86115 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0029957 | OH | Sus | 45198399 | No | 2022 | MAR | Yes | Line to Ground | 1714627 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0036776&numberofmonths=24&showchangehistorylog=1 | 22-0036776 | SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1101 | 42571101 | FUSE | 1709 | 20220322 | 1003 | 1653412 | 503 | Distribution Circuit | Vegetation | Tree - fell into line | 171 | 44193 | 38.3737 | -122.8687 | 4185BURNSIDERD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0036776 | OH | Sus | 31597987 | No | 2022 | MAR | Yes | Line to Ground | 1719045 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0038883&numberofmonths=24&showchangehistorylog=1 | 22-0038883 | SONOMA | FIELD OPS NORTH | Tier 2 | FITCH MOUNTAIN-1113 | 42751113 | JUMPER | TREEINLINES | 20220326 | 1059 | 1656334 | 425 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 888 | 38.6033 | -122.9162 | 10SPANSLDSIDEOF6049 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 22-0038883 | OH | Sus | 31599357 | No | 2022 | MAR | Yes | Line to Ground | 1720236 | CAW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0038965&numberofmonths=24&showchangehistorylog=1 | 22-0038965 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 17907 | 20220327 | 356 | 1656572 | 473 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 17974 | 38.5034 | -123.0289 | 1SPANSSOF7709 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0038965 | OH | Sus | 31599660 | No | 2022 | MAR | Yes | Line to Line | 1720301 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0039974&numberofmonths=24&showchangehistorylog=1 | 22-0039974 | SONOMA | FIELD OPS NORTH | Tier 3 | FORT ROSS-1121 | 42851121 | RECLOSER | 70288 | 20220329 | 1039 | 1658845 | 469 | Distribution Circuit | Equipment Failure/Involved | Overhead | 845 | 240098 | 38.5286 | -123.1572 | 2LDSIDEOF4195 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 22-0039974 | OH | Sus | 45234284 | No | 2022 | MAR | Yes | Line to Ground | 1721034 | CSO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0042594&numberofmonths=24&showchangehistorylog=1 | 22-0042594 | SONOMA | FIELD OPS NORTH | Tier 3 | CLOVERDALE-1102 | 42821102 | OTHER | WIREDOWN1381 | 20220404 | 1620 | 1662818 | 372 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 12270 | 38.7728 | -122.9075 | AT1381LDSIDE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0042594 | OH | Sus | 45239659 | No | 2022 | APR | Yes | Line to Ground | 1722613 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0045060&numberofmonths=24&showchangehistorylog=1 | 22-0045060 | SONOMA | FIELD OPS NORTH | Tier 2 | SONOMA-1105 | 42721105 | RECLOSER | 229588 | 20220410 | 243 | 1667201 | 797 | Distribution Circuit | Vegetation | Tree - fell into line | 184 | 99704 | 38.2871 | -122.4188 | 2SPANSLDSIDESAP104008045 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0045060 | OH | Sus | 0 | No | 2022 | APR | Yes | Three Phase Fault | 1724216 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0045542&numberofmonths=24&showchangehistorylog=1 | 22-0045542 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 2943 | 20220411 | 1235 | 1668675 | 691 | Distribution Circuit | Vegetation | Tree - fell into line | 136 | 65456 | 38.499 | -122.9038 | INGRAM38889365CHAMPSDEELYSSES | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0045542 | OH | Sus | 0 | No | 2022 | APR | Yes | Line to Ground | 1724620 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0045480&numberofmonths=24&showchangehistorylog=1 | 22-0045480 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER | 37520 | 20220411 | 1223 | 1668650 | 606 | Distribution Circuit | Vegetation | Tree - branch fell on line | 76 | 46056 | 38.5086 | -123.0693 | Arvig347115960EAustinCreekRdCazadero | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0045480 | OH | Sus | 0 | No | 2022 | APR | Yes | Line to Line | 1724573 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0048130&numberofmonths=24&showchangehistorylog=1 | 22-0048130 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | TRIP-SAVER | 53477 | 20220414 | 927 | 1672383 | 297 | Distribution Circuit | Vegetation | Tree - branch fell on line | 57 | 16929 | 38.4962 | -123.0694 | 1SSOF8139 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0048130 | OH | Sus | 45255922 | No | 2022 | APR | Yes | Multi-Fault | 1726654 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0050371&numberofmonths=24&showchangehistorylog=1 | 22-0050371 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | RECLOSER | 87402 | 20220416 | 321 | 1674075 | 497 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 15407 | 38.1632 | -122.8903 | 8000marshallpetalumard | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0050371 | OH | Sus | 0 | No | 2022 | APR | Yes | Line to Ground | 1728466 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0050714&numberofmonths=24&showchangehistorylog=1 | 22-0050714 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE | 487 | 20220417 | 1514 | 1675216 | 603 | Distribution Circuit | Vegetation | Tree - fell into line | 148 | 64390 | 38.4646 | -123.0101 | ATFUCO6759 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0050714 | OH | Sus | 31601202 | No | 2022 | APR | Yes | Line to Ground | 1728790 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0051365&numberofmonths=24&showchangehistorylog=1 | 22-0051365 | SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 779 | 20220419 | 433 | 1676170 | 907 | Distribution Circuit | Vegetation | Tree - bark fell into line | 43 | 39001 | 38.5969 | -122.9892 | 2SPANSSSOFCGC217168532845 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0051365 | OH | Sus | 45260912 | No | 2022 | APR | Yes | Line to Ground | 1729293 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0056301&numberofmonths=24&showchangehistorylog=1 | 22-0056301 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER | 969182 | 20220429 | 2056 | 1684910 | 688 | Distribution Circuit | Vegetation | Tree - branch fell on line | 564 | 141956 | 38.4901 | -123.0598 | 1SPANLDSIDEOFMETER1007661081 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0056301 | OH | Sus | 31602139 | No | 2022 | APR | Yes | Line to Ground | 1732347 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0057487&numberofmonths=24&showchangehistorylog=1 | 22-0057487 | SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1108 | 42631108 | FUSE | 1623 | 20220503 | 1819 | 1687643 | 442 | Distribution Circuit | Equipment Failure/Involved | Overhead | 85 | 20383 | 38.2421 | -122.7086 | 1SPANWOF1131 | Clear-32-90F | Connector or Splice (OH) | Broken, wire on ground | 22-0057487 | OH | Sus | 45277718 | No | 2022 | MAY | Yes | Line to Ground | 1733311 | CSO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0059343&numberofmonths=24&showchangehistorylog=1 | 22-0059343 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | FUSE | 2435 | 20220507 | 1545 | 1690803 | 369 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 19926 | 38.2418 | -122.9052 | 1SPANSSOF7841 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0059343 | OH | Sus | 45285269 | No | 2022 | MAY | Yes | Line to Line | 1734466 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0059774&numberofmonths=24&showchangehistorylog=1 | 22-0059774 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | RECLOSER | 66006 | 20220509 | 1230 | 1692187 | 804 | Distribution Circuit | Vegetation | Tree - fell into line | 255 | 74533 | 38.4053 | -122.9477 | 3SPANSLDSIDEOFLR66006 | Clear-32-90F | Crossarm, Wood | Broken, wire on ground | 22-0059774 | OH | Sus | 31603055 | No | 2022 | MAY | Yes | Multi-Fault | 1734864 | CAW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0059553&numberofmonths=24&showchangehistorylog=1 | 22-0059553 | SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | RECLOSER | 568 | 20220509 | 532 | 1691664 | 616 | Distribution Circuit | Equipment Failure/Involved | Overhead | 162 | 99980 | 38.5166 | -122.6547 | 6SPANSLDSIDEOFREGS69228 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0059553 | OH | Sus | 45285896 | No | 2022 | MAY | Yes | Line to Ground | 1734652 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0060396&numberofmonths=24&showchangehistorylog=1 | 22-0060396 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | OTHER | WIREDOWNNOF1667 | 20220510 | 1617 | 1693275 | 526 | Distribution Circuit | Equipment Failure/Involved | Overhead | 857 | 431930 | 38.2761 | -122.9 | WIREDOWNNOF1667 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0060396 | OH | Sus | 45291413 | No | 2022 | MAY | Yes | Open Circuit | 1735219 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0067275&numberofmonths=24&showchangehistorylog=1 | 22-0067275 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | RECLOSER | 937000 | 20220526 | 2248 | 1712145 | 1006 | Distribution Circuit | Vegetation | Tree - branch fell on line | 24 | 20153 | 38.4887 | -123.017 | JUMPERSFUSESAVER9370001SSOFCGC217055730092 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0067275 | OH | Sus | 45319554 | No | 2022 | MAY | Yes | Line to Ground | 1739803 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0072518&numberofmonths=24&showchangehistorylog=1 | 22-0072518 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER | 969182 | 20220610 | 411 | 1726907 | 561 | Distribution Circuit | Vegetation | Tree - fell into line | 564 | 175142 | 38.5087 | -123.0696 | SCHILLINGJASON27781SPSSCO3901 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0072518 | OH | Sus | 45333774 | No | 2022 | JUN | Yes | Line to Line | 1743329 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0111541&numberofmonths=24&showchangehistorylog=1 | 22-0111541 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 8003 | 20220918 | 334 | 1813679 | 441 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 8379 | 38.4777 | -123.0236 | 1SPANPAST21955DUNCANRD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0111541 | OH | Sus | 31616241 | No | 2022 | SEP | Yes | Line to Ground | 1769569 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0114528&numberofmonths=24&showchangehistorylog=1 | 22-0114528 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | RECLOSER | 64682 | 20220924 | 1426 | 1820871 | 379 | Distribution Circuit | Vegetation | Tree - fell into line | 148 | 21133 | 38.4646 | -123.0101 | PEDERSONRYLEY347321452BonitaTerraceMonteRio | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0114528 | OH | Sus | 31616916 | No | 2022 | SEP | Yes | Line to Line | 1771654 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0119954&numberofmonths=24&showchangehistorylog=1 | 22-0119954 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | RECLOSER | 132 | 20221011 | 708 | 1834602 | 485 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1019 | 111011 | 38.2648 | -122.8056 | HLEBAKOSFRANK12772spanssourcesideoffuses4221 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0119954 | OH | Sus | 31618136 | No | 2022 | OCT | Yes | Line to Ground | 1775476 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0126297&numberofmonths=24&showchangehistorylog=1 | 22-0126297 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | RECLOSER | 104 | 20221101 | 235 | 1849540 | 424 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1524 | 253551 | 38.4031 | -122.9214 | 5PLDSIDEOF1689 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0126297 | OH | Sus | 0 | No | 2022 | NOV | Yes | Line to Ground | 1780356 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0128461&numberofmonths=24&showchangehistorylog=1 | 22-0128461 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 17803 | 20221107 | 905 | 1855764 | 310 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 2790 | 38.5216 | -123.0962 | 2SPANSLDSIDEOFFUSES17803 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0128461 | OH | Sus | 0 | No | 2022 | NOV | Yes | Line to Ground | 1781880 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0130652&numberofmonths=24&showchangehistorylog=1 | 22-0130652 | SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1108 | 42631108 | FUSE | 3171 | 20221113 | 805 | 1861522 | 318 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 3498 | 38.2437 | -122.8114 | 1315TOMALESPETALUMARD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0130652 | OH | Sus | 45526121 | No | 2022 | NOV | Yes | Line to Ground | 1783380 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0133983&numberofmonths=24&showchangehistorylog=1 | 22-0133983 | SONOMA | FIELD OPS NORTH | Tier 2 | FITCH MOUNTAIN-1112 | 42751112 | FUSE | 150571 | 20221123 | 1947 | 1868638 | 828 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 5238 | 38.6225 | -122.8282 | 2SPANSLDSIDEOF2353 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0133983 | OH | Sus | 45571532 | No | 2022 | NOV | Yes | Line to Line | 1785361 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0136972&numberofmonths=24&showchangehistorylog=1 | 22-0136972 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | RECLOSER | 495692 | 20221206 | 954 | 1877209 | 419 | Distribution Circuit | Vegetation | Tree - fell into line | 347 | 145393 | 38.4098 | -122.9354 | METER1009704269 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0136972 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Line | 1787888 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0141645&numberofmonths=24&showchangehistorylog=1 | 22-0141645 | SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1112 | 42751112 | OTHER | WIREDOWN3LDSIDEOF3031 | 20221227 | 900 | 1898840 | 710 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 8460 | 38.606 | -122.9771 | 3LDSIDEOF3031 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0141645 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1793329 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0141748&numberofmonths=24&showchangehistorylog=1 | 22-0141748 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 6561 | 20221227 | 839 | 1898794 | 515 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 23175 | 38.4296 | -122.9335 | 82620 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0141748 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Line | 1793436 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0141580&numberofmonths=24&showchangehistorylog=1 | 22-0141580 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 8139 | 20221227 | 747 | 1898657 | 529 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 19044 | 38.4982 | -123.0729 | 66SUNRISEMOUNTAINRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0141580 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1793259 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0142248&numberofmonths=24&showchangehistorylog=1 | 22-0142248 | SONOMA | FIELD OPS NORTH | Tier 3 | FORT ROSS-1121 | 42851121 | FUSE | 4523 | 20221230 | 1355 | 1902054 | 192 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 3072 | 38.536 | -123.1403 | 3SPANSSSOF8971TWD4523 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0142248 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1794037 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0142188&numberofmonths=24&showchangehistorylog=1 | 22-0142188 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | TRIP-SAVER | 1989 | 20221230 | 928 | 1901926 | 269 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 11567 | 38.5219 | -122.9971 | 16201RIONIDORDGUERNEVILLE | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0142188 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Line | 1793968 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0005190&numberofmonths=24&showchangehistorylog=1 | 23-0005190 | SONOMA | FIELD OPS NORTH | Tier 3 | CLOVERDALE-1102 | 42821102 | FUSE | 12905 | 20230103 | 1242 | 1911519 | 304 | Distribution Circuit | Equipment Failure/Involved | Overhead | 40 | 11241 | 38.7762 | -122.9308 | 1SPANSS76875 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0005190 | OH | Sus | 45615957 | No | 2023 | JAN | Yes | Line to Ground | 1795708 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0013708&numberofmonths=24&showchangehistorylog=1 | 23-0013708 | SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1112 | 42751112 | FUSE | 769 | 20230111 | 1134 | 1947762 | 576 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 16128 | 38.5962 | -122.9148 | 2SPANLDSIDE769 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0013708 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Line | 1803119 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0014485&numberofmonths=24&showchangehistorylog=1 | 23-0014485 | SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE | 13075 | 20230112 | 1205 | 1950055 | 135 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 135 | 38.549 | -123.2446 | UNKONWHARMONONSITEANDFUCOWEREOPENALREADY | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0014485 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Line | 1803757 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0015168&numberofmonths=24&showchangehistorylog=1 | 23-0015168 | SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | JUMPER | OJSLINEBUS1POLSESOFFUCO18673 | 20230113 | 952 | 1951610 | 164 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 164 | 38.5968 | -123.3025 | NA | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0015168 | OH | Sus | 0 | No | 2023 | JAN | Yes | None | 1804210 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0016519&numberofmonths=24&showchangehistorylog=1 | 23-0016519 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 429 | 20230115 | 342 | 1955455 | 470 | Distribution Circuit | Vegetation | Tree - fell into line | 66 | 22110 | 38.4735 | -123.023 | CGC217070829564 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0016519 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Line | 1805277 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0018655&numberofmonths=24&showchangehistorylog=1 | 23-0018655 | SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1101 | 42091101 | OTHER | 933786 | 20230119 | 327 | 1961765 | 623 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 17965 | 38.4881 | -122.9208 | VELLUTINIRDANDYELLOWBRICKRD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0018655 | OH | Sus | 45644913 | No | 2023 | JAN | Yes | Force Out | 1806720 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0020034&numberofmonths=24&showchangehistorylog=1 | 23-0020034 | SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | FUSE | 6113 | 20230123 | 336 | 1965271 | 575 | Distribution Circuit | Vegetation | Tree - branch fell on line | 52 | 29900 | 38.5382 | -122.6465 | 1SSOF6119 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0020034 | OH | Sus | 45647247 | No | 2023 | JAN | Yes | Line to Ground | 1807447 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0022536&numberofmonths=24&showchangehistorylog=1 | 23-0022536 | SONOMA | FIELD OPS NORTH | Tier 2 | SALMON CREEK-1101 | 43161101 | FUSE | 14095 | 20230127 | 1414 | 1970006 | 406 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 812 | 38.3449 | -123.0029 | 1SPLDSIDEOF14095 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0022536 | OH | Sus | 45653110 | No | 2023 | JAN | Yes | Line to Ground | 1808720 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0022968&numberofmonths=24&showchangehistorylog=1 | 23-0022968 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 2305 | 20230130 | 414 | 1971885 | 827 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2876 | 38.5104 | -123.0963 | FIRSTPOLETHATBUCKESNELOADSIDEOF2325 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0022968 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Line | 1809188 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0025387&numberofmonths=24&showchangehistorylog=1 | 23-0025387 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | FUSE | 1343 | 20230205 | 704 | 1977264 | 575 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 10440 | 38.2758 | -122.7662 | 4LDSIDEOF1343 | Clear-32-90 F | Other | Broken, wire on ground | 23-0025387 | OH | Sus | 45658909 | No | 2023 | FEB | Yes | Line to Ground | 1810681 | NON | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0025542&numberofmonths=24&showchangehistorylog=1 | 23-0025542 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE | 551 | 20230206 | 532 | 1977827 | 437 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 3933 | 38.4246 | -122.9568 | 2SPANSSSOFCGC217268327843 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0025542 | OH | Sus | 31636316 | No | 2023 | FEB | Yes | Line to Line | 1810818 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0028419&numberofmonths=24&showchangehistorylog=1 | 23-0028419 | SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | JUMPER | HOTWIREDOWN1SPANSSSIDECGC313088563110 | 20230214 | 305 | 1984287 | 538 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2360 | 38.2079 | -122.9073 | 1SPANSSSIDECGC313088563110 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0028419 | OH | Sus | 45671479 | No | 2023 | FEB | Yes | Open Circuit | 1812961 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0028888&numberofmonths=24&showchangehistorylog=1 | 23-0028888 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 1997 | 20230214 | 1457 | 1985172 | 393 | Distribution Circuit | Vegetation | Tree - fell into line | 112 | 44016 | 38.5018 | -123.0238 | 15607OLDCAZADERORD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0028888 | OH | Sus | 31636881 | No | 2023 | FEB | Yes | Line to Ground | 1813248 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0040543&numberofmonths=24&showchangehistorylog=1 | 23-0040543 | SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1101 | 42571101 | RECLOSER | 322 | 20230306 | 448 | 2024220 | 610 | Distribution Circuit | Vegetation | Tree - fell into line | 376 | 66267 | 38.3871 | -122.89 | CGC217430925728 | Clear-32-90F | Connector or Splice (OH) | Broken, wire on ground | 23-0040543 | OH | Sus | 45688981 | No | 2023 | MAR | Yes | Line to Ground | 1822279 | CSO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0041489&numberofmonths=24&showchangehistorylog=1 | 23-0041489 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER | 64758 | 20230308 | 706 | 2026266 | 662 | Distribution Circuit | Vegetation | Tree - fell into line | 284 | 45592 | 38.5087 | -123.0696 | 18595KINGRIDGEROAD | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0041489 | OH | Sus | 45690155 | No | 2023 | MAR | Yes | Line to Ground | 1822811 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0042735&numberofmonths=24&showchangehistorylog=1 | 23-0042735 | SONOMA | FIELD OPS NORTH | Tier 3 | DUNBAR-1103 | 43071103 | JUMPER | OJSSSOFCGC218359528520 | 20230310 | 246 | 2030063 | 793 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 7214 | 38.4477 | -122.5738 | 7SPANSLOADSIDEOF107941 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0042735 | OH | Sus | 0 | No | 2023 | MAR | Yes | None | 1823549 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0042772&numberofmonths=24&showchangehistorylog=1 | 23-0042772 | SONOMA | FIELD OPS NORTH | Tier 3 | FORT ROSS-1121 | 42851121 | TRIP-SAVER | 2987 | 20230310 | 237 | 2029958 | 283 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 7075 | 38.5423 | -123.0896 | 4SPANSLDSIDEOF4947 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0042772 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Line | 1823575 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0042772&numberofmonths=24&showchangehistorylog=1 | 23-0042772 | SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | TRIP-SAVER | 4947 | 20230310 | 241 | 2030288 | 732 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 39528 | 38.5579 | -123.0951 | 4SPANSLDSIDEOF4947 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0042772 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1823576 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0043723&numberofmonths=24&showchangehistorylog=1 | 23-0043723 | SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1101 | 42571101 | JUMPER | WIREDOWNCGC217489025790 | 20230312 | 1100 | 2033267 | 546 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 3474 | 38.3721 | -122.876 | CGC217489025790 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0043723 | OH | Sus | 45698202 | No | 2023 | MAR | Yes | Force Out | 1824239 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0043956&numberofmonths=24&showchangehistorylog=1 | 23-0043956 | SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1102 | 42571102 | RECLOSER | 658 | 20230313 | 722 | 2034041 | 688 | Distribution Circuit | Vegetation | Tree - fell into line | 132 | 70584 | 38.4451 | -122.9104 | 2SPANSLDSIDECGC217362028517 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0043956 | OH | Sus | 31639884 | No | 2023 | MAR | Yes | Multi-Fault | 1824457 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0046349&numberofmonths=24&showchangehistorylog=1 | 23-0046349 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 42419 | 20230315 | 910 | 2045634 | 511 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1022 | 38.5214 | -123.0614 | 3600EAUSTINCREEKRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0046349 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Line | 1826165 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0048603&numberofmonths=24&showchangehistorylog=1 | 23-0048603 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 2561 | 20230320 | 320 | 2052548 | 563 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 11823 | 38.4113 | -122.9652 | 4618TIMBERLN | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0048603 | OH | Sus | 31640126 | No | 2023 | MAR | Yes | Line to Line | 1827811 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0051682&numberofmonths=24&showchangehistorylog=1 | 23-0051682 | SONOMA | FIELD OPS NORTH | Tier 2 | SALMON CREEK-1101 | 43161101 | RECLOSER | 37368 | 20230324 | 647 | 2065569 | 458 | Distribution Circuit | Equipment Failure/Involved | Overhead | 187 | 41889 | 38.3809 | -123.079 | 3SPANSLDSIDEOF87781JUSTLDSIDEOFR4071 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0051682 | OH | Sus | 45708581 | No | 2023 | MAR | Yes | Line to Line | 1829827 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0052509&numberofmonths=24&showchangehistorylog=1 | 23-0052509 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | TRIP-SAVER | 1989 | 20230325 | 1341 | 2067060 | 300 | Distribution Circuit | Vegetation | Tree - branch fell on line | 43 | 12900 | 38.5219 | -122.9971 | 16270RIONIDORD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0052509 | OH | Sus | 31640450 | No | 2023 | MAR | Yes | Line to Ground | 1830463 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0053220&numberofmonths=24&showchangehistorylog=1 | 23-0053220 | SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER | 560 | 20230328 | 514 | 2069508 | 587 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 6452 | 38.5561 | -123.3034 | 6NORTHOF6745ONMAINLINE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0053220 | OH | Sus | 45709597 | No | 2023 | MAR | Yes | Line to Line | 1830975 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0053369&numberofmonths=24&showchangehistorylog=1 | 23-0053369 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 6543 | 20230328 | 745 | 2069584 | 815 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 19560 | 38.3681 | -122.9641 | 1658BURLLN | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0053369 | OH | Sus | 0 | No | 2023 | MAR | Yes | Force Out | 1831072 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0053413&numberofmonths=24&showchangehistorylog=1 | 23-0053413 | SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 11455 | 20230328 | 853 | 2070167 | 367 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 367 | 38.3997 | -122.9585 | LDSIDEOF11455 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0053413 | OH | Sus | 0 | No | 2023 | MAR | Yes | Force Out | 1831093 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0057887&numberofmonths=24&showchangehistorylog=1 | 23-0057887 | SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | FUSE | 2225 | 20230406 | 932 | 2081629 | 486 | Distribution Circuit | 3rd Party | Vehicle | 92 | 44712 | 38.5247 | -122.6543 | 5SPANSLDSIDEOF2225 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 23-0057887 | OH | Sus | 0 | No | 2023 | APR | Yes | Line to Ground | 1833790 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0060242&numberofmonths=24&showchangehistorylog=1 | 23-0060242 | SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER | 612266 | 20230412 | 1411 | 2086786 | 679 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 26481 | 38.5329 | -123.2715 | 5SPANSLDSIDEOF612266 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0060242 | OH | Sus | 31642129 | No | 2023 | APR | Yes | Three Phase Fault | 1835254 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0060686&numberofmonths=24&showchangehistorylog=1 | 23-0060686 | SONOMA | FIELD OPS NORTH | Tier 2 | GEYSERVILLE-1101 | 42891101 | FUSE | 4703 | 20230413 | 1250 | 2087725 | 187 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 748 | 38.6718 | -123.0456 | 3SPANSNOF217018536815 | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 23-0060686 | OH | Sus | 31641956 | No | 2023 | APR | Yes | Force Out | 1835571 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0079839&numberofmonths=24&showchangehistorylog=1 | 23-0079839 | SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | RECLOSER | 120 | 20230607 | 1119 | 2131913 | 574 | Distribution Circuit | Vegetation | Tree - fell into line | 492 | 89723 | 38.4637 | -123.0083 | 3SPANSLDSIDE164359 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0079839 | OH | Sus | 31651531 | No | 2023 | JUN | Yes | Multi-Fault | 1848761 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0085899&numberofmonths=24&showchangehistorylog=1 | 23-0085899 | SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 769 | 20230627 | 438 | 2146585 | 683 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 18499 | 38.5962 | -122.9148 | 3485WALLACECREEKRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0085899 | OH | Sus | 31653687 | No | 2023 | JUN | Yes | Line to Ground | 1853344 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0086263&numberofmonths=24&showchangehistorylog=1 | 23-0086263 | SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1102 | 42571102 | FUSE | 671411 | 20230627 | 1546 | 2147176 | 237 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 4503 | 38.4149 | -122.8997 | 2SPANSLDSIDEOFFUCO671411 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0086263 | OH | Sus | 45862191 | No | 2023 | JUN | Yes | Line to Ground | 1853527 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0087372&numberofmonths=24&showchangehistorylog=1 | 23-0087372 | SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | RECLOSER | 448 | 20230629 | 2143 | 2149402 | 825 | Distribution Circuit | Vegetation | Tree - fell into line | 610 | 163342 | 38.3443 | -122.5144 | PEPPERNICK20962207moringsidemountaindr | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0087372 | OH | Sus | 45865302 | No | 2023 | JUN | Yes | Line to Ground | 1854186 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0001587&numberofmonths=24&showchangehistorylog=1 | 13-0001587 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | OTHER |  | 20130102 | 47 | 724284 | 684 | Distribution Circuit | Equipment Failure/Involved | Other | 38 | 25540 | 38.4034 | -120.6493 | 1SPANNOFB527 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0001587 | OH | Sus | 41832834 | No | 2013 | JAN | Yes | Line to Ground | 99306156 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0011031&numberofmonths=24&showchangehistorylog=1 | 13-0011031 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | FROGTOWN-1701 | 163451701 | FUSE | L2659 | 20130219 | 1653 | 744211 | 472 | Distribution Circuit | Vegetation | Tree - bark fell into line | 345 | 155267 | 38.1373 | -120.4595 | Berry18538407095798Algiersst | Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 13-0011031 | OH | Sus | 41856435 | yes | 2013 | FEB | Yes | Line to Line | 99300281 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0011242&numberofmonths=24&showchangehistorylog=1 | 13-0011242 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | ELECTRA-1102 | 162161102 | RECLOSER | 2646 | 20130220 | 1003 | 745076 | 510 | Distribution Circuit | Equipment Failure/Involved | Other | 417 | 103071 | 38.2993 | -120.6981 | MAINLINEATFUCO1299 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0011242 | OH | Sus | 41856821 | yes | 2013 | FEB | Yes | Line to Line | 99300067 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0011104&numberofmonths=24&showchangehistorylog=1 | 13-0011104 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | RECLOSER | 3168 | 20130220 | 146 | 744751 | 794 | Distribution Circuit | Vegetation | Tree - fell into line | 877 | 31224 | 38.4143 | -120.6543 | 15815PINEGROVEVOLCANORDVOLCANO | Snow-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0011104 | OH | Sus | 30978350 | yes | 2013 | FEB | Yes | Line to Ground | 99300195 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0016794&numberofmonths=24&showchangehistorylog=1 | 13-0016794 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | L3713 | 20130315 | 652 | 757119 | 558 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 50 | 27900 | 38.4197 | -120.4887 | 16POLESLDSIDEOFFUSESL3713 | Partly cloudy-32 - 90 F | Conductor, Overhead | On Ground | 13-0016794 | OH | Sus | 0 | No | 2013 | MAR | Yes | Line to Ground | 99296306 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0026940&numberofmonths=24&showchangehistorylog=1 | 13-0026940 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | MARTELL-1101 | 163011101 | FUSE | 1519 | 20130424 | 1122 | 781045 | 965 | Distribution Circuit | 3rd Party | Vehicle | 84 | 79468 | 38.4353 | -120.7496 | L3161 | Clear-32 - 90 F | Pole-Wood | Broken, wire on object | 13-0026940 | OH | Sus | 30992203 | No | 2013 | APR | Yes | Line to Ground | 99288652 | PW | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0042961&numberofmonths=24&showchangehistorylog=1 | 13-0042961 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | ELECTRA-1102 | 162161102 | OTHER |  | 20130626 | 1810 | 818017 | 509 | Distribution Circuit | Equipment Failure/Involved | Other | 1169 | 141469 | 38.3608 | -120.5661 | MBLHMEREARENCOGASSTAACRFRMCALPBAR | Clear-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 13-0042961 | OH | Sus | 0 | No | 2013 | JUN | Yes | Line to Ground | 99277465 | CSO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0046552&numberofmonths=24&showchangehistorylog=1 | 13-0046552 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1704 | 163781704 | FUSE | L7523 | 20130710 | 2315 | 829516 | 439 | Distribution Circuit | Vegetation | Tree - fell into line | 162 | 25626 | 37.9364 | -120.62 | 1PNOFL3583 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0046552 | OH | Sus | 31007860 | No | 2013 | JUL | Yes | Three Phase Fault | 99274800 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0064236&numberofmonths=24&showchangehistorylog=1 | 13-0064236 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | ELECTRA-1101 | 162161101 | OTHER |  | 20130923 | 1448 | 871860 | 199 | Distribution Circuit | Vegetation | Tree - fell into line | 223 | 38118 | 38.361 | -120.7524 | EOFL65752locationsoftroublle | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0064236 | OH | Sus | 0 | No | 2013 | SEP | Yes | Line to Ground | 99262289 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0066136&numberofmonths=24&showchangehistorylog=1 | 13-0066136 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | FROGTOWN-1702 | 163451702 | FUSE | L3803 | 20131001 | 1016 | 875960 | 599 | Distribution Circuit | 3rd Party | Vehicle | 233 | 29449 | 38.1116 | -120.5082 | NOFMETER1009846495 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0066136 | OH | Sus | 31025379 | No | 2013 | OCT | Yes | Line to Line | 99260927 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0067151&numberofmonths=24&showchangehistorylog=1 | 13-0067151 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | FUSE | 1711 | 20131004 | 149 | 878035 | 379 | Distribution Circuit | Vegetation | Tree - fell into line | 145 | 27922 | 38.4982 | -120.5042 | SILVATONY21256sierracirclepioneer | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0067151 | OH | Sus | 0 | yes | 2013 | OCT | Yes | Line to Ground | 99260289 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0069685&numberofmonths=24&showchangehistorylog=1 | 13-0069685 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | L5681 | 20131015 | 1023 | 885041 | 547 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 12 | 6564 | 38.3876 | -120.447 | MachiAndrew7980SCHAADRDWILSEYVILE | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0069685 | OH | Sus | 31028552 | No | 2013 | OCT | Yes |  | 99258276 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0081173&numberofmonths=24&showchangehistorylog=1 | 13-0081173 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE | 1277 | 20131207 | 120 | 921641 | 563 | Distribution Circuit | Equipment Failure/Involved | Other | 38 | 11824 | 38.2355 | -120.4994 | COFOFMCKINNEYDIGGINSRDMCKINNEYDIGGINSPL | Snow-Below 32 F | Connector or Splice (OH) | Broken, wire on ground | 13-0081173 | OH | Sus | 0 | yes | 2013 | DEC | Yes | Line to Line | 99249032 | CSO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0081336&numberofmonths=24&showchangehistorylog=1 | 13-0081336 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | FROGTOWN-1701 | 163451701 | FUSE | 1623 | 20131207 | 1024 | 922662 | 364 | Distribution Circuit | Equipment Failure/Involved | Other | 264 | 96096 | 38.1245 | -120.4497 | L3347 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0081336 | OH | Sus | 0 | yes | 2013 | DEC | Yes | Line to Ground | 99248887 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0081374&numberofmonths=24&showchangehistorylog=1 | 13-0081374 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | FROGTOWN-1701 | 163451701 | FUSE | 1969 | 20131207 | 1708 | 923040 | 1319 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 3957 | 38.1075 | -120.4951 | 1STSPANLOADSIDE1969 | Partly cloudy-32 - 90 F | Cutout, fuse holder | Broken, wire on ground | 13-0081374 | OH | Sus | 0 | yes | 2013 | DEC | Yes | Line to Ground | 99248801 | CFH | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0081170&numberofmonths=24&showchangehistorylog=1 | 13-0081170 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | FROGTOWN-1702 | 163451702 | FUSE | L3803 | 20131207 | 224 | 921783 | 168 | Distribution Circuit | Equipment Failure/Involved | Other | 233 | 39144 | 38.1116 | -120.5082 | Berry185384070952947murphysgraderd | Snow-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0081170 | OH | Sus | 0 | yes | 2013 | DEC | Yes |  | 99249035 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0081213&numberofmonths=24&showchangehistorylog=1 | 13-0081213 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | FROGTOWN-1702 | 163451702 | FUSE | 1639 | 20131207 | 446 | 921908 | 479 | Distribution Circuit | Environmental/External | Ice or snow | 50 | 23950 | 38.0925 | -120.4782 | METER1004720871 | Snow-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0081213 | OH | Sus | 0 | yes | 2013 | DEC | Yes | Line to Ground | 99248997 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0081225&numberofmonths=24&showchangehistorylog=1 | 13-0081225 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | FROGTOWN-1702 | 163451702 | FUSE | L3319 | 20131207 | 333 | 921870 | 602 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 14432 | 38.0983 | -120.53 | Snowden188347100574418ranchroad | Snow-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0081225 | OH | Sus | 0 | yes | 2013 | DEC | Yes |  | 99248983 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0081303&numberofmonths=24&showchangehistorylog=1 | 13-0081303 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | WEST POINT-1102 | 163201102 | OTHER |  | 20131207 | 927 | 922765 | 487 | Distribution Circuit | Equipment Failure/Involved | Other | 163 | 59361 | 38.2833 | -120.5572 | JESUSMARIARDFUSES1289 | Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 13-0081303 | OH | Sus | 0 | yes | 2013 | DEC | Yes | Line to Ground | 99248914 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0005303&numberofmonths=24&showchangehistorylog=1 | 14-0005303 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE | 1051 | 20140121 | 835 | 944674 | 813 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 34 | 27642 | 38.4185 | -120.6471 | 2PNOFMTR1004741030 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0005303 | OH | Sus | 31050832 | No | 2014 | JAN | Yes |  | 99243512 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0006407&numberofmonths=24&showchangehistorylog=1 | 14-0006407 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | 1391 | 20140125 | 1425 | 947652 | 790 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 41 | 32390 | 38.3305 | -120.5353 | METER10047343771588SIMPSONRDENDOFTHEROADRAILROADFLAT | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0006407 | OH | Sus | 31052233 | No | 2014 | JAN | Yes | Three Phase Fault | 99242795 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0017406&numberofmonths=24&showchangehistorylog=1 | 14-0017406 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | RECLOSER | 4786 | 20140312 | 53 | 982849 | 868 | Distribution Circuit | Vegetation | Tree - fell into line | 180 | 46968 | 38.2321 | -120.5341 | BennettTom7043TROUTLN | Heavy rain-32 - 90 F | Pole-Wood | Broken, wire on object | 14-0017406 | OH | Sus | 31062478 | yes | 2014 | MAR | Yes | Line to Line | 99235359 | PW | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0017417&numberofmonths=24&showchangehistorylog=1 | 14-0017417 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE | L2303 | 20140312 | 219 | 982867 | 851 | Distribution Circuit | Vegetation | Tree - branch fell on line | 46 | 9820 | 38.4175 | -120.5975 | MTR1005560465 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 14-0017417 | OH | Sus | 31062473 | yes | 2014 | MAR | Yes | Line to Line | 99235353 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0017413&numberofmonths=24&showchangehistorylog=1 | 14-0017413 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | OTHER |  | 20140312 | 234 | 982877 | 401 | Distribution Circuit | Vegetation | Tree - branch fell on line | 304 | 145622 | 38.4928 | -120.5131 | MTR1004861686 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0017413 | OH | Sus | 42091067 | yes | 2014 | MAR | Yes | Line to Ground | 99235355 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0017437&numberofmonths=24&showchangehistorylog=1 | 14-0017437 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | RECLOSER | 12256 | 20140312 | 623 | 982998 | 965 | Distribution Circuit | Vegetation | Tree - fell into line | 2084 | 604367 | 38.4439 | -120.509 | Borgen30806026786REAR16470MCKENZIE | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0017437 | OH | Sus | 0 | yes | 2014 | MAR | Yes | Multi-Fault | 99235336 | PW | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0017470&numberofmonths=24&showchangehistorylog=1 | 14-0017470 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | WEST POINT-1102 | 163201102 | RECLOSER | 4788 | 20140312 | 751 | 983119 | 739 | Distribution Circuit | Vegetation | Tree - fell into line | 781 | 374884 | 38.3316 | -120.5186 | DeValle170476846006821RRFLATRD | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0017470 | OH | Sus | 0 | yes | 2014 | MAR | Yes |  | 99235131 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0018328&numberofmonths=24&showchangehistorylog=1 | 14-0018328 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | 1341 | 20140315 | 1213 | 985063 | 307 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 89 | 27323 | 38.3173 | -120.5211 | 1159TONETRAILMTR1004933640 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 14-0018328 | OH | Sus | 42093855 | No | 2014 | MAR | Yes |  | 99234724 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0018390&numberofmonths=24&showchangehistorylog=1 | 14-0018390 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | NORTH BRANCH-1101 | 163231101 | FUSE | 1115 | 20140316 | 652 | 985250 | 379 | Distribution Circuit | Equipment Failure/Involved | Other | 157 | 58105 | 38.2442 | -120.845 | Borgen3080602678614337HUNTERDR | Clear-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 14-0018390 | OH | Sus | 42093926 | No | 2014 | MAR | Yes | Line to Line | 99234657 | CSO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0025154&numberofmonths=24&showchangehistorylog=1 | 14-0025154 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | RECLOSER | 4786 | 20140415 | 1010 | 999750 | 812 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 735 | 104509 | 38.2321 | -120.5341 | Berry1853840709517255JesusMariaRd | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0025154 | OH | Sus | 31069548 | No | 2014 | APR | Yes | Line to Line | 99230101 | PW | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0028449&numberofmonths=24&showchangehistorylog=1 | 14-0028449 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1101 | 163751101 | OTHER |  | 20140430 | 1908 | 1008340 | 1002 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1002 | 38.3826 | -120.7433 | SILVATONY11970newyorkranchrd | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0028449 | OH | Sus | 42115463 | yes | 2014 | APR | Yes | Open Circuit | 99227818 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0034334&numberofmonths=24&showchangehistorylog=1 | 14-0034334 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | WEST POINT-1102 | 163201102 | FUSE | L1485 | 20140527 | 511 | 1024357 | 499 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 6302 | 38.3839 | -120.5611 | METER1004807098 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0034334 | OH | Sus | 31078507 | No | 2014 | MAY | Yes | Line to Ground | 99223879 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0034596&numberofmonths=24&showchangehistorylog=1 | 14-0034596 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | OLETA-1101 | 163541101 | RECLOSER | 1208 | 20140528 | 705 | 1025021 | 350 | Distribution Circuit | Animal | Squirrel | 478 | 60045 | 38.4373 | -120.8358 | MTR1004974181 | Clear-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 14-0034596 | OH | Sus | 31078774 | No | 2014 | MAY | Yes | Line to Ground | 99223721 | CSO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0035427&numberofmonths=24&showchangehistorylog=1 | 14-0035427 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1101 | 163751101 | FUSE | 1491 | 20140601 | 1227 | 1027061 | 704 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 156 | 28370 | 38.3987 | -120.6771 | BRASWELLDAVID18121bourbonst | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0035427 | OH | Sus | 31079751 | No | 2014 | JUN | Yes | Line to Line | 99223091 | PW | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0036758&numberofmonths=24&showchangehistorylog=1 | 14-0036758 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | MARTELL-1101 | 163011101 | FUSE | L3801 | 20140606 | 1948 | 1029772 | 958 | Distribution Circuit | Vegetation | Tree - fell into line | 84 | 37557 | 38.4355 | -120.7474 | LINEBUCKPOLESOURCESIDEOFFCOL5671 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0036758 | OH | Sus | 31081234 | No | 2014 | JUN | Yes | Line to Ground | 99222290 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0044571&numberofmonths=24&showchangehistorylog=1 | 14-0044571 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | OTHER |  | 20140715 | 900 | 1049638 | 567 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 30485 | 38.4205 | -120.5175 | Bell19147703677914Skullflatrd | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0044571 | OH | Sus | 42154654 | No | 2014 | JUL | Yes | Open Circuit | 99216326 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0047686&numberofmonths=24&showchangehistorylog=1 | 14-0047686 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | IONE-1101 | 163881101 | FUSE | 305417 | 20140729 | 828 | ODB-9921 | 354 | Distribution Circuit | 3rd Party | Contact with High Voltage- 3rd party | 1 | 354 | 38.3742 | -120.9337 | 3WOFFUSES305417 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0047686 | OH | Sus | 0 | No | 2014 | JUL | Yes |  | 99214432 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0048447&numberofmonths=24&showchangehistorylog=1 | 14-0048447 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | OLETA-1102 | 163541102 | RECLOSER | 2642 | 20140731 | 1815 | 1059064 | 343 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 6174 | 38.5013 | -120.8481 | MTR1004736134 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 14-0048447 | OH | Sus | 42161937 | yes | 2014 | JUL | Yes | Line to Ground | 99213997 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0048840&numberofmonths=24&showchangehistorylog=1 | 14-0048840 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | FROGTOWN-1702 | 163451702 | RECLOSER | 11212 | 20140803 | 1851 | 1060442 | 553 | Distribution Circuit | 3rd Party | Vehicle | 119 | 10085 | 38.0864 | -120.572 | CAROLKENNEDYANDHWY49 | Overcast-32 - 90 F | Conductor, Overhead | On Ground | 14-0048840 | OH | Sus | 31092736 | No | 2014 | AUG | Yes | Three Phase Fault | 99213608 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0049534&numberofmonths=24&showchangehistorylog=1 | 14-0049534 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | FROGTOWN-1701 | 163451701 | FUSE | 8865 | 20140806 | 1435 | 1062237 | 305 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 915 | 38.1604 | -120.477 | COFSANDOMINGOSHEEPRANCHRD | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0049534 | OH | Sus | 31093560 | No | 2014 | AUG | Yes | Line to Ground | 99213167 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0050134&numberofmonths=24&showchangehistorylog=1 | 14-0050134 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE | 9149 | 20140810 | 1014 | 1063884 | 253 | Distribution Circuit | Equipment Failure/Involved | Other | 43 | 10879 | 38.2111 | -120.6848 | BennettTom5SPANSEOGOLDSTRIKEONLEONARDRD | Clear-32 - 90 F | Insulator | Broken, wire on object | 14-0050134 | OH | Sus | 31094086 | No | 2014 | AUG | Yes |  | 99212723 | INS | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0050974&numberofmonths=24&showchangehistorylog=1 | 14-0050974 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | FROGTOWN-1702 | 163451702 | FUSE | 1573 | 20140814 | 1046 | 1066350 | 863 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 123 | 22433 | 38.0467 | -120.63 | BRASWELLDAVID1281AppaloosaWy | Clear-32 - 90 F | Conductor, Overhead | On Ground | 14-0050974 | OH | Sus | 31095029 | No | 2014 | AUG | Yes | Line to Ground | 99212012 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0056893&numberofmonths=24&showchangehistorylog=1 | 14-0056893 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | 1535 | 20140914 | 2050 | 1081289 | 985 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 11035 | 38.3845 | -120.513 | MTR1004935532 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0056893 | OH | Sus | 31101088 | No | 2014 | SEP | Yes | Line to Ground | 99207978 | PW | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0058183&numberofmonths=24&showchangehistorylog=1 | 14-0058183 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | FROGTOWN-1702 | 163451702 | FUSE | L1147 | 20140920 | 2005 | 1085021 | 893 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 5358 | 38.1049 | -120.4657 | MTR1004821671 | Lightning-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0058183 | OH | Sus | 0 | No | 2014 | SEP | Yes | Line to Line | 99207118 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0058177&numberofmonths=24&showchangehistorylog=1 | 14-0058177 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | STANISLAUS-1702 | 162821702 | OCB | OCB | 20140920 | 1944 | 1085015 | 1338 | Distribution Circuit | Vegetation | Tree - fell into line | 11494 | 4724375 | 38.1401 | -120.37 | 6SPANSSOUTHOFMTR1004820426 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0058177 | OH | Sus | 0 | No | 2014 | SEP | Yes | Three Phase Fault | 99207041 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0059349&numberofmonths=24&showchangehistorylog=1 | 14-0059349 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CORRAL-1101 | 162991101 | RECLOSER | 12606 | 20140925 | 1005 | 1087775 | 356 | Distribution Circuit | Equipment Failure/Involved | Other | 319 | 67537 | 38.1805 | -120.9261 | SSOFMTR878R09 | Drizzle-32 - 90 F | Conductor, Overhead | On Ground | 14-0059349 | OH | Sus | 0 | yes | 2014 | SEP | Yes | None | 99206316 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0062956&numberofmonths=24&showchangehistorylog=1 | 14-0062956 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | OCB | OCB | 20141011 | 1019 | 1096002 | 392 | Distribution Circuit | Animal | Bird found | 2882 | 388696 | 38.1702 | -120.6684 | DEVALLECLAYL13424 | Clear-32 - 90 F | Recloser | Broken, wire on ground | 14-0062956 | OH | Sus | 31106807 | No | 2014 | OCT | Yes | Line to Line | 99203984 | RCA | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0070350&numberofmonths=24&showchangehistorylog=1 | 14-0070350 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | OLETA-1101 | 163541101 | RECLOSER | 4768 | 20141117 | 641 | 1113819 | 369 | Distribution Circuit | Animal | Bird found | 192 | 37523 | 38.4804 | -120.8598 | MTR1006423995 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0070350 | OH | Sus | 42275168 | No | 2014 | NOV | Yes | Line to Ground | 99199026 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0076838&numberofmonths=24&showchangehistorylog=1 | 14-0076838 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | OLETA-1101 | 163541101 | FUSE | L3481 | 20141214 | 452 | 1140256 | 343 | Distribution Circuit | Equipment Failure/Involved | Other | 66 | 22638 | 38.42 | -120.8237 | LOC14581CHURCHSTAMADORCITYMTR1005017167 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on object | 14-0076838 | OH | Sus | 0 | No | 2014 | DEC | Yes | Line to Ground | 99193185 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079722&numberofmonths=24&showchangehistorylog=1 | 14-0079722 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | OTHER |  | 20141231 | 1030 | 1157159 | 474 | Distribution Circuit | Equipment Failure/Involved | Other | 1486 | 504423 | 38.4778 | -120.521 | Crane2234817539218505TIMBERLINRD | Combination wind/rain/lightning-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079722 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Open Circuit | 99189992 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0012625&numberofmonths=24&showchangehistorylog=1 | 15-0012625 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | L3851 | 20150211 | 225 | 1188265 | 527 | Distribution Circuit | 3rd Party | Vehicle | 52 | 18044 | 38.2632 | -120.4876 | 6829SWISSRANCHROADMOUNTAINRANCHCAAMADORCOUNTYANGELSCAMPDISTRICT | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0012625 | OH | Sus | 0 | No | 2015 | FEB | Yes | Line to Line | 99182486 | PW | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0019709&numberofmonths=24&showchangehistorylog=1 | 15-0019709 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | L2013 | 20150315 | 2247 | 1203958 | 343 | Distribution Circuit | 3rd Party | Vehicle | 57 | 14520 | 38.3347 | -120.5327 | BellD19147703677364RIDGERDRAILROADFLATRD | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0019709 | OH | Sus | 0 | No | 2015 | MAR | Yes | Line to Ground | 99178032 | PW | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0022835&numberofmonths=24&showchangehistorylog=1 | 15-0022835 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE | 1257 | 20150330 | 624 | 1209603 | 587 | Distribution Circuit | 3rd Party | Vehicle | 241 | 21815 | 38.4415 | -120.5418 | MTR1009642348 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0022835 | OH | Sus | 31144444 | No | 2015 | MAR | Yes | Line to Ground | 99176311 | PW | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0029586&numberofmonths=24&showchangehistorylog=1 | 15-0029586 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | MARTELL-1101 | 163011101 | OTHER |  | 20150425 | 1728 | 1225060 | 797 | Distribution Circuit | 3rd Party | Vehicle | 2 | 1594 | 38.3846 | -120.7864 | 12900RIDGERD7THDAYCURCH | Partly cloudy-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0029586 | OH | Sus | 31150881 | yes | 2015 | APR | Yes | Line to Ground | 99171763 | PW | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0037733&numberofmonths=24&showchangehistorylog=1 | 15-0037733 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE | L1701 | 20150601 | 1601 | 1242306 | 681 | Distribution Circuit | 3rd Party | Vehicle | 17 | 5541 | 38.1632 | -120.6483 | UNIONMINERDHWY49 | Partly cloudy-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0037733 | OH | Sus | 31158463 | No | 2015 | JUN | Yes | Line to Line | 99166126 | PW | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0041211&numberofmonths=24&showchangehistorylog=1 | 15-0041211 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | MARTELL-1103 | 163011103 | RECLOSER | 3152 | 20150616 | 207 | 1251448 | 878 | Distribution Circuit | 3rd Party | Vehicle | 140 | 13731 | 38.3597 | -120.8198 | MTR1009322364POLEWITHTRANSFORMERONITWASHIT | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0041211 | OH | Sus | 31161547 | No | 2015 | JUN | Yes | Line to Ground | 99163487 | PW | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0043798&numberofmonths=24&showchangehistorylog=1 | 15-0043798 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | FROGTOWN-1702 | 163451702 | FUSE | L5423 | 20150627 | 2228 | 1257975 | 517 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 517 | 38.1206 | -120.6253 | 1SPANNWOFMTR5000016211 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0043798 | OH | Sus | 31164725 | No | 2015 | JUN | Yes | Line to Line | 99161554 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0045207&numberofmonths=24&showchangehistorylog=1 | 15-0045207 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | SALT SPRINGS-2102 | 163692102 | FUSE | L7283 | 20150702 | 1726 | 1262081 | 696 | Distribution Circuit | Environmental/External | Lightning | 47 | 19192 | 38.314 | -120.2558 | Berry185384070954599BigfootCir | Partly Cloudy-Lightning-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0045207 | OH | Sus | 31165781 | yes | 2015 | JUL | Yes | Line to Line | 1143624 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0047581&numberofmonths=24&showchangehistorylog=1 | 15-0047581 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE | L3679 | 20150715 | 827 | 1268384 | 949 | Distribution Circuit | Vegetation | Tree - fell into line | 153 | 58620 | 38.4444 | -120.5319 | L3539 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0047581 | OH | Sus | 0 | No | 2015 | JUL | Yes | Line to Line | 1145381 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0052033&numberofmonths=24&showchangehistorylog=1 | 15-0052033 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | WEST POINT-1102 | 163201102 | OTHER | WIREDOWNMTR1004974732 | 20150731 | 2113 | 1281058 | 1384 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 337 | 33559 | 38.3817 | -120.5615 | MTR1004974732 | Clear-32-90 F | Conductor, Overhead | On Ground | 15-0052033 | OH | Sus | 31173255 | No | 2015 | JUL | Yes | Line to Ground | 1148537 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0058273&numberofmonths=24&showchangehistorylog=1 | 15-0058273 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | WEST POINT-1102 | 163201102 | FUSE | 1369 | 20150830 | 1705 | 1297344 | 738 | Distribution Circuit | Vegetation | Tree - fell into line | 75 | 40298 | 38.4058 | -120.5359 | TAP1SPANEOF1487JUSTEASTOFHARDTAPMTR1004807425TWD1369 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0058273 | OH | Sus | 42460498 | No | 2015 | AUG | Yes | Line to Ground | 1152983 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0060626&numberofmonths=24&showchangehistorylog=1 | 15-0060626 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | RECLOSER | 80930 | 20150910 | 2219 | 1303762 | 17249 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 351 | 744282 | 38.1945 | -120.5851 | FIELD | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 15-0060626 | OH | Sus | 0 | yes | 2015 | SEP | Yes | Line to Line | 1154676 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0063655&numberofmonths=24&showchangehistorylog=1 | 15-0063655 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | MARTELL-1102 | 163011102 | RECLOSER | 99214 | 20150925 | 1546 | 1312067 | 434 | Distribution Circuit | Vegetation | Tree - branch fell on line | 449 | 49114 | 38.3629 | -120.7749 | 1PSOF517665 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0063655 | OH | Sus | 0 | No | 2015 | SEP | Yes | Line to Line | 1156938 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0063635&numberofmonths=24&showchangehistorylog=1 | 15-0063635 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | L1733 | 20150925 | 1231 | 1311974 | 997 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 8680 | 38.3147 | -120.5269 | 2PSOFMTR1004858779 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 15-0063635 | OH | Sus | 0 | No | 2015 | SEP | Yes | Line to Line | 1156928 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0068520&numberofmonths=24&showchangehistorylog=1 | 15-0068520 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L2685 | 20151006 | 2113 | 1318006 | 648 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 27216 | 38.2356 | -120.374 | STAGGDRANDLAKEMONTDREASTINTERSECTION | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 15-0068520 | OH | Sus | 31189166 | No | 2015 | OCT | Yes | Line to Line | 1161061 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0071215&numberofmonths=24&showchangehistorylog=1 | 15-0071215 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE | 1825 | 20151017 | 823 | 1323987 | 608 | Distribution Circuit | Environmental/External | Lightning | 32 | 19456 | 38.4138 | -120.6545 | MACHIANDREWmultidamagesoncrestview | Partly Cloudy-Lightning-32-90 F | Transformer (OH) | Broken, wire on ground | 15-0071215 | OH | Sus | 0 | yes | 2015 | OCT | Yes | Line to Line | 1162938 | TXO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0075359&numberofmonths=24&showchangehistorylog=1 | 15-0075359 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | ELECTRA-1102 | 162161102 | FUSE | 2135 | 20151103 | 1504 | 1334793 | 574 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 19 | 5146 | 38.2997 | -120.6874 | MTR1008760777 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0075359 | OH | Sus | 31197345 | yes | 2015 | NOV | Yes | Line to Ground | 1166250 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0079403&numberofmonths=24&showchangehistorylog=1 | 15-0079403 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | RECLOSER | 93116 | 20151119 | 2036 | 1345622 | 474 | Distribution Circuit | Equipment Failure/Involved | Overhead | 605 | 97926 | 38.3838 | -120.527 | MTR1004805594 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0079403 | OH | Sus | 42573669 | No | 2015 | NOV | Yes | Line to Ground | 1169570 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0081245&numberofmonths=24&showchangehistorylog=1 | 15-0081245 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CLAY-1101 | 163341101 | OCB | 11012 | 20151126 | 635 | 1348962 | 440 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1694 | 210766 | 38.3422 | -120.9349 | IONE60KVTAPPOLE012GUYACROSSPRIANDWIREDOWNBETPOLES13AND12ONMAINLINE | Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 15-0081245 | OH | Sus | 42577479 | No | 2015 | NOV | Yes | Line to Line | 1171057 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0082530&numberofmonths=24&showchangehistorylog=1 | 15-0082530 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | ELECTRA-1101 | 162161101 | FUSE | L1749 | 20151203 | 1319 | 1352930 | 353 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 3177 | 38.3564 | -120.6496 | MTR1004741366 | Overcast-Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 15-0082530 | OH | Sus | 31204115 | yes | 2015 | DEC | Yes | Line to Line | 1172215 | CAW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0083435&numberofmonths=24&showchangehistorylog=1 | 15-0083435 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE | L2643 | 20151208 | 1241 | 1355825 | 224 | Distribution Circuit | 3rd Party | Other | 5 | 1120 | 38.2154 | -120.6748 | DEVALLECLAYLOADSIDEFUSESL26437026RAILROADFLATRD | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0083435 | OH | Sus | 0 | No | 2015 | DEC | Yes | Line to Ground | 1173059 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0083882&numberofmonths=24&showchangehistorylog=1 | 15-0083882 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CORRAL-1101 | 162991101 | FUSE | 11809 | 20151210 | 747 | 1357315 | 507 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 10647 | 38.1836 | -120.8903 | 7PNWOF11809 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0083882 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Line | 1173524 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0086564&numberofmonths=24&showchangehistorylog=1 | 15-0086564 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | OCB | 4786 | 20151222 | 59 | 1368388 | 660 | Distribution Circuit | Vegetation | Tree - fell into line | 2941 | 915497 | 38.4208 | -120.549 | MAINLINESOFL1613 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0086564 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Line | 1176558 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0086994&numberofmonths=24&showchangehistorylog=1 | 15-0086994 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | FROGTOWN-1702 | 163451702 | FUSE | 6851 | 20151223 | 1405 | 1370440 | 1549 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 18100 | 38.0944 | -120.5858 | 3PSOFMTR1004240428 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 15-0086994 | OH | Sus | 0 | No | 2015 | DEC | Yes | Three Phase Fault | 1177059 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0002583&numberofmonths=24&showchangehistorylog=1 | 16-0002583 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | L3851 | 20160103 | 1802 | 1376245 | 20 | Distribution Circuit | Equipment Failure/Involved | Overhead | 53 | 1060 | 38.2633 | -120.4871 | 2POLESNEOFMTR1004720562 | Overcast-32-90 F | Insulator | Broken, wire on object | 16-0002583 | OH | Sus | 0 | No | 2016 | JAN | Yes | Force Out | 1178509 | INS | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0003656&numberofmonths=24&showchangehistorylog=1 | 16-0003656 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L5379 | 20160106 | 2049 | 1379123 | 769 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 5953 | 38.2519 | -120.3527 | SILVATONY17051455lilacdrivearnold | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0003656 | OH | Sus | 31210820 | yes | 2016 | JAN | Yes | Line to Ground | 1179150 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0004864&numberofmonths=24&showchangehistorylog=1 | 16-0004864 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | 1311 | 20160112 | 1530 | 1382301 | 536 | Distribution Circuit | 3rd Party | Vehicle | 81 | 43416 | 38.3832 | -120.5328 | MTR1004974677 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 16-0004864 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Line | 1180143 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0006261&numberofmonths=24&showchangehistorylog=1 | 16-0006261 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CLAY-1103 | 163341103 | FUSE | 721 | 20160119 | 811 | 1386837 | 255 | Distribution Circuit | Vegetation | Tree - branch fell on line | 42 | 8224 | 38.308 | -120.974 | MTR1009848417 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0006261 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1181188 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0006691&numberofmonths=24&showchangehistorylog=1 | 16-0006691 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | OTHER | WIREDOWNSSMTR1004733972 | 20160119 | 2133 | 1388193 | 342 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 6624 | 38.4009 | -120.4973 | 2SPANSSSMTR1004733972 | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0006691 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Open Circuit | 1181499 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0011082&numberofmonths=24&showchangehistorylog=1 | 16-0011082 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE | L1149 | 20160206 | 1457 | 1399528 | 468 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 27 | 12636 | 38.4772 | -120.6269 | 18621PONDEROSAWAY | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0011082 | OH | Sus | 31217942 | No | 2016 | FEB | Yes | Line to Line | 1184753 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0011182&numberofmonths=24&showchangehistorylog=1 | 16-0011182 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CORRAL-1102 | 162991102 | FUSE | D3227 | 20160207 | 1851 | 1399867 | 655 | Distribution Circuit | 3rd Party | Vehicle | 41 | 26855 | 38.1397 | -120.8926 | 1PNOF12397 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0011182 | OH | Sus | 31217991 | No | 2016 | FEB | Yes | Line to Ground | 1184845 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0011552&numberofmonths=24&showchangehistorylog=1 | 16-0011552 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | WEST POINT-1102 | 163201102 | FUSE | 1341 | 20160209 | 955 | 1400699 | 906 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 91 | 82446 | 38.3173 | -120.5209 | MTR10049336421PWOFMTR1004933642 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0011552 | OH | Sus | 0 | No | 2016 | FEB | Yes | Line to Line | 1185108 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0013747&numberofmonths=24&showchangehistorylog=1 | 16-0013747 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | ELECTRA-1102 | 162161102 | FUSE | 1299 | 20160218 | 701 | 1407903 | 512 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 8192 | 38.34 | -120.5899 | MTR1004840443 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013747 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Line to Ground | 1186792 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0018291&numberofmonths=24&showchangehistorylog=1 | 16-0018291 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | WEST POINT-1102 | 163201102 | FUSE | L1639 | 20160306 | 446 | 1421089 | 590 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 5170 | 38.2673 | -120.5033 | BennettTom6085CALAVERASCIRCLE | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018291 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190155 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0020641&numberofmonths=24&showchangehistorylog=1 | 16-0020641 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | ELECTRA-1102 | 162161102 | FUSE | 1299 | 20160311 | 1825 | 1428633 | 399 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 6384 | 38.34 | -120.5899 | 5LDSIDEOF1299 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0020641 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1192013 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0020710&numberofmonths=24&showchangehistorylog=1 | 16-0020710 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | SALT SPRINGS-2102 | 163692102 | RECLOSER | 3142 | 20160312 | 24 | 1428993 | 680 | Distribution Circuit | Environmental/External | Ice or snow | 1538 | 297003 | 38.3018 | -120.277 | WIREDOWNPOLELDSIDEMIDSPANOFMTR1004652960 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0020710 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1192083 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0020943&numberofmonths=24&showchangehistorylog=1 | 16-0020943 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE | 1485 | 20160313 | 1010 | 1430105 | 418 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 6270 | 38.4866 | -120.6121 | MTR1004863193 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0020943 | OH | Sus | 42655924 | yes | 2016 | MAR | Yes | Open Circuit | 1192320 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0029045&numberofmonths=24&showchangehistorylog=1 | 16-0029045 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | MARTELL-1101 | 163011101 | FUSE | L2363 | 20160415 | 1642 | 1451621 | 736 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 4472 | 38.4567 | -120.7864 | REANOANTHONYQUARTZMNT | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0029045 | OH | Sus | 42680311 | yes | 2016 | APR | Yes | Line to Line | 1198202 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0029047&numberofmonths=24&showchangehistorylog=1 | 16-0029047 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | OLETA-1102 | 163541102 | OTHER | WIREDOWNSSOFMTR1004837569 | 20160415 | 1828 | 1451686 | 497 | Distribution Circuit | Vegetation | Tree - branch fell on line | 79 | 13823 | 38.5476 | -120.7431 | REANOANTHONYMTR1004837569 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0029047 | OH | Sus | 42680307 | yes | 2016 | APR | Yes | Line to Ground | 1198204 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0030729&numberofmonths=24&showchangehistorylog=1 | 16-0030729 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | FROGTOWN-1702 | 163451702 | OTHER | WIREDOWN1PEOF2227 | 20160422 | 1411 | 1455963 | 349 | Distribution Circuit | Equipment Failure/Involved | Overhead | 433 | 110405 | 38.0915 | -120.4822 | 1PEOF2227 | Overcast-Rain-32-90 F | Transformer (OH) | Broken, wire on ground | 16-0030729 | OH | Sus | 0 | yes | 2016 | APR | Yes | Open Circuit | 1199401 | TXO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0030926&numberofmonths=24&showchangehistorylog=1 | 16-0030926 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | WEST POINT-1102 | 163201102 | FUSE | 1417 | 20160423 | 1025 | 1456639 | 775 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2118 | 38.3245 | -120.507 | MTR1008760565 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 16-0030926 | OH | Sus | 0 | No | 2016 | APR | Yes | Line to Line | 1199590 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0031146&numberofmonths=24&showchangehistorylog=1 | 16-0031146 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | MARTELL-1101 | 163011101 | OTHER | WIREDOWNHOTMTR100499747 | 20160424 | 2035 | 1457509 | 847 | Distribution Circuit | Environmental/External | Lightning | 27 | 5625 | 38.4451 | -120.7083 | MTR1004979747 | Overcast-Drizzle-Lightning-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0031146 | OH | Sus | 0 | yes | 2016 | APR | Yes | Open Circuit | 1199824 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0031156&numberofmonths=24&showchangehistorylog=1 | 16-0031156 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | MARTELL-1101 | 163011101 | FUSE | L3887 | 20160424 | 2026 | 1457497 | 299 | Distribution Circuit | Environmental/External | Lightning | 6 | 1794 | 38.4417 | -120.7024 | L3887 | Overcast-Drizzle-Lightning-32-90 F | Transformer (OH) | Broken, wire on ground | 16-0031156 | OH | Sus | 0 | yes | 2016 | APR | Yes | Line to Line | 1199835 | TXO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0031342&numberofmonths=24&showchangehistorylog=1 | 16-0031342 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE | 1601 | 20160425 | 1129 | 1458393 | 480 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 3 | 1440 | 38.2662 | -120.5857 | 8SPANSLDSIDEOFMTR1009024466 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 16-0031342 | OH | Sus | 0 | yes | 2016 | APR | Yes | Line to Ground | 1199993 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0031326&numberofmonths=24&showchangehistorylog=1 | 16-0031326 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | OCB | 11022 | 20160425 | 1331 | 1458561 | 338 | Distribution Circuit | Environmental/External | Lightning | 4589 | 208981 | 38.4128 | -120.6607 | R283 | Partly Cloudy-32-90 F | Regulator | Broken, wire on ground | 16-0031326 | OH | Sus | 0 | yes | 2016 | APR | Yes | Force Out | 1199984 | REG | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0032820&numberofmonths=24&showchangehistorylog=1 | 16-0032820 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | 83331 | 20160430 | 630 | 1461941 | 446 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2230 | 38.3503 | -120.5124 | MTR1008715744 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0032820 | OH | Sus | 31235538 | yes | 2016 | APR | Yes | Line to Line | 1201087 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0038096&numberofmonths=24&showchangehistorylog=1 | 16-0038096 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | FROGTOWN-1702 | 163451702 | FUSE | 9825 | 20160524 | 1236 | 1475918 | 234 | Distribution Circuit | 3rd Party | Vehicle | 87 | 10678 | 38.0811 | -120.668 | 5PSSMTR1008707903 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 16-0038096 | OH | Sus | 0 | No | 2016 | MAY | Yes | Line to Ground | 1205070 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0039612&numberofmonths=24&showchangehistorylog=1 | 16-0039612 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | FUSE | L1971 | 20160529 | 1318 | 1478884 | 399 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 17 | 5019 | 38.4607 | -120.5192 | 1008924127 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0039612 | OH | Sus | 31242865 | No | 2016 | MAY | Yes | Three Phase Fault | 1206238 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0043476&numberofmonths=24&showchangehistorylog=1 | 16-0043476 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | MARTELL-1101 | 163011101 | FUSE | L3161 | 20160615 | 1309 | 1489479 | 409 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 23963 | 38.4433 | -120.7568 | MTR1008907771 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0043476 | OH | Sus | 0 | No | 2016 | JUN | Yes | Line to Ground | 1209214 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0044284&numberofmonths=24&showchangehistorylog=1 | 16-0044284 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L5111 | 20160618 | 2153 | 1492015 | 554 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 4432 | 38.2328 | -120.349 | 1SPANWESTOFMTR1004163032 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0044284 | OH | Sus | 0 | No | 2016 | JUN | Yes | Line to Line | 1209749 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0045212&numberofmonths=24&showchangehistorylog=1 | 16-0045212 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | FROGTOWN-1702 | 163451702 | OTHER | WIREDOWN3SEOFL6633 | 20160622 | 2346 | 1494395 | 482 | Distribution Circuit | Equipment Failure/Involved | Overhead | 115 | 33595 | 38.0426 | -120.5157 | 3SEOFL6633 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0045212 | OH | Sus | 42729949 | No | 2016 | JUN | Yes | Line to Ground | 1210482 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0046761&numberofmonths=24&showchangehistorylog=1 | 16-0046761 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | L1641 | 20160629 | 2144 | 1498659 | 871 | Distribution Circuit | Vegetation | Tree - fell into line | 121 | 32325 | 38.2679 | -120.5027 | MTR5000058458 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0046761 | OH | Sus | 0 | No | 2016 | JUN | Yes | Line to Line | 1211569 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0052398&numberofmonths=24&showchangehistorylog=1 | 16-0052398 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | ELECTRA-1101 | 162161101 | FUSE | L3849 | 20160725 | 1532 | 1515845 | 705 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 19951 | 38.3426 | -120.6963 | 3NOFMTR1004804388 | Clear-Above 90 | Conductor, Overhead | On Ground | 16-0052398 | OH | Sus | 31259507 | yes | 2016 | JUL | Yes | Line to Ground | 1215580 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0053688&numberofmonths=24&showchangehistorylog=1 | 16-0053688 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CORRAL-1102 | 162991102 | FUSE | 93139 | 20160729 | 1529 | 1518569 | 594 | Distribution Circuit | 3rd Party | Vehicle | 11 | 6534 | 38.1604 | -120.8539 | 2SOF93139 | Clear-Above 90 | Pole-Wood | Broken, wire on ground | 16-0053688 | OH | Sus | 0 | No | 2016 | JUL | Yes | Line to Ground | 1216438 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0065085&numberofmonths=24&showchangehistorylog=1 | 16-0065085 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CORRAL-1101 | 162991101 | FUSE | 11653 | 20160916 | 744 | 1542606 | 391 | Distribution Circuit | 3rd Party | Vehicle | 51 | 7566 | 38.1496 | -120.945 | MTR1004160881 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0065085 | OH | Sus | 0 | No | 2016 | SEP | Yes | Line to Line | 1224063 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0066724&numberofmonths=24&showchangehistorylog=1 | 16-0066724 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE | L2875 | 20160922 | 1058 | 1546224 | 247 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 10 | 2470 | 38.2414 | -120.5816 | 10351STOREYRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0066724 | OH | Sus | 0 | No | 2016 | SEP | Yes | Line to Ground | 1225269 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0072896&numberofmonths=24&showchangehistorylog=1 | 16-0072896 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1101 | 163751101 | FUSE | L699 | 20161016 | 1358 | 1562979 | 390 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 5878 | 38.3951 | -120.6789 | MTR1004977967 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 16-0072896 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Ground | 1229930 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0073060&numberofmonths=24&showchangehistorylog=1 | 16-0073060 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | SALT SPRINGS-2101 | 163692101 | FUSE | 4913 | 20161016 | 2120 | 1563737 | 438 | Distribution Circuit | Vegetation | Tree - fell into line | 136 | 59568 | 38.4203 | -120.0971 | MTR1004655410 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0073060 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Line | 1230087 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0073085&numberofmonths=24&showchangehistorylog=1 | 16-0073085 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | FUSE | L1725 | 20161016 | 2231 | 1563804 | 1007 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 31217 | 38.4831 | -120.5485 | 1SOFL3291 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 16-0073085 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Line | 1230109 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0080737&numberofmonths=24&showchangehistorylog=1 | 16-0080737 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | OLETA-1102 | 163541102 | OTHER | WIREDOWN16600TYLERRD | 20161118 | 17 | 1583771 | 409 | Distribution Circuit | Equipment Failure/Involved | Overhead | 53 | 21677 | 38.5231 | -120.7194 | 16600TYLERRDFIDDLETONCA | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0080737 | OH | Sus | 42882054 | yes | 2016 | NOV | Yes | Line to Ground | 1235856 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0081190&numberofmonths=24&showchangehistorylog=1 | 16-0081190 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | OTHER | WIREDOWNHOTATMTR1006417107 | 20161119 | 1950 | 1585409 | 563 | Distribution Circuit | Vegetation | Tree - fell into line | 682 | 139923 | 38.2948 | -120.5023 | MTR10064171074354ROLLINGOAKDR | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0081190 | OH | Sus | 42882762 | yes | 2016 | NOV | Yes | Line to Ground | 1236210 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0081866&numberofmonths=24&showchangehistorylog=1 | 16-0081866 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | MARTELL-1101 | 163011101 | FUSE | L2775 | 20161123 | 511 | 1587628 | 309 | Distribution Circuit | Vegetation | Tree - branch fell on line | 23 | 4020 | 38.4267 | -120.7159 | 3SSOFTRASNFMTR1004804486 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0081866 | OH | Sus | 42884040 | No | 2016 | NOV | Yes | Line to Ground | 1236716 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0082411&numberofmonths=24&showchangehistorylog=1 | 16-0082411 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | ELECTRA-1101 | 162161101 | OTHER | L2229 | 20161127 | 702 | 1589715 | 292 | Distribution Circuit | Animal | Bird found | 6 | 1752 | 38.3523 | -120.7468 | 1NOFFUCOL2229 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0082411 | OH | Sus | 42884853 | yes | 2016 | NOV | Yes | Open Circuit | 1237166 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0082416&numberofmonths=24&showchangehistorylog=1 | 16-0082416 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L5009 | 20161127 | 535 | 1589679 | 378 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 7938 | 38.2641 | -120.3217 | 1654PEBBLEBEACHWAY | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0082416 | OH | Sus | 31285764 | yes | 2016 | NOV | Yes | Line to Line | 1237168 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0082957&numberofmonths=24&showchangehistorylog=1 | 16-0082957 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | L1613 | 20161129 | 1256 | 1591392 | 446 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 3 | 1338 | 38.3922 | -120.5236 | MCCARTNEYMARK2024LOADSIDEOFL1613 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0082957 | OH | Sus | 42885891 | No | 2016 | NOV | Yes | Three Phase Fault | 1237584 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0086819&numberofmonths=24&showchangehistorylog=1 | 16-0086819 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | ELECTRA-1101 | 162161101 | FUSE | L3849 | 20161223 | 1401 | 1609833 | 674 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 21194 | 38.3426 | -120.6963 | 5SPANSEASTOFTXMTR1004937836 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0086819 | OH | Sus | 0 | No | 2016 | DEC | Yes | Line to Line | 1242002 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0014374&numberofmonths=24&showchangehistorylog=1 | 17-0014374 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L2049 | 20170124 | 714 | 1665577 | 2076 | Distribution Circuit | Vegetation | Tree - fell into line | 118 | 244968 | 38.2997 | -120.2717 | LDSIDEL2049 | Partly Cloudy-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0014374 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1253095 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0017847&numberofmonths=24&showchangehistorylog=1 | 17-0017847 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | 1391 | 20170206 | 1308 | 1676727 | 397 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 16674 | 38.3307 | -120.5351 | JUSTLDSIDE1391 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0017847 | OH | Sus | 31304205 | yes | 2017 | FEB | Yes | Three Phase Fault | 1255730 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0018858&numberofmonths=24&showchangehistorylog=1 | 17-0018858 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | RECLOSER | 3172 | 20170208 | 623 | 1681394 | 608 | Distribution Circuit | Vegetation | Tree - fell into line | 2926 | 420168 | 38.4101 | -120.6517 | L2149 | Overcast-Fog-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 17-0018858 | OH | Sus | 31304629 | yes | 2017 | FEB | Yes | Three Phase Fault | 1256602 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0019838&numberofmonths=24&showchangehistorylog=1 | 17-0019838 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CORRAL-1101 | 162991101 | RECLOSER | 12606 | 20170210 | 922 | 1684797 | 387 | Distribution Circuit | Equipment Failure/Involved | Overhead | 321 | 71727 | 38.1805 | -120.9262 | 3TO4SPANSWESTOFC3440 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019838 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1257280 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0020638&numberofmonths=24&showchangehistorylog=1 | 17-0020638 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE | 1419 | 20170213 | 645 | 1687085 | 370 | Distribution Circuit | Equipment Failure/Involved | Overhead | 133 | 49210 | 38.2128 | -120.5592 | MTR1006983823 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0020638 | OH | Sus | 31305376 | No | 2017 | FEB | Yes | Line to Line | 1257987 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0026851&numberofmonths=24&showchangehistorylog=1 | 17-0026851 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | STANISLAUS-1701 | 162821701 | FUSE | 2697 | 20170226 | 625 | 1714246 | 1026 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 7182 | 38.1508 | -120.4404 | 1NOF2697 | Clear-Below 32 F | Pole-Wood | Broken, wire on ground | 17-0026851 | OH | Sus | 0 | No | 2017 | FEB | Yes | Line to Line | 1263551 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0026980&numberofmonths=24&showchangehistorylog=1 | 17-0026980 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | RECLOSER | 11236 | 20170227 | 801 | 1714824 | 734 | Distribution Circuit | 3rd Party | Vehicle | 181 | 17834 | 38.1697 | -120.6677 | 4PSEOFL4131 | Partly Cloudy-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 17-0026980 | OH | Sus | 0 | No | 2017 | FEB | Yes | Line to Line | 1263658 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0027326&numberofmonths=24&showchangehistorylog=1 | 17-0027326 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | SALT SPRINGS-2102 | 163692102 | FUSE | L1695 | 20170228 | 808 | 1715732 | 1815 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3630 | 38.3556 | -120.2074 | 1LDSIDEOFL1695 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0027326 | OH | Sus | 31308301 | No | 2017 | FEB | Yes | Line to Line | 1263941 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0029389&numberofmonths=24&showchangehistorylog=1 | 17-0029389 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | SALT SPRINGS-2102 | 163692102 | FUSE | 91563 | 20170308 | 927 | 1722369 | 430 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 17279 | 38.3186 | -120.2549 | LDSIDEOFMTR1004242168 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0029389 | OH | Sus | 31311290 | No | 2017 | MAR | Yes | Line to Line | 1265529 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0031432&numberofmonths=24&showchangehistorylog=1 | 17-0031432 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | ELECTRA-1101 | 162161101 | OTHER | WIREDOWN3SPANSSWOFMTR1004974986 | 20170317 | 710 | 1728905 | 349 | Distribution Circuit | Animal | Bird found | 1970 | 89126 | 38.3603 | -120.7527 | 3SPANSSWOFMTR1004974986 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0031432 | OH | Sus | 42972728 | No | 2017 | MAR | Yes | Open Circuit | 1267045 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0033710&numberofmonths=24&showchangehistorylog=1 | 17-0033710 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | JUMPER | OJ15585HINTONRD | 20170325 | 1111 | 1735314 | 463 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 6679 | 38.4345 | -120.568 | 15585HINTONRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0033710 | OH | Sus | 31314730 | yes | 2017 | MAR | Yes | Open Circuit | 1268660 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0038429&numberofmonths=24&showchangehistorylog=1 | 17-0038429 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE | L3335 | 20170409 | 740 | 1753424 | 159 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 159 | 38.236 | -120.5825 | 2POLESLOADSIDEOFTRANSFORMERMTR1010146917 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0038429 | OH | Sus | 0 | No | 2017 | APR | Yes | Line to Line | 1272484 | CSO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0042499&numberofmonths=24&showchangehistorylog=1 | 17-0042499 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | MARTELL-1101 | 163011101 | RECLOSER | 91216 | 20170424 | 1151 | 1765994 | 932 | Distribution Circuit | Equipment Failure/Involved | Overhead | 427 | 63099 | 38.4349 | -120.7501 | FUCO70951 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0042499 | OH | Sus | 0 | No | 2017 | APR | Yes | Three Phase Fault | 1275546 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0047377&numberofmonths=24&showchangehistorylog=1 | 17-0047377 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | ELECTRA-1102 | 162161102 | FUSE | 92251 | 20170511 | 1515 | 1780195 | 715 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 715 | 38.3436 | -120.5834 | JUSTEOF92251 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0047377 | OH | Sus | 31325324 | No | 2017 | MAY | Yes | Line to Line | 1279125 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0054145&numberofmonths=24&showchangehistorylog=1 | 17-0054145 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | FUSE | L6515 | 20170609 | 2150 | 1800879 | 671 | Distribution Circuit | 3rd Party | Vehicle | 3 | 2013 | 38.461 | -120.5263 | 1WOFFUCOL6515 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 17-0054145 | OH | Sus | 0 | No | 2017 | JUN | Yes | Line to Line | 1284037 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0057686&numberofmonths=24&showchangehistorylog=1 | 17-0057686 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | OTHER | WIREDOWN1PNOF1PEOFMTR1004935044 | 20170622 | 936 | 1814850 | 428 | Distribution Circuit | Equipment Failure/Involved | Overhead | 59 | 22732 | 38.3975 | -120.4724 | 1PNOF1PEOFMTR1004935044 | Clear-Heat Wave-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0057686 | OH | Sus | 0 | yes | 2017 | JUN | Yes | Line to Ground | 1286967 | CAW | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0060070&numberofmonths=24&showchangehistorylog=1 | 17-0060070 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | ELECTRA-1102 | 162161102 | FUSE | L5783 | 20170702 | 1151 | 1822355 | 448 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 20 | 7740 | 38.3459 | -120.5659 | DORRISRYAN19144556INDEPENDENCERD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0060070 | OH | Sus | 43048182 | No | 2017 | JUL | Yes | Line to Line | 1288750 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0061333&numberofmonths=24&showchangehistorylog=1 | 17-0061333 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CORRAL-1102 | 162991102 | FUSE | L3665 | 20170707 | 1812 | 1825836 | 423 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 1593 | 38.1365 | -120.8679 | ON1PHASETAP2EOFL3665 | Clear-Drizzle-Above 90 | Conductor, Overhead | Broken, wire on ground | 17-0061333 | OH | Sus | 43052361 | yes | 2017 | JUL | Yes | Line to Ground | 1289539 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0061874&numberofmonths=24&showchangehistorylog=1 | 17-0061874 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | ELECTRA-1101 | 162161101 | FUSE | 1557 | 20170710 | 1850 | 1828569 | 550 | Distribution Circuit | Equipment Failure/Involved | Other | 11 | 6050 | 38.354 | -120.7422 | REANOANTHONY20091SEOFMTR1009024412 | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 17-0061874 | OH | Sus | 31336353 | No | 2017 | JUL | Yes | Line to Ground | 1289987 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0065145&numberofmonths=24&showchangehistorylog=1 | 17-0065145 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | ELECTRA-1101 | 162161101 | OTHER | WIREDWN4NWOFMTR1004804388 | 20170724 | 1952 | 1839110 | 530 | Distribution Circuit | Vegetation | Tree - bark fell into line | 55 | 14281 | 38.3528 | -120.7112 | 4NWOFMTR1004804388 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0065145 | OH | Sus | 31338986 | No | 2017 | JUL | Yes | Open Circuit | 1292432 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0065604&numberofmonths=24&showchangehistorylog=1 | 17-0065604 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | L3233 | 20170726 | 955 | 1840145 | 453 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2718 | 38.382 | -120.5086 | 2POLESLDSIDEL3233 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0065604 | OH | Sus | 0 | No | 2017 | JUL | Yes | Line to Line | 1292751 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0068000&numberofmonths=24&showchangehistorylog=1 | 17-0068000 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | NORTH BRANCH-1101 | 163231101 | OTHER | WIREDOWNSSOFMTR1005574893 | 20170804 | 1009 | 1846312 | 326 | Distribution Circuit | Environmental/External | Lightning | 398 | 4134 | 38.2171 | -120.8411 | SSOFMTR1005574893 | Partly Cloudy-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0068000 | OH | Sus | 0 | No | 2017 | AUG | Yes | Open Circuit | 1294353 | CSO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0068306&numberofmonths=24&showchangehistorylog=1 | 17-0068306 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L5369 | 20170806 | 1856 | 1847455 | 616 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 10472 | 38.2558 | -120.3537 | 3SOFFUCOL5369 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0068306 | OH | Sus | 31341116 | No | 2017 | AUG | Yes | Multi-Fault | 1294587 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0069789&numberofmonths=24&showchangehistorylog=1 | 17-0069789 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | RECLOSER | 93116 | 20170812 | 336 | 1850967 | 682 | Distribution Circuit | Vegetation | Tree - fell into line | 341 | 41834 | 38.3838 | -120.527 | 2PEOFR281 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0069789 | OH | Sus | 0 | No | 2017 | AUG | Yes | Three Phase Fault | 1295624 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0073275&numberofmonths=24&showchangehistorylog=1 | 17-0073275 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE | L2313 | 20170828 | 458 | 1861006 | 450 | Distribution Circuit | Vegetation | Tree - fell into line | 112 | 37600 | 38.4171 | -120.5863 | MTR1004932770 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0073275 | OH | Sus | 0 | yes | 2017 | AUG | Yes | Line to Ground | 1298152 | CAW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0073393&numberofmonths=24&showchangehistorylog=1 | 17-0073393 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1701 | 162821701 | FUSE | 1113 | 20170828 | 948 | 1861247 | 196 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 4116 | 38.2084 | -120.3676 | BennettTom18511POLESEOFCO1113 | Clear-Heat Wave-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0073393 | OH | Sus | 0 | yes | 2017 | AUG | Yes | Line to Line | 1298233 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0092535&numberofmonths=24&showchangehistorylog=1 | 17-0092535 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1101 | 163751101 | FUSE | L4043 | 20171103 | 1549 | 1915405 | 1451 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 5652 | 38.4265 | -120.6929 | MTR5000059906 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 17-0092535 | OH | Sus | 0 | yes | 2017 | NOV | Yes | Line to Line | 1312048 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0095804&numberofmonths=24&showchangehistorylog=1 | 17-0095804 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | TRIP-SAVER | 1305 | 20171117 | 518 | 1924527 | 478 | Distribution Circuit | Vegetation | Tree - fell into line | 94 | 44932 | 38.4009 | -120.5045 | REANOANTHONY20096LDSIDE1305 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0095804 | OH | Sus | 0 | yes | 2017 | NOV | Yes | Line to Ground | 1314572 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0100245&numberofmonths=24&showchangehistorylog=1 | 17-0100245 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | SALT SPRINGS-2102 | 163692102 | FUSE | 2681 | 20171206 | 823 | 1937158 | 364 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 364 | 38.3199 | -120.2635 | SILVATONY1705co2681acrossfromUSFSfirestationDORRINGTON | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0100245 | OH | Sus | 31368584 | No | 2017 | DEC | Yes | Line to Ground | 1317949 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0003970&numberofmonths=24&showchangehistorylog=1 | 18-0003970 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | ELECTRA-1102 | 162161102 | RECLOSER | 4756 | 20180106 | 432 | 3051 | 796 | Distribution Circuit | Vegetation | Tree - fell into line | 524 | 41613 | 38.3164 | -120.713 | 3SPANSNORTHWESTOF4756 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on object | 18-0003970 | OH | Sus | 43245624 | No | 2018 | JAN | Yes | Three Phase Fault | 1323411 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0008066&numberofmonths=24&showchangehistorylog=1 | 18-0008066 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | ELECTRA-1102 | 162161102 | FUSE | L5783 | 20180123 | 610 | 12282 | 437 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 4007 | 38.3456 | -120.5659 | MTR1004933343 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0008066 | OH | Sus | 0 | No | 2018 | JAN | Yes | Line to Ground | 1326008 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0011684&numberofmonths=24&showchangehistorylog=1 | 18-0011684 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | ELECTRA-1101 | 162161101 | OTHER | 67293 | 20180205 | 1751 | 19826 | 453 | Distribution Circuit | Equipment Failure/Involved | Overhead | 223 | 33935 | 38.3628 | -120.7315 | 1SPANEOFL6575 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0011684 | OH | Sus | 43267571 | No | 2018 | FEB | Yes | Line to Ground | 1328354 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0017600&numberofmonths=24&showchangehistorylog=1 | 18-0017600 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | SALT SPRINGS-2102 | 163692102 | RECLOSER | 97924 | 20180227 | 700 | 32522 | 75 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 1500 | 38.3232 | -120.2538 | 7EOF4691 | Partly Cloudy-Below 32 F | Conductor, Overhead | Broken, wire on ground | 18-0017600 | OH | Sus | 0 | yes | 2018 | FEB | Yes | Line to Line | 1332333 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0018972&numberofmonths=24&showchangehistorylog=1 | 18-0018972 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | RECLOSER | 3168 | 20180302 | 507 | 35947 | 191 | Distribution Circuit | 3rd Party | Vehicle | 1064 | 119266 | 38.4142 | -120.6538 | 1EOFL2471 | Overcast-Snow-32-90 F | Pole-Wood | Broken, wire on ground | 18-0018972 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1333324 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0019392&numberofmonths=24&showchangehistorylog=1 | 18-0019392 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | OTHER | WIREDOWN1NO35576 | 20180303 | 1023 | 37379 | 299 | Distribution Circuit | Vegetation | Tree - fell into line | 73 | 11986 | 38.418 | -120.6133 | MTR10047374941NO35576 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0019392 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Open Circuit | 1333597 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0019409&numberofmonths=24&showchangehistorylog=1 | 18-0019409 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | FUSE | 1711 | 20180303 | 831 | 37253 | 564 | Distribution Circuit | Vegetation | Tree - fell into line | 147 | 77288 | 38.4983 | -120.5045 | MTR1004856510 | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0019409 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1333611 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0019550&numberofmonths=24&showchangehistorylog=1 | 18-0019550 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE | L685 | 20180304 | 607 | 37893 | 437 | Distribution Circuit | Vegetation | Tree - branch fell on line | 47 | 8821 | 38.4011 | -120.6359 | 2SPANSEOFMTR1004840824 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 18-0019550 | OH | Sus | 0 | No | 2018 | MAR | Yes | Line to Ground | 1333745 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0020396&numberofmonths=24&showchangehistorylog=1 | 18-0020396 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CLAY-1103 | 163341103 | OCB | 11032 | 20180306 | 1757 | 39447 | 400 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1435 | 142000 | 38.3422 | -120.935 | REANOANTHONY20093ldside1495 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0020396 | OH | Sus | 43290263 | No | 2018 | MAR | Yes | Multi-Fault | 1334390 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0024229&numberofmonths=24&showchangehistorylog=1 | 18-0024229 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | SALT SPRINGS-2101 | 163692101 | RECLOSER | 10416 | 20180317 | 125 | 48277 | 5125 | Distribution Circuit | Equipment Failure/Involved | Overhead | 57 | 292125 | 38.4983 | -120.2183 | SOFMTR1006494939 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 18-0024229 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1336934 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0025152&numberofmonths=24&showchangehistorylog=1 | 18-0025152 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE | L3843 | 20180321 | 1553 | 49639 | 777 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2856 | 38.2313 | -120.7083 | MTR1005428037 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 18-0025152 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1337366 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0033415&numberofmonths=24&showchangehistorylog=1 | 18-0033415 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | OTHER | WIREDOWNLDSIDEL1137 | 20180418 | 1152 | 69502 | 335 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 2010 | 38.4024 | -120.4877 | BETWEEN3RD4THPOLELDSIDEOFL1137 | Overcast-32-90 F | Crossarm, Wood | Broken, wire on ground | 18-0033415 | OH | Sus | 31389222 | No | 2018 | APR | Yes | Open Circuit | 1343537 | CAW | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0044636&numberofmonths=24&showchangehistorylog=1 | 18-0044636 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | RECLOSER | 93116 | 20180526 | 1323 | 94502 | 555 | Distribution Circuit | Vegetation | Tree - fell into line | 611 | 77540 | 38.3838 | -120.527 | 77204 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0044636 | OH | Sus | 31393676 | No | 2018 | MAY | Yes | Line to Line | 1351727 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0049807&numberofmonths=24&showchangehistorylog=1 | 18-0049807 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | RECLOSER | 3172 | 20180611 | 1948 | 106752 | 633 | Distribution Circuit | 3rd Party | Vehicle | 2928 | 364608 | 38.4101 | -120.6517 | MTR1004804494 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 18-0049807 | OH | Sus | 31395449 | No | 2018 | JUN | Yes | Line to Ground | 1355812 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0060187&numberofmonths=24&showchangehistorylog=1 | 18-0060187 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | TRIP-SAVER | 1391 | 20180716 | 1031 | 132762 | 683 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 42 | 28686 | 38.3306 | -120.5352 | MTR1004734375 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 18-0060187 | OH | Sus | 0 | No | 2018 | JUL | Yes | Three Phase Fault | 1364140 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0060592&numberofmonths=24&showchangehistorylog=1 | 18-0060592 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | L5681 | 20180717 | 944 | 133661 | 378 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 5292 | 38.3878 | -120.4469 | MTR1008768437 | Clear-32-90F | Conductor, Overhead | On Ground | 18-0060592 | OH | Sus | 31400217 | yes | 2018 | JUL | Yes | Line to Line | 1364442 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0061254&numberofmonths=24&showchangehistorylog=1 | 18-0061254 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | OTHER | WIREDOWNSOF1167 | 20180718 | 2043 | 135145 | 511 | Distribution Circuit | Vegetation | Tree - fell into line | 607 | 75822 | 38.2291 | -120.5411 | SOF1167 | Clear-32-90F | Crossarm, Wood | Broken, wire on ground | 18-0061254 | OH | Sus | 31400334 | yes | 2018 | JUL | Yes | Line to Ground | 1364864 | CAW | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0060882&numberofmonths=24&showchangehistorylog=1 | 18-0060882 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | 2111 | 20180718 | 114 | 134352 | 642 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 6420 | 38.3631 | -120.5613 | REANOANTHONY20092SPANSNEOFLINEBUCKMTR1004978425 | Clear-32-90F | Crossarm, Wood | Broken, wire on ground | 18-0060882 | OH | Sus | 31400322 | yes | 2018 | JUL | Yes | Line to Ground | 1364592 | CAW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0061291&numberofmonths=24&showchangehistorylog=1 | 18-0061291 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | OLETA-1102 | 163541102 | FUSE | L3821 | 20180719 | 402 | 135246 | 683 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 3590 | 38.4976 | -120.7714 | MACHIANDREW1852near20050quartzmntrd | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0061291 | OH | Sus | 0 | yes | 2018 | JUL | Yes | Line to Line | 1364899 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0065131&numberofmonths=24&showchangehistorylog=1 | 18-0065131 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1701 | 162821701 | FUSE | 1681 | 20180730 | 1436 | 145323 | 745 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 17880 | 38.1987 | -120.3647 | DEVALLECLAY1704FUSES1681 | Clear-32-90F | Crossarm, Wood | Broken, wire on ground | 18-0065131 | OH | Sus | 31401706 | No | 2018 | JUL | Yes | Multi-Fault | 1367828 | CAW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0065131&numberofmonths=24&showchangehistorylog=1 | 18-0065131 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1701 | 162821701 | JUMPER | DDE1SPSOF1681 | 20180730 | 2130 | 145552 | 325 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 650 | 38.198 | -120.3648 | 1681 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 18-0065131 | OH | Sus | 31401706 | No | 2018 | JUL | Yes | Force Out | 1367869 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0075993&numberofmonths=24&showchangehistorylog=1 | 18-0075993 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | FROGTOWN-1701 | 163451701 | TRIP-SAVER | 1623 | 20180903 | 1334 | 167457 | 540 | Distribution Circuit | Vegetation | Tree - branch fell on line | 276 | 149040 | 38.1247 | -120.45 | 1203GREENMEADOWCT | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0075993 | OH | Sus | 43453134 | No | 2018 | SEP | Yes | Line to Line | 1375348 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0087904&numberofmonths=24&showchangehistorylog=1 | 18-0087904 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE | L1631 | 20181007 | 843 | 190049 | 943 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 53751 | 38.2641 | -120.5842 | DORRISRYAN19142POLESNOCOsL5253 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 18-0087904 | OH | Sus | 31411666 | yes | 2018 | OCT | Yes | Line to Line | 1383832 | PW | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0091459&numberofmonths=24&showchangehistorylog=1 | 18-0091459 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | L3851 | 20181017 | 1414 | 197492 | 726 | Distribution Circuit | 3rd Party | Vehicle | 53 | 13192 | 38.2633 | -120.4871 | 6323SWISSRANCH | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 18-0091459 | OH | Sus | 0 | No | 2018 | OCT | Yes | Line to Ground | 1386450 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0092066&numberofmonths=24&showchangehistorylog=1 | 18-0092066 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CORRAL-1101 | 162991101 | FUSE | 11783 | 20181019 | 906 | 198424 | 224 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 672 | 38.1813 | -120.9632 | BEYOND11783BETWHERELINEBUCKSTOTHEWESTANDEOL | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0092066 | OH | Sus | 43511611 | No | 2018 | OCT | Yes | Line to Ground | 1386827 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0093086&numberofmonths=24&showchangehistorylog=1 | 18-0093086 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | MARTELL-1101 | 163011101 | FUSE | 65557 | 20181022 | 1948 | 200452 | 571 | Distribution Circuit | 3rd Party | Vehicle | 3 | 1713 | 38.4246 | -120.756 | 2POLENOFMTR1004732928 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 18-0093086 | OH | Sus | 0 | No | 2018 | OCT | Yes | Line to Line | 1387465 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0102567&numberofmonths=24&showchangehistorylog=1 | 18-0102567 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1101 | 163751101 | RECLOSER | 3166 | 20181123 | 1214 | 222905 | 266 | Distribution Circuit | Vegetation | Tree - fell into line | 330 | 39424 | 38.4065 | -120.6704 | 3EOFMTR1004933366ONMANZANITAWAY | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0102567 | OH | Sus | 0 | yes | 2018 | NOV | Yes | Line to Line | 1394698 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0104666&numberofmonths=24&showchangehistorylog=1 | 18-0104666 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | FROGTOWN-1701 | 163451701 | TRIP-SAVER | 6807 | 20181128 | 2324 | 227115 | 139 | Distribution Circuit | Vegetation | Tree - fell into line | 186 | 25854 | 38.1241 | -120.4507 | ATMTR1005419154 | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0104666 | OH | Sus | 43587893 | yes | 2018 | NOV | Yes | Line to Ground | 1395980 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0110299&numberofmonths=24&showchangehistorylog=1 | 18-0110299 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | FROGTOWN-1702 | 163451702 | FUSE | 9825 | 20181221 | 2018 | 245366 | 502 | Distribution Circuit | Vegetation | Tree - fell into line | 91 | 12040 | 38.081 | -120.668 | 7240TAPADEROST | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0110299 | OH | Sus | 43621105 | No | 2018 | DEC | Yes | Line to Ground | 1401320 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0111275&numberofmonths=24&showchangehistorylog=1 | 18-0111275 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | WEST POINT-1102 | 163201102 | TRIP-SAVER | 1341 | 20181231 | 1606 | 250846 | 2691 | Distribution Circuit | Vegetation | Tree - fell into line | 86 | 16801 | 38.3173 | -120.5209 | MTR1008760756 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 18-0111275 | OH | Sus | 0 | yes | 2018 | DEC | Yes | Line to Ground | 1402530 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0003906&numberofmonths=24&showchangehistorylog=1 | 19-0003906 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | MARTELL-1102 | 163011102 | OTHER | WIREDOWN | 20190103 | 654 | 252303 | 350 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1254 | 100562 | 38.3709 | -120.7863 | SEOFL7467 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0003906 | OH | Sus | 43625061 | No | 2019 | JAN | Yes | Line to Ground | 1402836 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0004169&numberofmonths=24&showchangehistorylog=1 | 19-0004169 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | WEST POINT-1102 | 163201102 | RECLOSER | 4788 | 20190103 | 1340 | 252606 | 979 | Distribution Circuit | 3rd Party | Vehicle | 710 | 207088 | 38.3314 | -120.5187 | 1NOFMTR1004818961 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 19-0004169 | OH | Sus | 31420230 | No | 2019 | JAN | Yes | Line to Ground | 1402924 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0005736&numberofmonths=24&showchangehistorylog=1 | 19-0005736 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | SALT SPRINGS-2102 | 163692102 | FUSE | 1151 | 20190107 | 807 | 259085 | 581 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 1922 | 38.2774 | -120.3184 | LINEBUCKLDSIDEOF1151GOINGSOUTH | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005736 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Three Phase Fault | 1404145 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0009271&numberofmonths=24&showchangehistorylog=1 | 19-0009271 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | WEST POINT-1102 | 163201102 | JUMPER | WIREDOWN2PWOFLBFEEDINGMTR1008714431 | 20190115 | 1631 | 266167 | 613 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1839 | 38.2743 | -120.5266 | 2PWOFLBFEEDINGMTR1008714431 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009271 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Open Circuit | 1406408 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0012775&numberofmonths=24&showchangehistorylog=1 | 19-0012775 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | FROGTOWN-1701 | 163451701 | FUSE | L2969 | 20190120 | 2211 | 277814 | 1089 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 5445 | 38.1385 | -120.4131 | 3NOFL2969 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0012775 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1409107 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0014840&numberofmonths=24&showchangehistorylog=1 | 19-0014840 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | MARTELL-1101 | 163011101 | RECLOSER | 6074 | 20190127 | 1709 | 282207 | 237 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1419 | 113230 | 38.3928 | -120.7927 | SHAKERIDGESTONEJUGG | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0014840 | OH | Sus | 43659377 | No | 2019 | JAN | Yes | Line to Ground | 1410250 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0015289&numberofmonths=24&showchangehistorylog=1 | 19-0015289 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | MARTELL-1101 | 163011101 | OTHER | WIREDOWNMTR1004979750 | 20190128 | 1859 | 282898 | 397 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1844 | 92290 | 38.4417 | -120.709 | MTR100497975017125SHAKERIDGERD | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0015289 | OH | Sus | 0 | No | 2019 | JAN | Yes | Force Out | 1410431 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0017438&numberofmonths=24&showchangehistorylog=1 | 19-0017438 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L2065 | 20190203 | 455 | 288435 | 717 | Distribution Circuit | Vegetation | Tree - fell into line | 333 | 238761 | 38.3008 | -120.2732 | LDSIDEOFL2065 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0017438 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1411854 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019539&numberofmonths=24&showchangehistorylog=1 | 19-0019539 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | CALAVERAS CEMENT-1101 | 162211101 | FUSE | L3851 | 20190206 | 1948 | 295181 | 2528 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 96064 | 38.2633 | -120.4871 | LDSIDEOFL3851 | Partly Cloudy-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0019539 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1413439 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019543&numberofmonths=24&showchangehistorylog=1 | 19-0019543 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | CALAVERAS CEMENT-1101 | 162211101 | FUSE | 1425 | 20190206 | 1948 | 295191 | 1339 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 64272 | 38.2709 | -120.4948 | LDSIDE | Partly Cloudy-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0019543 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1413442 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0018803&numberofmonths=24&showchangehistorylog=1 | 19-0018803 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | RECLOSER | 35576 | 20190206 | 118 | 293818 | 1203 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 67368 | 38.4176 | -120.6137 | MACHIANDREW185214500pioneervolcanord | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018803 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1412869 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019445&numberofmonths=24&showchangehistorylog=1 | 19-0019445 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | WEST POINT-1101 | 163201101 | FUSE | 1315 | 20190206 | 2216 | 294936 | 3654 | Distribution Circuit | Vegetation | Tree - branch fell on line | 53 | 187097 | 38.3776 | -120.554 | MTR1004980757 | Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0019445 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1413379 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019509&numberofmonths=24&showchangehistorylog=1 | 19-0019509 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | FUSE | 1391 | 20190206 | 2040 | 295088 | 2275 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 91000 | 38.3306 | -120.5352 | ATMTR1010390315 | Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0019509 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1413407 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019656&numberofmonths=24&showchangehistorylog=1 | 19-0019656 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | JUMPER | OJ1EOFMTR1004732874 | 20190206 | 2040 | 295420 | 2924 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 29240 | 38.336 | -120.5283 | MTR1004732874 | Fog-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0019656 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1413506 | PW | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019673&numberofmonths=24&showchangehistorylog=1 | 19-0019673 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | FUSE | L2013 | 20190206 | 2040 | 295094 | 1025 | Distribution Circuit | Equipment Failure/Involved | Overhead | 51 | 52275 | 38.3346 | -120.5325 | MTR1004732874 | Fog-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0019673 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1413510 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019787&numberofmonths=24&showchangehistorylog=1 | 19-0019787 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | WEST POINT-1101 | 163201101 | TRIP-SAVER | 1369 | 20190206 | 1509 | 294489 | 2936 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 217264 | 38.4058 | -120.5359 | 3PNE14872PNE1487ATCOUTPOLE1487 | Partly Cloudy-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0019787 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1413574 | CAW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019551&numberofmonths=24&showchangehistorylog=1 | 19-0019551 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | CALAVERAS CEMENT-1101 | 162211101 | FUSE | L5217 | 20190207 | 1024 | 295217 | 544 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1088 | 38.2786 | -120.5069 | 2SPLOADSIDEOFL5217 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0019551 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1413449 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019796&numberofmonths=24&showchangehistorylog=1 | 19-0019796 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE | L5701 | 20190207 | 1825 | 295676 | 1195 | Distribution Circuit | 3rd Party | Vehicle | 34 | 8762 | 38.4046 | -120.6618 | 2SEOFMTR1005450797 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0019796 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1413581 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019696&numberofmonths=24&showchangehistorylog=1 | 19-0019696 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | FUSE | 6829 | 20190207 | 1207 | 295356 | 7368 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 36840 | 38.3422 | -120.4522 | 6829 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 19-0019696 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1413520 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020286&numberofmonths=24&showchangehistorylog=1 | 19-0020286 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | FUSE | L3231 | 20190207 | 1105 | 295282 | 3205 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 27937 | 38.3802 | -120.5157 | MTR1004980198 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020286 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1413991 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019972&numberofmonths=24&showchangehistorylog=1 | 19-0019972 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | FUSE | L5725 | 20190208 | 758 | 295953 | 472 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 7552 | 38.3744 | -120.4772 | MTR1004934423MTR1004934433JUSTWOFTHATTRANSFBEFORETHE4WAY | Partly Cloudy-Below 32 F | Conductor, Overhead | On Ground | 19-0019972 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1413739 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020368&numberofmonths=24&showchangehistorylog=1 | 19-0020368 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | TRANSFORMER | 320041568630 | 20190208 | 1452 | 296390 | 2776 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 2776 | 38.3849 | -120.4866 | HOLLANDDONAVON3030JURSRD | Overcast-32-90 F | Transformer | Broken, wire on ground | 19-0020368 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1414043 | TX | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021240&numberofmonths=24&showchangehistorylog=1 | 19-0021240 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | TRIP-SAVER | L3355 | 20190211 | 1823 | 300242 | 1277 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 61296 | 38.5061 | -120.4938 | GRANILLOD199024PWOL3355 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0021240 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1414833 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021035&numberofmonths=24&showchangehistorylog=1 | 19-0021035 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | RECLOSER | 37276 | 20190211 | 1144 | 299632 | 237 | Distribution Circuit | Vegetation | Tree - fell into line | 794 | 84848 | 38.2391 | -120.3364 | MTR1004162048 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0021035 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1414707 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0025609&numberofmonths=24&showchangehistorylog=1 | 19-0025609 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | SALT SPRINGS-2101 | 163692101 | FUSE | 5885 | 20190218 | 1148 | 317552 | 219 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 3066 | 38.416 | -120.1334 | SOFCGC321061870005 | Clear-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025609 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1418656 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0026181&numberofmonths=24&showchangehistorylog=1 | 19-0026181 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE | L7247 | 20190219 | 1258 | 318834 | 1380 | Distribution Circuit | Vegetation | Tree - fell into line | 73 | 3541 | 38.4316 | -120.6246 | LOADSIDEOFL7247 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0026181 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1419035 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0026181&numberofmonths=24&showchangehistorylog=1 | 19-0026181 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | JUMPER | JPRS1NOFL7253 | 20190219 | 1749 | 319170 | 1089 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1089 | 38.4324 | -120.6245 | L7247LOADSIDE | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0026181 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1419054 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0026963&numberofmonths=24&showchangehistorylog=1 | 19-0026963 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | TRIP-SAVER | L3355 | 20190221 | 1140 | 320571 | 560 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 26880 | 38.5061 | -120.4938 | 6SOFWANDERINGHILLSRDANDSHAKERIDGERD | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0026963 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1419468 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0037584&numberofmonths=24&showchangehistorylog=1 | 19-0037584 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | MARTELL-1101 | 163011101 | FUSE | L1141 | 20190327 | 1533 | 348730 | 673 | Distribution Circuit | Vegetation | Tree - fell into line | 64 | 43072 | 38.4083 | -120.7513 | MCCARTNEYMARK2024SAP101263171 | Overcast-Rain-Lightning-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0037584 | OH | Sus | 31431366 | yes | 2019 | MAR | Yes | Line to Line | 1426726 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0040663&numberofmonths=24&showchangehistorylog=1 | 19-0040663 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CORRAL-1102 | 162991102 | OTHER | WIREDOWN | 20190408 | 1701 | 356063 | 294 | Distribution Circuit | Equipment Failure/Involved | Overhead | 123 | 36001 | 38.1384 | -120.8902 | COLLINSEAN2028iro5479PLEASANTOAKSRD | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0040663 | OH | Sus | 43730362 | No | 2019 | APR | Yes | Open Circuit | 1428893 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0041071&numberofmonths=24&showchangehistorylog=1 | 19-0041071 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | STANISLAUS-1701 | 162821701 | FUSE | L3165 | 20190409 | 1609 | 356929 | 278 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 4448 | 38.158 | -120.3859 | 3PSSOFMTR1008776717 | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0041071 | OH | Sus | 43731286 | yes | 2019 | APR | Yes | Line to Ground | 1429165 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0044584&numberofmonths=24&showchangehistorylog=1 | 19-0044584 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | RECLOSER | 45292 | 20190420 | 1347 | 364491 | 1021 | Distribution Circuit | Vegetation | Tree - fell into line | 1355 | 314836 | 38.4536 | -120.53 | DORRISRYAN191417480BARTONDRPIONEER | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 19-0044584 | OH | Sus | 31434346 | yes | 2019 | APR | Yes | Line to Ground | 1431749 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0046919&numberofmonths=24&showchangehistorylog=1 | 19-0046919 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | FROGTOWN-1702 | 163451702 | OTHER | WIREDOWN1SPANSOURCESIDEOF12282OPEN | 20190429 | 559 | 369820 | 208 | Distribution Circuit | Animal | Bird found | 1031 | 166155 | 38.088 | -120.5377 | WIREDOWN1SPANSOURCESIDEOF1228215POLESLOADSIDEOF12282 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0046919 | OH | Sus | 43754618 | yes | 2019 | APR | Yes | Line to Ground | 1433312 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0049573&numberofmonths=24&showchangehistorylog=1 | 19-0049573 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | RECLOSER | 93116 | 20190507 | 924 | 375424 | 581 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 609 | 95077 | 38.3838 | -120.527 | 2754INDEPENDENCERD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0049573 | OH | Sus | 0 | No | 2019 | MAY | Yes | Line to Line | 1435055 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0057644&numberofmonths=24&showchangehistorylog=1 | 19-0057644 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | JUMPER | WIREDOWN1SOURCEMTR1005018683 | 20190525 | 2013 | 390290 | 48 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 48 | 38.4189 | -120.4893 | 1SOURCESIDEOFMTR1005018683 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0057644 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Open Circuit | 1441146 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0057919&numberofmonths=24&showchangehistorylog=1 | 19-0057919 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | MARTELL-1101 | 163011101 | JUMPER | L9755FUSES | 20190527 | 106 | 391053 | 603 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 6633 | 38.4538 | -120.7931 | MTR1004807122 | Overcast-Fog-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0057919 | OH | Sus | 0 | No | 2019 | MAY | Yes | Line to Line | 1441436 | CAW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0059265&numberofmonths=24&showchangehistorylog=1 | 19-0059265 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | WEST POINT-1102 | 163201102 | FUSE | 1315 | 20190529 | 2026 | 393040 | 1115 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 41235 | 38.3776 | -120.554 | MCCARTNEYMARK20241958QUAILLNWESTPOINT | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0059265 | OH | Sus | 31449052 | yes | 2019 | MAY | Yes | Line to Line | 1442510 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0067460&numberofmonths=24&showchangehistorylog=1 | 19-0067460 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE | 1037 | 20190613 | 2013 | 409536 | 446 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 19178 | 38.4171 | -120.646 | AQUEDUCTSOFMTR1004857915 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0067460 | OH | Sus | 31453653 | No | 2019 | JUN | Yes | Line to Line | 1448964 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0077733&numberofmonths=24&showchangehistorylog=1 | 19-0077733 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | OTHER | L2079 | 20190715 | 2112 | 453176 | 870 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2199 | 38.3883 | -120.4955 | SOURCESIDEOFMTR1009606599 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0077733 | OH | Sus | 31457526 | No | 2019 | JUL | Yes | Line to Ground | 1456418 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0079343&numberofmonths=24&showchangehistorylog=1 | 19-0079343 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1101 | 163751101 | FUSE | L1499 | 20190719 | 1655 | 462353 | 449 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 8229 | 38.405 | -120.6925 | MTR1004803981 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0079343 | OH | Sus | 31458835 | No | 2019 | JUL | Yes | Line to Line | 1457437 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0086467&numberofmonths=24&showchangehistorylog=1 | 19-0086467 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | FROGTOWN-1702 | 163451702 | FUSE | L3723 | 20190809 | 2233 | 498264 | 1289 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 28687 | 38.0653 | -120.6563 | MTR1010518203 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0086467 | OH | Sus | 0 | No | 2019 | AUG | Yes | Line to Line | 1462016 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0088785&numberofmonths=24&showchangehistorylog=1 | 19-0088785 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | FROGTOWN-1702 | 163451702 | OCB | 17022 | 20190816 | 1056 | 517156 | 1010 | Distribution Circuit | 3rd Party | Vehicle | 4171 | 1026547 | 38.0572 | -120.5343 | SILVATONY1705536hwy49 | Clear-Above 90 | Pole-Wood | Broken, wire on ground | 19-0088785 | OH | Sus | 0 | yes | 2019 | AUG | Yes | Line to Ground | 1463649 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0090318&numberofmonths=24&showchangehistorylog=1 | 19-0090318 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | MARTELL-1101 | 163011101 | RECLOSER | 6074 | 20190821 | 926 | 527279 | 274 | Distribution Circuit | 3rd Party | Vehicle | 2307 | 155934 | 38.3928 | -120.7927 | MCDANIELTONY17041neofL6021 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0090318 | OH | Sus | 0 | No | 2019 | AUG | Yes | Line to Line | 1464798 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0099234&numberofmonths=24&showchangehistorylog=1 | 19-0099234 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | NORTH BRANCH-1101 | 163231101 | OTHER | WIREDOWN3SEOFMTR1004657060 | 20190915 | 936 | 583270 | 574 | Distribution Circuit | 3rd Party | Vehicle | 32 | 5378 | 38.1203 | -120.8036 | WIREDOWN4SEOFMTR1004657060 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0099234 | OH | Sus | 0 | No | 2019 | SEP | Yes | Open Circuit | 1470127 | PW | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0107224&numberofmonths=24&showchangehistorylog=1 | 19-0107224 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | RECLOSER | 34416 | 20191003 | 1936 | 642177 | 504 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 451 | 39585 | 38.3988 | -120.5256 | MTR1004736704 | Clear-32-90 F | Conductor, Overhead | On Ground | 19-0107224 | OH | Sus | 31474097 | No | 2019 | OCT | Yes | Line to Ground | 1475191 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0113616&numberofmonths=24&showchangehistorylog=1 | 19-0113616 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | RECLOSER | 93116 | 20191018 | 1640 | 670813 | 571 | Distribution Circuit | 3rd Party | Vehicle | 610 | 91899 | 38.3838 | -120.527 | REANOTONY2009CURTOUTPOLE2111 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0113616 | OH | Sus | 44010843 | No | 2019 | OCT | Yes | Line to Line | 1481081 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0130759&numberofmonths=24&showchangehistorylog=1 | 19-0130759 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | OCB | 11022 | 20191128 | 525 | 722583 | 494 | Distribution Circuit | Vegetation | Tree - fell into line | 1476 | 555862 | 38.4208 | -120.549 | 8SOFL1503 | Partly Cloudy-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0130759 | OH | Sus | 0 | yes | 2019 | NOV | Yes | Multi-Fault | 1495444 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0134178&numberofmonths=24&showchangehistorylog=1 | 19-0134178 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1101 | 163751101 | FUSE | L3725 | 20191206 | 114 | 731012 | 582 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 13128 | 38.4029 | -120.7073 | 17401KITLN | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0134178 | OH | Sus | 0 | yes | 2019 | DEC | Yes | Line to Line | 1498098 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0007379&numberofmonths=24&showchangehistorylog=1 | 20-0007379 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CORRAL-1101 | 162991101 | FUSE | 4587 | 20200110 | 1250 | 758799 | 704 | Distribution Circuit | 3rd Party | Vehicle | 115 | 80960 | 38.16 | -120.8954 | 1POLEEO16057 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 20-0007379 | OH | Sus | 0 | No | 2020 | JAN | Yes | Three Phase Fault | 1505548 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0013746&numberofmonths=24&showchangehistorylog=1 | 20-0013746 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1101 | 163751101 | FUSE | L7437 | 20200126 | 729 | 770280 | 774 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 7740 | 38.4155 | -120.6897 | 1NOFL7437 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 20-0013746 | OH | Sus | 0 | No | 2020 | JAN | Yes | Line to Line | 1509282 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0014330&numberofmonths=24&showchangehistorylog=1 | 20-0014330 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | RECLOSER | 1888 | 20200128 | 846 | 771490 | 412 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 1469 | 89467 | 38.2367 | -120.3628 | 5SPANSSSOFL2041 | Partly Cloudy-32-90 F | Crossarm, Wood | Broken, wire on ground | 20-0014330 | OH | Sus | 0 | No | 2020 | JAN | Yes | Line to Ground | 1509707 | CAW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0016192&numberofmonths=24&showchangehistorylog=1 | 20-0016192 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | ELECTRA-1101 | 162161101 | TRIP-SAVER | L1697 | 20200201 | 751 | 774884 | 449 | Distribution Circuit | 3rd Party | Vehicle | 247 | 24557 | 38.3794 | -120.6379 | RobertsRon209986662811875tabeaurdpinegrove | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0016192 | OH | Sus | 0 | No | 2020 | FEB | Yes | Line to Line | 1510938 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0018323&numberofmonths=24&showchangehistorylog=1 | 20-0018323 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | NORTH BRANCH-1101 | 163231101 | TRIP-SAVER | TS1115 | 20200206 | 1801 | 779682 | 452 | Distribution Circuit | Equipment Failure/Involved | Overhead | 160 | 27840 | 38.2444 | -120.8446 | 2NEOF1287 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0018323 | OH | Sus | 44180491 | No | 2020 | FEB | Yes | Line to Ground | 1512479 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0021734&numberofmonths=24&showchangehistorylog=1 | 20-0021734 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | RECLOSER | 4790 | 20200213 | 842 | 790173 | 800 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 1961 | 303344 | 38.3868 | -120.5244 | MTR1004934080 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 20-0021734 | OH | Sus | 31490856 | No | 2020 | FEB | Yes | Multi-Fault | 1515063 | CAW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0023357&numberofmonths=24&showchangehistorylog=1 | 20-0023357 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | SALT SPRINGS-2101 | 163692101 | FUSE | 1591 | 20200219 | 818 | 795357 | 470 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1410 | 38.529 | -120.2331 | 5LDSIDEOF1591 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0023357 | OH | Sus | 0 | No | 2020 | FEB | Yes | Three Phase Fault | 1516167 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0027609&numberofmonths=24&showchangehistorylog=1 | 20-0027609 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | SALT SPRINGS-2102 | 163692102 | FUSE | L2065 | 20200302 | 38 | 821111 | 683 | Distribution Circuit | Vegetation | Tree - fell into line | 334 | 59492 | 38.3008 | -120.2732 | 1NOFMTR1004652233 | Clear-Strong Winds-Below 32 F | Crossarm, Wood | Broken, wire on ground | 20-0027609 | OH | Sus | 31493732 | yes | 2020 | MAR | Yes | Line to Ground | 1518804 | CAW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0034294&numberofmonths=24&showchangehistorylog=1 | 20-0034294 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | JUMPER | L3431 | 20200319 | 1400 | 859044 | 275 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 2200 | 38.3748 | -120.4573 | SSOF66916135BLUEMOUNTAINRD | Overcast-Drizzle-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 20-0034294 | OH | Sus | 0 | yes | 2020 | MAR | Yes | Line to Ground | 1523032 | CSO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0034738&numberofmonths=24&showchangehistorylog=1 | 20-0034738 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | OTHER | 13438 | 20200320 | 1419 | 859761 | 283 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1489 | 136103 | 38.4738 | -120.6265 | BETL2133ANDMTR1004938591 | Partly Cloudy-32-90 F | Conductor, Overhead | On Ground | 20-0034738 | OH | Sus | 0 | No | 2020 | MAR | Yes | Open Circuit | 1523286 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0035978&numberofmonths=24&showchangehistorylog=1 | 20-0035978 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | RECLOSER | 6080 | 20200325 | 1014 | 864714 | 258 | Distribution Circuit | Equipment Failure/Involved | Overhead | 938 | 121015 | 38.4612 | -120.6579 | CGC223701528497ONSHAKERIDGEEOL581 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0035978 | OH | Sus | 44273623 | No | 2020 | MAR | Yes | Line to Ground | 1523917 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0038511&numberofmonths=24&showchangehistorylog=1 | 20-0038511 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | WEST POINT-1102 | 163201102 | RECLOSER | 72036 | 20200405 | 834 | 882744 | 471 | Distribution Circuit | Vegetation | Tree - fell into line | 614 | 76694 | 38.4129 | -120.5501 | 1WOF679 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0038511 | OH | Sus | 31498948 | yes | 2020 | APR | Yes | Line to Ground | 1525345 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0038929&numberofmonths=24&showchangehistorylog=1 | 20-0038929 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | SALT SPRINGS-2102 | 163692102 | OTHER | 5343 | 20200406 | 936 | 884761 | 504 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1088 | 38.2741 | -120.3308 | 8LDSIDEOF5343 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0038929 | OH | Sus | 0 | yes | 2020 | APR | Yes | Line to Ground | 1525700 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0046596&numberofmonths=24&showchangehistorylog=1 | 20-0046596 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE | 1597 | 20200502 | 1301 | 905923 | 375 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 22500 | 38.3023 | -120.708 | RobertsRon20998666288900cenerst | Partly Cloudy-32-90 F | Conductor, Overhead | On Ground | 20-0046596 | OH | Sus | 0 | No | 2020 | MAY | Yes | Force Out | 1530370 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0047960&numberofmonths=24&showchangehistorylog=1 | 20-0047960 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | OLETA-1102 | 163541102 | RECLOSER | 2642 | 20200506 | 2224 | 908540 | 381 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 7332 | 38.5013 | -120.8481 | SOUTHONMAINLINEJUSTWESTOFCGC223299131604 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0047960 | OH | Sus | 44312283 | No | 2020 | MAY | Yes | Line to Ground | 1531181 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0050999&numberofmonths=24&showchangehistorylog=1 | 20-0050999 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | MARTELL-1103 | 163011103 | FUSE | L1247 | 20200517 | 1208 | 915203 | 248 | Distribution Circuit | Vegetation | Tree - branch fell on line | 27 | 6696 | 38.3448 | -120.867 | L3863 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0050999 | OH | Sus | 44325937 | yes | 2020 | MAY | Yes | Line to Ground | 1532936 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0055553&numberofmonths=24&showchangehistorylog=1 | 20-0055553 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | JUMPER | 43019 | 20200529 | 901 | 925055 | 488 | Distribution Circuit | 3rd Party | Vehicle | 5 | 2440 | 38.4183 | -120.5983 | 43019TOEOL | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 20-0055553 | OH | Sus | 0 | yes | 2020 | MAY | Yes | Open Circuit | 1535529 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0056751&numberofmonths=24&showchangehistorylog=1 | 20-0056751 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | L3377 | 20200602 | 1725 | 928804 | 1212 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 23028 | 38.3522 | -120.5093 | 1NOF17795SPANSEOF1779ONEOL3SPANTAPGOINGTWDEAST | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0056751 | OH | Sus | 31504818 | No | 2020 | JUN | Yes | Line to Line | 1536514 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0062494&numberofmonths=24&showchangehistorylog=1 | 20-0062494 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | ELECTRA-1101 | 162161101 | FUSE | 9775 | 20200618 | 543 | 941648 | 304 | Distribution Circuit | Vegetation | Tree - branch fell on line | 40 | 11454 | 38.3435 | -120.7179 | 4POLESSEOF9775ONSINGLEPHASETAP4SOF | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0062494 | OH | Sus | 31506312 | No | 2020 | JUN | Yes | Line to Ground | 1540610 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0062922&numberofmonths=24&showchangehistorylog=1 | 20-0062922 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | OLETA-1101 | 163541101 | OTHER | WIREDOWN3SNOF1563 | 20200619 | 430 | 942335 | 398 | Distribution Circuit | Vegetation | Tree - fell into line | 563 | 90879 | 38.4186 | -120.822 | 3SPNOF1563 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0062922 | OH | Sus | 44360219 | No | 2020 | JUN | Yes | Line to Ground | 1540858 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0069539&numberofmonths=24&showchangehistorylog=1 | 20-0069539 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE | L3679 | 20200708 | 1051 | 960063 | 355 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 155 | 16523 | 38.4444 | -120.5319 | CGC224250028465 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0069539 | OH | Sus | 35185532 | No | 2020 | JUL | Yes | Line to Line | 1545157 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0098791&numberofmonths=24&showchangehistorylog=1 | 20-0098791 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1101 | 163751101 | RECLOSER | 3170 | 20200917 | 2312 | 1079641 | 572 | Distribution Circuit | Vegetation | Tree - fell into line | 691 | 163626 | 38.4151 | -120.6853 | BETWEENSBCO92011FUCO515715 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0098791 | OH | Sus | 31514032 | No | 2020 | SEP | Yes | Three Phase Fault | 1564419 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0106078&numberofmonths=24&showchangehistorylog=1 | 20-0106078 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | SALT SPRINGS-2102 | 163692102 | FUSE | 6681 | 20201007 | 1142 | 1112858 | 241 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 1068 | 28005 | 38.3079 | -120.2673 | SILVATONY17053737shoshonevdr | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0106078 | OH | Sus | 0 | No | 2020 | OCT | Yes | Line to Ground | 1569158 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0120920&numberofmonths=24&showchangehistorylog=1 | 20-0120920 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | MARTELL-1103 | 163011103 | FUSE | L9743 | 20201114 | 310 | 1144676 | 598 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 3678 | 38.349 | -120.8505 | CGC223283625255 | Clear-32-90F | Crossarm, Wood | Broken, wire on ground | 20-0120920 | OH | Sus | 0 | No | 2020 | NOV | Yes | Line to Line | 1579740 | CAW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0121066&numberofmonths=24&showchangehistorylog=1 | 20-0121066 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | L5791 | 20201115 | 936 | 1145483 | 554 | Distribution Circuit | 3rd Party | Vandalism | 13 | 7202 | 38.4102 | -120.5557 | 1LDSIDEOFL5791 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0121066 | OH | Sus | 0 | No | 2020 | NOV | Yes | Line to Line | 1579984 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0122213&numberofmonths=24&showchangehistorylog=1 | 20-0122213 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CORRAL-1101 | 162991101 | FUSE | 16059 | 20201118 | 115 | 1148100 | 747 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 27 | 10105 | 38.1634 | -120.9181 | 1POLEEOFMTR1004597795 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 20-0122213 | OH | Sus | 0 | No | 2020 | NOV | Yes | Line to Line | 1580836 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0128489&numberofmonths=24&showchangehistorylog=1 | 20-0128489 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | OTHER | WIREDOWNSOFMTR1005790897 | 20201207 | 1013 | 1168428 | 489 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 489 | 38.4864 | -120.5352 | SOFMTR1005790897 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 20-0128489 | OH | Sus | 0 | No | 2020 | DEC | Yes | Line to Ground | 1585093 | CAW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0130994&numberofmonths=24&showchangehistorylog=1 | 20-0130994 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | FROGTOWN-1702 | 163451702 | RECLOSER | 11212 | 20201217 | 2023 | 1193112 | 178 | Distribution Circuit | Equipment Failure/Involved | Overhead | 126 | 10962 | 38.0863 | -120.5718 | 15SSOFL1085 | Clear-32-90 F | Woodpin | Broken, wire on ground | 20-0130994 | OH | Sus | 0 | No | 2020 | DEC | Yes | Line to Ground | 1588245 | WP | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0001110&numberofmonths=24&showchangehistorylog=1 | 21-0001110 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | OTHER | 4786 | 20210106 | 849 | 1205163 | 264 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 840 | 82440 | 38.2321 | -120.5349 | EASTPHASESOUTHOFL5209 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0001110 | OH | Sus | 35124428 | No | 2021 | JAN | Yes | Open Circuit | 1591254 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0018118&numberofmonths=24&showchangehistorylog=1 | 21-0018118 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CORRAL-1101 | 162991101 | RECLOSER | 12612 | 20210129 | 330 | 1240917 | 641 | Distribution Circuit | 3rd Party | Vehicle | 323 | 119678 | 38.1783 | -120.927 | 2POLESEOFD7987l1SPANSEOFD4719 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 21-0018118 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1600142 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0044502&numberofmonths=24&showchangehistorylog=1 | 21-0044502 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE | L1117 | 20210403 | 2157 | 1306557 | 1134 | Distribution Circuit | Vegetation | Tree - fell into line | 154 | 13972 | 38.4914 | -120.7132 | 1SPANWOF1SPANSWOFL1117 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0044502 | OH | Sus | 31535240 | No | 2021 | APR | Yes | Line to Line | 1617431 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0047191&numberofmonths=24&showchangehistorylog=1 | 21-0047191 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CLAY-1103 | 163341103 | OTHER | WIREDOWNHOTBETPOLES72A01 | 20210410 | 1244 | 1312804 | 485 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 2560 | 38.3413 | -120.9179 | BETPOLES72A01 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 21-0047191 | OH | Sus | 44734994 | No | 2021 | APR | Yes | Open Circuit | 1619164 | CSO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0059047&numberofmonths=24&showchangehistorylog=1 | 21-0059047 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | RECLOSER | 3168 | 20210510 | 541 | 1344619 | 257 | Distribution Circuit | Animal | Bird found | 1072 | 247380 | 38.4143 | -120.6541 | MAINLINEJUSTSSOF43777 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0059047 | OH | Sus | 31540124 | No | 2021 | MAY | Yes | Line to Line | 1627035 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0076748&numberofmonths=24&showchangehistorylog=1 | 21-0076748 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | MARTELL-1101 | 163011101 | OTHER | WIREDOWN14055QUARTZMTNRD | 20210620 | 619 | 1380092 | 323 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 15045 | 38.455 | -120.7668 | TAKEOFFPOLETOCGC22353302891014055QUARTZMTNRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0076748 | OH | Sus | 31544220 | No | 2021 | JUN | Yes | Line to Ground | 1639015 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0084076&numberofmonths=24&showchangehistorylog=1 | 21-0084076 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1101 | 163751101 | RECLOSER | 3166 | 20210702 | 826 | 1390474 | 320 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 8000 | 38.4069 | -120.6707 | FIRSTSPANLDSIDEOFL699 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0084076 | OH | Sus | 31545297 | No | 2021 | JUL | Yes | Line to Line | 1644874 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0087916&numberofmonths=24&showchangehistorylog=1 | 21-0087916 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | RECLOSER | 47968 | 20210712 | 836 | 1400622 | 549 | Distribution Circuit | 3rd Party | Vehicle | 211 | 97511 | 38.2321 | -120.5505 | WhiskeyslidrdCGC319795563520 | Clear-32-90F | Pole-Wood | Broken, wire on object | 21-0087916 | OH | Sus | 35270908 | No | 2021 | JUL | Yes | Line to Line | 1647401 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0088390&numberofmonths=24&showchangehistorylog=1 | 21-0088390 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | JUMPER | WIREDOWNHOT2SPSWOF90421 | 20210712 | 1558 | 1402206 | 191 | Distribution Circuit | 3rd Party | Vehicle | 1779 | 317357 | 38.4601 | -120.5194 | 2SPSWOF9042127258COLUMBIADR | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0088390 | OH | Sus | 44905839 | No | 2021 | JUL | Yes | Line to Ground | 1647603 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0104892&numberofmonths=24&showchangehistorylog=1 | 21-0104892 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | OTHER | 6080 | 20210816 | 827 | 1443717 | 301 | Distribution Circuit | Vegetation | Tree - branch fell on line | 316 | 5764 | 38.4854 | -120.7005 | 1SPANSOURCESIDEOF846131 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0104892 | OH | Sus | 31549627 | No | 2021 | AUG | Yes | Line to Ground | 1657852 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0112466&numberofmonths=24&showchangehistorylog=1 | 21-0112466 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CORRAL-1101 | 162991101 | OTHER | D9321 | 20210902 | 521 | 1460560 | 416 | Distribution Circuit | Equipment Failure/Involved | Overhead | 148 | 43539 | 38.1447 | -120.9447 | 3PSOFCGCCGC318723360051 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 21-0112466 | OH | Sus | 44962460 | No | 2021 | SEP | Yes | Open Circuit | 1662939 | CSO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0116590&numberofmonths=24&showchangehistorylog=1 | 21-0116590 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | FROGTOWN-1702 | 163451702 | RECLOSER | 8482 | 20210913 | 315 | 1470330 | 628 | Distribution Circuit | 3rd Party | Vehicle | 876 | 399562 | 38.0748 | -120.5688 | CGC319540458038 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0116590 | OH | Sus | 0 | No | 2021 | SEP | Yes | Line to Ground | 1665219 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0139435&numberofmonths=24&showchangehistorylog=1 | 21-0139435 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | WEST POINT-1102 | 163201102 | FUSE | L1481 | 20211028 | 1312 | 1524311 | 446 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 4026 | 38.388 | -120.5428 | 1WOFCGC319851368620 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0139435 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Line | 1679974 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0005179&numberofmonths=24&showchangehistorylog=1 | 22-0005179 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE | 2143 | 20220102 | 1056 | 1592399 | 435 | Distribution Circuit | Equipment Failure/Involved | Overhead | 67 | 29145 | 38.2303 | -120.6003 | CGC319710663215 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 22-0005179 | OH | Sus | 0 | No | 2022 | JAN | Yes | Force Out | 1700365 | CAW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0005310&numberofmonths=24&showchangehistorylog=1 | 22-0005310 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L5111 | 20220102 | 828 | 1592624 | 1778 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 21336 | 38.2329 | -120.3486 | MULTIPLELOCATIONS | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 22-0005310 | OH | Sus | 0 | No | 2022 | JAN | Yes | Line to Ground | 1700555 | CAW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0007601&numberofmonths=24&showchangehistorylog=1 | 22-0007601 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE | 685 | 20220108 | 1044 | 1598184 | 381 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 381 | 38.4551 | -120.5307 | CGC224214029047 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 22-0007601 | OH | Sus | 0 | No | 2022 | JAN | Yes | Line to Ground | 1701597 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0053709&numberofmonths=24&showchangehistorylog=1 | 22-0053709 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | ELECTRA-1101 | 162161101 | OTHER | WIREDOWNHOTCGC223717525700 | 20220423 | 2012 | 1680111 | 481 | Distribution Circuit | Equipment Failure/Involved | Overhead | 374 | 39757 | 38.3651 | -120.7047 | CGC223717525700 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 22-0053709 | OH | Sus | 0 | No | 2022 | APR | Yes | Line to Ground | 1730551 | CAW | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0063647&numberofmonths=24&showchangehistorylog=1 | 22-0063647 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | SALT SPRINGS-2101 | 163692101 | FUSE | 1769 | 20220518 | 1614 | 1702310 | 202 | Distribution Circuit | Environmental/External | Ice or snow | 1 | 202 | 38.5365 | -120.2383 | 6POLESSWOFCGC225071832440 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0063647 | OH | Sus | 0 | No | 2022 | MAY | Yes | Line to Line | 1737412 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0073392&numberofmonths=24&showchangehistorylog=1 | 22-0073392 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | STANISLAUS-1701 | 162821701 | RECLOSER | 1812 | 20220612 | 931 | 1729337 | 669 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 913 | 219673 | 38.1832 | -120.3754 | 3034FORESTLN | Clear-32-90F | Pole-Wood | Broken, wire on ground | 22-0073392 | OH | Sus | 0 | No | 2022 | JUN | Yes | Line to Line | 1743964 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0094664&numberofmonths=24&showchangehistorylog=1 | 22-0094664 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CORRAL-1101 | 162991101 | RECLOSER | 12612 | 20220807 | 555 | 1775173 | 692 | Distribution Circuit | 3rd Party | Vehicle | 322 | 58394 | 38.1783 | -120.927 | 3NOFD4719 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 22-0094664 | OH | Sus | 35375981 | No | 2022 | AUG | Yes | Line to Line | 1758220 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0111655&numberofmonths=24&showchangehistorylog=1 | 22-0111655 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | MARTELL-1101 | 163011101 | RECLOSER | 91216 | 20220918 | 1319 | 1814511 | 443 | Distribution Circuit | Vegetation | Tree - fell into line | 427 | 113921 | 38.4351 | -120.7495 | GIANGREGORIOSEAN16520Lakecanyonrdsuttercreek | Clear-32-90F | Crossarm, Wood | Broken, wire on ground | 22-0111655 | OH | Sus | 0 | No | 2022 | SEP | Yes | Line to Line | 1769687 | CAW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0124982&numberofmonths=24&showchangehistorylog=1 | 22-0124982 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE | L359 | 20221026 | 957 | 1845856 | 304 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 49 | 8368 | 38.3968 | -120.6591 | DORRISRYAN1914Sap1012551844SPANSSOFMTR1004804127 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0124982 | OH | Sus | 31619503 | No | 2022 | OCT | Yes | Line to Line | 1779272 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0127266&numberofmonths=24&showchangehistorylog=1 | 22-0127266 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | RECLOSER | 1850 | 20221103 | 116 | 1852099 | 813 | Distribution Circuit | Vegetation | Tree - fell into line | 4398 | 922647 | 38.2413 | -120.3611 | WALSHPETE1850ChoctawRd | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0127266 | OH | Sus | 0 | No | 2022 | NOV | Yes | Line to Ground | 1781018 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0138815&numberofmonths=24&showchangehistorylog=1 | 22-0138815 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE | 1439 | 20221211 | 345 | 1884921 | 680 | Distribution Circuit | Vegetation | Tree - fell into line | 244 | 52336 | 38.4905 | -120.7137 | 16130MTWHITNEYFIDDLETOWN | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0138815 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1789643 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0139418&numberofmonths=24&showchangehistorylog=1 | 22-0139418 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | SALT SPRINGS-2101 | 163692101 | FUSE | 5149 | 20221212 | 1547 | 1887956 | 754 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 10556 | 38.4477 | -120.0711 | 5SPLDSIDE | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0139418 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Line | 1790243 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0139410&numberofmonths=24&showchangehistorylog=1 | 22-0139410 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | CLAY-1103 | 163341103 | OCB | 11032 | 20221213 | 32 | 1887885 | 879 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1655 | 423897 | 38.3422 | -120.935 | 1102CIRAT95933 | Clear-32-90F | Connector or Splice (OH) | Broken, wire on ground | 22-0139410 | OH | Sus | 31631451 | No | 2022 | DEC | Yes | Line to Ground | 1790229 | CSO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0141529&numberofmonths=24&showchangehistorylog=1 | 22-0141529 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE | 5163 | 20221227 | 536 | 1898463 | 382 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 22538 | 38.4381 | -120.5702 | 2POLESSWOFCGC2241163286723POLESSWOFCGC2241163286724POLESSWOFCGC224116328672 | Clear-32-90F | Crossarm, Wood | Broken, wire on ground | 22-0141529 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Line | 1793205 | CAW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0141959&numberofmonths=24&showchangehistorylog=1 | 22-0141959 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | SALT SPRINGS-2101 | 163692101 | JUMPER | WIREDOWN1PSOFCGC321061870005 | 20221228 | 1139 | 1900654 | 751 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 8102 | 38.4218 | -120.1306 | 1POLESOFCGC321061870005 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0141959 | OH | Sus | 45606422 | No | 2022 | DEC | Yes | Line to Ground | 1793691 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0142150&numberofmonths=24&showchangehistorylog=1 | 22-0142150 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | SALT SPRINGS-2101 | 163692101 | FUSE | 1232 | 20221230 | 315 | 1901763 | 682 | Distribution Circuit | Equipment Failure/Involved | Overhead | 920 | 221369 | 38.4163 | -120.1332 | CGC321216470585 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0142150 | OH | Sus | 45611062 | No | 2022 | DEC | Yes | Line to Ground | 1793923 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0015389&numberofmonths=24&showchangehistorylog=1 | 23-0015389 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE | 1541 | 20230113 | 1216 | 1951898 | 524 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 17816 | 38.4504 | -120.644 | CGC223833228338 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0015389 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Line | 1804297 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0016528&numberofmonths=24&showchangehistorylog=1 | 23-0016528 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | SALT SPRINGS-2102 | 163692102 | RECLOSER | 3142 | 20230115 | 605 | 1955514 | 356 | Distribution Circuit | Vegetation | Tree - fell into line | 911 | 249076 | 38.3016 | -120.277 | SOFCGC320651965215 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 23-0016528 | OH | Sus | 0 | No | 2023 | JAN | Yes | Multi-Fault | 1805285 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0017527&numberofmonths=24&showchangehistorylog=1 | 23-0017527 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L2679 | 20230117 | 224 | 1959040 | 709 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 49630 | 38.2417 | -120.3725 | LDSIDEOFCGC320372063492 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0017527 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Line | 1806161 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0025357&numberofmonths=24&showchangehistorylog=1 | 23-0025357 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE | L359 | 20230205 | 611 | 1977225 | 465 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 22785 | 38.3968 | -120.6591 | 1SOFCGC2238080266954SOFCGC223808026695 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0025357 | OH | Sus | 31636190 | No | 2023 | FEB | Yes | Line to Ground | 1810655 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0029985&numberofmonths=24&showchangehistorylog=1 | 23-0029985 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | SALT SPRINGS-2102 | 163692102 | OTHER | WIREDOWN10POLESSWOFR203 | 20230217 | 705 | 1987311 | 544 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3546 | 1697082 | 38.3231 | -120.2534 | 10POLESSWOFR203 | Overcast-Below 32 F | Conductor, Overhead | Broken, wire on ground | 23-0029985 | OH | Sus | 45677824 | No | 2023 | FEB | Yes | Line to Ground | 1813843 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0040306&numberofmonths=24&showchangehistorylog=1 | 23-0040306 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE | L1629 | 20230305 | 606 | 2023271 | 743 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2972 | 38.4327 | -120.5956 | CGC224023528229 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0040306 | OH | Sus | 0 | No | 2023 | MAR | Yes | Force Out | 1822043 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0043335&numberofmonths=24&showchangehistorylog=1 | 23-0043335 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | RECLOSER | 4790 | 20230311 | 556 | 2031960 | 746 | Distribution Circuit | Vegetation | Tree - fell into line | 1978 | 189178 | 38.3869 | -120.5242 | 5NOFL3231 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0043335 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1823932 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0053500&numberofmonths=24&showchangehistorylog=1 | 23-0053500 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | CALAVERAS CEMENT-1101 | 162211101 | FUSE | L1637 | 20230328 | 1039 | 2070348 | 503 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 17605 | 38.2444 | -120.512 | 34POLELDSIDEOFCGC319977363606 | Overcast-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 23-0053500 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1831148 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0053588&numberofmonths=24&showchangehistorylog=1 | 23-0053588 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | OLETA-1102 | 163541102 | FUSE | 1241 | 20230328 | 1134 | 2070383 | 343 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 27440 | 38.5461 | -120.744 | 2LDSIDEOF1241 | Overcast-Drizzle-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 23-0053588 | OH | Sus | 0 | No | 2023 | MAR | Yes | Three Phase Fault | 1831198 | CAW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0053435&numberofmonths=24&showchangehistorylog=1 | 23-0053435 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE | 1439 | 20230328 | 938 | 2070003 | 471 | Distribution Circuit | Vegetation | Tree - fell into line | 245 | 55374 | 38.4905 | -120.7137 | 3SRDSIDEOFL2997 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0053435 | OH | Sus | 31640556 | No | 2023 | MAR | Yes | Three Phase Fault | 1831101 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0053483&numberofmonths=24&showchangehistorylog=1 | 23-0053483 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE | 67999 | 20230328 | 1006 | 2070159 | 412 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1648 | 38.4043 | -120.6516 | 2POLESLDSIDEFOUNDOF67999 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0053483 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Line | 1831135 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0053485&numberofmonths=24&showchangehistorylog=1 | 23-0053485 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE | 352707 | 20230328 | 1021 | 2070153 | 165 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 1320 | 38.4377 | -120.5666 | 1LDSIDEOF352707 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0053485 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1831137 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0054727&numberofmonths=24&showchangehistorylog=1 | 23-0054727 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | OLETA-1102 | 163541102 | FUSE | L1185 | 20230330 | 37 | 2073816 | 643 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 4501 | 38.5054 | -120.7667 | 5SPANSWOL1185WESTBUCK | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0054727 | OH | Sus | 31640714 | No | 2023 | MAR | Yes | Line to Ground | 1831815 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0059069&numberofmonths=24&showchangehistorylog=1 | 23-0059069 | STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | 2121 | 20230410 | 857 | 2084210 | 379 | Distribution Circuit | 3rd Party | Vehicle | 91 | 13396 | 38.4725 | -120.5271 | 1POLESOFCGC224202729842 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 23-0059069 | OH | Sus | 0 | No | 2023 | APR | Yes | Line to Line | 1834530 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0064908&numberofmonths=24&showchangehistorylog=1 | 23-0064908 | STOCKTON | FIELD OPS CENTRAL | Tier 2 | SALT SPRINGS-2101 | 163692101 | JUMPER | WIREDOWNCGC321158870104 | 20230426 | 719 | 2097470 | 294 | Distribution Circuit | Equipment Failure/Involved | Overhead | 46 | 3935 | 38.4248 | -120.0965 | CGC321158870104 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0064908 | OH | Sus | 0 | No | 2023 | APR | Yes | Line to Ground | 1838724 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0003895&numberofmonths=24&showchangehistorylog=1 | 13-0003895 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1701 | 163781701 | RECLOSER | 9250 | 20130113 | 1254 | 729361 | 896 | Distribution Circuit | 3rd Party | Vehicle | 1495 | 194905 | 37.8368 | -120.2611 | 20580FERRETTIRDGROVELAND | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on object | 13-0003895 | OH | Sus | 30970915 | No | 2013 | JAN | Yes |  | 99304744 | PW | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0011038&numberofmonths=24&showchangehistorylog=1 | 13-0011038 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2102 | 254432102 | OCB | OCB | 20130219 | 1931 | 744442 | 503 | Distribution Circuit | Equipment Failure/Involved | Other | 1332 | 595572 | 37.2272 | -119.6902 | 2PWOF69105 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0011038 | OH | Sus | 0 | yes | 2013 | FEB | Yes | Line to Ground | 99300185 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0011129&numberofmonths=24&showchangehistorylog=1 | 13-0011129 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE | 19625 | 20130219 | 1955 | 744504 | 1141 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 32123 | 37.2667 | -119.6968 | LOADSIDEOFMTR1005877687 | Rain-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0011129 | OH | Sus | 0 | yes | 2013 | FEB | Yes | Line to Line | 99300181 | PW | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0011179&numberofmonths=24&showchangehistorylog=1 | 13-0011179 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE | 6288 | 20130219 | 2045 | 744569 | 1410 | Distribution Circuit | Environmental/External | Ice or snow | 174 | 170760 | 37.264 | -119.7336 | Dahlem18475594938472WELLSRD | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0011179 | OH | Sus | 0 | yes | 2013 | FEB | Yes | Line to Ground | 99300138 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0011090&numberofmonths=24&showchangehistorylog=1 | 13-0011090 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | FUSE | 9197 | 20130219 | 1817 | 744667 | 461 | Distribution Circuit | Equipment Failure/Involved | Other | 137 | 67361 | 37.9493 | -120.364 | 2SPANSLDSIDE19598 | Snow-Below 32 F | Conductor, Overhead | On Ground | 13-0011090 | OH | Sus | 0 | yes | 2013 | FEB | Yes | Line to Ground | 99300240 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0011079&numberofmonths=24&showchangehistorylog=1 | 13-0011079 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1705 | 163351705 | FUSE | L1209 | 20130219 | 1625 | 744141 | 456 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 74 | 59136 | 37.9627 | -120.2913 | Trujillo1708768353216106TUOLUMNERD | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0011079 | OH | Sus | 0 | yes | 2013 | FEB | Yes | Line to Ground | 99300201 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0011081&numberofmonths=24&showchangehistorylog=1 | 13-0011081 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2101 | 254452101 | FUSE | 10309 | 20130219 | 2117 | 744636 | 1331 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 41261 | 37.5642 | -119.94 | Cederlof207655976078195008coloradord | Snow-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0011081 | OH | Sus | 0 | yes | 2013 | FEB | Yes | Line to Ground | 99300200 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0011070&numberofmonths=24&showchangehistorylog=1 | 13-0011070 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | OAKHURST-1101 | 254421101 | RECLOSER | 6220 | 20130219 | 1936 | 744467 | 2652 | Distribution Circuit | Equipment Failure/Involved | Other | 141 | 346388 | 37.3598 | -119.7398 | CANYONCROSSING2SPANSNOFUCO1066541125ROAD600AHWAHNEE | Snow-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0011070 | OH | Sus | 0 | yes | 2013 | FEB | Yes | Line to Line | 99299964 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0011092&numberofmonths=24&showchangehistorylog=1 | 13-0011092 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1703 | 163761703 | FUSE | 21894 | 20130219 | 1813 | 744385 | 542 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 7046 | 37.9834 | -120.3927 | McKinnon20745730394SOURCESPANMETER1009435712 | Snow-32 - 90 F | Conductor, Overhead | On Ground | 13-0011092 | OH | Sus | 0 | yes | 2013 | FEB | Yes | Multi-Fault | 99300238 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0011113&numberofmonths=24&showchangehistorylog=1 | 13-0011113 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | FUSE | 5596 | 20130219 | 1904 | 744398 | 888 | Distribution Circuit | Equipment Failure/Involved | Other | 270 | 134560 | 37.2121 | -119.5536 | 53611ROAD200NORTHFORKTOWARDSMETER34H486 | Snow-32 - 90 F | Conductor, Overhead | Broken, wire on object | 13-0011113 | OH | Sus | 0 | yes | 2013 | FEB | Yes | None | 99300191 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0011111&numberofmonths=24&showchangehistorylog=1 | 13-0011111 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE | 12193 | 20130220 | 212 | 744763 | 681 | Distribution Circuit | Equipment Failure/Involved | Other | 84 | 57204 | 37.2524 | -119.7038 | Dahlem18475594938472VEATERRANCHRD | Snow-Below 32 F | Connector or Splice (OH) | Broken, wire on ground | 13-0011111 | OH | Sus | 0 | yes | 2013 | FEB | Yes |  | 99300193 | CSO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0011125&numberofmonths=24&showchangehistorylog=1 | 13-0011125 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE | 5514 | 20130220 | 201 | 744766 | 859 | Distribution Circuit | Equipment Failure/Involved | Other | 268 | 230212 | 37.2281 | -119.7628 | METER1006637546 | Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 13-0011125 | OH | Sus | 0 | yes | 2013 | FEB | Yes | Multi-Fault | 99300184 | PW | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0011234&numberofmonths=24&showchangehistorylog=1 | 13-0011234 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE | 5676 | 20130220 | 710 | 744819 | 875 | Distribution Circuit | Environmental/External | Ice or snow | 48 | 42000 | 37.2413 | -119.7369 | UNKNOWN | Snow-Below 32 F | Conductor, Overhead | On Ground | 13-0011234 | OH | Sus | 0 | yes | 2013 | FEB | Yes |  | 99300071 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0011346&numberofmonths=24&showchangehistorylog=1 | 13-0011346 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE | 5683 | 20130220 | 1333 | 745346 | 1272 | Distribution Circuit | Equipment Failure/Involved | Other | 33 | 21015 | 37.254 | -119.7116 | METER1009133633 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0011346 | OH | Sus | 0 | yes | 2013 | FEB | Yes | None | 99299958 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0011317&numberofmonths=24&showchangehistorylog=1 | 13-0011317 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2102 | 254452102 | OTHER |  | 20130220 | 1237 | 745269 | 368 | Distribution Circuit | Equipment Failure/Involved | Other | 2 | 736 | 37.3967 | -119.8398 | Wheeler568655933323603711INDIANPEAKROAD | Partly cloudy-32 - 90 F | Conductor, Overhead | On Ground | 13-0011317 | OH | Sus | 0 | yes | 2013 | FEB | Yes | Line to Ground | 99300032 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0011349&numberofmonths=24&showchangehistorylog=1 | 13-0011349 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SAN JOAQUIN #3 PH-1103 | 252531103 | OTHER |  | 20130220 | 1208 | 745242 | 337 | Distribution Circuit | Equipment Failure/Involved | Other | 9 | 2301 | 37.1881 | -119.4662 | Stewart2037675033559412rd225 | Clear-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 13-0011349 | OH | Sus | 0 | yes | 2013 | FEB | Yes | Line to Ground | 99300021 | CSO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0011447&numberofmonths=24&showchangehistorylog=1 | 13-0011447 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | FUSE | 6345 | 20130220 | 1232 | 745263 | 392 | Distribution Circuit | Equipment Failure/Involved | Other | 12 | 3824 | 37.1873 | -119.5494 | WOFMTR1005671114 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0011447 | OH | Sus | 0 | yes | 2013 | FEB | Yes | Line to Ground | 99299993 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0022850&numberofmonths=24&showchangehistorylog=1 | 13-0022850 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | SAN JOAQUIN #3 PH-1103 | 252531103 | RECLOSER | 5100 | 20130409 | 601 | 771299 | 529 | Distribution Circuit | Vegetation | Tree - fell into line | 454 | 47526 | 37.2315 | -119.4946 | HARDTAPWOFMETER1006020128BLACKOAKTREE | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0022850 | OH | Sus | 30988320 | yes | 2013 | APR | Yes | Multi-Fault | 99291752 | PW | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0031293&numberofmonths=24&showchangehistorylog=1 | 13-0031293 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1703 | 163761703 | FUSE | 63269 | 20130511 | 1848 | 791479 | 507 | Distribution Circuit | 3rd Party | Vehicle | 1 | 507 | 38.0019 | -120.4097 | McKinnon20745730394TXPOLETO20920JAMESTOWNRD | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0031293 | OH | Sus | 0 | No | 2013 | MAY | Yes | Line to Line | 99285479 | PW | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0040053&numberofmonths=24&showchangehistorylog=1 | 13-0040053 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MARIPOSA-2101 | 254452101 | FUSE | 4575 | 20130616 | 1805 | 811455 | 383 | Distribution Circuit | 3rd Party | Vehicle | 14 | 2901 | 37.5436 | -119.9147 | 2PSOFMTR1009698943 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0040053 | OH | Sus | 31003225 | No | 2013 | JUN | Yes | Line to Ground | 99279573 | PW | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0043441&numberofmonths=24&showchangehistorylog=1 | 13-0043441 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | FUSE | 5596 | 20130628 | 1139 | 819340 | 357 | Distribution Circuit | Vegetation | Tree - grew into line | 270 | 46790 | 37.2121 | -119.5536 | MULTIPLELOCATIONSHOTPOLEATMTR1006023239 | Clear-Above 90 F | Conductor, Overhead | Broken, wire on object | 13-0043441 | OH | Sus | 31005986 | yes | 2013 | JUN | Yes | None | 99277339 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0044893&numberofmonths=24&showchangehistorylog=1 | 13-0044893 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | RECLOSER | 9210 | 20130703 | 838 | 824645 | 761 | Distribution Circuit | Vegetation | Tree - fell into line | 169 | 42749 | 37.8185 | -120.0962 | Murch18517703673LR9210LOCKEDOUTTREEFELLINCAMPTAWONGA | Partly cloudy-Above 90 F | Conductor, Overhead | On Ground | 13-0044893 | OH | Sus | 0 | yes | 2013 | JUL | Yes | Line to Ground | 99276092 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0045616&numberofmonths=24&showchangehistorylog=1 | 13-0045616 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1701 | 163351701 | FUSE | S1625 | 20130707 | 1227 | 827169 | 543 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 2741 | 37.9819 | -120.3828 | 240WESTCHURCHLANESONORAMETER1004901167 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0045616 | OH | Sus | 41922324 | No | 2013 | JUL | Yes | Line to Ground | 99275474 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0048472&numberofmonths=24&showchangehistorylog=1 | 13-0048472 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE | 6165 | 20130718 | 1452 | 833751 | 422 | Distribution Circuit | 3rd Party | Vehicle | 203 | 84691 | 37.2004 | -119.7556 | Dahlem1847559493847231444NORTHDOME | Clear-Above 90 F | Pole-Wood | Broken, wire on ground | 13-0048472 | OH | Sus | 31009571 | No | 2013 | JUL | Yes | Multi-Fault | 99273551 | PW | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0050622&numberofmonths=24&showchangehistorylog=1 | 13-0050622 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | CURTIS-1703 | 163351703 | RECLOSER | 9330 | 20130727 | 1738 | 839542 | 818 | Distribution Circuit | Vegetation | Tree - fell into line | 599 | 316014 | 37.8309 | -120.237 | MAINLINE2203721665 | Clear-Above 90 F | Pole-Wood | Broken, wire on ground | 13-0050622 | OH | Sus | 31011381 | No | 2013 | JUL | Yes | Line to Line | 99271981 | PW | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0053389&numberofmonths=24&showchangehistorylog=1 | 13-0053389 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1705 | 163351705 | FUSE | 21461 | 20130808 | 1518 | 845194 | 747 | Distribution Circuit | 3rd Party | Vehicle | 129 | 96363 | 37.9572 | -120.3101 | METER1004902511 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0053389 | OH | Sus | 31013734 | No | 2013 | AUG | Yes | Three Phase Fault | 99270287 | PW | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0060371&numberofmonths=24&showchangehistorylog=1 | 13-0060371 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2102 | 254452102 | FUSE | 10375 | 20130906 | 2350 | 862093 | 494 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 19760 | 37.457 | -119.9454 | 1PEOF10375 | Lightning-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0060371 | OH | Sus | 41952123 | No | 2013 | SEP | Yes | Line to Ground | 99265210 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0060687&numberofmonths=24&showchangehistorylog=1 | 13-0060687 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | RECLOSER | 9210 | 20130909 | 847 | 863087 | 425 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 169 | 45380 | 37.8185 | -120.0962 | McKinnon2074573039412SPANSLOADSIDEL429 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0060687 | OH | Sus | 41952803 | No | 2013 | SEP | Yes | Line to Ground | 99264805 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0062991&numberofmonths=24&showchangehistorylog=1 | 13-0062991 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE | 6285 | 20130918 | 2234 | 868318 | 848 | Distribution Circuit | 3rd Party | Vehicle | 217 | 114648 | 37.191 | -119.7891 | Dahlem1847559493847241252LILLYMTDRIVE | Clear-32 - 90 F | Pole-Wood | Broken, wire on object | 13-0062991 | OH | Sus | 31022502 | No | 2013 | SEP | Yes | Multi-Fault | 99263268 | PW | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0063833&numberofmonths=24&showchangehistorylog=1 | 13-0063833 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2103 | 254432103 | FUSE | 5868 | 20130921 | 1646 | 870577 | 855 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 10222 | 37.2051 | -119.7163 | Dahlem1847559493847230666HOGANSMTRD | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0063833 | OH | Sus | 0 | yes | 2013 | SEP | Yes | Line to Line | 99262631 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0076317&numberofmonths=24&showchangehistorylog=1 | 13-0076317 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1704 | 163781704 | OTHER |  | 20131115 | 830 | 902810 | 324 | Distribution Circuit | Equipment Failure/Involved | Other | 130 | 12858 | 37.8885 | -120.5175 | 6060OBYRNESFERRYRD | Clear-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 13-0076317 | OH | Sus | 41987733 | No | 2013 | NOV | Yes |  | 99253292 | CSO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0077206&numberofmonths=24&showchangehistorylog=1 | 13-0077206 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | BEAR VALLEY-2105 | 252192105 | OTHER |  | 20131120 | 353 | 905649 | 417 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 194 | 70708 | 37.733 | -120.2139 | 1SPANNOBOOSTER823710678HWY49SEOFPENONBLANCOROAD | Drizzle-32 - 90 F | Jumper | Broken, wire on ground | 13-0077206 | OH | Sus | 41990268 | yes | 2013 | NOV | Yes |  | 99252612 | JMP | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0081305&numberofmonths=24&showchangehistorylog=1 | 13-0081305 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | FUSE | 19692 | 20131207 | 615 | 921971 | 332 | Distribution Circuit | Vegetation | Tree - branch fell on line | 37 | 12284 | 37.9537 | -120.3893 | WIREDOWNMETER1004239993 | Snow-Below 32 F | Conductor, Overhead | On Ground | 13-0081305 | OH | Sus | 0 | yes | 2013 | DEC | Yes | Line to Line | 99248912 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0081305&numberofmonths=24&showchangehistorylog=1 | 13-0081305 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | FUSE | 19692 | 20131207 | 1259 | 922840 | 251 | Distribution Circuit | Vegetation | Tree - branch fell on line | 37 | 9287 | 37.9537 | -120.3893 | ATMTR100423993 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0081305 | OH | Sus | 0 | yes | 2013 | DEC | Yes | Line to Line | 99248888 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0081335&numberofmonths=24&showchangehistorylog=1 | 13-0081335 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1704 | 163351704 | FUSE | 1257 | 20131207 | 1321 | 922865 | 193 | Distribution Circuit | Equipment Failure/Involved | Other | 86 | 16598 | 38.0388 | -120.3834 | 11920YANKEEHILLROAD | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0081335 | OH | Sus | 0 | yes | 2013 | DEC | Yes |  | 99248889 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0081359&numberofmonths=24&showchangehistorylog=1 | 13-0081359 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | CURTIS-1704 | 163351704 | FUSE | 20809 | 20131207 | 1416 | 922926 | 345 | Distribution Circuit | Equipment Failure/Involved | Other | 49 | 14025 | 38.0332 | -120.3676 | WIREDOWN1PEOF20809 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0081359 | OH | Sus | 0 | yes | 2013 | DEC | Yes | Line to Ground | 99248869 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0081178&numberofmonths=24&showchangehistorylog=1 | 13-0081178 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MARIPOSA-2102 | 254452102 | RECLOSER | 10880 | 20131207 | 403 | 921903 | 522 | Distribution Circuit | Equipment Failure/Involved | Other | 467 | 222853 | 37.462 | -119.9505 | MTR1005642481 | Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 13-0081178 | OH | Sus | 0 | yes | 2013 | DEC | Yes | Line to Ground | 99249029 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0081295&numberofmonths=24&showchangehistorylog=1 | 13-0081295 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2102 | 254452102 | FUSE | 7429 | 20131207 | 510 | 921924 | 464 | Distribution Circuit | Equipment Failure/Involved | Other | 18 | 8352 | 37.3738 | -119.8728 | METER1006382130 | Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 13-0081295 | OH | Sus | 0 | yes | 2013 | DEC | Yes | Line to Ground | 99248919 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0081372&numberofmonths=24&showchangehistorylog=1 | 13-0081372 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2102 | 254452102 | FUSE | 4555 | 20131207 | 1619 | 923096 | 1211 | Distribution Circuit | Equipment Failure/Involved | Other | 56 | 67816 | 37.3532 | -119.9576 | LDSIDEOF4555 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0081372 | OH | Sus | 0 | yes | 2013 | DEC | Yes | Line to Ground | 99248802 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0081378&numberofmonths=24&showchangehistorylog=1 | 13-0081378 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MARIPOSA-2102 | 254452102 | OTHER |  | 20131207 | 1604 | 923131 | 1381 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 4423 | 37.4347 | -119.9804 | Lafata184847032844168BURLDRMARIPOSA | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0081378 | OH | Sus | 0 | yes | 2013 | DEC | Yes | Line to Ground | 99248800 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0081180&numberofmonths=24&showchangehistorylog=1 | 13-0081180 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1701 | 163781701 | RECLOSER | 84318 | 20131207 | 322 | 921845 | 954 | Distribution Circuit | Vegetation | Tree - fell into line | 584 | 324597 | 37.8547 | -120.2039 | Breaux1806768352220461PineMountainDrGroveland | Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 13-0081180 | OH | Sus | 0 | yes | 2013 | DEC | Yes | Line to Line | 99249027 | PW | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0081147&numberofmonths=24&showchangehistorylog=1 | 13-0081147 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1705 | 163781705 | FUSE | L349 | 20131207 | 147 | 921682 | 848 | Distribution Circuit | Equipment Failure/Involved | Other | 988 | 18417 | 37.96 | -120.4251 | TrujilloM1708768353218468DALYCT | Snow-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0081147 | OH | Sus | 0 | yes | 2013 | DEC | Yes | Line to Ground | 99249047 | PW | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0081184&numberofmonths=24&showchangehistorylog=1 | 13-0081184 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1703 | 163761703 | FUSE | 1637 | 20131207 | 256 | 921959 | 370 | Distribution Circuit | Equipment Failure/Involved | Other | 226 | 106978 | 37.999 | -120.392 | 1167SHAWFLATROAD | Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 13-0081184 | OH | Sus | 0 | yes | 2013 | DEC | Yes | Line to Ground | 99249023 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0081361&numberofmonths=24&showchangehistorylog=1 | 13-0081361 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1703 | 163761703 | FUSE | 26345 | 20131207 | 1128 | 922820 | 451 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 7667 | 38.0174 | -120.3958 | 2PSOF26345 | Overcast-32 - 90 F | Conductor, Overhead | On Ground | 13-0081361 | OH | Sus | 0 | yes | 2013 | DEC | Yes | Three Phase Fault | 99248868 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0081176&numberofmonths=24&showchangehistorylog=1 | 13-0081176 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1704 | 163761704 | RECLOSER | 8070 | 20131207 | 305 | 921939 | 691 | Distribution Circuit | Environmental/External | Ice or snow | 295 | 160699 | 37.9758 | -120.4466 | HaygoodK20115641084RAWHIDE | Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 13-0081176 | OH | Sus | 31040995 | yes | 2013 | DEC | Yes | Line to Ground | 99249030 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=13-0081222&numberofmonths=24&showchangehistorylog=1 | 13-0081222 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | TAR FLAT-0401 | 163240401 | FUSE | 1875 | 20131207 | 810 | 922117 | 253 | Distribution Circuit | Vegetation | Tree - branch fell on line | 143 | 36179 | 37.9872 | -120.3797 | MTR1004902713WIREDOWNONBACKFEEDFUSESSTILLCLOSED | Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 13-0081222 | OH | Sus | 0 | yes | 2013 | DEC | Yes | Line to Ground | 99248986 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0008172&numberofmonths=24&showchangehistorylog=1 | 14-0008172 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1703 | 163761703 | RECLOSER | 9190 | 20140202 | 1341 | 958562 | 408 | Distribution Circuit | Vegetation | Tree - fell into line | 797 | 105286 | 38.0054 | -120.4054 | 21875SHAWSFLAT | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0008172 | OH | Sus | 42069010 | yes | 2014 | FEB | Yes | Line to Ground | 99241676 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0010162&numberofmonths=24&showchangehistorylog=1 | 14-0010162 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1705 | 163781705 | RECLOSER | 10580 | 20140209 | 1437 | 964368 | 722 | Distribution Circuit | Vegetation | Tree - grew into line | 357 | 184218 | 37.9489 | -120.4258 | MTR1009244698 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0010162 | OH | Sus | 31055666 | yes | 2014 | FEB | Yes | Line to Line | 99240376 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0013744&numberofmonths=24&showchangehistorylog=1 | 14-0013744 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2101 | 254452101 | FUSE | 13446 | 20140227 | 408 | 973448 | 412 | Distribution Circuit | Vegetation | Tree - fell into line | 110 | 45320 | 37.5349 | -119.9826 | 1SPANEOFUSE13446ONTHELOADSIDE | Rain-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 14-0013744 | OH | Sus | 31059422 | yes | 2014 | FEB | Yes | Line to Ground | 99237981 | CAW | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0017396&numberofmonths=24&showchangehistorylog=1 | 14-0017396 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1103 | 254421103 | OTHER |  | 20140311 | 2309 | 982845 | 499 | Distribution Circuit | Vegetation | Tree - fell into line | 139 | 26740 | 37.3223 | -119.5647 | BETWEENMETER1006579700ANDMETER1006636418 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0017396 | OH | Sus | 31062491 | yes | 2014 | MAR | Yes | Line to Ground | 99234592 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0017428&numberofmonths=24&showchangehistorylog=1 | 14-0017428 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1103 | 254421103 | FUSE | 10592 | 20140312 | 610 | 982980 | 433 | Distribution Circuit | Vegetation | Tree - fell into line | 128 | 47438 | 37.3224 | -119.6338 | WIREDOWNATFUSE2946 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0017428 | OH | Sus | 0 | yes | 2014 | MAR | Yes | Multi-Fault | 99235345 | PW | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0022328&numberofmonths=24&showchangehistorylog=1 | 14-0022328 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1705 | 163351705 | FUSE | 20084 | 20140402 | 140 | 993880 | 379 | Distribution Circuit | Equipment Failure/Involved | Other | 55 | 20845 | 37.9499 | -120.2813 | 16580VERGUSROADMETER1005716287 | Snow-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0022328 | OH | Sus | 42100970 | yes | 2014 | APR | Yes | Multi-Fault | 99231942 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0026114&numberofmonths=24&showchangehistorylog=1 | 14-0026114 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1704 | 163761704 | FUSE | 1001 | 20140421 | 509 | 1002049 | 718 | Distribution Circuit | 3rd Party | Vehicle | 66 | 29686 | 37.9977 | -120.44 | TrujilloM17087683532HWY49FRAGUERO | Partly cloudy-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0026114 | OH | Sus | 31070494 | No | 2014 | APR | Yes | Line to Ground | 99229470 | PW | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0027140&numberofmonths=24&showchangehistorylog=1 | 14-0027140 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1701 | 163781701 | OTHER |  | 20140425 | 643 | 1004277 | 458 | Distribution Circuit | Animal | Other | 1891 | 259264 | 37.8514 | -120.3611 | TrujilloM170876835321NO40265 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0027140 | OH | Sus | 31071604 | yes | 2014 | APR | Yes | Three Phase Fault | 99228806 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0027473&numberofmonths=24&showchangehistorylog=1 | 14-0027473 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1703 | 163761703 | FUSE | 2443 | 20140426 | 247 | 1004938 | 590 | Distribution Circuit | Vegetation | Tree - fell into line | 119 | 70210 | 38.0312 | -120.4259 | BREAUXPARIS22466SAirportRdinfieldacrossfromspc46 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0027473 | OH | Sus | 0 | yes | 2014 | APR | Yes | Line to Line | 99228585 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0029794&numberofmonths=24&showchangehistorylog=1 | 14-0029794 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | BEAR VALLEY-2101 | 252192101 | RECLOSER | 4500 | 20140506 | 1718 | 1011222 | 491 | Distribution Circuit | Equipment Failure/Involved | Other | 518 | 74331 | 37.4301 | -120.0996 | MTR1006161463 | Lightning-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0029794 | OH | Sus | 0 | yes | 2014 | MAY | Yes | Line to Ground | 99227007 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0035481&numberofmonths=24&showchangehistorylog=1 | 14-0035481 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1704 | 163781704 | OCB | OCB | 20140602 | 835 | 1027300 | 514 | Distribution Circuit | 3rd Party | Vehicle | 2965 | 555049 | 37.9042 | -120.4979 | METER10044575851SNWOFCAP | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0035481 | OH | Sus | 31080048 | No | 2014 | JUN | Yes | Three Phase Fault | 99223035 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0047004&numberofmonths=24&showchangehistorylog=1 | 14-0047004 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | OAKHURST-1102 | 254421102 | OTHER |  | 20140725 | 1357 | 1055335 | 127 | Distribution Circuit | 3rd Party | Vehicle | 928 | 10324 | 37.3124 | -119.648 | WIREDOWNHOT1PNOF5830 | Clear-Above 90 F | Conductor, Overhead | Broken, wire on ground | 14-0047004 | OH | Sus | 0 | yes | 2014 | JUL | Yes | None | 99215010 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0051918&numberofmonths=24&showchangehistorylog=1 | 14-0051918 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | FUSE | 21665 | 20140819 | 2105 | 1069073 | 690 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 29846 | 37.8179 | -120.1278 | 23111ELMORERDGROVELAND | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0051918 | OH | Sus | 31095961 | No | 2014 | AUG | Yes | Line to Line | 99211398 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0056874&numberofmonths=24&showchangehistorylog=1 | 14-0056874 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MERCED FALLS-1102 | 252811102 | RECLOSER | 9480 | 20140914 | 1447 | 1081192 | 658 | Distribution Circuit | Equipment Failure/Involved | Other | 1561 | 101377 | 37.646 | -120.3112 |  | Partly cloudy-Above 90 F | Crossarm, Wood | Broken, wire on ground | 14-0056874 | OH | Sus | 0 | No | 2014 | SEP | Yes |  | 99208019 | CAW | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0067019&numberofmonths=24&showchangehistorylog=1 | 14-0067019 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2101 | 254452101 | OCB | OCB | 20141030 | 812 | 1106111 | 706 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 3741 | 330890 | 37.5045 | -120.0082 | 4836TRAINGLERD | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0067019 | OH | Sus | 31111654 | No | 2014 | OCT | Yes | Line to Line | 99201365 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0070276&numberofmonths=24&showchangehistorylog=1 | 14-0070276 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SAN JOAQUIN #3 PH-1101 | 252531101 | RECLOSER | 10060 | 20141116 | 656 | 1113516 | 512 | Distribution Circuit | Equipment Failure/Involved | Other | 2701 | 402672 | 37.2925 | -119.5318 | 322673030153 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0070276 | OH | Sus | 42274323 | No | 2014 | NOV | Yes | Three Phase Fault | 99199090 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0072412&numberofmonths=24&showchangehistorylog=1 | 14-0072412 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MIWUK-1702 | 163661702 | RECLOSER | 47143 | 20141129 | 1032 | 1119284 | 442 | Distribution Circuit | Vegetation | Tree - fell into line | 339 | 48950 | 38.0046 | -120.2627 | MCGETTIGANMATTHEWCOAMERICANRIVERANDCRYSTALFALLS | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0072412 | OH | Sus | 31118086 | No | 2014 | NOV | Yes | Line to Ground | 99197573 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=14-0079606&numberofmonths=24&showchangehistorylog=1 | 14-0079606 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1103 | 254421103 | FUSE | 24876 | 20141231 | 303 | 1156075 | 807 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 3228 | 37.3528 | -119.6035 | 1PNOFMTR1006017845 | Combination wind/rain/lightning-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0079606 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99189553 | PW | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0009479&numberofmonths=24&showchangehistorylog=1 | 15-0009479 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1701 | 163781701 | FUSE | 1335 | 20150205 | 912 | 1172571 | 307 | Distribution Circuit | Equipment Failure/Involved | Other | 1 | 307 | 37.8035 | -120.2944 | 5SSOF1335 | Clear-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 15-0009479 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99185514 | CSO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0013366&numberofmonths=24&showchangehistorylog=1 | 15-0013366 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1103 | 254421103 | FUSE | 5732 | 20150214 | 1422 | 1190152 | 608 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 45 | 6462 | 37.399 | -119.7004 | Cederlof2076559760781946617rd620 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0013366 | OH | Sus | 31134717 | No | 2015 | FEB | Yes | Line to Line | 99182001 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0014469&numberofmonths=24&showchangehistorylog=1 | 15-0014469 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | FUSE | 48691 | 20150220 | 213 | 1192885 | 427 | Distribution Circuit | Vegetation | Tree - fell into line | 75 | 22905 | 37.9909 | -120.2789 | MTR1004862569 | Clear-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 15-0014469 | OH | Sus | 42336014 | No | 2015 | FEB | Yes | Line to Line | 99181274 | CSO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0025059&numberofmonths=24&showchangehistorylog=1 | 15-0025059 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | CURTIS-1704 | 163351704 | FUSE | 20809 | 20150407 | 1515 | 1215267 | 297 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 13959 | 38.0332 | -120.3676 | MCGETTIGANMATTHEWCOGUNSIGHTANDQUAILMINE | Combination wind/rain/lightning-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0025059 | OH | Sus | 0 | yes | 2015 | APR | Yes | Line to Ground | 99174885 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0039059&numberofmonths=24&showchangehistorylog=1 | 15-0039059 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | RECLOSER | 47488 | 20150606 | 1635 | 1244902 | 620 | Distribution Circuit | 3rd Party | Vehicle | 575 | 100729 | 37.9652 | -120.2511 | 1PNOFL1655WILLOWOAK | Lightning-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0039059 | OH | Sus | 31159521 | No | 2015 | JUN | Yes | Line to Ground | 99165221 | PW | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0043803&numberofmonths=24&showchangehistorylog=1 | 15-0043803 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MARIPOSA-2101 | 254452101 | FUSE | 12236 | 20150627 | 2344 | 1257983 | 675 | Distribution Circuit | Vegetation | Tree - fell into line | 217 | 126790 | 37.5328 | -119.835 | DANIELIPRESTON2PNOFMTR1009072170 | Partly Cloudy-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 15-0043803 | OH | Sus | 31164730 | No | 2015 | JUN | Yes | Line to Ground | 99161552 | CSO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0043784&numberofmonths=24&showchangehistorylog=1 | 15-0043784 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1704 | 163761704 | FUSE | 20361 | 20150627 | 1851 | 1257894 | 181 | Distribution Circuit | Vegetation | Tree - branch fell on line | 29 | 5249 | 37.992 | -120.4398 | TXFEEDINGMTR1004862914 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0043784 | OH | Sus | 42416769 | No | 2015 | JUN | Yes | Line to Line | 99161600 | CO | OH | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0047765&numberofmonths=24&showchangehistorylog=1 | 15-0047765 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | FUSE | 64615 | 20150715 | 1901 | 1268745 | 264 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 6 | 1584 | 38.0125 | -120.2842 | LINEANDBUCKTAPTOWESTNORTHOF64615 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0047765 | OH | Sus | 42427185 | No | 2015 | JUL | Yes | Line to Ground | 1145448 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0050806&numberofmonths=24&showchangehistorylog=1 | 15-0050806 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1702 | 163661702 | FUSE | 2363 | 20150727 | 1711 | 1278241 | 1078 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 12649 | 38.0408 | -120.2291 | LDSIDEOFMTR1005428415 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0050806 | OH | Sus | 0 | No | 2015 | JUL | Yes | Line to Line | 1147780 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0051772&numberofmonths=24&showchangehistorylog=1 | 15-0051772 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | FUSE | 2181 | 20150730 | 1911 | 1280503 | 565 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 26776 | 37.8103 | -120.133 | BREAUXPARIS23057HellsHollowRd2spnsSWCOs2181 | Partly Cloudy-Above 90 | Conductor, Overhead | Broken, wire on ground | 15-0051772 | OH | Sus | 31173089 | No | 2015 | JUL | Yes | Line to Ground | 1148362 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0055160&numberofmonths=24&showchangehistorylog=1 | 15-0055160 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1704 | 163781704 | FUSE | 21433 | 20150814 | 1744 | 1288636 | 863 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1726 | 37.8872 | -120.4978 | McKinnon20745730394TXPOLETOCALTRANMETER1005427921 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 15-0055160 | OH | Sus | 0 | No | 2015 | AUG | Yes | Three Phase Fault | 1150780 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0059433&numberofmonths=24&showchangehistorylog=1 | 15-0059433 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SPRING GAP-1701 | 162831701 | FUSE | L1123 | 20150904 | 1431 | 1300264 | 519 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 155 | 44725 | 38.1976 | -120.0125 | MTR1004717958 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0059433 | OH | Sus | 31181717 | No | 2015 | SEP | Yes | Line to Line | 1153811 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0062207&numberofmonths=24&showchangehistorylog=1 | 15-0062207 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1701 | 163781701 | RECLOSER | 76030 | 20150918 | 1705 | 1308318 | 638 | Distribution Circuit | 3rd Party | Vehicle | 181 | 35222 | 37.8992 | -120.4551 | 1SPSOFMTR1006424138 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 15-0062207 | OH | Sus | 0 | No | 2015 | SEP | Yes | Three Phase Fault | 1155832 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0067853&numberofmonths=24&showchangehistorylog=1 | 15-0067853 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1702 | 163661702 | FUSE | 1887 | 20151004 | 1648 | 1316851 | 632 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 331 | 142141 | 38.0605 | -120.2692 | 16800ESTRALITADR | Partly Cloudy-32-90 F | Crossarm, Wood | Broken, wire on ground | 15-0067853 | OH | Sus | 31188456 | yes | 2015 | OCT | Yes | Line to Ground | 1160622 | CAW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0075831&numberofmonths=24&showchangehistorylog=1 | 15-0075831 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MARIPOSA-2101 | 254452101 | FUSE | 12236 | 20151105 | 816 | 1336024 | 493 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 217 | 27676 | 37.5328 | -119.835 | MTR1006384892 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0075831 | OH | Sus | 31197887 | No | 2015 | NOV | Yes | Line to Line | 1166664 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0078375&numberofmonths=24&showchangehistorylog=1 | 15-0078375 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | BEAR VALLEY-2101 | 252192101 | FUSE | 10522 | 20151116 | 1035 | 1343133 | 396 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 6182 | 37.6192 | -120.212 | MTR1006145230 | Clear-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0078375 | OH | Sus | 0 | yes | 2015 | NOV | Yes | Line to Line | 1168839 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0079868&numberofmonths=24&showchangehistorylog=1 | 15-0079868 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 1871 | 20151121 | 1036 | 1346464 | 367 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 50 | 18350 | 38.0679 | -120.1872 | 5POLESLDSIDEOF1871 | Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0079868 | OH | Sus | 42575176 | No | 2015 | NOV | Yes | Line to Ground | 1169988 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0080616&numberofmonths=24&showchangehistorylog=1 | 15-0080616 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | CURTIS-1702 | 163351702 | JUMPER | WIREDOWNMTR1004821585 | 20151124 | 1327 | 1348068 | 325 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1102 | 252460 | 38.0162 | -120.2723 | WIREDOWNMTR1004821585 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on object | 15-0080616 | OH | Sus | 42576397 | yes | 2015 | NOV | Yes | Line to Ground | 1170570 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0087043&numberofmonths=24&showchangehistorylog=1 | 15-0087043 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1103 | 254421103 | JUMPER | 21549 | 20151223 | 2328 | 1370621 | 519 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 19827 | 37.3738 | -119.6115 | SOFMTR1006021770 | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | On Ground | 15-0087043 | OH | Sus | 42597065 | No | 2015 | DEC | Yes | Line to Ground | 1177110 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0086925&numberofmonths=24&showchangehistorylog=1 | 15-0086925 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1705 | 163781705 | FUSE | 6697 | 20151223 | 604 | 1370108 | 414 | Distribution Circuit | Vegetation | Tree - fell into line | 178 | 73692 | 37.9607 | -120.426 | 4SPANSLOADSIDE6697 | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0086925 | OH | Sus | 31208459 | No | 2015 | DEC | Yes | Three Phase Fault | 1176956 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0087260&numberofmonths=24&showchangehistorylog=1 | 15-0087260 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | OAKHURST-1103 | 254421103 | FUSE | 5727 | 20151225 | 44 | 1371535 | 874 | Distribution Circuit | Environmental/External | Ice or snow | 259 | 87847 | 37.5461 | -119.647 | MTR1005536996 | Partly Cloudy-Fog-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 15-0087260 | OH | Sus | 0 | No | 2015 | DEC | Yes | Line to Ground | 1177341 | CSO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=15-0087944&numberofmonths=24&showchangehistorylog=1 | 15-0087944 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2103 | 254432103 | RECLOSER | 10820 | 20151231 | 1327 | 1375337 | 177 | Distribution Circuit | 3rd Party | Vehicle | 764 | 73036 | 37.1549 | -119.7343 | 1SSOF8191 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 15-0087944 | OH | Sus | 0 | No | 2015 | DEC | Yes | Line to Ground | 1178278 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0003663&numberofmonths=24&showchangehistorylog=1 | 16-0003663 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | CURTIS-1705 | 163351705 | FUSE | 20315 | 20160106 | 2159 | 1379171 | 841 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 73167 | 37.9905 | -120.2264 | MTR1004860965 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 16-0003663 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Line | 1179157 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0003668&numberofmonths=24&showchangehistorylog=1 | 16-0003668 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1103 | 254421103 | RECLOSER | 5120 | 20160106 | 2125 | 1379151 | 2632 | Distribution Circuit | Environmental/External | Ice or snow | 519 | 1024009 | 37.4809 | -119.6372 | 6SPNNEOFMTR1005515876SS5120 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0003668 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Three Phase Fault | 1179162 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0003679&numberofmonths=24&showchangehistorylog=1 | 16-0003679 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1705 | 163351705 | FUSE | 19484 | 20160107 | 109 | 1379247 | 357 | Distribution Circuit | Environmental/External | Ice or snow | 48 | 17136 | 37.9961 | -120.2528 | BREAUXPARIS20538CharlotteCt | Overcast-Fog-Drizzle-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 16-0003679 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1179175 | CSO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0004409&numberofmonths=24&showchangehistorylog=1 | 16-0004409 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1103 | 254421103 | OCB | 11032 | 20160110 | 2214 | 1381282 | 550 | Distribution Circuit | Animal | Other | 3525 | 253505 | 37.3218 | -119.6342 | 1PEOF6302 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 16-0004409 | OH | Sus | 0 | No | 2016 | JAN | Yes | Three Phase Fault | 1179848 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0004505&numberofmonths=24&showchangehistorylog=1 | 16-0004505 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MIWUK-1702 | 163661702 | FUSE | S2125 | 20160111 | 944 | 1381464 | 636 | Distribution Circuit | 3rd Party | Vehicle | 11 | 1586 | 38.0059 | -120.2667 | EOLMTR1004856563 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 16-0004505 | OH | Sus | 0 | No | 2016 | JAN | Yes | Line to Line | 1179933 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0005757&numberofmonths=24&showchangehistorylog=1 | 16-0005757 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE | 6285 | 20160116 | 609 | 1384836 | 622 | Distribution Circuit | Animal | Other | 367 | 120150 | 37.191 | -119.789 | 6285 | Overcast-Fog-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 16-0005757 | OH | Sus | 0 | No | 2016 | JAN | Yes | Line to Line | 1180727 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0006622&numberofmonths=24&showchangehistorylog=1 | 16-0006622 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MERCED FALLS-1102 | 252811102 | RECLOSER | 9470 | 20160119 | 1828 | 1388089 | 680 | Distribution Circuit | 3rd Party | Vehicle | 978 | 94490 | 37.646 | -120.3111 | 1EOF25108INBET25108C807 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 16-0006622 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Multi-Fault | 1181431 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0006847&numberofmonths=24&showchangehistorylog=1 | 16-0006847 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | FUSE | 57503 | 20160120 | 906 | 1388415 | 420 | Distribution Circuit | 3rd Party | Vehicle | 6 | 2520 | 37.2212 | -119.5117 | 56646WILDPLUM | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 16-0006847 | OH | Sus | 0 | No | 2016 | JAN | Yes | Line to Line | 1181619 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0008703&numberofmonths=24&showchangehistorylog=1 | 16-0008703 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | WOODWARD-2108 | 255292108 | OTHER | WIREDOWNFEEDINGTWD22865RD211 | 20160127 | 1136 | 1393077 | 404 | Distribution Circuit | Equipment Failure/Involved | Overhead | 57 | 8194 | 37.081 | -119.6926 | 22865RD211 | Partly Cloudy-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 16-0008703 | OH | Sus | 31215430 | No | 2016 | JAN | Yes | Line to Ground | 1182952 | CSO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0009416&numberofmonths=24&showchangehistorylog=1 | 16-0009416 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | INDIAN FLAT-1104 | 252691104 | JUMPER | WIREDOWNBETWEEN10344 | 20160131 | 938 | 1394754 | 554 | Distribution Circuit | Equipment Failure/Involved | Overhead | 60 | 17622 | 37.6986 | -119.7605 | Bebout5596761325CO10344 | Overcast-Snow-Below 32 F | Connector or Splice (OH) | Broken, wire on ground | 16-0009416 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1183492 | CSO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0009474&numberofmonths=24&showchangehistorylog=1 | 16-0009474 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MARIPOSA-2101 | 254452101 | RECLOSER | 10240 | 20160131 | 1637 | 1395231 | 733 | Distribution Circuit | Vegetation | Tree - fell into line | 464 | 115224 | 37.5245 | -119.9173 | BETWEENC50910002 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0009474 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1183551 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0009358&numberofmonths=24&showchangehistorylog=1 | 16-0009358 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1103 | 254421103 | RECLOSER | 5120 | 20160131 | 507 | 1394729 | 2098 | Distribution Circuit | Vegetation | Tree - fell into line | 420 | 698189 | 37.4809 | -119.6372 | 11POLESLDSIDEOF5589 | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0009358 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Three Phase Fault | 1183448 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0011042&numberofmonths=24&showchangehistorylog=1 | 16-0011042 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | FUSE | 23239 | 20160206 | 259 | 1399304 | 885 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 13581 | 37.9858 | -120.2825 | BREAUXPARIS20140ChipmunkRd | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 16-0011042 | OH | Sus | 0 | No | 2016 | FEB | Yes | Line to Line | 1184711 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0011565&numberofmonths=24&showchangehistorylog=1 | 16-0011565 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1702 | 163661702 | FUSE | 23489 | 20160209 | 1041 | 1400784 | 219 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 1314 | 38.0309 | -120.2404 | MTR1004814981 | Clear-32-90 F | Conductor, Overhead | On Ground | 16-0011565 | OH | Sus | 42626799 | No | 2016 | FEB | Yes | Line to Line | 1185112 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0013806&numberofmonths=24&showchangehistorylog=1 | 16-0013806 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1704 | 163761704 | FUSE | S1341 | 20160218 | 1049 | 1408303 | 176 | Distribution Circuit | Vegetation | Tree - branch fell on line | 113 | 10966 | 37.9601 | -120.4519 | MTR1004734206 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013806 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Line to Ground | 1186828 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0017076&numberofmonths=24&showchangehistorylog=1 | 16-0017076 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | FUSE | 1993 | 20160303 | 1557 | 1415341 | 754 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 20 | 15080 | 37.8233 | -120.1928 | MTR10047328041PSOFMTR1004732804 | Overcast-32-90 F | Crossarm, Wood | Broken, wire on ground | 16-0017076 | OH | Sus | 31222952 | No | 2016 | MAR | Yes | Line to Line | 1189088 | CAW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0018355&numberofmonths=24&showchangehistorylog=1 | 16-0018355 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | COARSEGOLD-2102 | 254432102 | JUMPER | WIREDOWN38045 | 20160306 | 736 | 1421365 | 274 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 716 | 37.3062 | -119.6091 | 38045CEADERCREEK | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018355 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Open Circuit | 1190207 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0018111&numberofmonths=24&showchangehistorylog=1 | 16-0018111 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | RECLOSER | 9180 | 20160306 | 107 | 1420859 | 362 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3016 | 480667 | 37.9527 | -120.3681 | BETS115L1207WOFL1207TAKEOFFPOLE | Strong Winds-Heavy Rain-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018111 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1189981 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0018287&numberofmonths=24&showchangehistorylog=1 | 16-0018287 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1103 | 254421103 | FUSE | 48853 | 20160306 | 623 | 1421203 | 221 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 11608 | 37.3294 | -119.6363 | MTR1006380894 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018287 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190151 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0018479&numberofmonths=24&showchangehistorylog=1 | 16-0018479 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1703 | 163761703 | FUSE | 26356 | 20160306 | 1158 | 1422022 | 494 | Distribution Circuit | Vegetation | Tree - bark fell into line | 4 | 1976 | 38.034 | -120.3803 | MTR1005418968 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018479 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1190317 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0018471&numberofmonths=24&showchangehistorylog=1 | 16-0018471 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SAN JOAQUIN #3 PH-1102 | 252531102 | JUMPER | WIREDOWNONTREE2NOFMTR1006639337 | 20160306 | 1254 | 1422248 | 236 | Distribution Circuit | Equipment Failure/Involved | Overhead | 168 | 6164 | 37.2603 | -119.54 | 2NOFMTR1006639337 | Partly Cloudy-32-90 F | Insulator | Broken, wire on object | 16-0018471 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190309 | INS | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0018897&numberofmonths=24&showchangehistorylog=1 | 16-0018897 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | FUSE | 19717 | 20160307 | 1221 | 1424020 | 184 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 3162 | 37.9238 | -120.3513 | 16880LIMEKILNRD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018897 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Three Phase Fault | 1190690 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0021356&numberofmonths=24&showchangehistorylog=1 | 16-0021356 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1705 | 163351705 | RECLOSER | 65908 | 20160314 | 1759 | 1431500 | 478 | Distribution Circuit | Vegetation | Tree - fell into line | 660 | 60845 | 37.9575 | -120.3133 | 1404413978TUOLUMNERD | Partly Cloudy-32-90 F | Crossarm, Wood | Broken, wire on ground | 16-0021356 | OH | Sus | 31225116 | yes | 2016 | MAR | Yes | Line to Line | 1192644 | CAW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0021136&numberofmonths=24&showchangehistorylog=1 | 16-0021136 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1703 | 163761703 | FUSE | S1933 | 20160314 | 511 | 1430821 | 577 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 6924 | 38.0109 | -120.4198 | BREAUXPARIS10231VonKleiben | Overcast-Fog-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 16-0021136 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1192505 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0024994&numberofmonths=24&showchangehistorylog=1 | 16-0024994 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2101 | 254452101 | FUSE | 4579 | 20160330 | 951 | 1441569 | 474 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 33 | 8762 | 37.5502 | -119.9259 | MTR1007098643 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 16-0024994 | OH | Sus | 31228132 | No | 2016 | MAR | Yes | Line to Ground | 1195383 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0027399&numberofmonths=24&showchangehistorylog=1 | 16-0027399 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MERCED FALLS-1102 | 252811102 | FUSE | 22768 | 20160409 | 603 | 1447405 | 633 | Distribution Circuit | Equipment Failure/Involved | Overhead | 75 | 47475 | 37.6532 | -120.3201 | Mayo2078631138814377AvenidaCentral | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 16-0027399 | OH | Sus | 0 | yes | 2016 | APR | Yes | Line to Line | 1196988 | PW | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0027865&numberofmonths=24&showchangehistorylog=1 | 16-0027865 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | RECLOSER | 9210 | 20160411 | 1453 | 1448988 | 474 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 157 | 38354 | 37.8183 | -120.0961 | SIUDZINSKIMARK3spansloadsideofL429 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0027865 | OH | Sus | 31230611 | No | 2016 | APR | Yes | Line to Ground | 1197401 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0029685&numberofmonths=24&showchangehistorylog=1 | 16-0029685 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1704 | 163781704 | RECLOSER | 88630 | 20160419 | 1032 | 1453641 | 296 | Distribution Circuit | 3rd Party | Contact with High Voltage- 3rd party | 4 | 1184 | 37.9006 | -120.5169 | 4SPLOADSIDEOF88630 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0029685 | OH | Sus | 42682191 | No | 2016 | APR | Yes | Line to Ground | 1198767 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0030736&numberofmonths=24&showchangehistorylog=1 | 16-0030736 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE | 10788 | 20160422 | 1438 | 1455954 | 439 | Distribution Circuit | Vegetation | Tree - fell into line | 76 | 16776 | 37.2869 | -119.6558 | 3SOF10426 | Overcast-Rain-Lightning-32-90 F | Pole-Wood | Broken, wire on ground | 16-0030736 | OH | Sus | 0 | yes | 2016 | APR | Yes | Line to Line | 1199403 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0032119&numberofmonths=24&showchangehistorylog=1 | 16-0032119 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1704 | 163761704 | FUSE | S1341 | 20160427 | 2012 | 1460508 | 176 | Distribution Circuit | Equipment Failure/Involved | Overhead | 114 | 7084 | 37.9601 | -120.4519 | MTR1004902373 | Overcast-Rain-Lightning-32-90 F | Crossarm, Wood | Broken, wire on object | 16-0032119 | OH | Sus | 0 | yes | 2016 | APR | Yes | Force Out | 1200554 | CAW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0033372&numberofmonths=24&showchangehistorylog=1 | 16-0033372 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1704 | 163351704 | FUSE | L1473 | 20160502 | 2338 | 1463600 | 370 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 4070 | 38.0425 | -120.3774 | MTR1004861032 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0033372 | OH | Sus | 42689117 | No | 2016 | MAY | Yes | Line to Line | 1201580 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0033937&numberofmonths=24&showchangehistorylog=1 | 16-0033937 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | BEAR VALLEY-2105 | 252192105 | RECLOSER | 9480 | 20160505 | 834 | 1464885 | 394 | Distribution Circuit | Vegetation | Tree - branch fell on line | 595 | 63870 | 37.6317 | -120.1547 | 1SOF4543 | Overcast-32-90 F | Conductor, Overhead | On Ground | 16-0033937 | OH | Sus | 31236727 | yes | 2016 | MAY | Yes | Line to Ground | 1202029 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0036163&numberofmonths=24&showchangehistorylog=1 | 16-0036163 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | BEAR VALLEY-2101 | 252192101 | OCB | 21012 | 20160516 | 239 | 1470120 | 569 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1248 | 252330 | 37.5858 | -120.1258 | WIREDOWN1PNOFFUCO24029 | Clear-32-90 F | Insulator | Broken, wire on ground | 16-0036163 | OH | Sus | 31238692 | No | 2016 | MAY | Yes | Line to Ground | 1203574 | INS | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0043496&numberofmonths=24&showchangehistorylog=1 | 16-0043496 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | COARSEGOLD-2102 | 254432102 | FUSE | 10022 | 20160615 | 1431 | 1489544 | 371 | Distribution Circuit | Vegetation | Tree - branch fell on line | 74 | 15253 | 37.3042 | -119.6009 | TXMTR1005673188 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0043496 | OH | Sus | 31247634 | No | 2016 | JUN | Yes | Line to Line | 1209222 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0043854&numberofmonths=24&showchangehistorylog=1 | 16-0043854 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | TAR FLAT-0402 | 163240402 | OTHER | WIREDOWNDEADENDPOLEAT11928CA49 | 20160616 | 1952 | 1491046 | 688 | Distribution Circuit | 3rd Party | Vehicle | 2 | 1376 | 38.0034 | -120.3829 | DEADENDPOLEAT11928CA49 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on object | 16-0043854 | OH | Sus | 0 | No | 2016 | JUN | Yes | Open Circuit | 1209460 | PW | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0047689&numberofmonths=24&showchangehistorylog=1 | 16-0047689 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1703 | 163761703 | RECLOSER | 8120 | 20160703 | 1500 | 1500598 | 480 | Distribution Circuit | Vegetation | Tree - fell into line | 418 | 38812 | 38.0254 | -120.405 | 49507FUCO | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 16-0047689 | OH | Sus | 31250855 | No | 2016 | JUL | Yes | Line to Line | 1212234 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0049939&numberofmonths=24&showchangehistorylog=1 | 16-0049939 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | TAR FLAT-0401 | 163240401 | FUSE | 1875 | 20160714 | 1343 | 1510054 | 383 | Distribution Circuit | Vegetation | Tree - fell into line | 144 | 23094 | 37.9871 | -120.3797 | MTR1004902703 | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 16-0049939 | OH | Sus | 31257404 | yes | 2016 | JUL | Yes | Line to Line | 1213886 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0051534&numberofmonths=24&showchangehistorylog=1 | 16-0051534 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 2487 | 20160721 | 1051 | 1513601 | 332 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 244 | 30527 | 38.0618 | -120.1974 | MCGETTIGANMATTHEWCOREDCEDARWHITEFIR | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0051534 | OH | Sus | 31258517 | No | 2016 | JUL | Yes | Line to Line | 1214972 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0051771&numberofmonths=24&showchangehistorylog=1 | 16-0051771 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | COARSEGOLD-2102 | 254432102 | RECLOSER | 5380 | 20160722 | 847 | 1514091 | 353 | Distribution Circuit | 3rd Party | Vehicle | 354 | 27810 | 37.3089 | -119.5849 | MTR1005616117 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0051771 | OH | Sus | 0 | No | 2016 | JUL | Yes | Line to Line | 1215113 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0052942&numberofmonths=24&showchangehistorylog=1 | 16-0052942 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1704 | 163781704 | RECLOSER | 8040 | 20160727 | 1153 | 1517098 | 385 | Distribution Circuit | Vegetation | Tree - fell into line | 139 | 14734 | 37.8996 | -120.5039 | EOFANDNOFMTR1007303471 | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 16-0052942 | OH | Sus | 42754212 | yes | 2016 | JUL | Yes | Line to Ground | 1215995 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0056786&numberofmonths=24&showchangehistorylog=1 | 16-0056786 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | RECLOSER | 90320 | 20160811 | 2351 | 1525164 | 702 | Distribution Circuit | 3rd Party | Vehicle | 996 | 217504 | 37.8474 | -120.2022 | 1POLESOUTHOFLR90320 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0056786 | OH | Sus | 0 | No | 2016 | AUG | Yes | Three Phase Fault | 1218499 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0057170&numberofmonths=24&showchangehistorylog=1 | 16-0057170 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE | 90589 | 20160814 | 105 | 1526058 | 389 | Distribution Circuit | 3rd Party | Vehicle | 2 | 778 | 37.2244 | -119.769 | 1PNOF90859 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0057170 | OH | Sus | 0 | No | 2016 | AUG | Yes | Line to Line | 1218777 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0057465&numberofmonths=24&showchangehistorylog=1 | 16-0057465 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1701 | 163781701 | RECLOSER | 76030 | 20160815 | 1543 | 1526880 | 727 | Distribution Circuit | 3rd Party | Vehicle | 184 | 122905 | 37.8992 | -120.4551 | 1NOF4907 | Clear-Above 90 | Pole-Wood | Broken, wire on ground | 16-0057465 | OH | Sus | 31263432 | No | 2016 | AUG | Yes | Three Phase Fault | 1219008 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0062082&numberofmonths=24&showchangehistorylog=1 | 16-0062082 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2101 | 254452101 | FUSE | 21164 | 20160902 | 1300 | 1535955 | 147 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 2855 | 37.498 | -119.9094 | 134SPANNOFMTR1005640251 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0062082 | OH | Sus | 42780812 | No | 2016 | SEP | Yes | Line to Ground | 1222055 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0063252&numberofmonths=24&showchangehistorylog=1 | 16-0063252 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE | 10788 | 20160908 | 1313 | 1538472 | 519 | Distribution Circuit | 3rd Party | Vehicle | 76 | 6900 | 37.2869 | -119.6558 | MTR1006641890 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0063252 | OH | Sus | 0 | No | 2016 | SEP | Yes | Line to Ground | 1222855 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0065861&numberofmonths=24&showchangehistorylog=1 | 16-0065861 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1703 | 163761703 | FUSE | S1933 | 20160920 | 314 | 1544496 | 421 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 4631 | 38.0109 | -120.4198 | CGC320225554900 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0065861 | OH | Sus | 31272195 | No | 2016 | SEP | Yes | Line to Ground | 1224612 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0068471&numberofmonths=24&showchangehistorylog=1 | 16-0068471 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MARIPOSA-2101 | 254452101 | FUSE | 10496 | 20160929 | 1043 | 1549976 | 907 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 4834 | 37.4753 | -119.7295 | Lafata184847032846140CHOWCHILLAMTNRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0068471 | OH | Sus | 0 | No | 2016 | SEP | Yes | Line to Line | 1226542 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0072700&numberofmonths=24&showchangehistorylog=1 | 16-0072700 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MARIPOSA-2101 | 254452101 | FUSE | 10493 | 20161015 | 2102 | 1561981 | 438 | Distribution Circuit | Vegetation | Tree - fell into line | 168 | 73584 | 37.5639 | -119.8548 | 3SPANSNOF10493 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0072700 | OH | Sus | 31277975 | yes | 2016 | OCT | Yes | Line to Line | 1229739 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0072639&numberofmonths=24&showchangehistorylog=1 | 16-0072639 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 23544 | 20161015 | 1812 | 1561731 | 487 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 487 | 38.0887 | -120.1437 | MCGETTIGANMATTHEW2spansloadsideof23544 | Overcast-Drizzle-32-90 F | Insulator | Broken, wire on object | 16-0072639 | OH | Sus | 42815641 | yes | 2016 | OCT | Yes | Line to Ground | 1229680 | INS | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0072999&numberofmonths=24&showchangehistorylog=1 | 16-0072999 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | RECLOSER | 9210 | 20161016 | 1751 | 1563532 | 840 | Distribution Circuit | Vegetation | Tree - fell into line | 158 | 79992 | 37.8183 | -120.0961 | 2SPANSLDSIDES1215ANDS1999 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0072999 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Ground | 1230029 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0078045&numberofmonths=24&showchangehistorylog=1 | 16-0078045 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | RECLOSER | 10940 | 20161104 | 1056 | 1576553 | 283 | Distribution Circuit | 3rd Party | Vehicle | 7925 | 624024 | 37.9883 | -120.2832 | 2SSOF23515 | Clear-32-90 F | Pole-Wood | Broken, wire on object | 16-0078045 | OH | Sus | 0 | No | 2016 | NOV | Yes | Line to Line | 1233888 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0078863&numberofmonths=24&showchangehistorylog=1 | 16-0078863 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1103 | 254421103 | FUSE | 5571 | 20161109 | 906 | 1578699 | 218 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 9 | 1586 | 37.4532 | -119.6413 | Lafata18484703284HWY411MISOFSUGARPINERAILROAD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0078863 | OH | Sus | 31283226 | No | 2016 | NOV | Yes | Line to Ground | 1234512 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0078927&numberofmonths=24&showchangehistorylog=1 | 16-0078927 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SAN JOAQUIN #3 PH-1101 | 252531101 | FUSE | 5558 | 20161109 | 912 | 1578689 | 242 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 2 | 484 | 37.2948 | -119.5347 | BEYOND5558 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0078927 | OH | Sus | 31283231 | No | 2016 | NOV | Yes | Line to Ground | 1234560 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0080372&numberofmonths=24&showchangehistorylog=1 | 16-0080372 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2102 | 254432102 | OTHER | WIREDOWNSOMTR1005674918 | 20161116 | 2008 | 1582514 | 497 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 5712 | 37.1688 | -119.6683 | 1PSEOF2PSWOFMTR1005674918 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 16-0080372 | OH | Sus | 42881640 | No | 2016 | NOV | Yes | Line to Ground | 1235642 | CSO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0080459&numberofmonths=24&showchangehistorylog=1 | 16-0080459 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2103 | 254432103 | RECLOSER | 5020 | 20161117 | 931 | 1583123 | 339 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1149 | 157409 | 37.2065 | -119.7141 | MTR10060188971SOF10300 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 16-0080459 | OH | Sus | 42881870 | No | 2016 | NOV | Yes | Line to Ground | 1235749 | CSO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0082504&numberofmonths=24&showchangehistorylog=1 | 16-0082504 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MARIPOSA-2101 | 254452101 | FUSE | 10496 | 20161127 | 1848 | 1590136 | 396 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 7128 | 37.4753 | -119.7295 | 3PWOFMTR1008951638 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0082504 | OH | Sus | 0 | yes | 2016 | NOV | Yes | Force Out | 1237241 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0082424&numberofmonths=24&showchangehistorylog=1 | 16-0082424 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | S1217 | 20161127 | 242 | 1589606 | 599 | Distribution Circuit | Environmental/External | Ice or snow | 43 | 16523 | 38.047 | -120.2018 | BREAUXPARIS406222812CoffillRd | Overcast-Fog-Snow-Below 32 F | Insulator | Broken, wire on ground | 16-0082424 | OH | Sus | 0 | yes | 2016 | NOV | Yes | Line to Ground | 1237174 | INS | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0082435&numberofmonths=24&showchangehistorylog=1 | 16-0082435 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1702 | 163661702 | JUMPER | WIREDOWN2EOMTR1004211382 | 20161127 | 840 | 1589843 | 341 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 341 | 38.0563 | -120.2184 | 2EOFMTR1004211382 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0082435 | OH | Sus | 0 | yes | 2016 | NOV | Yes | Open Circuit | 1237182 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0082482&numberofmonths=24&showchangehistorylog=1 | 16-0082482 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1101 | 254421101 | FUSE | 5533 | 20161127 | 1642 | 1590066 | 604 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1208 | 37.4213 | -119.7113 | 1SOFMTR1006375881 | Partly Cloudy-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on ground | 16-0082482 | OH | Sus | 31285779 | yes | 2016 | NOV | Yes | Line to Ground | 1237223 | CAW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0082390&numberofmonths=24&showchangehistorylog=1 | 16-0082390 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1103 | 254421103 | RECLOSER | 5120 | 20161127 | 53 | 1589614 | 977 | Distribution Circuit | Equipment Failure/Involved | Overhead | 421 | 390149 | 37.4809 | -119.6372 | 5NOF5581LDSIDEOFMTR1005670817 | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0082390 | OH | Sus | 0 | yes | 2016 | NOV | Yes | Line to Line | 1237146 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0082669&numberofmonths=24&showchangehistorylog=1 | 16-0082669 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1101 | 254421101 | FUSE | 5533 | 20161128 | 859 | 1590335 | 513 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 1026 | 37.4213 | -119.7113 | 2SPANSSSOFMTR1006375880 | Overcast-Fog-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 16-0082669 | OH | Sus | 42885254 | No | 2016 | NOV | Yes | Line to Ground | 1237378 | CSO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0083541&numberofmonths=24&showchangehistorylog=1 | 16-0083541 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SAN JOAQUIN #3 PH-1103 | 252531103 | FUSE | 10279 | 20161202 | 653 | 1593180 | 127 | Distribution Circuit | Vegetation | Tree - fell into line | 180 | 22860 | 37.2326 | -119.4712 | MULTIPLELOCATIONSBEYONDFUCO10279 | Strong Winds-Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0083541 | OH | Sus | 0 | No | 2016 | DEC | Yes | Line to Ground | 1238110 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=16-0085046&numberofmonths=24&showchangehistorylog=1 | 16-0085046 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1702 | 163661702 | FUSE | 147619 | 20161210 | 2131 | 1599495 | 947 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 24536 | 38.0177 | -120.2686 | TXMETER1004816686 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 16-0085046 | OH | Sus | 0 | yes | 2016 | DEC | Yes | Line to Line | 1239600 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0004880&numberofmonths=24&showchangehistorylog=1 | 17-0004880 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1703 | 163761703 | FUSE | 1637 | 20170107 | 2259 | 1622433 | 283 | Distribution Circuit | Vegetation | Tree - fell into line | 230 | 58733 | 37.999 | -120.3919 | BET1637ANDMTR1004901902 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004880 | OH | Sus | 42914802 | yes | 2017 | JAN | Yes | Line to Ground | 1244678 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0008375&numberofmonths=24&showchangehistorylog=1 | 17-0008375 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1702 | 163661702 | JUMPER | WIREDOWNEOFMTR1005713488 | 20170112 | 719 | 1641289 | 544 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2176 | 38.0347 | -120.258 | EOFMTR1005713488 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0008375 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1247778 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0008796&numberofmonths=24&showchangehistorylog=1 | 17-0008796 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MIWUK-1702 | 163661702 | RECLOSER | 68380 | 20170113 | 1236 | 1642591 | 480 | Distribution Circuit | Vegetation | Tree - fell into line | 448 | 80801 | 38.0151 | -120.2744 | 19283 | Clear-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0008796 | OH | Sus | 31296346 | yes | 2017 | JAN | Yes | Line to Ground | 1248081 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0014466&numberofmonths=24&showchangehistorylog=1 | 17-0014466 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 23547 | 20170124 | 48 | 1666049 | 2292 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 77928 | 38.0922 | -120.1355 | 25929MONODR | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 17-0014466 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Multi-Fault | 1253159 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0014294&numberofmonths=24&showchangehistorylog=1 | 17-0014294 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SAN JOAQUIN #3 PH-1101 | 252531101 | FUSE | 5502 | 20170124 | 942 | 1665483 | 3182 | Distribution Circuit | Vegetation | Tree - fell into line | 81 | 184269 | 37.2959 | -119.5214 | LDSIDE5502 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0014294 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1253038 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0015706&numberofmonths=24&showchangehistorylog=1 | 17-0015706 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1702 | 163661702 | FUSE | L527 | 20170127 | 1356 | 1668850 | 209 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 150 | 31350 | 38.0498 | -120.2242 | L527 | Clear-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0015706 | OH | Sus | 42934234 | No | 2017 | JAN | Yes | Line to Ground | 1254159 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0016457&numberofmonths=24&showchangehistorylog=1 | 17-0016457 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | BEAR VALLEY-2105 | 252192105 | FUSE | 23939 | 20170131 | 1510 | 1671515 | 996 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 140 | 21346 | 37.7126 | -120.1088 | MTR1007101157 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0016457 | OH | Sus | 0 | No | 2017 | JAN | Yes | Line to Line | 1254739 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0017698&numberofmonths=24&showchangehistorylog=1 | 17-0017698 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | SAN JOAQUIN #3 PH-1103 | 252531103 | FUSE | 6095 | 20170206 | 541 | 1675873 | 574 | Distribution Circuit | Vegetation | Tree - fell into line | 96 | 16344 | 37.2381 | -119.519 | MTR1007053189 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0017698 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Three Phase Fault | 1255650 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0019153&numberofmonths=24&showchangehistorylog=1 | 17-0019153 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2101 | 254452101 | FUSE | 12238 | 20170208 | 1923 | 1682463 | 632 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 2227 | 37.4871 | -119.8032 | ONTAPSOUTHWESTOFMTR1006384409 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019153 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1256765 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0019112&numberofmonths=24&showchangehistorylog=1 | 17-0019112 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2102 | 254452102 | RECLOSER | 37282 | 20170208 | 1544 | 1682239 | 722 | Distribution Circuit | Animal | Other | 2066 | 127270 | 37.4622 | -119.9482 | CGC321611734129 | Overcast-Fog-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 17-0019112 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1256726 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0019082&numberofmonths=24&showchangehistorylog=1 | 17-0019082 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | OAKHURST-1101 | 254421101 | FUSE | 5672 | 20170208 | 1359 | 1682033 | 219 | Distribution Circuit | Equipment Failure/Involved | Overhead | 76 | 15369 | 37.3237 | -119.778 | MTR1006379018 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 17-0019082 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1256703 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0020321&numberofmonths=24&showchangehistorylog=1 | 17-0020321 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MARIPOSA-2101 | 254452101 | FUSE | 79097 | 20170211 | 1029 | 1685985 | 337 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 4044 | 37.5864 | -119.8512 | 3SPANSNEOF79097 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0020321 | OH | Sus | 31305295 | No | 2017 | FEB | Yes | Line to Ground | 1257702 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0021076&numberofmonths=24&showchangehistorylog=1 | 17-0021076 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | OAKHURST-1103 | 254421103 | FUSE | 10662 | 20170214 | 1323 | 1688485 | 767 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 6642 | 37.3652 | -119.712 | TXMTR1005283103 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0021076 | OH | Sus | 0 | No | 2017 | FEB | Yes | Line to Line | 1258343 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0028175&numberofmonths=24&showchangehistorylog=1 | 17-0028175 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1702 | 163661702 | FUSE | 92593 | 20170303 | 1215 | 1718680 | 395 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 290 | 114550 | 38.0594 | -120.268 | MTR10045590741004240462 | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0028175 | OH | Sus | 31309081 | No | 2017 | MAR | Yes | Line to Line | 1264564 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0028133&numberofmonths=24&showchangehistorylog=1 | 17-0028133 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1704 | 163761704 | RECLOSER | 8070 | 20170303 | 1011 | 1718531 | 341 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 363 | 39867 | 37.9758 | -120.4466 | MTR1004938867 | Partly Cloudy-32-90 F | Conductor, Overhead | On Ground | 17-0028133 | OH | Sus | 31308965 | No | 2017 | MAR | Yes | Line to Ground | 1264541 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0028471&numberofmonths=24&showchangehistorylog=1 | 17-0028471 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | OAKHURST-1103 | 254421103 | FUSE | 5727 | 20170305 | 839 | 1719815 | 864 | Distribution Circuit | Vegetation | Tree - fell into line | 259 | 110631 | 37.5461 | -119.647 | MTR10101949461STTXPOLENORTHOF5728 | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0028471 | OH | Sus | 42958963 | yes | 2017 | MAR | Yes | Three Phase Fault | 1264832 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0030274&numberofmonths=24&showchangehistorylog=1 | 17-0030274 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MERCED FALLS-1102 | 252811102 | RECLOSER | 38748 | 20170312 | 2035 | 1725652 | 494 | Distribution Circuit | Equipment Failure/Involved | Overhead | 293 | 70260 | 37.7017 | -120.3395 | 1PSOF55527 | Clear-32-90 F | Insulator | Broken, wire on object | 17-0030274 | OH | Sus | 31311908 | No | 2017 | MAR | Yes | Line to Ground | 1266210 | INS | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0032466&numberofmonths=24&showchangehistorylog=1 | 17-0032466 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1702 | 163661702 | FUSE | S1577 | 20170321 | 1439 | 1732167 | 930 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 85405 | 38.0263 | -120.2459 | L855 | Overcast-Fog-Heavy Rain-Lightning-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0032466 | OH | Sus | 31313851 | yes | 2017 | MAR | Yes | Multi-Fault | 1267816 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0036805&numberofmonths=24&showchangehistorylog=1 | 17-0036805 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 2485 | 20170405 | 1344 | 1744773 | 717 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 92 | 22970 | 38.0518 | -120.2027 | MTR100473762123495KREITZERWAY | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0036805 | OH | Sus | 0 | No | 2017 | APR | Yes | Line to Ground | 1271170 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0040109&numberofmonths=24&showchangehistorylog=1 | 17-0040109 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MARIPOSA-2102 | 254452102 | FUSE | 7247 | 20170413 | 1653 | 1757351 | 752 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 21794 | 37.4466 | -119.898 | 1EOF4WAYTHATISWOFMTR1005154786 | Partly Cloudy-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 17-0040109 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1273722 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0039888&numberofmonths=24&showchangehistorylog=1 | 17-0039888 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1703 | 163761703 | FUSE | 2657 | 20170413 | 911 | 1756844 | 322 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 4762 | 37.991 | -120.4135 | 1PSSOFMTR1004240574 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0039888 | OH | Sus | 42993699 | yes | 2017 | APR | Yes | Line to Ground | 1273596 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0040527&numberofmonths=24&showchangehistorylog=1 | 17-0040527 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 2477 | 20170415 | 1710 | 1758619 | 631 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 22 | 13882 | 38.02 | -120.2224 | MTR1004861524 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 17-0040527 | OH | Sus | 0 | No | 2017 | APR | Yes | Line to Line | 1274031 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0041781&numberofmonths=24&showchangehistorylog=1 | 17-0041781 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2104 | 254432104 | RECLOSER | 6210 | 20170420 | 1625 | 1762108 | 1005 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 32160 | 37.269 | -119.7137 | SOURCESIDEOF10322 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0041781 | OH | Sus | 31320810 | No | 2017 | APR | Yes | Line to Ground | 1274967 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0041788&numberofmonths=24&showchangehistorylog=1 | 17-0041788 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2102 | 254452102 | RECLOSER | 37288 | 20170420 | 1617 | 1762165 | 544 | Distribution Circuit | Vegetation | Tree - fell into line | 691 | 159420 | 37.4205 | -119.8772 | Elam191655976017743908INDIANPEAK | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0041788 | OH | Sus | 31320807 | No | 2017 | APR | Yes | Line to Ground | 1274974 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0042215&numberofmonths=24&showchangehistorylog=1 | 17-0042215 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | FUSE | 1715 | 20170423 | 1136 | 1765235 | 414 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 6888 | 37.9194 | -120.3504 | 15900LINEKILNRD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0042215 | OH | Sus | 31321143 | No | 2017 | APR | Yes | Line to Ground | 1275380 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0043794&numberofmonths=24&showchangehistorylog=1 | 17-0043794 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | OTHER | WIREDOWNMTR1009437218 | 20170428 | 1639 | 1769842 | 411 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1029 | 37.9122 | -120.258 | MTR1009437218 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0043794 | OH | Sus | 43003546 | yes | 2017 | APR | Yes | Open Circuit | 1276393 | CSO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0043886&numberofmonths=24&showchangehistorylog=1 | 17-0043886 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1703 | 163761703 | OTHER | WIREDOWNATMTR1004898140 | 20170429 | 1210 | 1770449 | 527 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 805 | 115347 | 38.0194 | -120.4093 | MTR1004898140NORTHINMAINLINE | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0043886 | OH | Sus | 31322660 | No | 2017 | APR | Yes | Open Circuit | 1276508 | CAW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0045793&numberofmonths=24&showchangehistorylog=1 | 17-0045793 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | FUSE | 5596 | 20170506 | 1106 | 1776149 | 466 | Distribution Circuit | Equipment Failure/Involved | Overhead | 263 | 59313 | 37.212 | -119.5539 | NEARMTR1006376365 | Overcast-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0045793 | OH | Sus | 43008063 | yes | 2017 | MAY | Yes | Line to Ground | 1277920 | CSO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0048096&numberofmonths=24&showchangehistorylog=1 | 17-0048096 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE | 6285 | 20170515 | 1600 | 1782596 | 606 | Distribution Circuit | Vegetation | Tree - fell into line | 224 | 20007 | 37.191 | -119.7891 | MTR1008855210 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 17-0048096 | OH | Sus | 31325928 | No | 2017 | MAY | Yes | Line to Line | 1279709 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0054164&numberofmonths=24&showchangehistorylog=1 | 17-0054164 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | COARSEGOLD-2102 | 254432102 | TRIP-SAVER | 10207 | 20170610 | 624 | 1800952 | 656 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 11166 | 37.2983 | -119.6165 | MTR1010203429 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 17-0054164 | OH | Sus | 0 | No | 2017 | JUN | Yes | Line to Line | 1284059 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0057405&numberofmonths=24&showchangehistorylog=1 | 17-0057405 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 20587 | 20170621 | 1356 | 1813936 | 464 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 11 | 5104 | 38.1013 | -120.125 | BREAUXPARIS406226494CrystalRdLongBarn | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 17-0057405 | OH | Sus | 0 | yes | 2017 | JUN | Yes | Line to Ground | 1286691 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0061288&numberofmonths=24&showchangehistorylog=1 | 17-0061288 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MARIPOSA-2101 | 254452101 | RECLOSER | 4410 | 20170707 | 1431 | 1825609 | 896 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 658 | 554306 | 37.5011 | -119.809 | Lafata18484703284WESTFALLRD3SO87467 | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 17-0061288 | OH | Sus | 43052231 | yes | 2017 | JUL | Yes | Line to Ground | 1289510 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0062203&numberofmonths=24&showchangehistorylog=1 | 17-0062203 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1704 | 163761704 | RECLOSER | 55798 | 20170712 | 20 | 1829522 | 378 | Distribution Circuit | Equipment Failure/Involved | Overhead | 364 | 56929 | 37.9759 | -120.4466 | 1POLENOF95951 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0062203 | OH | Sus | 43058076 | No | 2017 | JUL | Yes | Line to Ground | 1290249 | CSO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0063524&numberofmonths=24&showchangehistorylog=1 | 17-0063524 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1704 | 163761704 | FUSE | 20361 | 20170717 | 1905 | 1834185 | 290 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 2950 | 37.992 | -120.4398 | SOFMTR1004858721 | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 17-0063524 | OH | Sus | 0 | No | 2017 | JUL | Yes | Line to Ground | 1291298 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0063494&numberofmonths=24&showchangehistorylog=1 | 17-0063494 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | BEAR VALLEY-2105 | 252192105 | OCB | 9470 | 20170718 | 123 | 1834361 | 11132 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 2284 | 14358 | 37.5858 | -120.1258 | Lafata18484703284detwilerfireMAINLINENOBVSUBGONE | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0063494 | OH | Sus | 0 | No | 2017 | JUL | Yes | Force Out | 1291312 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0067149&numberofmonths=24&showchangehistorylog=1 | 17-0067149 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MARIPOSA-2101 | 254452101 | JUMPER | WIREDOWNHOTMTR1005642690 | 20170801 | 1745 | 1844119 | 565 | Distribution Circuit | Vegetation | Tree - fell into line | 396 | 15180 | 37.4636 | -119.7386 | MTR1005642690 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0067149 | OH | Sus | 0 | No | 2017 | AUG | Yes | Line to Ground | 1293744 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0073823&numberofmonths=24&showchangehistorylog=1 | 17-0073823 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1103 | 254421103 | FUSE | 5571 | 20170829 | 1247 | 1862552 | 15986 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 946 | 5894785 | 37.4532 | -119.6413 | SINGLEPHASETAPGOINGWESTOF5571 | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 17-0073823 | OH | Sus | 0 | No | 2017 | AUG | Yes | Line to Ground | 1298507 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0075888&numberofmonths=24&showchangehistorylog=1 | 17-0075888 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MERCED FALLS-1102 | 252811102 | FUSE | 8522 | 20170904 | 1756 | 1870000 | 608 | Distribution Circuit | 3rd Party | Vehicle | 50 | 30400 | 37.6559 | -120.3488 | 1NOFVILLARREALONALAMO | Clear-Heat Wave-Above 90 | Pole-Wood | Broken, wire on ground | 17-0075888 | OH | Sus | 31348994 | yes | 2017 | SEP | Yes | Line to Line | 1300130 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0077137&numberofmonths=24&showchangehistorylog=1 | 17-0077137 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | RECLOSER | 6064 | 20170908 | 2114 | 1873727 | 395 | Distribution Circuit | Vegetation | Tree - fell into line | 377 | 49858 | 37.9604 | -120.3764 | 1SEOF21067 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0077137 | OH | Sus | 43102388 | No | 2017 | SEP | Yes | Line to Ground | 1301030 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0079858&numberofmonths=24&showchangehistorylog=1 | 17-0079858 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1705 | 163781705 | OCB | 17052 | 20170918 | 2350 | 1881407 | 905 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2523 | 382303 | 37.9035 | -120.4971 | POLES789LOADSIDEOFSWITCH9059 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0079858 | OH | Sus | 31351880 | No | 2017 | SEP | Yes | Line to Ground | 1303099 | CSO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0082961&numberofmonths=24&showchangehistorylog=1 | 17-0082961 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1702 | 163661702 | FUSE | S1557 | 20170929 | 1445 | 1888267 | 574 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 135 | 36746 | 38.0657 | -120.2752 | 16630HILLSIDEDR | Clear-32-90 F | Crossarm, Wood | Broken, wire on object | 17-0082961 | OH | Sus | 0 | No | 2017 | SEP | Yes | Line to Line | 1305048 | CAW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0083893&numberofmonths=24&showchangehistorylog=1 | 17-0083893 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1704 | 163351704 | TRIP-SAVER | 803 | 20171003 | 1715 | 1890287 | 274 | Distribution Circuit | Vegetation | Tree - fell into line | 109 | 29866 | 38.0417 | -120.3867 | 2PWOFMTR1004899087 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0083893 | OH | Sus | 43123846 | yes | 2017 | OCT | Yes | Line to Line | 1305689 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0083873&numberofmonths=24&showchangehistorylog=1 | 17-0083873 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1704 | 163761704 | FUSE | 20361 | 20171003 | 1523 | 1890256 | 232 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 6728 | 37.992 | -120.4398 | 9624MORMANCREEK | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0083873 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1305678 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=17-0093234&numberofmonths=24&showchangehistorylog=1 | 17-0093234 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | OTHER | WIREDOWN2PS1PWOF961393 | 20171107 | 1133 | 1917580 | 201 | Distribution Circuit | Equipment Failure/Involved | Overhead | 23 | 4576 | 37.9435 | -120.2439 | 17555APPLECOLONYRDTUOLUMNE | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0093234 | OH | Sus | 43208252 | No | 2017 | NOV | Yes | Open Circuit | 1312681 | CSO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0004669&numberofmonths=24&showchangehistorylog=1 | 18-0004669 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | FUSE | S1793 | 20180109 | 856 | 4801 | 234 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 2470 | 37.9719 | -120.2605 | MTR1004858271 | Overcast-Drizzle-32-90 F | Conductor, Overhead | On Ground | 18-0004669 | OH | Sus | 31372953 | yes | 2018 | JAN | Yes | Line to Ground | 1323856 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0006595&numberofmonths=24&showchangehistorylog=1 | 18-0006595 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | BEAR VALLEY-2101 | 252192101 | RECLOSER | 21012 | 20180116 | 2055 | 9406 | 553 | Distribution Circuit | Animal | Bird found | 1254 | 300920 | 37.4958 | -120.0437 | ATMETER1007101268WIREDOWNSOF24006 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0006595 | OH | Sus | 43254875 | No | 2018 | JAN | Yes | Line to Line | 1325108 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0007573&numberofmonths=24&showchangehistorylog=1 | 18-0007573 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1705 | 163351705 | OTHER | WIREDOWN | 20180120 | 654 | 11195 | 496 | Distribution Circuit | Animal | Bird found | 2813 | 214833 | 37.963 | -120.3137 | ONTUOLUMNERDFUCO27308 | Clear-Below 32 F | Connector or Splice (OH) | Broken, wire on ground | 18-0007573 | OH | Sus | 43258181 | No | 2018 | JAN | Yes | Open Circuit | 1325672 | CSO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0007922&numberofmonths=24&showchangehistorylog=1 | 18-0007922 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | INDIAN FLAT-1104 | 252691104 | OTHER | WIREDOWNWOF13434 | 20180122 | 1406 | 12095 | 222 | Distribution Circuit | Equipment Failure/Involved | Overhead | 605 | 131122 | 37.6742 | -119.7856 | WOF13434 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 18-0007922 | OH | Sus | 0 | No | 2018 | JAN | Yes | Line to Ground | 1325927 | CSO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0008877&numberofmonths=24&showchangehistorylog=1 | 18-0008877 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1101 | 254421101 | FUSE | 5533 | 20180125 | 834 | 13664 | 498 | Distribution Circuit | Environmental/External | Ice or snow | 2 | 996 | 37.4213 | -119.7113 | 7POLESLDSIDEOF5533 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 18-0008877 | OH | Sus | 43261223 | No | 2018 | JAN | Yes | Line to Ground | 1326479 | CSO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0016579&numberofmonths=24&showchangehistorylog=1 | 18-0016579 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2102 | 254452102 | FUSE | 4681 | 20180222 | 2205 | 29736 | 597 | Distribution Circuit | Vegetation | Tree - fell into line | 97 | 57909 | 37.4515 | -119.8508 | 2SOFMTR1006382204 | Partly Cloudy-Fog-Below 32 F | Crossarm, Wood | Broken, wire on ground | 18-0016579 | OH | Sus | 31380339 | yes | 2018 | FEB | Yes | Line to Ground | 1331601 | CAW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0017587&numberofmonths=24&showchangehistorylog=1 | 18-0017587 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | RECLOSER | 10320 | 20180227 | 228 | 32463 | 552 | Distribution Circuit | Equipment Failure/Involved | Overhead | 244 | 92134 | 37.2141 | -119.5525 | 7NOF10320 | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0017587 | OH | Sus | 31381332 | yes | 2018 | FEB | Yes | Line to Ground | 1332322 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0018775&numberofmonths=24&showchangehistorylog=1 | 18-0018775 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | OAKHURST-1101 | 254421101 | FUSE | 5532 | 20180301 | 1557 | 35253 | 1411 | Distribution Circuit | Vegetation | Tree - fell into line | 262 | 156058 | 37.4022 | -119.7329 | 2SPANSSOF22743 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 18-0018775 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1333149 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0018841&numberofmonths=24&showchangehistorylog=1 | 18-0018841 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SPRING GAP-1702 | 162831702 | FUSE | L1123 | 20180301 | 1740 | 35459 | 1065 | Distribution Circuit | Vegetation | Tree - fell into line | 155 | 165075 | 38.1976 | -120.0125 | McKinnon20745730394wtr1004759552 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 18-0018841 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1333199 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0018960&numberofmonths=24&showchangehistorylog=1 | 18-0018960 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SPRING GAP-1702 | 162831702 | FUSE | 26305 | 20180301 | 2253 | 35850 | 835 | Distribution Circuit | Vegetation | Tree - fell into line | 100 | 46424 | 38.1956 | -120.0115 | MTR1004717551 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 18-0018960 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1333316 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0019226&numberofmonths=24&showchangehistorylog=1 | 18-0019226 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SPRING GAP-1702 | 162831702 | FUSE | 26312 | 20180301 | 2218 | 35816 | 2544 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 53424 | 38.1963 | -120.0118 | 1EOF26312 | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 18-0019226 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1333425 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0019030&numberofmonths=24&showchangehistorylog=1 | 18-0019030 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | FUSE | 76863 | 20180302 | 716 | 36009 | 716 | Distribution Circuit | Vegetation | Tree - fell into line | 127 | 90932 | 37.8492 | -120.2097 | MTR1004815059 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 18-0019030 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Three Phase Fault | 1333350 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0019065&numberofmonths=24&showchangehistorylog=1 | 18-0019065 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | FUSE | 27335 | 20180302 | 959 | 35957 | 405 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 25410 | 37.8134 | -120.1192 | MTR10049020812NO2029 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0019065 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1333363 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0019033&numberofmonths=24&showchangehistorylog=1 | 18-0019033 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1704 | 163351704 | TRIP-SAVER | 803 | 20180302 | 532 | 35953 | 879 | Distribution Circuit | Vegetation | Tree - fell into line | 109 | 49059 | 38.0417 | -120.3867 | SIUDZINSKIMARK12543remingtonmine | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 18-0019033 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1333352 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0019246&numberofmonths=24&showchangehistorylog=1 | 18-0019246 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2102 | 254452102 | RECLOSER | 37282 | 20180302 | 1943 | 36795 | 1103 | Distribution Circuit | Vegetation | Tree - fell into line | 2078 | 146446 | 37.4622 | -119.9482 | MTR1005154020 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0019246 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1333452 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0019485&numberofmonths=24&showchangehistorylog=1 | 18-0019485 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | CURTIS-1702 | 163351702 | FUSE | 1289 | 20180303 | 1616 | 37674 | 1134 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 32886 | 38.0394 | -120.2346 | MTR1008707943LDSIDEOF1289 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0019485 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1333674 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0019342&numberofmonths=24&showchangehistorylog=1 | 18-0019342 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | RECLOSER | 9210 | 20180303 | 120 | 36997 | 2288 | Distribution Circuit | Equipment Failure/Involved | Overhead | 157 | 312642 | 37.8183 | -120.0961 | SOURCESIDEOFFUCO27342S1999 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0019342 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1333545 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0019325&numberofmonths=24&showchangehistorylog=1 | 18-0019325 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | INDIAN FLAT-1104 | 252691104 | FUSE | 10213 | 20180303 | 713 | 37139 | 33 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 33 | 37.6731 | -119.7998 | 2SOF10213 | Overcast-Below 32 F | Conductor, Overhead | Broken, wire on ground | 18-0019325 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Force Out | 1333530 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0019314&numberofmonths=24&showchangehistorylog=1 | 18-0019314 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 21548 | 20180303 | 333 | 37088 | 685 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2055 | 38.0454 | -120.2079 | 23310HWY108 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 18-0019314 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1333517 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0019356&numberofmonths=24&showchangehistorylog=1 | 18-0019356 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 8667 | 20180303 | 302 | 37256 | 828 | Distribution Circuit | Vegetation | Tree - fell into line | 354 | 240996 | 38.0355 | -120.2262 | MTR1004856780 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 18-0019356 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1333561 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0019376&numberofmonths=24&showchangehistorylog=1 | 18-0019376 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 2525 | 20180303 | 640 | 37123 | 670 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 8710 | 38.0594 | -120.2154 | MTR1010376551004213122 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 18-0019376 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1333585 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0019411&numberofmonths=24&showchangehistorylog=1 | 18-0019411 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | S1219 | 20180303 | 1033 | 37377 | 305 | Distribution Circuit | Vegetation | Tree - branch fell on line | 403 | 34563 | 38.0581 | -120.1864 | 20792TELELETRL | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0019411 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1333613 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0019433&numberofmonths=24&showchangehistorylog=1 | 18-0019433 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | L2213 | 20180303 | 218 | 37117 | 2117 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 27712 | 38.0199 | -120.2222 | MTR1004861472 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on object | 18-0019433 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1333628 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0019299&numberofmonths=24&showchangehistorylog=1 | 18-0019299 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1702 | 163661702 | RECLOSER | 38218 | 20180303 | 158 | 37026 | 790 | Distribution Circuit | Vegetation | Tree - fell into line | 2969 | 1218636 | 38.0486 | -120.2438 | 23502MAINLINE812SPSOFL10051PSOF17713WOFL1615 | Overcast-Fog-Snow-Below 32 F | Crossarm, Wood | Broken, wire on ground | 18-0019299 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Three Phase Fault | 1333502 | CAW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0019317&numberofmonths=24&showchangehistorylog=1 | 18-0019317 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1702 | 163661702 | FUSE | S2243 | 20180303 | 202 | 37095 | 754 | Distribution Circuit | Vegetation | Tree - fell into line | 232 | 174928 | 38.0384 | -120.2478 | 1PEOFMTR1004720593 | Overcast-Fog-Below 32 F | Crossarm, Wood | Broken, wire on ground | 18-0019317 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1333523 | CAW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0019585&numberofmonths=24&showchangehistorylog=1 | 18-0019585 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SPRING GAP-1702 | 162831702 | FUSE | 2387 | 20180304 | 1037 | 38013 | 1871 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 11226 | 38.1518 | -120.0539 | 1PWOFMTR500140599 | Partly Cloudy-Snow-32-90 F | Pole-Wood | Broken, wire on ground | 18-0019585 | OH | Sus | 31382524 | No | 2018 | MAR | Yes | Three Phase Fault | 1333780 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0025504&numberofmonths=24&showchangehistorylog=1 | 18-0025504 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | FUSE | 19767 | 20180322 | 1127 | 50676 | 396 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 2772 | 38.0108 | -120.2918 | 3POLESNWAND2POLESSWOF19767 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0025504 | OH | Sus | 31385498 | yes | 2018 | MAR | Yes | Line to Line | 1337600 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0025621&numberofmonths=24&showchangehistorylog=1 | 18-0025621 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2101 | 254452101 | FUSE | 22075 | 20180322 | 1236 | 50725 | 489 | Distribution Circuit | Vegetation | Tree - fell into line | 86 | 20519 | 37.4974 | -119.8338 | MTR1005638184 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0025621 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1337636 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0025539&numberofmonths=24&showchangehistorylog=1 | 18-0025539 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | L1167 | 20180322 | 1110 | 50625 | 800 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 19781 | 38.0091 | -120.2316 | 21656SOUTHKNOX2SPSOFMTR1004938505 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 18-0025539 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1337609 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0025973&numberofmonths=24&showchangehistorylog=1 | 18-0025973 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1103 | 254421103 | TRANSFORMER | 66945 | 20180322 | 1723 | 51161 | 1362 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1362 | 37.3319 | -119.5727 | TRANSFORMERMTR1010246089 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 18-0025973 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1337898 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0025256&numberofmonths=24&showchangehistorylog=1 | 18-0025256 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1704 | 163761704 | FUSE | S1341 | 20180322 | 17 | 49953 | 708 | Distribution Circuit | Equipment Failure/Involved | Overhead | 114 | 55841 | 37.9601 | -120.4519 | 31POLESNOFS1341 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0025256 | OH | Sus | 43305954 | yes | 2018 | MAR | Yes | Line to Line | 1337472 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0026113&numberofmonths=24&showchangehistorylog=1 | 18-0026113 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 6819 | 20180323 | 1535 | 52091 | 232 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 232 | 38.0361 | -120.2101 | SIUDZINSKIMARK6819FUSES | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0026113 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1337977 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0033741&numberofmonths=24&showchangehistorylog=1 | 18-0033741 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | FUSE | 5596 | 20180419 | 1150 | 70113 | 560 | Distribution Circuit | Equipment Failure/Involved | Overhead | 266 | 61190 | 37.212 | -119.5539 | MTR1006579664 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 18-0033741 | OH | Sus | 0 | No | 2018 | APR | Yes | Line to Line | 1343760 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0037068&numberofmonths=24&showchangehistorylog=1 | 18-0037068 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | BEAR VALLEY-2101 | 252192101 | RECLOSER | 4500 | 20180430 | 2200 | 77063 | 545 | Distribution Circuit | 3rd Party | Vehicle | 531 | 104914 | 37.4304 | -120.0991 | REGS8216 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 18-0037068 | OH | Sus | 0 | No | 2018 | APR | Yes | Three Phase Fault | 1345979 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0044945&numberofmonths=24&showchangehistorylog=1 | 18-0044945 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | FUSE | L2107 | 20180529 | 4 | 95457 | 672 | Distribution Circuit | 3rd Party | Vehicle | 1861 | 110640 | 37.844 | -120.2114 | MTR1004736862 | Clear-32-90F | Pole-Wood | Broken, wire on object | 18-0044945 | OH | Sus | 0 | yes | 2018 | MAY | Yes | Line to Ground | 1351973 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0051812&numberofmonths=24&showchangehistorylog=1 | 18-0051812 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1701 | 163781701 | JUMPER | OJSMTR1004719395 | 20180618 | 252 | 111673 | 774 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 23220 | 37.8642 | -120.2177 | MTR1004241275 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0051812 | OH | Sus | 0 | No | 2018 | JUN | Yes | Line to Line | 1357276 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0052327&numberofmonths=24&showchangehistorylog=1 | 18-0052327 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2103 | 254432103 | OCB | 21032 | 20180619 | 1441 | 113097 | 186 | Distribution Circuit | Animal | Bird found | 2015 | 123838 | 37.2274 | -119.6906 | 2SOF10783 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0052327 | OH | Sus | 43376901 | No | 2018 | JUN | Yes | Three Phase Fault | 1357784 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0058587&numberofmonths=24&showchangehistorylog=1 | 18-0058587 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SAN JOAQUIN #3 PH-1103 | 252531103 | SWITCH | 5443 | 20180710 | 1908 | 128495 | 362 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 576 | 7488 | 37.2338 | -119.5041 | TRANSPOLE02 | Clear-32-90F | Connector or Splice (OH) | Broken, wire on object | 18-0058587 | OH | Sus | 0 | yes | 2018 | JUL | Yes | Force Out | 1362677 | CSO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0059705&numberofmonths=24&showchangehistorylog=1 | 18-0059705 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | BEAR VALLEY-2101 | 252192101 | RECLOSER | 4160 | 20180713 | 2234 | 131276 | 386 | Distribution Circuit | Animal | Bird found | 794 | 103372 | 37.4958 | -120.0437 | 1NOFMTR1006535500 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0059705 | OH | Sus | 43401025 | No | 2018 | JUL | Yes | Line to Ground | 1363668 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0059858&numberofmonths=24&showchangehistorylog=1 | 18-0059858 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1705 | 163781705 | FUSE | 53401 | 20180714 | 1522 | 131763 | 908 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 19976 | 37.9655 | -120.402 | BREAUXPARIS406211292McKibbonDrJamestown | Clear-32-90F | Pole-Wood | Broken, wire on ground | 18-0059858 | OH | Sus | 31399946 | No | 2018 | JUL | Yes | Multi-Fault | 1363797 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0060177&numberofmonths=24&showchangehistorylog=1 | 18-0060177 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | INDIAN FLAT-1104 | 252691104 | OTHER | WIREDOWNNEAR308805 | 20180716 | 811 | 132517 | 654 | Distribution Circuit | Equipment Failure/Involved | Overhead | 282 | 147760 | 37.6759 | -119.778 | JUSTLDSIDEOF308805 | Clear-32-90F | Connector or Splice (OH) | Broken, wire on object | 18-0060177 | OH | Sus | 0 | No | 2018 | JUL | Yes | Open Circuit | 1364138 | CSO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0065388&numberofmonths=24&showchangehistorylog=1 | 18-0065388 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1705 | 163351705 | OTHER | WIREDOWN19510PORTOFINO | 20180731 | 1157 | 145990 | 207 | Distribution Circuit | 3rd Party | Other | 13 | 2438 | 37.974 | -120.2465 | 19510PORTOFINO | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0065388 | OH | Sus | 43426691 | No | 2018 | JUL | Yes | Line to Ground | 1368051 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0066905&numberofmonths=24&showchangehistorylog=1 | 18-0066905 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | OAKHURST-1101 | 254421101 | FUSE | 27200 | 20180805 | 1356 | 149354 | 293 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 7325 | 37.393 | -119.7516 | 1PE1PSOFMTR1005022933 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 18-0066905 | OH | Sus | 0 | No | 2018 | AUG | Yes | Force Out | 1369204 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0080882&numberofmonths=24&showchangehistorylog=1 | 18-0080882 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1703 | 163761703 | RECLOSER | 8120 | 20180918 | 1151 | 176594 | 771 | Distribution Circuit | 3rd Party | Vehicle | 430 | 79100 | 38.0254 | -120.405 | L2073WITH3SPANSGOINGBACKTOSOURCE | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 18-0080882 | OH | Sus | 31406728 | No | 2018 | SEP | Yes | Line to Ground | 1378917 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0084242&numberofmonths=24&showchangehistorylog=1 | 18-0084242 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1703 | 163761703 | RECLOSER | 8120 | 20180927 | 1447 | 182845 | 517 | Distribution Circuit | Vegetation | Tree - fell into line | 430 | 51706 | 38.0254 | -120.405 | 1WOF26354 | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 18-0084242 | OH | Sus | 31409835 | No | 2018 | SEP | Yes | Line to Line | 1381230 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0085648&numberofmonths=24&showchangehistorylog=1 | 18-0085648 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | FUSE | L2155 | 20181002 | 1037 | 185849 | 636 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 9540 | 37.9491 | -120.2563 | DEADENDPOLEMTR5T3502 | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 18-0085648 | OH | Sus | 0 | yes | 2018 | OCT | Yes | Line to Line | 1382358 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0087112&numberofmonths=24&showchangehistorylog=1 | 18-0087112 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | CURTIS-1704 | 163351704 | FUSE | 20775 | 20181004 | 1835 | 188647 | 490 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 980 | 38.0172 | -120.3564 | BREAUXPARIS40622PNEFUCO20775behind21156LyonsBaldMountain | Overcast-32-90 F | Crossarm, Wood | Broken, wire on ground | 18-0087112 | OH | Sus | 31411068 | yes | 2018 | OCT | Yes | Line to Ground | 1383195 | CAW | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0089960&numberofmonths=24&showchangehistorylog=1 | 18-0089960 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2104 | 254432104 | RECLOSER | 5310 | 20181012 | 1532 | 194032 | 472 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 1123 | 51894 | 37.2286 | -119.7102 | DAHLEM1847559493847236902CEDARMOUNTAINLN | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 18-0089960 | OH | Sus | 31412549 | No | 2018 | OCT | Yes | Line to Ground | 1385212 | CAW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0092506&numberofmonths=24&showchangehistorylog=1 | 18-0092506 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2103 | 254432103 | FUSE | 87159 | 20181020 | 1727 | 199424 | 573 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 2292 | 37.2053 | -119.6845 | ATMTR1010207042 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 18-0092506 | OH | Sus | 0 | No | 2018 | OCT | Yes | Line to Ground | 1387116 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0096783&numberofmonths=24&showchangehistorylog=1 | 18-0096783 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1702 | 163661702 | JUMPER | UNNUMBEREDFUCO | 20181103 | 1156 | 208092 | 613 | Distribution Circuit | 3rd Party | Vehicle | 19 | 7891 | 38.0646 | -120.2707 | MTR1004240193 | Clear-32-90 F | Pole-Wood | Broken, wire on object | 18-0096783 | OH | Sus | 0 | No | 2018 | NOV | Yes | Line to Line | 1390272 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0097463&numberofmonths=24&showchangehistorylog=1 | 18-0097463 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1703 | 163761703 | FUSE | 26389 | 20181106 | 1128 | 209829 | 379 | Distribution Circuit | Vegetation | Tree - branch fell on line | 472 | 39666 | 37.9882 | -120.3881 | MTR1010471275 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0097463 | OH | Sus | 0 | No | 2018 | NOV | Yes | Line to Ground | 1390947 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0098890&numberofmonths=24&showchangehistorylog=1 | 18-0098890 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1704 | 163351704 | RECLOSER | 8140 | 20181110 | 2337 | 213194 | 633 | Distribution Circuit | 3rd Party | Vehicle | 824 | 58920 | 38.0069 | -120.3478 | FUCO91773 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 18-0098890 | OH | Sus | 0 | No | 2018 | NOV | Yes | Line to Line | 1391968 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0099049&numberofmonths=24&showchangehistorylog=1 | 18-0099049 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2102 | 254452102 | FUSE | 10373 | 20181111 | 1409 | 213501 | 761 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 19 | 1769 | 37.4787 | -119.8686 | MTR1005639143 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 18-0099049 | OH | Sus | 0 | No | 2018 | NOV | Yes | Line to Ground | 1392031 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0102252&numberofmonths=24&showchangehistorylog=1 | 18-0102252 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | S2253 | 20181122 | 300 | 221664 | 902 | Distribution Circuit | Vegetation | Tree - fell into line | 96 | 31687 | 38.0331 | -120.233 | 1SPSOFMTR1004861015 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | On Ground | 18-0102252 | OH | Sus | 0 | yes | 2018 | NOV | Yes | Line to Ground | 1394394 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0103021&numberofmonths=24&showchangehistorylog=1 | 18-0103021 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1705 | 163781705 | FUSE | 24314 | 20181124 | 2042 | 223941 | 528 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 29568 | 37.9619 | -120.4178 | 2EOF24314 | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0103021 | OH | Sus | 31416760 | No | 2018 | NOV | Yes | Line to Line | 1394992 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0104308&numberofmonths=24&showchangehistorylog=1 | 18-0104308 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1701 | 163781701 | RECLOSER | 76030 | 20181128 | 1106 | 226483 | 590 | Distribution Circuit | 3rd Party | Vehicle | 189 | 31404 | 37.8992 | -120.4551 | 1NWOFMTR1005427965 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 18-0104308 | OH | Sus | 0 | yes | 2018 | NOV | Yes | Line to Line | 1395801 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0106023&numberofmonths=24&showchangehistorylog=1 | 18-0106023 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1703 | 163761703 | FUSE | 1673 | 20181202 | 305 | 231433 | 360 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2880 | 38.0112 | -120.4188 | MTR1004736683 | Partly Cloudy-Below 32 F | Conductor, Overhead | Broken, wire on ground | 18-0106023 | OH | Sus | 31417481 | No | 2018 | DEC | Yes | Line to Line | 1396940 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0106528&numberofmonths=24&showchangehistorylog=1 | 18-0106528 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | CURTIS-1702 | 163351702 | FUSE | 22618 | 20181203 | 1319 | 232741 | 684 | Distribution Circuit | 3rd Party | Vehicle | 30 | 5720 | 38.0513 | -120.2135 | MTR100473340 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 18-0106528 | OH | Sus | 0 | No | 2018 | DEC | Yes | Line to Line | 1397364 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0107501&numberofmonths=24&showchangehistorylog=1 | 18-0107501 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1705 | 163351705 | RECLOSER | 65908 | 20181206 | 641 | 234728 | 126 | Distribution Circuit | Animal | Bird found | 666 | 55227 | 37.9575 | -120.3133 | BET21459SW96519 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0107501 | OH | Sus | 0 | No | 2018 | DEC | Yes | Line to Ground | 1397902 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0108787&numberofmonths=24&showchangehistorylog=1 | 18-0108787 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2102 | 254452102 | FUSE | 46623 | 20181212 | 1035 | 238654 | 264 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 14 | 3696 | 37.5072 | -119.8434 | 1WOF46623 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0108787 | OH | Sus | 43614020 | No | 2018 | DEC | Yes | Line to Ground | 1399200 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0109600&numberofmonths=24&showchangehistorylog=1 | 18-0109600 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1705 | 163351705 | FUSE | L1209 | 20181217 | 502 | 242036 | 373 | Distribution Circuit | Vegetation | Tree - fell into line | 75 | 8463 | 37.9627 | -120.2916 | 3PEOFMTR1004899449 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0109600 | OH | Sus | 31418781 | yes | 2018 | DEC | Yes | Line to Line | 1400239 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0109845&numberofmonths=24&showchangehistorylog=1 | 18-0109845 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | FUSE | 23223 | 20181218 | 1011 | 242960 | 566 | Distribution Circuit | Equipment Failure/Involved | Overhead | 80 | 10112 | 37.9786 | -120.3151 | 1SSOFMTR1008772966 | Clear-32-90 F | Woodpin | Broken, wire on ground | 18-0109845 | OH | Sus | 0 | No | 2018 | DEC | Yes | Line to Ground | 1400590 | WP | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0110140&numberofmonths=24&showchangehistorylog=1 | 18-0110140 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MARIPOSA-2101 | 254452101 | FUSE | 10353 | 20181220 | 1025 | 244675 | 904 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 19 | 17176 | 37.5762 | -119.8532 | 15SPSOFMTR1007100759 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 18-0110140 | OH | Sus | 31419421 | No | 2018 | DEC | Yes | Line to Line | 1401100 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0110545&numberofmonths=24&showchangehistorylog=1 | 18-0110545 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | CURTIS-1704 | 163351704 | TRIP-SAVER | 803 | 20181224 | 1809 | 246730 | 221 | Distribution Circuit | Vegetation | Tree - fell into line | 109 | 9704 | 38.0461 | -120.3654 | 23255WOODSCREEKWAY | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0110545 | OH | Sus | 43621705 | yes | 2018 | DEC | Yes | Line to Ground | 1401624 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0110948&numberofmonths=24&showchangehistorylog=1 | 18-0110948 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2102 | 254432102 | JUMPER | 43403FUSESOHTAPDOWN | 20181228 | 711 | 248583 | 355 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 355 | 37.2561 | -119.5653 | 34969RD223 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 18-0110948 | OH | Sus | 31419920 | No | 2018 | DEC | Yes | Line to Ground | 1402130 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0111258&numberofmonths=24&showchangehistorylog=1 | 18-0111258 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1103 | 254421103 | FUSE | 96353 | 20181231 | 957 | 250142 | 563 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 6756 | 37.3231 | -119.5648 | DAHLEM1847559493847239500BRIERPLACE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0111258 | OH | Sus | 0 | yes | 2018 | DEC | Yes | Line to Line | 1402513 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=18-0111180&numberofmonths=24&showchangehistorylog=1 | 18-0111180 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SAN JOAQUIN #3 PH-1101 | 252531101 | RECLOSER | 10060 | 20181231 | 911 | 250074 | 1940 | Distribution Circuit | Vegetation | Tree - fell into line | 104 | 85232 | 37.2927 | -119.5325 | PORTERJRJOHN37907EMORYLN | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 18-0111180 | OH | Sus | 31420266 | yes | 2018 | DEC | Yes | Line to Line | 1402415 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0004870&numberofmonths=24&showchangehistorylog=1 | 19-0004870 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1705 | 163351705 | FUSE | L1773 | 20190105 | 1547 | 254496 | 243 | Distribution Circuit | Vegetation | Tree - branch fell on line | 252 | 39971 | 37.9584 | -120.3215 | JEO460215 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0004870 | OH | Sus | 43626634 | yes | 2019 | JAN | Yes | Line to Ground | 1403406 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0007321&numberofmonths=24&showchangehistorylog=1 | 19-0007321 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2104 | 254432104 | RECLOSER | 10400 | 20190110 | 251 | 262158 | 788 | Distribution Circuit | 3rd Party | Vehicle | 1458 | 136681 | 37.2216 | -119.7687 | JNO10573 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 19-0007321 | OH | Sus | 31421646 | No | 2019 | JAN | Yes | Line to Line | 1405162 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0012778&numberofmonths=24&showchangehistorylog=1 | 19-0012778 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2102 | 254452102 | FUSE | 46623 | 20190120 | 2137 | 277757 | 348 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 4872 | 37.5072 | -119.8434 | 1WOF46623 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0012778 | OH | Sus | 43641240 | yes | 2019 | JAN | Yes | Line to Ground | 1409110 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0012889&numberofmonths=24&showchangehistorylog=1 | 19-0012889 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1703 | 163761703 | FUSE | S1359 | 20190121 | 1523 | 278453 | 707 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 2121 | 38.0211 | -120.4329 | SIUDZINSKIMARK1POLEAND3POLELOADSIDEOFS1359 | Partly Cloudy-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 19-0012889 | OH | Sus | 0 | No | 2019 | JAN | Yes | Line to Line | 1409230 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0017501&numberofmonths=24&showchangehistorylog=1 | 19-0017501 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2104 | 254432104 | JUMPER | ABPHASESBROKENCGC322360028030 | 20190203 | 826 | 288734 | 334 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 13706 | 37.2679 | -119.69 | CGC322360028030 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017501 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1411916 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0020041&numberofmonths=24&showchangehistorylog=1 | 19-0020041 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | OTHER | WIREDOWN1SPLDSIDEOFL465 | 20190206 | 1517 | 294500 | 2793 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2793 | 37.8504 | -120.1685 | 1SPLDOFL465 | Partly Cloudy-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 19-0020041 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1413776 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019685&numberofmonths=24&showchangehistorylog=1 | 19-0019685 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1705 | 163351705 | FUSE | 9817 | 20190206 | 1001 | 294123 | 3134 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 27360 | 37.9659 | -120.3132 | 3SPSSOFCGC320570053500 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0019685 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1413515 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0019986&numberofmonths=24&showchangehistorylog=1 | 19-0019986 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | CURTIS-1702 | 163351702 | JUMPER | WIREDOWNNOFMTR1004902033 | 20190208 | 830 | 295973 | 1563 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 43785 | 38.0265 | -120.2865 | MTR1004902033 | Partly Cloudy-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0019986 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1413749 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021176&numberofmonths=24&showchangehistorylog=1 | 19-0021176 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | BEAR VALLEY-2105 | 252192105 | JUMPER | WIREDOWNMTR1007092937 | 20190211 | 1503 | 300038 | 182 | Distribution Circuit | Vegetation | Tree - fell into line | 129 | 1846 | 37.7563 | -120.1393 | MTR1007092937 | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 19-0021176 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1414774 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0021061&numberofmonths=24&showchangehistorylog=1 | 19-0021061 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1103 | 254421103 | FUSE | 5544 | 20190211 | 1335 | 299929 | 146 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 1168 | 37.4554 | -119.6411 | LDSIDEOF5544 | Clear-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021061 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1414721 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0030438&numberofmonths=24&showchangehistorylog=1 | 19-0030438 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | BEAR VALLEY-2101 | 252192101 | OTHER | WIREDOWN1EOFMTR1007063322 | 20190304 | 919 | 330713 | 296 | Distribution Circuit | Equipment Failure/Involved | Overhead | 81 | 23692 | 37.5965 | -120.1861 | 1EOFMTR1007063322 | Partly Cloudy-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0030438 | OH | Sus | 43689822 | No | 2019 | MAR | Yes | Line to Ground | 1421861 | CSO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0031485&numberofmonths=24&showchangehistorylog=1 | 19-0031485 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2102 | 254452102 | FUSE | 7427 | 20190306 | 1656 | 333179 | 290 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 4060 | 37.4002 | -119.8783 | 5SPANEOFMTR1005643945 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0031485 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Line to Ground | 1422421 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0032670&numberofmonths=24&showchangehistorylog=1 | 19-0032670 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2102 | 254452102 | FUSE | 10516 | 20190311 | 1245 | 336301 | 615 | Distribution Circuit | Animal | Other | 36 | 5446 | 37.4723 | -119.8758 | MTR1005637063 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0032670 | OH | Sus | 0 | No | 2019 | MAR | Yes | Line to Ground | 1423308 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0035101&numberofmonths=24&showchangehistorylog=1 | 19-0035101 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1704 | 163351704 | FUSE | 23334 | 20190319 | 1252 | 342984 | 244 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 313 | 70602 | 37.9892 | -120.3328 | 2SEOFMTR100424175120502PHOENIXLAKERD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0035101 | OH | Sus | 43711436 | No | 2019 | MAR | Yes | Line to Line | 1425124 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0038234&numberofmonths=24&showchangehistorylog=1 | 19-0038234 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1704 | 163781704 | RECLOSER | 8040 | 20190329 | 938 | 350118 | 535 | Distribution Circuit | Equipment Failure/Involved | Overhead | 135 | 25839 | 37.8996 | -120.5039 | 5PLDSIDEOFMTR1005775132OPEN | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0038234 | OH | Sus | 43722795 | No | 2019 | MAR | Yes | Line to Ground | 1427185 | CSO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0041008&numberofmonths=24&showchangehistorylog=1 | 19-0041008 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | BEAR VALLEY-2105 | 252192105 | RECLOSER | 4170 | 20190409 | 1521 | 356875 | 885 | Distribution Circuit | Vegetation | Tree - fell into line | 662 | 162762 | 37.6103 | -120.1339 | SOF77095 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0041008 | OH | Sus | 0 | yes | 2019 | APR | Yes | Line to Ground | 1429121 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0041008&numberofmonths=24&showchangehistorylog=1 | 19-0041008 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | BEAR VALLEY-2105 | 252192105 | FUSE | 4597 | 20190409 | 1527 | 357224 | 950 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 17100 | 37.733 | -120.0818 | MTR1006385569 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 19-0041008 | OH | Sus | 0 | yes | 2019 | APR | Yes | Line to Ground | 1429180 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0041056&numberofmonths=24&showchangehistorylog=1 | 19-0041056 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | FUSE | 1949 | 20190409 | 1510 | 356846 | 914 | Distribution Circuit | Vegetation | Tree - bark fell into line | 155 | 28200 | 37.853 | -120.1659 | MTR1008889962 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 19-0041056 | OH | Sus | 31433234 | yes | 2019 | APR | Yes | Line to Ground | 1429152 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0041006&numberofmonths=24&showchangehistorylog=1 | 19-0041006 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1704 | 163351704 | FUSE | 22357 | 20190409 | 1454 | 356832 | 174 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 696 | 37.9799 | -120.3298 | SIUDZINSKIMARK14381edgemontacres | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0041006 | OH | Sus | 43731033 | yes | 2019 | APR | Yes | Line to Line | 1429120 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0044583&numberofmonths=24&showchangehistorylog=1 | 19-0044583 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE | 2262 | 20190420 | 1106 | 364366 | 749 | Distribution Circuit | Vegetation | Tree - bark fell into line | 84 | 16586 | 37.2859 | -119.6311 | MTR1005022497 | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 19-0044583 | OH | Sus | 0 | yes | 2019 | APR | Yes | Line to Ground | 1431748 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0050592&numberofmonths=24&showchangehistorylog=1 | 19-0050592 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | WOODWARD-2108 | 255292108 | FUSE | 13044 | 20190510 | 42 | 377434 | 328 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 15744 | 37.0505 | -119.6495 | MTR1005773068 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0050592 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Line to Ground | 1435739 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0052471&numberofmonths=24&showchangehistorylog=1 | 19-0052471 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1703 | 163761703 | RECLOSER | 8120 | 20190515 | 2326 | 381650 | 546 | Distribution Circuit | Vegetation | Tree - branch fell on line | 431 | 193382 | 38.0254 | -120.405 | MTR1005519957 | Overcast-Heavy Rain-32-90 F | Jumper | Broken, wire on ground | 19-0052471 | OH | Sus | 43783264 | yes | 2019 | MAY | Yes | Line to Line | 1437119 | JMP | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0052499&numberofmonths=24&showchangehistorylog=1 | 19-0052499 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1704 | 163351704 | RECLOSER | 8140 | 20190516 | 155 | 381827 | 468 | Distribution Circuit | Vegetation | Tree - fell into line | 921 | 70461 | 38.0069 | -120.3478 | 2POLESLDSIDEOF22953 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0052499 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Multi-Fault | 1437145 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0053957&numberofmonths=24&showchangehistorylog=1 | 19-0053957 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | FUSE | 48691 | 20190519 | 1218 | 385202 | 503 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 8794 | 37.9911 | -120.2788 | MTR1008770243 | Overcast-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0053957 | OH | Sus | 31442854 | yes | 2019 | MAY | Yes | Line to Line | 1438171 | CAW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0078981&numberofmonths=24&showchangehistorylog=1 | 19-0078981 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | FUSE | L2153 | 20190718 | 1758 | 459745 | 737 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 5955 | 37.9496 | -120.2648 | 1NOF2NOFMTR1004934029 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0078981 | OH | Sus | 31458821 | No | 2019 | JUL | Yes | Line to Line | 1457198 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0079030&numberofmonths=24&showchangehistorylog=1 | 19-0079030 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | FUSE | 1715 | 20190719 | 638 | 459930 | 507 | Distribution Circuit | Vegetation | Tree - fell into line | 78 | 24042 | 37.9194 | -120.3504 | SIUDZINSKIMARKmtr1004862052 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0079030 | OH | Sus | 0 | No | 2019 | JUL | Yes | Line to Line | 1457250 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0080383&numberofmonths=24&showchangehistorylog=1 | 19-0080383 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | OTHER | WIREDOWN1EOF4SOF89943 | 20190723 | 1652 | 469660 | 427 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1206 | 513358 | 37.2143 | -119.5059 | 1EOF4SOF89943 | Partly Cloudy-Above 90 | Conductor, Overhead | Broken, wire on ground | 19-0080383 | OH | Sus | 43897222 | yes | 2019 | JUL | Yes | Open Circuit | 1458207 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0081040&numberofmonths=24&showchangehistorylog=1 | 19-0081040 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | TAR FLAT-0402 | 163240402 | JUMPER | 1WOFCGC320343554108 | 20190725 | 954 | 471056 | 481 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 481 | 37.9859 | -120.382 | CGC320343554108 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 19-0081040 | OH | Sus | 0 | No | 2019 | JUL | Yes | Force Out | 1458643 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0083631&numberofmonths=24&showchangehistorylog=1 | 19-0083631 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1701 | 163781701 | RECLOSER | 3186 | 20190801 | 2302 | 477534 | 634 | Distribution Circuit | 3rd Party | Vehicle | 1257 | 316121 | 37.8621 | -120.2265 | MTR1004239590 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0083631 | OH | Sus | 0 | No | 2019 | AUG | Yes | Line to Line | 1460260 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0084621&numberofmonths=24&showchangehistorylog=1 | 19-0084621 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | FUSE | 5324 | 20190806 | 748 | 485513 | 413 | Distribution Circuit | 3rd Party | Vehicle | 1053 | 74454 | 37.1952 | -119.5872 | 51469ROAD200NORTHFORK | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0084621 | OH | Sus | 0 | No | 2019 | AUG | Yes | Line to Ground | 1460992 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0085048&numberofmonths=24&showchangehistorylog=1 | 19-0085048 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | CURTIS-1704 | 163351704 | FUSE | 20809 | 20190807 | 43 | 487604 | 307 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 15964 | 38.0332 | -120.3676 | MTR1004899970 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0085048 | OH | Sus | 43910494 | No | 2019 | AUG | Yes | Line to Ground | 1461219 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0093607&numberofmonths=24&showchangehistorylog=1 | 19-0093607 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | BEAR VALLEY-2101 | 252192101 | FUSE | 24006 | 20190829 | 1121 | 546808 | 498 | Distribution Circuit | 3rd Party | Vehicle | 5 | 2490 | 37.5032 | -120.0458 | EOLTX | Clear-32-90 F | Anchor or Guy | Broken, wire on ground | 19-0093607 | OH | Sus | 0 | No | 2019 | AUG | Yes | Line to Line | 1466659 | ANC | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0099772&numberofmonths=24&showchangehistorylog=1 | 19-0099772 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2102 | 254452102 | RECLOSER | 37288 | 20190916 | 1435 | 585340 | 359 | Distribution Circuit | Vegetation | Tree - fell into line | 698 | 121254 | 37.4205 | -119.8772 | 3RDSPANNORTHOFFUCO7429 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0099772 | OH | Sus | 31471919 | yes | 2019 | SEP | Yes | Line to Ground | 1470445 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0102232&numberofmonths=24&showchangehistorylog=1 | 19-0102232 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MARIPOSA-2101 | 254452101 | OTHER | WIREDOWN1WOFMTR1007099599 | 20190922 | 1152 | 603613 | 644 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2287 | 133232 | 37.5168 | -119.9162 | 1WOFMTR1007099599 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0102232 | OH | Sus | 0 | No | 2019 | SEP | Yes | Line to Ground | 1471900 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0104172&numberofmonths=24&showchangehistorylog=1 | 19-0104172 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SAN JOAQUIN #3 PH-1103 | 252531103 | FUSE | 10524 | 20190926 | 1227 | 618220 | 328 | Distribution Circuit | 3rd Party | Vehicle | 20 | 6560 | 37.2323 | -119.4693 | 2S1WOF105242S1WOF10524 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0104172 | OH | Sus | 0 | yes | 2019 | SEP | Yes | Line to Line | 1473259 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0105922&numberofmonths=24&showchangehistorylog=1 | 19-0105922 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | S1767 | 20191001 | 934 | 633866 | 569 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 7 | 3983 | 38.016 | -120.225 | MTR1004733921 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0105922 | OH | Sus | 0 | No | 2019 | OCT | Yes | Line to Line | 1474419 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0111263&numberofmonths=24&showchangehistorylog=1 | 19-0111263 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 2269 | 20191014 | 1132 | 657193 | 648 | Distribution Circuit | 3rd Party | Vehicle | 85 | 10560 | 38.0392 | -120.2091 | 1WOFMTR1010108793 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0111263 | OH | Sus | 0 | No | 2019 | OCT | Yes | Line to Ground | 1479936 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0111571&numberofmonths=24&showchangehistorylog=1 | 19-0111571 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | COARSEGOLD-2102 | 254432102 | FUSE | 97905 | 20191015 | 35 | 658753 | 247 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 741 | 37.3223 | -119.6173 | 2NOF97905 | Clear-32-90 F | Insulator | Broken, wire on ground | 19-0111571 | OH | Sus | 43999647 | No | 2019 | OCT | Yes | Force Out | 1480022 | INS | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0120594&numberofmonths=24&showchangehistorylog=1 | 19-0120594 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1703 | 163761703 | OCB | 17032 | 20191104 | 109 | 698909 | 743 | Distribution Circuit | 3rd Party | Vehicle | 3603 | 465345 | 37.9799 | -120.4136 | L399 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0120594 | OH | Sus | 0 | No | 2019 | NOV | Yes | Three Phase Fault | 1489010 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0123520&numberofmonths=24&showchangehistorylog=1 | 19-0123520 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1701 | 163781701 | RECLOSER | 76030 | 20191111 | 943 | 704321 | 823 | Distribution Circuit | 3rd Party | Vehicle | 191 | 38170 | 37.8992 | -120.4551 | 2SPANSLDSIDEOFS1057 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 19-0123520 | OH | Sus | 0 | No | 2019 | NOV | Yes | Line to Line | 1490478 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0130769&numberofmonths=24&showchangehistorylog=1 | 19-0130769 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2102 | 254432102 | RECLOSER | 10330 | 20191128 | 710 | 722633 | 478 | Distribution Circuit | Vegetation | Tree - fell into line | 1273 | 211524 | 37.2516 | -119.562 | 35972TEAFORDPOYAH | Overcast-Snow-32-90 F | Pole-Wood | Broken, wire on ground | 19-0130769 | OH | Sus | 0 | yes | 2019 | NOV | Yes | Three Phase Fault | 1495452 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0131036&numberofmonths=24&showchangehistorylog=1 | 19-0131036 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | FUSE | 601 | 20191129 | 748 | 723366 | 284 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 7668 | 37.9771 | -120.2718 | 19310BLACKOAK | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0131036 | OH | Sus | 0 | yes | 2019 | NOV | Yes | Line to Line | 1495737 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0131068&numberofmonths=24&showchangehistorylog=1 | 19-0131068 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2102 | 254452102 | JUMPER | OJNWOF321820030723 | 20191129 | 1140 | 723581 | 245 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 490 | 37.3483 | -119.8761 | 321820030723 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0131068 | OH | Sus | 0 | yes | 2019 | NOV | Yes | Line to Ground | 1495767 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0134001&numberofmonths=24&showchangehistorylog=1 | 19-0134001 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SAN JOAQUIN #3 PH-1101 | 252531101 | FUSE | 74256 | 20191205 | 1505 | 730810 | 102 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 102 | 37.2909 | -119.5303 | DAHLEMJUSTIN1847BASSLAKE | Partly Cloudy-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0134001 | OH | Sus | 0 | No | 2019 | DEC | Yes | Line to Ground | 1498016 | CSO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=19-0134964&numberofmonths=24&showchangehistorylog=1 | 19-0134964 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | BEAR VALLEY-2101 | 252192101 | RECLOSER | 4160 | 20191207 | 2225 | 733463 | 703 | Distribution Circuit | Vegetation | Tree - branch fell on line | 794 | 113872 | 37.4958 | -120.0437 | MartinBlair55947452963151HIGHWAY140CATHYSVALLEY | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0134964 | OH | Sus | 44115323 | yes | 2019 | DEC | Yes | Multi-Fault | 1498753 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0033110&numberofmonths=24&showchangehistorylog=1 | 20-0033110 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SAN JOAQUIN #3 PH-1101 | 252531101 | RECLOSER | 673480 | 20200317 | 3 | 856091 | 1032 | Distribution Circuit | Environmental/External | Ice or snow | 499 | 178373 | 37.2881 | -119.5197 | BET5TH6THPOLELDSIDEOF673480 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 20-0033110 | OH | Sus | 0 | yes | 2020 | MAR | Yes | Line to Ground | 1522256 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0034376&numberofmonths=24&showchangehistorylog=1 | 20-0034376 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 2267 | 20200319 | 1706 | 859170 | 170 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 1360 | 38.0857 | -120.1565 | 5POLESLDSIDE2267 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0034376 | OH | Sus | 0 | yes | 2020 | MAR | Yes | Line to Ground | 1523062 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0039003&numberofmonths=24&showchangehistorylog=1 | 20-0039003 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SPRING GAP-1702 | 162831702 | RECLOSER | 86032 | 20200406 | 247 | 885954 | 996 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 18888 | 38.1849 | -119.9915 | MTR1005419520 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 20-0039003 | OH | Sus | 0 | yes | 2020 | APR | Yes | Force Out | 1525727 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0039456&numberofmonths=24&showchangehistorylog=1 | 20-0039456 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | OTHER | WIREDOWNSOURCESIDE21017 | 20200407 | 2055 | 890343 | 1134 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 50795 | 37.8011 | -119.8806 | WIREDOWNSOURCESIDE21017WIREONCROSSARM4SPANSSOURCESIDEOF714303 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0039456 | OH | Sus | 0 | No | 2020 | APR | Yes | Line to Ground | 1525982 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0042489&numberofmonths=24&showchangehistorylog=1 | 20-0042489 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE | FUSE10623 | 20200417 | 2128 | 897284 | 350 | Distribution Circuit | Environmental/External | Lightning | 72 | 18128 | 37.2251 | -119.716 | 2POLESLDSIDEOFMTR1005670488 | Overcast-Drizzle-32-90 F | Insulator | Broken, wire on ground | 20-0042489 | OH | Sus | 0 | No | 2020 | APR | Yes | Line to Ground | 1527830 | INS | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0043246&numberofmonths=24&showchangehistorylog=1 | 20-0043246 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1705 | 163351705 | FUSE | 19515 | 20200421 | 1142 | 898787 | 433 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 43 | 7257 | 37.9969 | -120.2396 | MTR1010355192 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0043246 | OH | Sus | 31500881 | No | 2020 | APR | Yes | Line to Ground | 1528304 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0043178&numberofmonths=24&showchangehistorylog=1 | 20-0043178 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2102 | 254452102 | FUSE | 4562 | 20200421 | 915 | 898638 | 490 | Distribution Circuit | Animal | Other | 73 | 4450 | 37.4517 | -119.8524 | CGC321846934885EOLSINGLE | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0043178 | OH | Sus | 0 | No | 2020 | APR | Yes | Line to Line | 1528274 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0050990&numberofmonths=24&showchangehistorylog=1 | 20-0050990 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1703 | 163761703 | RECLOSER | 11270 | 20200517 | 1146 | 915182 | 351 | Distribution Circuit | Equipment Failure/Involved | Overhead | 369 | 90769 | 38.022 | -120.4318 | BREAUXPARIS40623NOFLR11270 | Partly Cloudy-32-90 F | Crossarm, Wood | Broken, wire on ground | 20-0050990 | OH | Sus | 31503288 | yes | 2020 | MAY | Yes | Line to Ground | 1532928 | CAW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0051495&numberofmonths=24&showchangehistorylog=1 | 20-0051495 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | BEAR VALLEY-2101 | 252192101 | RECLOSER | 4160 | 20200518 | 1544 | 917008 | 228 | Distribution Circuit | Equipment Failure/Involved | Overhead | 797 | 151997 | 37.4958 | -120.0437 | 2SPANSWOFCGC321301335635 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0051495 | OH | Sus | 44326528 | yes | 2020 | MAY | Yes | Line to Line | 1533192 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0065766&numberofmonths=24&showchangehistorylog=1 | 20-0065766 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | FUSE | 23223 | 20200627 | 2338 | 949159 | 767 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 13899 | 37.9786 | -120.3151 | 20261BARBARARD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0065766 | OH | Sus | 31507184 | No | 2020 | JUN | Yes | Line to Line | 1542986 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0070883&numberofmonths=24&showchangehistorylog=1 | 20-0070883 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | FUSE | 63417 | 20200711 | 2003 | 962555 | 476 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 2024 | 37.1945 | -119.5016 | CGC322930025358 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0070883 | OH | Sus | 31508460 | yes | 2020 | JUL | Yes | Force Out | 1545946 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0071879&numberofmonths=24&showchangehistorylog=1 | 20-0071879 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1101 | 254421101 | OCB | 11012 | 20200729 | 847 | 974232 | 140 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 3025 | 329234 | 37.3218 | -119.6343 | FB10249 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 20-0071879 | OH | Sus | 35117329 | No | 2020 | JUL | Yes | Line to Ground | 1550128 | CSO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0086575&numberofmonths=24&showchangehistorylog=1 | 20-0086575 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1103 | 254421103 | FUSE | 2421 | 20200818 | 748 | 1018339 | 627 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 6506 | 37.3642 | -119.6262 | 50600ROAD220 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0086575 | OH | Sus | 0 | yes | 2020 | AUG | Yes | Line to Line | 1556617 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0118516&numberofmonths=24&showchangehistorylog=1 | 20-0118516 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2102 | 254452102 | FUSE | 10374 | 20201108 | 1327 | 1139518 | 430 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 6700 | 37.46 | -119.9017 | 3PEOFMTR1006908337 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0118516 | OH | Sus | 0 | No | 2020 | NOV | Yes | Three Phase Fault | 1578139 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0121825&numberofmonths=24&showchangehistorylog=1 | 20-0121825 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1705 | 163781705 | FUSE | 2677 | 20201117 | 1006 | 1147108 | 288 | Distribution Circuit | Equipment Failure/Involved | Overhead | 58 | 8876 | 37.9271 | -120.4202 | MTR1004904132RO16827DUTCHMINERD | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 20-0121825 | OH | Sus | 44543276 | No | 2020 | NOV | Yes | Line to Line | 1580593 | CSO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0128990&numberofmonths=24&showchangehistorylog=1 | 20-0128990 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | FUSE | 22189 | 20201208 | 1410 | 1172607 | 369 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 11 | 4059 | 37.981 | -120.3064 | MTR1004858631 | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 20-0128990 | OH | Sus | 31520053 | No | 2020 | DEC | Yes | Line to Line | 1585514 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=20-0131868&numberofmonths=24&showchangehistorylog=1 | 20-0131868 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | OTHER | WIREDOWN1SSS1753 | 20201226 | 914 | 1199057 | 486 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1887 | 383213 | 38.0064 | -120.3015 | WIREDOWNJUSTSSOF1753SBCO | Clear-32-90F | Connector or Splice (OH) | Broken, wire on ground | 20-0131868 | OH | Sus | 0 | No | 2020 | DEC | Yes | Line to Ground | 1589584 | CSO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0012463&numberofmonths=24&showchangehistorylog=1 | 21-0012463 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | CURTIS-1705 | 163351705 | JUMPER | OJ1SSOFMTR1004737686 | 20210122 | 737 | 1220558 | 615 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 14145 | 38.0336 | -120.2287 | MTR1004737686 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0012463 | OH | Sus | 0 | No | 2021 | JAN | Yes | Force Out | 1595684 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0013255&numberofmonths=24&showchangehistorylog=1 | 21-0013255 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2102 | 254452102 | FUSE | 69311 | 20210123 | 1103 | 1221768 | 462 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1386 | 37.4859 | -119.8612 | 5360DORARD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0013255 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1596216 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0013297&numberofmonths=24&showchangehistorylog=1 | 21-0013297 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1103 | 254421103 | JUMPER | OJ1WOFCGC322346032763 | 20210123 | 1346 | 1221887 | 141 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 141 | 37.3971 | -119.6951 | 3SPANSSOURCESIDEOFCGC322340832682 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0013297 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1596247 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0018158&numberofmonths=24&showchangehistorylog=1 | 21-0018158 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | BEAR VALLEY-2105 | 252192105 | SWITCH | 23336 | 20210129 | 636 | 1241594 | 446 | Distribution Circuit | Equipment Failure/Involved | Overhead | 71 | 29090 | 37.7504 | -120.1216 | CGC321116845635 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0018158 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1600272 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0018521&numberofmonths=24&showchangehistorylog=1 | 21-0018521 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1702 | 163661702 | FUSE | 22613 | 20210129 | 1450 | 1242130 | 334 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 20040 | 38.0463 | -120.2244 | 6POLESLDSIDE226138LDSIDEOF22613 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 21-0018521 | OH | Sus | 0 | No | 2021 | JAN | Yes | Force Out | 1600421 | PW | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0018573&numberofmonths=24&showchangehistorylog=1 | 21-0018573 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1702 | 163661702 | OTHER | 825573 | 20210129 | 837 | 1241219 | 641 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 3205 | 38.0466 | -120.2191 | 825573 | Clear-32-90F | Conductor, Overhead | On Ground | 21-0018573 | OH | Sus | 0 | No | 2021 | JAN | Yes | Open Circuit | 1600459 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0018170&numberofmonths=24&showchangehistorylog=1 | 21-0018170 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1103 | 254421103 | RECLOSER | 10190 | 20210129 | 756 | 1241138 | 570 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 4560 | 37.4145 | -119.6272 | 45SPANSSSOF5459 | Clear-32-90F | Crossarm, Wood | Broken, wire on ground | 21-0018170 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Line | 1600178 | CAW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0018228&numberofmonths=24&showchangehistorylog=1 | 21-0018228 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SAN JOAQUIN #3 PH-1101 | 252531101 | RECLOSER | 673480 | 20210129 | 935 | 1241912 | 376 | Distribution Circuit | Vegetation | Tree - fell into line | 580 | 200302 | 37.3241 | -119.5481 | WIREWRAPPEDATMTR10063757811SPANOFWIREDOWN2EOF5663 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0018228 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Line | 1600357 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0024261&numberofmonths=24&showchangehistorylog=1 | 21-0024261 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1702 | 163661702 | SWITCH | 531976 | 20210210 | 1907 | 1252660 | 111 | Distribution Circuit | Equipment Failure/Involved | Overhead | 45 | 4995 | 38.0524 | -120.2316 | TUCKMATT2074twopolesloadsideoflr531976 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0024261 | OH | Sus | 44650637 | No | 2021 | FEB | Yes | Force Out | 1604389 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0024834&numberofmonths=24&showchangehistorylog=1 | 21-0024834 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MARIPOSA-2102 | 254452102 | FUSE | 4556 | 20210212 | 354 | 1253491 | 364 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 30940 | 37.4395 | -119.9413 | MARTINBLAIR55947452964118SULLIVANRD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0024834 | OH | Sus | 44651290 | No | 2021 | FEB | Yes | Line to Ground | 1604707 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0029436&numberofmonths=24&showchangehistorylog=1 | 21-0029436 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | FUSE | 22185 | 20210225 | 902 | 1262075 | 303 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1212 | 37.9697 | -120.2544 | 1POLELDSIDEOF2215 | Clear-32-90 F | Crossarm, Wood | Broken, wire on object | 21-0029436 | OH | Sus | 31531472 | No | 2021 | FEB | Yes | Force Out | 1607800 | CAW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0034304&numberofmonths=24&showchangehistorylog=1 | 21-0034304 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2102 | 254452102 | RECLOSER | 37288 | 20210310 | 419 | 1276711 | 496 | Distribution Circuit | Vegetation | Tree - branch fell on line | 705 | 253650 | 37.421 | -119.8768 | CGC321883633178 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0034304 | OH | Sus | 0 | No | 2021 | MAR | Yes | Line to Ground | 1610839 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0041874&numberofmonths=24&showchangehistorylog=1 | 21-0041874 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1705 | 163781705 | FUSE | 53159 | 20210328 | 514 | 1301829 | 349 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 1 | 349 | 37.9643 | -120.4048 | 1SPANLOADSIDEOF53159 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0041874 | OH | Sus | 31534520 | No | 2021 | MAR | Yes | Line to Ground | 1615606 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0052831&numberofmonths=24&showchangehistorylog=1 | 21-0052831 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE | 10588 | 20210424 | 2342 | 1333280 | 842 | Distribution Circuit | 3rd Party | Vehicle | 78 | 52465 | 37.2461 | -119.8825 | 2POLESLDSIDEOF10798 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0052831 | OH | Sus | 0 | No | 2021 | APR | Yes | Line to Ground | 1622888 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0052884&numberofmonths=24&showchangehistorylog=1 | 21-0052884 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | FUSE | 2497 | 20210425 | 1143 | 1333513 | 607 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 2510 | 38.0111 | -120.291 | SIUDZINSKIMARK180616304HIDDENVALLEYRD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0052884 | OH | Sus | 0 | No | 2021 | APR | Yes | Line to Line | 1622937 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0085296&numberofmonths=24&showchangehistorylog=1 | 21-0085296 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1704 | 163781704 | RECLOSER | 88630 | 20210706 | 1300 | 1392965 | 582 | Distribution Circuit | 3rd Party | Vehicle | 5 | 2910 | 37.9012 | -120.5175 | CASTILLOSTEVE19746000OYBRENESFERRYRD | Clear-32-90F | Pole-Wood | Broken, wire on ground | 21-0085296 | OH | Sus | 0 | No | 2021 | JUL | Yes | Three Phase Fault | 1645695 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0098088&numberofmonths=24&showchangehistorylog=1 | 21-0098088 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1705 | 163351705 | FUSE | S1617 | 20210731 | 1532 | 1427100 | 320 | Distribution Circuit | 3rd Party | Vehicle | 62 | 19840 | 37.9857 | -120.2645 | 1LDSIDEOFS1617 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0098088 | OH | Sus | 0 | No | 2021 | JUL | Yes | Line to Ground | 1653625 | PW | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0118278&numberofmonths=24&showchangehistorylog=1 | 21-0118278 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1705 | 163351705 | RECLOSER | 65908 | 20210916 | 907 | 1473025 | 192 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 682 | 77303 | 37.9574 | -120.3132 | 1SPLDSIDEOF27300 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0118278 | OH | Sus | 31551906 | No | 2021 | SEP | Yes | Line to Line | 1666225 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0127479&numberofmonths=24&showchangehistorylog=1 | 21-0127479 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | SAN JOAQUIN #3 PH-1103 | 252531103 | RECLOSER | 11032 | 20211008 | 626 | 1489916 | 386 | Distribution Circuit | Equipment Failure/Involved | Overhead | 899 | 347014 | 37.2537 | -119.5192 | ELAMJON1916SW5443 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 21-0127479 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Ground | 1671833 | CSO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0143097&numberofmonths=24&showchangehistorylog=1 | 21-0143097 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | RECLOSER | 11800 | 20211107 | 513 | 1536661 | 521 | Distribution Circuit | Vegetation | Tree - fell into line | 684 | 143860 | 38.0243 | -120.2213 | TUCKMATT207422500 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 21-0143097 | OH | Sus | 35300216 | No | 2021 | NOV | Yes | Three Phase Fault | 1682363 | CAW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0158961&numberofmonths=24&showchangehistorylog=1 | 21-0158961 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | BEAR VALLEY-2101 | 252192101 | RECLOSER | 4160 | 20211216 | 1625 | 1575080 | 338 | Distribution Circuit | Equipment Failure/Involved | Overhead | 804 | 251497 | 37.4963 | -120.0432 | CGC321273835729 | Clear-32-90F | Connector or Splice (OH) | Broken, wire on ground | 21-0158961 | OH | Sus | 45094600 | No | 2021 | DEC | Yes | Multi-Fault | 1696005 | CSO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=21-0160296&numberofmonths=24&showchangehistorylog=1 | 21-0160296 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | SAN JOAQUIN #3 PH-1102 | 252531102 | RECLOSER | 11022 | 20211223 | 1257 | 1579997 | 398 | Distribution Circuit | Vegetation | Tree - fell into line | 262 | 99056 | 37.2537 | -119.5192 | 2SPANSWESTO2212 | Clear-32-90F | Crossarm, Wood | Broken, wire on object | 21-0160296 | OH | Sus | 31588336 | No | 2021 | DEC | Yes | Line to Line | 1697736 | CAW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0006649&numberofmonths=24&showchangehistorylog=1 | 22-0006649 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | RECLOSER | 10940 | 20220106 | 14 | 1596289 | 458 | Distribution Circuit | Vegetation | Tree - fell into line | 1155 | 57096 | 37.9883 | -120.2832 | 17180ALDERMAN | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0006649 | OH | Sus | 31588904 | No | 2022 | JAN | Yes | Line to Ground | 1701240 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0007617&numberofmonths=24&showchangehistorylog=1 | 22-0007617 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1705 | 163351705 | FUSE | 4911 | 20220108 | 958 | 1598155 | 620 | Distribution Circuit | 3rd Party | Vehicle | 129 | 39466 | 37.9802 | -120.248 | S2041 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 22-0007617 | OH | Sus | 0 | No | 2022 | JAN | Yes | Line to Ground | 1701612 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0012748&numberofmonths=24&showchangehistorylog=1 | 22-0012748 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | SAN JOAQUIN #3 PH-1103 | 252531103 | FUSE | 6094 | 20220121 | 1609 | 1607644 | 228 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 3420 | 37.2424 | -119.52 | CGC322866727162 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 22-0012748 | OH | Sus | 0 | No | 2022 | JAN | Yes | Line to Line | 1704073 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0012472&numberofmonths=24&showchangehistorylog=1 | 22-0012472 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SPRING GAP-1702 | 162831702 | FUSE | L1123 | 20220121 | 1125 | 1607291 | 518 | Distribution Circuit | Vegetation | Tree - fell into line | 154 | 62753 | 38.1975 | -120.0126 | 1SPANSOFMTR1004717959 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0012472 | OH | Sus | 0 | No | 2022 | JAN | Yes | Line to Line | 1703981 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0030934&numberofmonths=24&showchangehistorylog=1 | 22-0030934 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1703 | 163761703 | FUSE | 5957 | 20220307 | 1752 | 1644317 | 545 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 7630 | 38.0329 | -120.4002 | 2PSOF5957 | Strong Winds-Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0030934 | OH | Sus | 45200355 | No | 2022 | MAR | Yes | Line to Line | 1715324 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0059025&numberofmonths=24&showchangehistorylog=1 | 22-0059025 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | BEAR VALLEY-2105 | 252192105 | FUSE | 4629 | 20220506 | 1023 | 1690002 | 582 | Distribution Circuit | Vegetation | Tree - fell into line | 144 | 26179 | 37.7103 | -120.111 | CGC321179944405 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 22-0059025 | OH | Sus | 0 | No | 2022 | MAY | Yes | Line to Line | 1734238 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0075391&numberofmonths=24&showchangehistorylog=1 | 22-0075391 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2102 | 254452102 | OTHER | 37282 | 20220617 | 244 | 1733585 | 372 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2122 | 396343 | 37.462 | -119.9483 | LDSIDEOF8686 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0075391 | OH | Sus | 45345168 | No | 2022 | JUN | Yes | Open Circuit | 1745379 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0089059&numberofmonths=24&showchangehistorylog=1 | 22-0089059 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | STANISLAUS-1701 | 162821701 | OCB | 17012 | 20220723 | 2147 | 1764226 | 1005 | Distribution Circuit | 3rd Party | Vehicle | 2188 | 1548232 | 38.1401 | -120.3697 | 1PWOFAND1PSOFL431HWY4XPARROTSFERRY | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 22-0089059 | OH | Sus | 0 | No | 2022 | JUL | Yes | Line to Line | 1754608 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0128695&numberofmonths=24&showchangehistorylog=1 | 22-0128695 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SPRING GAP-1702 | 162831702 | RECLOSER | 9690 | 20221107 | 1610 | 1856353 | 469 | Distribution Circuit | Equipment Failure/Involved | Overhead | 689 | 323141 | 38.1888 | -120.0082 | 31SPANSSOF9690 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0128695 | OH | Sus | 45513981 | No | 2022 | NOV | Yes | Line to Ground | 1781971 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0128833&numberofmonths=24&showchangehistorylog=1 | 22-0128833 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SPRING GAP-1702 | 162831702 | RECLOSER | 9690 | 20221108 | 739 | 1856839 | 509 | Distribution Circuit | Vegetation | Tree - fell into line | 689 | 347794 | 38.1888 | -120.0082 | 1SPANLOADSIDEOF79597 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0128833 | OH | Sus | 0 | No | 2022 | NOV | Yes | Line to Ground | 1782075 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0136254&numberofmonths=24&showchangehistorylog=1 | 22-0136254 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | COARSEGOLD-2102 | 254432102 | FUSE | 10142 | 20221203 | 435 | 1874858 | 437 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 24909 | 37.2725 | -119.5761 | CGC322679928348 | Clear-32-90F | Crossarm, Wood | Broken, wire on ground | 22-0136254 | OH | Sus | 31629359 | No | 2022 | DEC | Yes | Line to Ground | 1787189 | CAW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=22-0139354&numberofmonths=24&showchangehistorylog=1 | 22-0139354 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SPRING GAP-1702 | 162831702 | RECLOSER | 9690 | 20221212 | 1748 | 1887518 | 482 | Distribution Circuit | Environmental/External | Ice or snow | 689 | 169154 | 38.1888 | -120.0082 | CGC321282360288 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0139354 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1790175 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0016857&numberofmonths=24&showchangehistorylog=1 | 23-0016857 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE | 10788 | 20230115 | 2306 | 1956437 | 851 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 65527 | 37.2869 | -119.6558 | CGC322477828555 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 23-0016857 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Line | 1805555 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0016545&numberofmonths=24&showchangehistorylog=1 | 23-0016545 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SPRING GAP-1702 | 162831702 | OTHER | 2PHWIREDOWN1SPANSS83402 | 20230115 | 533 | 1955556 | 502 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 15806 | 38.139 | -120.0621 | 1SPANSS83402 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0016545 | OH | Sus | 0 | No | 2023 | JAN | Yes | Open Circuit | 1805297 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0017791&numberofmonths=24&showchangehistorylog=1 | 23-0017791 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SPRING GAP-1702 | 162831702 | FUSE | L1707 | 20230117 | 851 | 1959847 | 798 | Distribution Circuit | Equipment Failure/Involved | Overhead | 28 | 22344 | 38.1872 | -120.0021 | CGC321431461423 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 23-0017791 | OH | Sus | 0 | No | 2023 | JAN | Yes | Three Phase Fault | 1806252 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0038481&numberofmonths=24&showchangehistorylog=1 | 23-0038481 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | FUSE | 23243 | 20230301 | 653 | 2017666 | 3667 | Distribution Circuit | Equipment Failure/Involved | Overhead | 128 | 140606 | 37.9853 | -120.282 | L895 | Partly Cloudy-Below 32 F | Pole-Wood | Broken, wire on ground | 23-0038481 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1820670 | PW | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0040181&numberofmonths=24&showchangehistorylog=1 | 23-0040181 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2101 | 254452101 | FUSE | 11906 | 20230305 | 106 | 2023087 | 676 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 4472 | 37.5114 | -119.9943 | WIREDOWNNOFCGC321464837090 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0040181 | OH | Sus | 0 | No | 2023 | MAR | Yes | Force Out | 1821929 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0043624&numberofmonths=24&showchangehistorylog=1 | 23-0043624 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | FUSE | 1949 | 20230311 | 1744 | 2032772 | 1470 | Distribution Circuit | Environmental/External | Lightning | 155 | 227746 | 37.8529 | -120.1659 | 3209458498063209455498393209480498143209515498393209495497473209475497811SRCSIDEOFCGC320957549606 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0043624 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1824164 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0043929&numberofmonths=24&showchangehistorylog=1 | 23-0043929 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | RECLOSER | 90320 | 20230313 | 308 | 2033882 | 673 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3074 | 237044 | 37.8473 | -120.2023 | 1SSOFCGC321045049147 | Overcast-Fog-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on object | 23-0043929 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1824443 | CAW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0037696&numberofmonths=24&showchangehistorylog=1 | 23-0037696 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2103 | 254432103 | FUSE | 5519 | 20230326 | 839 | 2067531 | 18 | Distribution Circuit | Company Initiated | Return Circuit Normal | 120 | 2160 | 37.1415 | -119.6791 | 31511RIDGEWOODWAYNORTHFORK | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0037696 | OH | Sus | 0 | No | 2023 | MAR | Yes | None | 1830580 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0053777&numberofmonths=24&showchangehistorylog=1 | 23-0053777 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | FUSE | 48691 | 20230328 | 1418 | 2070801 | 505 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 37370 | 37.991 | -120.2788 | 3SPLOADSIDE48691 | Overcast-Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 23-0053777 | OH | Sus | 0 | No | 2023 | MAR | Yes | Three Phase Fault | 1831298 | PW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0055219&numberofmonths=24&showchangehistorylog=1 | 23-0055219 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | BEAR VALLEY-2105 | 252192105 | JUMPER | WIREDOWN1SPANWOMTR1010269803 | 20230330 | 1601 | 2074649 | 209 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 418 | 37.7344 | -120.07 | 1SPANWOMTR1010269803 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0055219 | OH | Sus | 0 | No | 2023 | MAR | Yes | Open Circuit | 1832020 | CO | OH | No | Yes
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0054760&numberofmonths=24&showchangehistorylog=1 | 23-0054760 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2102 | 254452102 | RECLOSER | 9590 | 20230330 | 714 | 2073888 | 467 | Distribution Circuit | Environmental/External | Ice or snow | 522 | 77014 | 37.4593 | -119.8997 | FUCO35689ATTHETAPONMAINLINE | Partly Cloudy-Fog-32-90 F | Crossarm, Wood | Broken, wire on object | 23-0054760 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1831828 | CAW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0054912&numberofmonths=24&showchangehistorylog=1 | 23-0054912 | YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | RECLOSER | 953336 | 20230330 | 1029 | 2074257 | 517 | Distribution Circuit | Vegetation | Tree - fell into line | 922 | 190030 | 38.0678 | -120.1869 | 1SPANWOFCGC321007957419 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0054912 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1831930 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0057169&numberofmonths=24&showchangehistorylog=1 | 23-0057169 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2102 | 254452102 | FUSE | 4969 | 20230404 | 1342 | 2080039 | 268 | Distribution Circuit | Vegetation | Tree - bark fell into line | 62 | 16616 | 37.4335 | -119.8958 | SOFCGC321731033285 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0057169 | OH | Sus | 45715581 | No | 2023 | APR | Yes | Line to Ground | 1833279 | CO | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0059794&numberofmonths=24&showchangehistorylog=1 | 23-0059794 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE | 2075 | 20230411 | 1837 | 2085985 | 496 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 5456 | 37.2731 | -119.6892 | CGC322365728282 | Partly Cloudy-32-90 F | Crossarm, Wood | Broken, wire on object | 23-0059794 | OH | Sus | 31641978 | No | 2023 | APR | Yes | Force Out | 1834958 | CAW | OH | No | No
http://dodappwlsprd2.cloud.pge.com:8003/ilis_rpt/dailyeventlogdetail.jsp?odbeventlogid=23-0087698&numberofmonths=24&showchangehistorylog=1 | 23-0087698 | YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1705 | 163351705 | RECLOSER | 39256 | 20230630 | 1450 | 2150015 | 644 | Distribution Circuit | 3rd Party | Vehicle | 523 | 147974 | 37.9571 | -120.3087 | CGC320632653326 | Clear-Above 90 | Pole-Wood | Broken, wire on ground | 23-0087698 | OH | Sus | 31653955 | No | 2023 | JUN | Yes | Line to Ground | 1854412 | PW | OH | No | No

## Metric 3.02
Metric 3.02: Wires Down non-MEDs (Distribution)
Definition | (# Events/HFTD Circuit Miles (D))*1000
2022 HFTD Circuit Miles (D) | 25270.5
2023 HFTD Circuit Miles (D) | 25059.94
2023 Target | 41.36
Year | WD Events | WD Events/1,000 Miles
2013 | 651 | 25.7613
2014 | 869 | 34.3879
2015 | 794 | 31.42
2016 | 1211 | 47.9215
2017 | 1074 | 42.5001
2018 | 877 | 34.7045
2019 | 945 | 37.3954
2020 | 460 | 18.203
2021 | 475 | 18.7966
2022 | 509 | 20.1421
2023 (YTD - June) | 325 | 12.9689
|  | 10.2347 | STD
|  | 31.1232 | Average
|  | 41.3579 | 1 STD

## HFTD WD non-MED Summary
HFTD WIRE-DOWN OUTAGE DETAILS (2013 - Jun 2023)
DISTRIBUTION CIRCUIT & TRANSFORMER-ONLY OUTAGES
(Excluding 2.5b ME Days)
System | Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
SYSTEM | 2013 | 39 | 57 | 54 | 72 | 59 | 67 | 45 | 40 | 57 | 53 | 28 | 80 | 651
SYSTEM | 2014 | 28 | 120 | 93 | 58 | 57 | 47 | 56 | 43 | 45 | 76 | 52 | 194 | 869
SYSTEM | 2015 | 38 | 112 | 48 | 50 | 33 | 65 | 47 | 56 | 55 | 41 | 57 | 192 | 794
SYSTEM | 2016 | 204 | 56 | 242 | 87 | 60 | 61 | 65 | 41 | 54 | 140 | 83 | 118 | 1211
SYSTEM | 2017 | 141 | 184 | 133 | 95 | 76 | 67 | 68 | 71 | 61 | 57 | 82 | 39 | 1074
SYSTEM | 2018 | 82 | 44 | 169 | 65 | 55 | 56 | 95 | 47 | 30 | 58 | 67 | 109 | 877
SYSTEM | 2019 | 138 | 129 | 141 | 65 | 115 | 63 | 59 | 52 | 67 | 25 | 42 | 49 | 945
SYSTEM | 2020 | 44 | 40 | 39 | 52 | 58 | 42 | 21 | 41 | 29 | 22 | 36 | 36 | 460
SYSTEM | 2021 | 53 | 33 | 59 | 31 | 24 | 38 | 36 | 25 | 31 | 41 | 45 | 59 | 475
SYSTEM | 2022 | 62 | 27 | 34 | 59 | 38 | 42 | 32 | 25 | 27 | 24 | 45 | 94 | 509
SYSTEM | 2023 | 80 | 33 | 137 | 34 | 22 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 325
System | Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
10-Year Averages (2013-2022) | Count of Events | 82.9 | 80.2 | 101.2 | 63.4 | 57.5 | 54.8 | 52.4 | 44.1 | 45.6 | 53.7 | 53.7 | 97 | 786.5
| Monthly Percentage | 10.54% | 10.2% | 12.87% | 8.061% | 7.311% | 6.968% | 6.662% | 5.607% | 5.798% | 6.828% | 6.828% | 12.33% | 100%
System | Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Targets | 2023 | 4.3595 | 4.2175 | 5.3218 | 3.334 | 3.0238 | 2.8818 | 2.7556 | 2.3191 | 2.398 | 2.8239 | 2.8239 | 5.101 | 41.36
System | Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Events | 2023 | 80 | 33 | 137 | 34 | 22 | 19 | [6 empty] | 325
Monthly Metric | 2023 | 3.1923 | 1.3168 | 5.4669 | 1.3567 | 0.8779 | 0.75818 | 0 | 0 | 0 | 0 | 0 | 0 | 12.9689
YTD Metric | 2023 | 3.1923 | 4.5092 | 9.9761 | 11.3328 | 12.2107 | 12.9689 | 12.9689 | 12.9689 | 12.9689 | 12.9689 | 12.9689 | 12.9689

## OH Dlines in HFTD
Source: Extracted from EDGIS as of 1/1/2023.
CIRCUITNAME | CIRCUITID | TOTALMILES | T3MILES | T2MILES | Z1MILES | T1MILES
2101 | 259932101 | 12.23 |  | 3.79 | 0.49 | 7.95
18TH STREET 0401 | 22390401 | 1.27 |  |  |  | 1.27
18TH STREET 0402 | 22390402 | 1.82 |  |  |  | 1.82
21ST AVENUE 0401 | 22550401 | 1.89 |  |  |  | 1.89
21ST AVENUE 0402 | 22550402 | 3.27 |  |  |  | 3.27
21ST AVENUE 0403 | 22550403 | 1.84 |  |  |  | 1.84
6TH AVENUE 0401 | 22530401 | 1.27 |  |  |  | 1.27
6TH AVENUE 0402 | 22530402 | 1.22 |  |  |  | 1.22
6TH AVENUE 0403 | 22530403 | 1.78 |  |  |  | 1.78
7TH STANDARD 2101 | 254582101 | 2.56 |  |  |  | 2.56
7TH STANDARD 2102 | 254582102 | 13.3 |  |  |  | 13.3
7TH STANDARD 2103 | 254582103 | 22.46 |  |  |  | 22.46
7TH STANDARD 2104 | 254582104 | 0.04 |  |  |  | 0.04
8TH AVENUE 0401 | 12670401 | 4.89 |  |  |  | 4.89
ACTON 0401 | 22470401 | 3.87 |  |  |  | 3.87
ACTON 0402 | 22470402 | 4.44 |  |  |  | 4.44
AIRWAYS 1101 | 252041101 | 1.48 |  |  |  | 1.48
AIRWAYS 1102 | 252041102 | 7.65 |  |  |  | 7.65
AIRWAYS 1103 | 252041103 | 7.65 |  |  |  | 7.65
AIRWAYS 1104 | 252041104 | 2 |  |  |  | 2
AIRWAYS 1105 | 252041105 | 1.35 |  |  |  | 1.35
AIRWAYS 1106 | 252041106 | 8.18 |  |  |  | 8.18
AIRWAYS 1107 | 252041107 | 43.6 |  |  |  | 43.6
AIRWAYS 1108 | 252041108 | 11.64 |  |  |  | 11.64
ALHAMBRA 1101 | 14101101 | 8.4 |  |  |  | 8.4
ALHAMBRA 1102 | 14101102 | 14.11 |  | 0.13 |  | 13.98
ALHAMBRA 1105 | 14101105 | 45.1 | 0.85 | 36.9 |  | 7.35
ALLEGHANY 1101 | 152101101 | 77.01 | 32.35 | 27.11 | 7.07 | 10.48
ALLEGHANY 1102 | 152101102 | 17.69 | 17.69 |  |  | 0
ALMADEN 1101 | 82311101 | 18.33 |  |  |  | 18.33
ALMADEN 1102 | 82311102 | 21.83 |  |  |  | 21.83
ALMADEN 1110 | 82311110 | 8.45 |  |  |  | 8.45
ALMADEN 1111 | 82311111 | 9.78 |  |  |  | 9.78
ALPAUGH 1103 | 254001103 | 26.94 |  |  |  | 26.94
ALPAUGH 1104 | 254001104 | 55.72 |  |  |  | 55.72
ALPAUGH 1106 | 254001106 | 52.45 |  |  |  | 52.45
ALPINE 1101 | 163561101 | 0.87 |  |  |  | 0.87
ALTO 1120 | 42031120 | 20.38 |  | 3.9 |  | 16.48
ALTO 1121 | 42031121 | 16.46 |  |  | 0.34 | 16.12
ALTO 1122 | 42031122 | 22.26 | 9.14 | 3.65 | 0.18 | 9.29
ALTO 1123 | 42031123 | 10.32 |  | 0.47 |  | 9.85
ALTO 1124 | 42031124 | 35 | 27.96 |  |  | 7.04
ALTO 1125 | 42031125 | 44.79 | 26.36 | 10.96 |  | 7.47
AMES 1101 | 83901101 | 0.12 |  |  |  | 0.12
AMES 1102 | 83901102 | 3.29 |  |  |  | 3.29
ANDERSON 1101 | 103261101 | 19.91 |  | 11.03 |  | 8.88
ANDERSON 1102 | 103261102 | 3.75 |  |  |  | 3.75
ANDERSON 1103 | 103261103 | 31.66 |  | 7.13 |  | 24.53
ANGIOLA 1102 | 252151102 | 35.82 |  |  |  | 35.82
ANGIOLA 1103 | 252151103 | 46.05 |  |  |  | 46.05
ANGIOLA 1104 | 252151104 | 19.61 |  |  |  | 19.61
ANITA 1101 | 102841101 | 34.47 |  |  |  | 34.47
ANITA 1102 | 102841102 | 34.8 |  |  |  | 34.8
ANITA 1105 | 102841105 | 16.84 |  |  |  | 16.84
ANITA 1106 | 102841106 | 90.29 |  | 0.48 |  | 89.81
ANNAPOLIS 1101 | 42861101 | 51 |  | 51 |  | 0
ANTELOPE 1101 | 252021101 | 39.88 |  | 0.92 |  | 38.96
ANTELOPE 1102 | 252021102 | 25.34 |  |  |  | 25.34
ANTLER 1101 | 103271101 | 61.21 | 8.17 | 51.94 |  | 1.1
APPLE HILL 1103 | 153661103 | 59.82 | 14.77 | 35.12 |  | 9.93
APPLE HILL 1104 | 153661104 | 95.48 | 55.35 | 35.42 |  | 4.71
APPLE HILL 2102 | 153662102 | 364.72 | 123.52 | 228.47 |  | 12.73
ARANA 0401 | 83010401 | 3.49 |  |  |  | 3.49
ARANA 0402 | 83010402 | 2.98 |  |  |  | 2.98
ARBUCKLE 1101 | 62081101 | 42.78 |  |  |  | 42.78
ARBUCKLE 1102 | 62081102 | 62.84 |  |  |  | 62.84
ARBUCKLE 1103 | 62081103 | 0.04 |  |  |  | 0.04
ARBUCKLE 1104 | 62081104 | 94.76 |  | 1.92 |  | 92.84
ARCATA 1105 | 192021105 | 43.95 |  |  |  | 43.95
ARCATA 1106 | 192021106 | 10.16 |  |  |  | 10.16
ARCATA 1121 | 192021121 | 28.95 |  | 6.84 |  | 22.11
ARCATA 1122 | 192021122 | 68.05 |  | 20.44 |  | 47.61
ARCATA 1123 | 192021123 | 5.97 |  |  |  | 5.97
ARCATA 1124 | 192021124 | 0 |  |  |  | 0
ARLINGTON 0401 | 13700401 | 4.17 |  | 0.94 |  | 3.23
ARVIN 1101 | 253801101 | 30.09 |  | 0.1 |  | 29.99
ARVIN 1102 | 253801102 | 17.87 |  |  |  | 17.87
ARVIN 1103 | 253801103 | 20.6 |  |  |  | 20.6
ASHLAN AVE 1102 | 252051102 | 13.21 |  |  |  | 13.21
ASHLAN AVE 1103 | 252051103 | 9.29 |  |  |  | 9.29
ASHLAN AVE 1104 | 252051104 | 14.01 |  |  |  | 14.01
ASHLAN AVE 1106 | 252051106 | 16.98 |  |  |  | 16.98
ASHLAN AVE 1107 | 252051107 | 8.32 |  |  |  | 8.32
ASHLAN AVE 1108 | 252051108 | 11.18 |  |  |  | 11.18
ASHLAN AVE 1109 | 252051109 | 15.66 |  |  |  | 15.66
ASHLAN AVE 1111 | 252051111 | 6.76 |  |  |  | 6.76
ASHLAN AVE 1112 | 252051112 | 9.52 |  |  |  | 9.52
ASHLAN AVE 1113 | 252051113 | 9.82 |  |  |  | 9.82
ASHLAN AVE 1114 | 252051114 | 8.36 |  |  |  | 8.36
ASHLAN AVE 1116 | 252051116 | 19.06 |  |  |  | 19.06
ASHLAN AVE 2101 | 252052101 | 2.23 |  |  |  | 2.23
ASHLAN AVE 2105 | 252052105 | 16.39 |  |  |  | 16.39
ASHLAN AVE 2110 | 252052110 | 6.72 |  |  |  | 6.72
ASHLAN AVE 2115 | 252052115 | 5.51 |  |  |  | 5.51
ASHLAN AVE 2117 | 252052117 | 1.88 |  |  |  | 1.88
ASHLAN AVE 2118 | 252052118 | 9.56 |  |  |  | 9.56
ASHLAN AVE 2119 | 252052119 | 14.08 |  |  |  | 14.08
ATASCADERO 1101 | 182541101 | 62.26 | 13.74 | 32.02 |  | 16.5
ATASCADERO 1102 | 182541102 | 17.38 |  | 3.4 |  | 13.98
ATASCADERO 1103 | 182541103 | 127.77 | 37.11 | 55.99 |  | 34.67
ATWATER 1102 | 253611102 | 84.23 |  |  |  | 84.23
ATWATER 1103 | 253611103 | 23.19 |  |  |  | 23.19
ATWATER 1104 | 253611104 | 12.89 |  |  |  | 12.89
ATWATER 1105 | 253611105 | 6.8 |  |  |  | 6.8
ATWATER 1106 | 253611106 | 36.74 |  |  |  | 36.74
ATWATER 1107 | 253611107 | 30.58 |  |  |  | 30.58
ATWATER 1108 | 253611108 | 61.07 |  |  |  | 61.07
AUBERRY 1101 | 254151101 | 241.34 | 32.07 | 206.96 |  | 2.31
AUBERRY 1102 | 254151102 | 129.03 |  | 129.03 |  | 0
AUBURN 1101 | 152161101 | 4.92 |  | 3.14 |  | 1.78
AUBURN 1102 | 152161102 | 8.96 |  | 2.98 |  | 5.98
AVENA 1701 | 163571701 | 90.74 |  |  |  | 90.74
AVENA 1702 | 163571702 | 80.23 |  |  |  | 80.23
AVENAL 2101 | 255002101 | 63.31 |  |  |  | 63.31
AVENAL 2102 | 255002102 | 2.46 |  |  |  | 2.46
AVENAL 2103 | 255002103 | 2.45 |  |  |  | 2.45
BABEL 0401 | 13850401 | 3.08 |  |  |  | 3.08
BAHIA 1101 | 43251101 | 3.06 |  |  |  | 3.06
BAHIA 1102 | 43251102 | 14.2 |  |  |  | 14.2
BAHIA 1103 | 43251103 | 11.04 |  |  |  | 11.04
BAHIA 1104 | 43251104 | 18.33 |  |  |  | 18.33
BAHIA 1105 | 43251105 | 13.99 |  |  |  | 13.99
BAIR 1103 | 24261103 | 0.53 |  |  |  | 0.53
BAIR 1105 | 24261105 | 2.15 |  |  |  | 2.15
BAKERSFIELD 1101 | 253371101 | 7.45 |  |  |  | 7.45
BAKERSFIELD 1102 | 253371102 | 17.62 |  |  |  | 17.62
BAKERSFIELD 1105 | 253371105 | 6.46 |  |  |  | 6.46
BAKERSFIELD 1106 | 253371106 | 11.77 |  |  |  | 11.77
BAKERSFIELD 1107 | 253371107 | 3.68 |  |  |  | 3.68
BAKERSFIELD 1110 | 253371110 | 5.95 |  |  |  | 5.95
BAKERSFIELD 1114 | 253371114 | 15.73 |  |  |  | 15.73
BAKERSFIELD 1115 | 253371115 | 5.68 |  |  |  | 5.68
BAKERSFIELD 1116 | 253371116 | 16.76 |  |  |  | 16.76
BAKERSFIELD 1118 | 253371118 | 11.39 |  |  |  | 11.39
BAKERSFIELD 2104 | 253372104 | 34.92 |  |  |  | 34.92
BAKERSFIELD 2106 | 253372106 | 31.5 |  |  |  | 31.5
BAKERSFIELD 2107 | 253372107 | 0.01 |  |  |  | 0.01
BAKERSFIELD 2109 | 253372109 | 32.08 |  |  |  | 32.08
BALCH NO 1 1101 | 252501101 | 14.65 |  | 14.65 |  | 0
BALFOUR 1101 | 14321101 | 49.93 |  |  |  | 49.93
BANCROFT 0401 | 13030401 | 8.41 |  | 0 |  | 8.41
BANCROFT 0402 | 13030402 | 4.59 |  | 0.12 |  | 4.47
BANGOR 1101 | 103191101 | 198 | 1.73 | 188.06 |  | 8.21
BANTA 1101 | 162471101 | 32.94 |  |  |  | 32.94
BANTA 1102 | 162471102 | 15.2 |  |  |  | 15.2
BANTA 1103 | 162471103 | 60.59 |  |  |  | 60.59
BARRETT 0401 | 13020401 | 6.59 |  |  |  | 6.59
BARRETT 0402 | 13020402 | 5.89 |  |  |  | 5.89
BARRY 1101 | 152111101 | 32.02 |  |  |  | 32.02
BARRY 1102 | 152111102 | 17.71 |  |  |  | 17.71
BARRY 1103 | 152111103 | 33.06 |  |  |  | 33.06
BARTON 1101 | 253571101 | 5.98 |  |  |  | 5.98
BARTON 1102 | 253571102 | 4.5 |  |  |  | 4.5
BARTON 1104 | 253571104 | 11.68 |  |  |  | 11.68
BARTON 1105 | 253571105 | 4.79 |  |  |  | 4.79
BARTON 1106 | 253571106 | 5.96 |  |  |  | 5.96
BARTON 1108 | 253571108 | 18.95 |  |  |  | 18.95
BARTON 1109 | 253571109 | 7.17 |  |  |  | 7.17
BARTON 1110 | 253571110 | 16.36 |  |  |  | 16.36
BARTON 1111 | 253571111 | 15.57 |  |  |  | 15.57
BARTON 1112 | 253571112 | 3.34 |  |  |  | 3.34
BARTON 1114 | 253571114 | 12.8 |  |  |  | 12.8
BARTON 1115 | 253571115 | 15.3 |  |  |  | 15.3
BARTON 1116 | 253571116 | 9.32 |  |  |  | 9.32
BASALT 1101 | 42461101 | 10.84 |  |  |  | 10.84
BASALT 1104 | 42461104 | 0.67 |  |  |  | 0.67
BASALT 1105 | 42461105 | 1.65 |  |  |  | 1.65
BASALT 1106 | 42461106 | 68.66 |  | 1.67 |  | 66.99
BAY MEADOWS 1102 | 24011102 | 4.99 |  |  |  | 4.99
BAY MEADOWS 1103 | 24011103 | 6.84 |  |  |  | 6.84
BAY MEADOWS 1104 | 24011104 | 16.71 |  |  |  | 16.71
BAY MEADOWS 1105 | 24011105 | 6.64 |  |  |  | 6.64
BAY MEADOWS 1106 | 24011106 | 0.86 |  |  |  | 0.86
BAY MEADOWS 1107 | 24011107 | 3.17 |  |  |  | 3.17
BAY MEADOWS 1108 | 24011108 | 1.05 |  |  |  | 1.05
BAY MEADOWS 2101 | 24012101 | 17.87 |  |  |  | 17.87
BAY MEADOWS 2102 | 24012102 | 14.26 |  | 3.98 |  | 10.28
BAY MEADOWS 2103 | 24012103 | 0 |  |  |  | 0
BAYWOOD 1101 | 182801101 | 29.06 |  | 3.37 |  | 25.69
BEACH (Q) 0402 | 22340402 | 2.01 |  |  |  | 2.01
BEAR VALLEY 2101 | 252192101 | 166.69 |  | 100.85 |  | 65.84
BEAR VALLEY 2105 | 252192105 | 157.18 | 7.5 | 149.68 |  | 0
BECK STREET 0401 | 12640401 | 1.58 |  |  |  | 1.58
BELL 1107 | 152701107 | 50.39 |  | 42.56 |  | 7.83
BELL 1108 | 152701108 | 66.64 |  | 54.7 |  | 11.94
BELL 1109 | 152701109 | 18.2 |  | 14.03 |  | 4.17
BELL 1110 | 152701110 | 11.18 |  | 0.16 |  | 11.02
BELLE HAVEN 0401 | 24020401 | 9.43 |  |  |  | 9.43
BELLE HAVEN 0402 | 24020402 | 4.67 |  |  |  | 4.67
BELLE HAVEN 0403 | 24020403 | 5.51 |  |  |  | 5.51
BELLE HAVEN 0404 | 24020404 | 8.64 |  |  |  | 8.64
BELLE HAVEN 0405 | 24020405 | 7.39 |  |  |  | 7.39
BELLE HAVEN 0406 | 24020406 | 9.28 |  |  |  | 9.28
BELLE HAVEN 0407 | 24020407 | 6.35 |  |  |  | 6.35
BELLE HAVEN 0408 | 24020408 | 5.2 |  |  |  | 5.2
BELLE HAVEN 0409 | 24020409 | 3.86 |  |  |  | 3.86
BELLE HAVEN 1101 | 24021101 | 1.59 |  |  |  | 1.59
BELLE HAVEN 1102 | 24021102 | 1.68 |  |  |  | 1.68
BELLE HAVEN 1103 | 24021103 | 1.89 |  |  |  | 1.89
BELLE HAVEN 1104 | 24021104 | 5.68 |  |  |  | 5.68
BELLE HAVEN 1105 | 24021105 | 10.56 |  |  |  | 10.56
BELLE HAVEN 1106 | 24021106 | 15.57 |  |  |  | 15.57
BELLE HAVEN 1107 | 24021107 | 1.27 |  |  |  | 1.27
BELLEVUE 1102 | 43181102 | 43.24 |  | 0.16 |  | 43.08
BELLEVUE 1104 | 43181104 | 12.56 |  |  |  | 12.56
BELLEVUE 2101 | 43182101 | 66.04 | 7.02 | 19 |  | 40.02
BELLEVUE 2103 | 43182103 | 5.72 |  |  |  | 5.72
BELLEVUE 2105 | 43182105 | 4.02 |  |  |  | 4.02
BELLEVUE 2107 | 43182107 | 11.32 |  |  |  | 11.32
BELMONT 0401 | 24030401 | 5.89 |  |  |  | 5.89
BELMONT 0402 | 24030402 | 6.99 |  |  |  | 6.99
BELMONT 0403 | 24030403 | 4.65 |  |  |  | 4.65
BELMONT 0406 | 24030406 | 5.02 |  |  |  | 5.02
BELMONT 1102 | 24031102 | 15.15 |  |  |  | 15.15
BELMONT 1103 | 24031103 | 18.58 |  | 3.37 |  | 15.21
BELMONT 1104 | 24031104 | 7.05 |  |  |  | 7.05
BELMONT 1105 | 24031105 | 0.64 |  |  |  | 0.64
BELMONT 1106 | 24031106 | 1.65 |  |  |  | 1.65
BELMONT 1107 | 24031107 | 0.97 |  |  |  | 0.97
BELMONT 1109 | 24031109 | 0 |  |  |  | 0
BELMONT 1110 | 24031110 | 24.15 |  | 0.11 |  | 24.04
BELRIDGE 1A 1101 | 254371101 | 0.09 |  |  |  | 0.09
BELRIDGE 1B 1101 | 254381101 | 0.01 |  |  |  | 0.01
BEN LOMOND 0401 | 83040401 | 23.05 | 23.05 |  |  | 0
BEN LOMOND 1101 | 83041101 | 15.12 | 15.12 |  |  | 0
BERESFORD 0401 | 24040401 | 1.08 |  |  |  | 1.08
BERESFORD 0402 | 24040402 | 2.38 |  |  |  | 2.38
BERESFORD 0403 | 24040403 | 12.19 |  | 5.39 |  | 6.8
BERESFORD 0404 | 24040404 | 5.74 |  |  |  | 5.74
BERKELEY F 0401 | 12060401 | 0 |  |  |  | 0
BERKELEY F 0402 | 12060402 | 2.13 |  | 0.14 |  | 1.99
BERKELEY F 0403 | 12060403 | 2.19 |  |  |  | 2.19
BERKELEY F 0404 | 12060404 | 3.68 |  |  |  | 3.68
BERKELEY F 0405 | 12060405 | 0.97 |  |  |  | 0.97
BERKELEY F 0406 | 12060406 | 3.79 |  |  |  | 3.79
BERKELEY F 0407 | 12060407 | 0.01 |  |  |  | 0.01
BERKELEY F 0408 | 12060408 | 0.79 |  |  |  | 0.79
BERKELEY F 0409 | 12060409 | 3.58 |  |  |  | 3.58
BERKELEY F 0410 | 12060410 | 2.86 |  |  |  | 2.86
BERKELEY F 0411 | 12060411 | 4.42 |  |  |  | 4.42
BERKELEY F 1102 | 12061102 | 0.27 |  |  |  | 0.27
BERKELEY F 1103 | 12061103 | 6.52 | 1.96 |  |  | 4.56
BERKELEY F 1104 | 12061104 | 3.25 |  |  |  | 3.25
BERKELEY F 1105 | 12061105 | 11.37 |  | 1.78 |  | 9.59
BERKELEY T 0401 | 12660401 | 2.5 |  |  |  | 2.5
BERKELEY T 0402 | 12660402 | 1.35 |  |  |  | 1.35
BERKELEY T 0403 | 12660403 | 0.86 |  |  |  | 0.86
BERKELEY T 0404 | 12660404 | 1.08 |  |  |  | 1.08
BERRENDA A 1101 | 254261101 | 0.02 |  |  |  | 0.02
BERRENDA C 0401 | 254480401 | 0.02 |  |  |  | 0.02
BETHEL BANK 0401 | 18150401 | 0.78 |  |  |  | 0.78
BIG BASIN 1101 | 82841101 | 54.98 | 54.98 |  |  | 0
BIG BASIN 1102 | 82841102 | 66.99 | 63.85 | 3.14 |  | 0
BIG BEND 1101 | 103751101 | 56.91 | 42.41 | 14.49 |  | 0.01
BIG BEND 1102 | 103751102 | 18.14 | 18.04 |  |  | 0.1
BIG MEADOWS 2101 | 102812101 | 70.18 |  | 53.01 |  | 17.17
BIG RIVER 1101 | 43081101 | 86.02 |  | 69.95 |  | 16.07
BIOLA 1101 | 252211101 | 90.07 |  |  |  | 90.07
BIOLA 1102 | 252211102 | 32.39 |  |  |  | 32.39
BIOLA 1103 | 252211103 | 80.25 |  |  |  | 80.25
BIOLA 1104 | 252211104 | 50.08 |  |  |  | 50.08
BLACKWELL 1102 | 254681102 | 30.4 |  |  |  | 30.4
BLACKWELL 2101 | 254682101 | 22.89 |  |  |  | 22.89
BLUE LAKE 1101 | 192181101 | 7.32 |  |  | 0.31 | 7.01
BLUE LAKE 1102 | 192181102 | 68.77 |  |  | 0.02 | 68.75
BOGARD 1101 | 103301101 | 0.51 |  | 0.51 |  | 0
BOGUE 1102 | 153781102 | 17.69 |  |  |  | 17.69
BOGUE 1103 | 153781103 | 16.17 |  |  |  | 16.17
BOGUE 1104 | 153781104 | 9.44 |  |  |  | 9.44
BOGUE 1105 | 153781105 | 10.46 |  |  |  | 10.46
BOGUE 1106 | 153781106 | 59.4 |  |  |  | 59.4
BOGUE 1107 | 153781107 | 15.81 |  |  |  | 15.81
BOGUE 1108 | 63781108 | 0.54 |  |  |  | 0.54
BOLINAS 1101 | 42261101 | 51.63 | 27.17 | 7.48 |  | 16.98
BOLTHOUSE FARMS 1101 | 258181101 | 0.02 |  |  |  | 0.02
BONITA 1101 | 255391101 | 53.96 |  |  |  | 53.96
BONITA 1102 | 255391102 | 30.43 |  |  |  | 30.43
BONITA 1103 | 255391103 | 44.61 |  |  |  | 44.61
BONNIE NOOK 1101 | 152301101 | 14.44 | 14.44 |  |  | 0
BONNIE NOOK 1102 | 152301102 | 33.99 | 33.99 |  |  | 0
BONNIE NOOK 1103 | 152301103 | 0.33 | 0.33 |  |  | 0
BORDEN 1101 | 255121101 | 68.11 |  |  |  | 68.11
BORDEN 1102 | 255121102 | 25.89 |  |  |  | 25.89
BORDEN 1103 | 255121103 | 86.39 |  |  |  | 86.39
BORONDA 1101 | 182461101 | 7.92 |  |  |  | 7.92
BORONDA 1102 | 182461102 | 4.35 |  |  |  | 4.35
BOSWELL 1101 | 254941101 | 0.02 |  |  |  | 0.02
BOWLES 1101 | 253531101 | 69.15 |  |  |  | 69.15
BOWLES 1102 | 253531102 | 33.46 |  |  |  | 33.46
BOWLES 1103 | 253531103 | 26.61 |  |  |  | 26.61
BOWLES 1104 | 253531104 | 41.49 |  |  |  | 41.49
BRENTWOOD 2104 | 14592104 | 2.34 |  |  |  | 2.34
BRENTWOOD 2105 | 14592105 | 78.65 |  | 10.38 |  | 68.27
BRENTWOOD 2106 | 14592106 | 5.97 |  |  |  | 5.97
BRENTWOOD 2108 | 14592108 | 6.13 |  |  |  | 6.13
BRENTWOOD 2109 | 14592109 | 1.28 |  |  |  | 1.28
BRENTWOOD 2110 | 14592110 | 3.44 |  |  |  | 3.44
BRENTWOOD 2111 | 14592111 | 7.29 |  |  |  | 7.29
BRENTWOOD 2112 | 14592112 | 94.53 |  |  |  | 94.53
BRENTWOOD 2113 | 14592113 | 8.18 |  |  |  | 8.18
BRIDGEVILLE 1101 | 192461101 | 24.84 | 4.67 | 17.93 |  | 2.24
BRIDGEVILLE 1102 | 192461102 | 43.26 | 20.63 | 10.32 |  | 12.31
BRITTON 1104 | 83611104 | 1.18 |  |  |  | 1.18
BRITTON 1105 | 83611105 | 5.11 |  |  |  | 5.11
BRITTON 1106 | 83611106 | 3.72 |  |  |  | 3.72
BRITTON 1107 | 83611107 | 5.45 |  |  |  | 5.45
BRITTON 1108 | 83611108 | 1.73 |  |  |  | 1.73
BRITTON 1109 | 83611109 | 2.44 |  |  |  | 2.44
BRITTON 1110 | 83611110 | 11.66 |  |  |  | 11.66
BRITTON 1111 | 83611111 | 1.27 |  |  |  | 1.27
BRITTON 1112 | 83611112 | 1.84 |  |  |  | 1.84
BRITTON 1113 | 83611113 | 1.35 |  |  |  | 1.35
BRITTON 1114 | 83611114 | 4.99 |  |  |  | 4.99
BRITTON 1115 | 83611115 | 1.12 |  |  |  | 1.12
BROOKSIDE 0401 | 13210401 | 3.69 |  |  |  | 3.69
BROWNS VALLEY 1101 | 152921101 | 66.44 |  | 44.15 |  | 22.29
BRUNSWICK 1102 | 152481102 | 54.25 | 46.98 | 4.7 |  | 2.57
BRUNSWICK 1103 | 152481103 | 66.02 | 40.51 | 17.91 |  | 7.6
BRUNSWICK 1104 | 152481104 | 57.96 | 26.28 | 29.68 |  | 2
BRUNSWICK 1105 | 152481105 | 118.4 | 113.95 | 4.2 |  | 0.25
BRUNSWICK 1106 | 152481106 | 178.45 | 119.58 | 49.39 |  | 9.48
BRUNSWICK 1107 | 152481107 | 19.52 | 3.13 | 5.71 |  | 10.68
BRUNSWICK 1110 | 152481110 | 32.9 |  | 22.79 |  | 10.11
BUCKS CREEK 1102 | 102211102 | 0.03 | 0.03 |  |  | 0
BUCKS CREEK 1103 | 102211103 | 12.87 | 9.91 | 2.66 |  | 0.3
BUELLTON 1101 | 183041101 | 104.22 | 4.83 | 72.61 |  | 26.78
BUELLTON 1102 | 183041102 | 28.19 |  | 16.03 |  | 12.16
BUENA VISTA 1101 | 182261101 | 0.71 |  |  |  | 0.71
BUENA VISTA 1102 | 182261102 | 11.11 |  |  |  | 11.11
BUENA VISTA 1103 | 182261103 | 7.59 |  |  |  | 7.59
BUENA VISTA 1104 | 182261104 | 3.97 |  |  |  | 3.97
BUENA VISTA 1106 | 182261106 | 12.92 |  |  |  | 12.92
BULLARD 1101 | 253961101 | 14.34 |  |  |  | 14.34
BULLARD 1102 | 253961102 | 2.78 |  |  |  | 2.78
BULLARD 1103 | 253961103 | 8.11 |  |  |  | 8.11
BULLARD 1104 | 253961104 | 8.04 |  |  |  | 8.04
BULLARD 1105 | 253961105 | 3.46 |  |  |  | 3.46
BULLARD 1106 | 253961106 | 3.69 |  |  |  | 3.69
BULLARD 1107 | 253961107 | 2.4 |  |  |  | 2.4
BULLARD 1108 | 253961108 | 1.62 |  |  |  | 1.62
BULLARD 1109 | 253961109 | 5.4 |  |  |  | 5.4
BULLARD 1110 | 253961110 | 4.21 |  |  |  | 4.21
BULLARD 1113 | 253961113 | 5.22 |  |  |  | 5.22
BULLARD 2111 | 253962111 | 4.45 |  |  |  | 4.45
BULLARD 2112 | 253962112 | 11.11 |  |  |  | 11.11
BULLARD 2114 | 253962114 | 5.36 |  |  |  | 5.36
BURLINGAME 0401 | 24050401 | 3.14 |  |  |  | 3.14
BURLINGAME 0402 | 24050402 | 5.89 |  |  |  | 5.89
BURLINGAME 0403 | 24050403 | 3.86 |  |  |  | 3.86
BURLINGAME 0404 | 24050404 | 3.98 |  |  |  | 3.98
BURLINGAME 0405 | 24050405 | 3.25 |  |  |  | 3.25
BURLINGAME 2101 | 24052101 | 6.82 |  |  |  | 6.82
BURNEY 1101 | 103311101 | 59.78 |  | 50.93 |  | 8.85
BURNEY 1102 | 103311102 | 4.06 |  | 0.64 |  | 3.42
BURNS 2101 | 183582101 | 29.14 | 29.14 |  |  | 0
BUTTE 1103 | 103081103 | 60.18 |  |  |  | 60.18
BUTTE 1104 | 103081104 | 52.15 |  |  |  | 52.15
BUTTE 1105 | 103081105 | 37.8 | 26.62 | 3.43 |  | 7.75
BUTTE 1106 | 103081106 | 11.84 |  |  |  | 11.84
BUTTE 1107 | 103081107 | 109.39 |  |  |  | 109.39
CABRILLO 1103 | 183101103 | 102.06 |  | 57.4 |  | 44.66
CABRILLO 1104 | 183101104 | 76.03 |  | 30.33 |  | 45.7
CADET 1101 | 254821101 | 0.03 |  |  |  | 0.03
CAL WATER 1102 | 255451102 | 26.43 |  | 3.72 |  | 22.71
CAL WATER 1103 | 255451103 | 8.81 |  |  |  | 8.81
CALAVERAS CEMENT 1101 | 162211101 | 242.75 | 7.77 | 218.19 |  | 16.79
CALFLAX 1101 | 253441101 | 27.49 |  |  |  | 27.49
CALFLAX 1102 | 253441102 | 20.43 |  |  |  | 20.43
CALFLAX 1103 | 253441103 | 29.03 |  |  |  | 29.03
CALFLAX 1104 | 253441104 | 18.61 |  |  |  | 18.61
CALIFORNIA AVE 1102 | 252281102 | 11.42 |  |  |  | 11.42
CALIFORNIA AVE 1103 | 252281103 | 7.76 |  |  |  | 7.76
CALIFORNIA AVE 1104 | 252281104 | 3.58 |  |  |  | 3.58
CALIFORNIA AVE 1106 | 252281106 | 9.78 |  |  |  | 9.78
CALIFORNIA AVE 1108 | 252281108 | 9.61 |  |  |  | 9.61
CALIFORNIA AVE 1110 | 252281110 | 11.08 |  |  |  | 11.08
CALIFORNIA AVE 1111 | 252281111 | 6.73 |  |  |  | 6.73
CALIFORNIA AVE 1112 | 252281112 | 4.93 |  |  |  | 4.93
CALIFORNIA AVE 1113 | 252281113 | 6.5 |  |  |  | 6.5
CALIFORNIA AVE 1114 | 252281114 | 19.38 |  |  |  | 19.38
CALIFORNIA AVE 1116 | 252281116 | 9.35 |  |  |  | 9.35
CALIFORNIA AVE 1117 | 252281117 | 1.27 |  |  |  | 1.27
CALISTOGA 1101 | 42711101 | 115.63 | 83.32 | 15.49 |  | 16.82
CALISTOGA 1102 | 42711102 | 45.68 | 22.32 | 1.53 |  | 21.83
CALPELLA 1101 | 43411101 | 101.17 | 4.03 | 77.84 |  | 19.3
CALPELLA 1102 | 43411102 | 7.52 |  | 1.79 |  | 5.73
CALPINE 1144 | 48011144 | 30.59 | 28.37 | 2.22 |  | 0
CALPINE 1146 | 48011146 | 5.61 | 5.61 |  |  | 0
CAMBRIA 1101 | 182771101 | 31.04 |  | 24.35 |  | 6.69
CAMBRIA 1102 | 182771102 | 27.24 |  | 15.77 |  | 11.47
CAMDEN 1102 | 252301102 | 40.15 |  |  |  | 40.15
CAMDEN 1103 | 252301103 | 127.81 |  |  |  | 127.81
CAMDEN 1104 | 252301104 | 77.5 |  |  |  | 77.5
CAMDEN 1105 | 252301105 | 58.83 |  |  |  | 58.83
CAMP EVERS 2103 | 83622103 | 61.29 | 44.84 | 0.83 |  | 15.62
CAMP EVERS 2104 | 83622104 | 36.49 | 26.64 | 0.58 |  | 9.27
CAMP EVERS 2105 | 83622105 | 78.47 | 73.46 | 2.13 |  | 2.88
CAMP EVERS 2106 | 83622106 | 145.75 | 132.84 | 2.97 |  | 9.94
CAMPHORA 0401 | 182070401 | 0.43 |  |  |  | 0.43
CAMPHORA 1101 | 182071101 | 51.89 |  | 3.89 |  | 48
CANAL 1101 | 252091101 | 56.42 |  |  |  | 56.42
CANAL 1102 | 252091102 | 15.33 |  |  |  | 15.33
CANAL 1103 | 252091103 | 53.58 |  |  |  | 53.58
CANAL 1104 | 252091104 | 9.93 |  |  |  | 9.93
CANAL 1105 | 252091105 | 17.32 |  |  |  | 17.32
CANAL 1106 | 252091106 | 7.86 |  |  |  | 7.86
CANTUA 1101 | 253591101 | 24.04 |  |  |  | 24.04
CANTUA 1102 | 253591102 | 47.75 |  |  |  | 47.75
CANTUA 1103 | 253591103 | 35.78 |  |  |  | 35.78
CANTUA 1104 | 253591104 | 0.17 |  |  |  | 0.17
CANTUA 1105 | 253591105 | 15.12 |  |  |  | 15.12
CANTUA 1106 | 253591106 | 0.16 |  |  |  | 0.16
CAPAY 1101 | 102111101 | 48.81 |  |  |  | 48.81
CAPAY 1102 | 102111102 | 73.95 |  |  |  | 73.95
CARBONA 1101 | 163091101 | 39.11 |  |  |  | 39.11
CARBONA 1103 | 163091103 | 3.63 |  |  |  | 3.63
CARLOTTA 1121 | 192291121 | 51.97 |  | 21.08 |  | 30.89
CARNATION 2101 | 255282101 | 0.01 |  |  |  | 0.01
CARNERAS 1102 | 252321102 | 16.83 |  |  |  | 16.83
CARNERAS 1103 | 252321103 | 41.62 |  |  |  | 41.62
CAROLANDS 0401 | 24060401 | 4.52 |  |  |  | 4.52
CAROLANDS 0402 | 24060402 | 0.03 |  |  |  | 0.03
CAROLANDS 0403 | 24060403 | 13.35 |  |  |  | 13.35
CAROLANDS 0404 | 24060404 | 10.2 |  | 4.16 |  | 6.04
CARQUINEZ 1103 | 43281103 | 14.67 |  |  |  | 14.67
CARQUINEZ 1104 | 43281104 | 0.38 |  |  |  | 0.38
CARQUINEZ 1105 | 43281105 | 5.68 |  |  |  | 5.68
CARRIZO PLAINS 1101 | 253461101 | 105.92 |  |  |  | 105.92
CARUTHERS 1101 | 252371101 | 81.8 |  |  |  | 81.8
CARUTHERS 1102 | 252371102 | 69.76 |  |  |  | 69.76
CARUTHERS 1104 | 252371104 | 80.71 |  |  |  | 80.71
CARUTHERS 1105 | 252371105 | 56.41 |  |  |  | 56.41
CASSERLY 0401 | 83110401 | 3.07 |  |  |  | 3.07
CASSIDY 2107 | 254272107 | 59.41 |  |  |  | 59.41
CASSIDY 2108 | 254272108 | 34.09 |  |  |  | 34.09
CASTRO 0401 | 22480401 | 2.93 |  |  |  | 2.93
CASTRO 0402 | 22480402 | 2.62 |  |  |  | 2.62
CASTRO VALLEY 1102 | 14091102 | 22.74 | 0.35 | 1.15 |  | 21.24
CASTRO VALLEY 1103 | 14091103 | 15.67 |  |  |  | 15.67
CASTRO VALLEY 1104 | 14091104 | 7.33 |  |  |  | 7.33
CASTRO VALLEY 1105 | 14091105 | 30.22 |  | 2.18 |  | 28.04
CASTRO VALLEY 1107 | 14091107 | 16.06 |  |  |  | 16.06
CASTRO VALLEY 1108 | 14091108 | 38.75 | 12.59 | 4.16 |  | 22
CASTRO VALLEY 1109 | 14091109 | 8.02 |  |  |  | 8.02
CASTRO VALLEY 1110 | 14091110 | 24.81 | 15.57 | 6.7 |  | 2.54
CASTRO VALLEY 1111 | 14091111 | 7.89 | 1.54 | 3.92 |  | 2.43
CASTROVILLE 2103 | 182352103 | 81.37 |  |  |  | 81.37
CASTROVILLE 2104 | 182352104 | 50.51 |  |  |  | 50.51
CATLETT 1101 | 153761101 | 0.03 |  |  |  | 0.03
CATLETT 1102 | 153761102 | 106.14 |  |  |  | 106.14
CATLETT 1105 | 153761105 | 54.16 |  |  |  | 54.16
CAWELO B 1101 | 252621101 | 0.01 |  |  |  | 0.01
CAWELO C 1101 | 252631101 | 0.02 |  |  |  | 0.02
CAYETANO 2109 | 14422109 | 49.59 | 12.1 | 21.65 |  | 15.84
CAYETANO 2111 | 14422111 | 12.25 |  | 5.36 |  | 6.89
CAYUCOS 1101 | 182551101 | 46.25 |  | 0.46 |  | 45.79
CAYUCOS 1102 | 182551102 | 57.27 | 9.06 | 4.98 |  | 43.23
CEDAR CREEK 1101 | 103321101 | 109.66 | 20.98 | 88.68 |  | 0
CELERON 1101 | 255271101 | 0.15 |  |  |  | 0.15
CHALLENGE 1101 | 103201101 | 48.27 | 48.04 | 0.23 |  | 0
CHALLENGE 1102 | 103201102 | 62.85 | 60.21 | 2.64 |  | 0
CHANNEL 1101 | 163071101 | 9.93 |  |  |  | 9.93
CHANNEL 1102 | 163071102 | 8.38 |  |  |  | 8.38
CHARCA 1102 | 254501102 | 47.97 |  |  |  | 47.97
CHARCA 1103 | 254501103 | 41.41 |  |  |  | 41.41
CHARCA 1106 | 254501106 | 18.69 |  |  |  | 18.69
CHEROKEE 1101 | 163651101 | 19.87 |  |  |  | 19.87
CHEROKEE 1102 | 163651102 | 36.3 |  |  |  | 36.3
CHESTER 1101 | 103181101 | 8.16 |  | 2.12 |  | 6.04
CHESTER 1102 | 103181102 | 5.3 |  | 2.31 |  | 2.99
CHICO A 0401 | 102050401 | 2.2 |  |  |  | 2.2
CHICO A 0402 | 102050402 | 5.65 |  |  |  | 5.65
CHICO A 1101 | 102051101 | 8.09 |  |  |  | 8.09
CHICO A 1102 | 102051102 | 9.3 |  |  |  | 9.3
CHICO A 1103 | 102051103 | 4.86 |  |  |  | 4.86
CHICO B 1101 | 102491101 | 4.56 |  |  |  | 4.56
CHICO B 1103 | 102491103 | 8.02 |  |  |  | 8.02
CHICO B 1105 | 102491105 | 10.85 |  |  |  | 10.85
CHICO B 1106 | 102491106 | 2.01 |  |  |  | 2.01
CHICO C 0401 | 102650401 | 2.77 |  |  |  | 2.77
CHOLAME 1101 | 182561101 | 96.97 |  |  |  | 96.97
CHOLAME 2102 | 182562102 | 215.33 |  | 59 |  | 156.33
CHOWCHILLA 1101 | 254101101 | 63.03 |  |  |  | 63.03
CHOWCHILLA 1102 | 254101102 | 13.15 |  |  |  | 13.15
CHOWCHILLA 1103 | 254101103 | 46.85 |  |  |  | 46.85
CHOWCHILLA 1104 | 254101104 | 80.6 |  |  |  | 80.6
CHOWCHILLA 1105 | 254101105 | 11.89 |  |  |  | 11.89
CHOWCHILLA 1106 | 254101106 | 54.75 |  |  |  | 54.75
CLARK ROAD 1101 | 103091101 | 0.02 |  | 0.02 |  | 0
CLARK ROAD 1102 | 103091102 | 136.63 | 32.87 | 89.63 |  | 14.13
CLARKSVILLE 2103 | 153612103 | 50.41 | 19.61 | 10.52 |  | 20.28
CLARKSVILLE 2104 | 153612104 | 75.66 | 41.19 | 21.88 |  | 12.59
CLARKSVILLE 2105 | 153612105 | 13.34 | 5.79 | 4.75 |  | 2.8
CLARKSVILLE 2106 | 153612106 | 2.21 |  | 0.48 |  | 1.73
CLARKSVILLE 2109 | 153612109 | 12.26 | 1.98 | 1.96 |  | 8.32
CLARKSVILLE 2110 | 153612110 | 7.03 |  |  |  | 7.03
CLAY 1101 | 163341101 | 40.58 |  | 26.32 |  | 14.26
CLAY 1102 | 163341102 | 2.09 |  | 0.82 |  | 1.27
CLAY 1103 | 163341103 | 112.62 |  | 49.68 |  | 62.94
CLAYTON 1103 | 12021103 | 4.33 |  |  |  | 4.33
CLAYTON 1104 | 12021104 | 13.4 |  |  |  | 13.4
CLAYTON 2211 | 12022211 | 10.48 |  |  |  | 10.48
CLAYTON 2212 | 12022212 | 58.62 | 28.9 | 18.66 |  | 11.06
CLAYTON 2213 | 12022213 | 4.84 |  | 2.51 |  | 2.33
CLAYTON 2214 | 12022214 | 5.89 |  |  |  | 5.89
CLAYTON 2215 | 12022215 | 30.8 | 2.92 | 5.47 |  | 22.41
CLAYTON 2216 | 12022216 | 18.71 |  |  |  | 18.71
CLAYTON 2217 | 12022217 | 19.79 |  |  |  | 19.79
CLAYTON 2218 | 12022218 | 8.34 |  |  |  | 8.34
CLEAR LAKE 1101 | 42141101 | 112.61 | 6.05 | 12.29 |  | 94.27
CLEAR LAKE 1102 | 42141102 | 36.63 |  | 3.97 |  | 32.66
CLOVERDALE 1101 | 42821101 | 36.64 |  | 24.35 |  | 12.29
CLOVERDALE 1102 | 42821102 | 108.77 | 47.23 | 30.21 |  | 31.33
CLOVIS 1101 | 254081101 | 3.97 |  |  |  | 3.97
CLOVIS 1102 | 254081102 | 25.59 |  |  |  | 25.59
CLOVIS 1103 | 254081103 | 1.95 |  |  |  | 1.95
CLOVIS 1104 | 254081104 | 0.43 |  |  |  | 0.43
CLOVIS 1105 | 254081105 | 7.73 |  |  |  | 7.73
CLOVIS 1106 | 254081106 | 4.99 |  |  |  | 4.99
CLOVIS 1107 | 254081107 | 10.71 |  |  |  | 10.71
CLOVIS 1108 | 254081108 | 11.47 |  |  |  | 11.47
CLOVIS 2109 | 254082109 | 3.85 |  |  |  | 3.85
CLOVIS 2110 | 254082110 | 11.47 |  |  |  | 11.47
CLOVIS 2111 | 254082111 | 8.84 |  |  |  | 8.84
CMC 1101 | 183111101 | 2.01 |  | 2.01 |  | 0
CMC 1102 | 183111102 | 0.48 |  | 0.48 |  | 0
COALINGA NO 1 1106 | 252161106 | 8.96 |  |  |  | 8.96
COALINGA NO 1 1107 | 252161107 | 4.04 |  |  |  | 4.04
COALINGA NO 1 1108 | 252161108 | 60.22 |  |  |  | 60.22
COALINGA NO 1 1109 | 252161109 | 27.26 |  |  |  | 27.26
COALINGA NO 2 1104 | 252381104 | 0.16 |  |  |  | 0.16
COALINGA NO 2 1105 | 252381105 | 76.34 |  |  |  | 76.34
COALINGA NO 2 1106 | 252381106 | 42.94 |  |  |  | 42.94
COALINGA NO 2 1107 | 252381107 | 38.43 |  |  |  | 38.43
COARSEGOLD 2102 | 254432102 | 72.98 | 58.15 | 14.83 |  | 0
COARSEGOLD 2103 | 254432103 | 122.4 |  | 93.29 |  | 29.11
COARSEGOLD 2104 | 254432104 | 265.16 | 2.83 | 243.51 |  | 18.82
COLONY 1101 | 162231101 | 28.9 |  |  |  | 28.9
COLONY 1102 | 162231102 | 47.74 |  |  |  | 47.74
COLUMBIA HILL 1101 | 152471101 | 89.55 | 71.94 | 17.61 |  | 0
COLUMBUS 1103 | 253951103 | 7.87 |  |  |  | 7.87
COLUMBUS 1104 | 253951104 | 8.27 |  |  |  | 8.27
COLUMBUS 1105 | 253951105 | 16.06 |  |  |  | 16.06
COLUMBUS 1106 | 253951106 | 14.29 |  |  |  | 14.29
COLUMBUS 1109 | 253951109 | 5.58 |  |  |  | 5.58
COLUMBUS 1110 | 253951110 | 6.52 |  |  |  | 6.52
COLUSA 1100 | 62021100 | 0.02 |  |  |  | 0.02
COLUSA 1101 | 62021101 | 113.67 |  |  |  | 113.67
COLUSA JUNCTION 1101 | 62071101 | 29 |  |  |  | 29
CONCORD NO 1 0401 | 12960401 | 4.75 |  |  |  | 4.75
CONCORD NO 1 0402 | 12960402 | 3.77 |  |  |  | 3.77
CONTRA COSTA 2103 | 13652103 | 22.62 |  |  |  | 22.62
CONTRA COSTA 2104 | 13652104 | 10.89 |  |  |  | 10.89
CONTRA COSTA 2105 | 13652105 | 0.04 |  |  |  | 0.04
CONTRA COSTA 2106 | 13652106 | 0.02 |  |  |  | 0.02
CONTRA COSTA 2107 | 13652107 | 12.73 |  |  |  | 12.73
CONTRA COSTA 2108 | 13652108 | 0.88 |  |  |  | 0.88
CONTRA COSTA 2109 | 13652109 | 13.87 |  |  |  | 13.87
CONTRA COSTA 2110 | 13652110 | 0.55 |  |  |  | 0.55
CONTRA COSTA 2112 | 13652112 | 0.04 |  |  |  | 0.04
CONTRA COSTA 2113 | 13652113 | 15.09 |  |  |  | 15.09
CONTRA COSTA 2114 | 13652114 | 1.91 |  |  |  | 1.91
CONTRA COSTA 2115 | 13652115 | 6.76 |  |  |  | 6.76
CONTRA COSTA 2116 | 13652116 | 23.1 |  |  |  | 23.1
COPPERMINE 1104 | 252411104 | 102.71 |  | 9.04 |  | 93.67
COPPERMINE 1106 | 252411106 | 7.93 |  |  |  | 7.93
COPPERMINE 1112 | 252411112 | 15.85 |  |  |  | 15.85
COPPERMINE 2110 | 252412110 | 0 |  |  |  | 0
COPUS 1102 | 253871102 | 30.83 |  |  |  | 30.83
COPUS 1103 | 253871103 | 24.39 |  |  |  | 24.39
COPUS 1104 | 253871104 | 39.16 |  |  |  | 39.16
CORCORAN 1101 | 252171101 | 0.52 |  |  |  | 0.52
CORCORAN 1102 | 252171102 | 0.04 |  |  |  | 0.04
CORCORAN 1104 | 252171104 | 26.71 |  |  |  | 26.71
CORCORAN 1106 | 252171106 | 45.04 |  |  |  | 45.04
CORCORAN 1108 | 252171108 | 23.47 |  |  |  | 23.47
CORCORAN 1112 | 252171112 | 45.42 |  |  |  | 45.42
CORCORAN 1116 | 252171116 | 56.58 |  |  |  | 56.58
CORCORAN 1117 | 252171117 | 0.54 |  |  |  | 0.54
CORCORAN 1118 | 252171118 | 52.18 |  |  |  | 52.18
CORDELIA 1101 | 62701101 | 0.02 |  |  |  | 0.02
CORDELIA 1102 | 62701102 | 0.04 |  |  |  | 0.04
CORDELIA 1104 | 62701104 | 61.99 |  |  |  | 61.99
CORDELIA 1110 | 62701110 | 8.94 |  |  |  | 8.94
CORDELIA 1112 | 62701112 | 16.1 |  |  |  | 16.1
CORNING 1101 | 103331101 | 143.58 |  | 49.53 |  | 94.05
CORNING 1102 | 103331102 | 192.36 |  | 79.8 |  | 112.56
CORNING 1103 | 103331103 | 66.42 |  |  |  | 66.42
CORNING 1104 | 103331104 | 106.3 |  |  |  | 106.3
CORONA 1101 | 43491101 | 22.81 |  |  |  | 22.81
CORONA 1102 | 43491102 | 1.38 |  |  |  | 1.38
CORONA 1103 | 43491103 | 17.44 |  | 0.46 |  | 16.98
CORRAL 1101 | 162991101 | 170.22 |  | 119.68 |  | 50.54
CORRAL 1102 | 162991102 | 64.32 |  | 48.46 |  | 15.86
CORRAL 1103 | 162991103 | 80.53 |  | 17.68 |  | 62.85
CORTINA 1101 | 63121101 | 76.57 |  | 1.32 |  | 75.25
COTATI 1102 | 42271102 | 34.61 |  | 15.6 |  | 19.01
COTATI 1103 | 42271103 | 110.88 |  | 84.03 |  | 26.85
COTATI 1104 | 42271104 | 19.32 |  | 8.43 |  | 10.89
COTATI 1105 | 42271105 | 131.49 |  | 42.8 |  | 88.69
COTTLE 1701 | 163711701 | 89.87 |  |  |  | 89.87
COTTLE 1702 | 163711702 | 37 |  |  |  | 37
COTTLE 1703 | 163711703 | 26.78 |  |  |  | 26.78
COTTLE 1704 | 163711704 | 14.6 |  |  |  | 14.6
COTTLE 1707 | 163711707 | 47.15 |  |  |  | 47.15
COTTLE 1708 | 163711708 | 129.9 |  |  |  | 129.9
COTTONWOOD 1101 | 102931101 | 100.91 |  | 69.99 |  | 30.92
COTTONWOOD 1102 | 102931102 | 82.71 |  | 55.8 |  | 26.91
COTTONWOOD 1103 | 102931103 | 161.03 |  | 133.87 |  | 27.16
COUNTRY CLUB 0401 | 163120401 | 2.11 |  |  |  | 2.11
COUNTRY CLUB 0402 | 163120402 | 4.65 |  |  |  | 4.65
COUNTRY CLUB 0403 | 163120403 | 2.7 |  |  |  | 2.7
COUNTRY CLUB 1101 | 163121101 | 12 |  |  |  | 12
COUNTRY CLUB 1102 | 163121102 | 1.34 |  |  |  | 1.34
COUNTRY CLUB 1103 | 163121103 | 6.25 |  |  |  | 6.25
COUNTRY CLUB 1104 | 163121104 | 7.2 |  |  |  | 7.2
COUNTRY CLUB 1105 | 163121105 | 1.64 |  |  |  | 1.64
COUNTRY CLUB 1106 | 163121106 | 8.96 |  |  |  | 8.96
COVELO 1101 | 43061101 | 120.63 |  | 17.54 |  | 103.09
CRESCENT MILLS 2101 | 103132101 | 79.32 |  | 42.08 |  | 37.24
CRESSEY 2103 | 254702103 | 152.7 |  |  |  | 152.7
CRESSEY 2104 | 254702104 | 94.86 |  |  |  | 94.86
CRESTA 1101 | 102251101 | 1.7 | 0.41 | 1.3 |  | -0.01
CROWS LANDING 1101 | 163251101 | 44.59 |  |  |  | 44.59
CROWS LANDING 1102 | 163251102 | 7.56 |  |  |  | 7.56
CURTIS 1701 | 163351701 | 20.14 |  | 12.23 |  | 7.91
CURTIS 1702 | 163351702 | 117.69 | 22.46 | 87.13 |  | 8.1
CURTIS 1703 | 163351703 | 197.92 | 17.43 | 177.18 |  | 3.31
CURTIS 1704 | 163351704 | 75.97 | 24.28 | 51.12 |  | 0.57
CURTIS 1705 | 163351705 | 88.26 | 14.37 | 69.8 |  | 4.09
CUYAMA 1103 | 253141103 | 79.98 |  | 2.58 |  | 77.4
CUYAMA 1104 | 253141104 | 17.89 |  |  |  | 17.89
CUYAMA 2101 | 253142101 | 63.13 |  | 3.39 |  | 59.74
CUYAMA 2102 | 253142102 | 35.86 |  |  |  | 35.86
DAIRYLAND 1102 | 252421102 | 81.4 |  |  |  | 81.4
DAIRYLAND 1105 | 252421105 | 64.77 |  |  |  | 64.77
DAIRYLAND 1109 | 252421109 | 48.59 |  |  |  | 48.59
DAIRYLAND 1110 | 252421110 | 35 |  |  |  | 35
DAIRYLAND 1111 | 252421111 | 26.7 |  |  |  | 26.7
DAIRYLAND 1112 | 252421112 | 62.34 |  |  |  | 62.34
DAIRYLAND 1113 | 252421113 | 83.52 |  |  |  | 83.52
DAIRYVILLE 1101 | 103341101 | 43.01 |  |  |  | 43.01
DALY CITY 0401 | 22640401 | 5.65 |  |  |  | 5.65
DALY CITY 1101 | 22641101 | 3.43 |  |  |  | 3.43
DALY CITY 1102 | 22641102 | 7.54 |  |  |  | 7.54
DALY CITY 1103 | 22641103 | 4.73 |  |  |  | 4.73
DALY CITY 1104 | 22641104 | 10.98 |  |  |  | 10.98
DALY CITY 1105 | 22641105 | 10.65 |  |  |  | 10.65
DALY CITY 1106 | 22641106 | 9.94 |  |  |  | 9.94
DALY CITY 1107 | 22641107 | 5.3 |  |  |  | 5.3
DALY CITY 1108 | 22641108 | 2.92 |  |  |  | 2.92
DALY CITY 1109 | 22641109 | 6.23 |  |  |  | 6.23
DALY CITY 1110 | 22641110 | 1.78 |  |  |  | 1.78
DALY CITY 1111 | 22641111 | 6.94 |  |  |  | 6.94
DALY CITY 1112 | 22641112 | 14.04 |  |  |  | 14.04
DALY CITY 1115 | 22641115 | 0.03 |  |  |  | 0.03
DAVIS 1101 | 62041101 | 37.51 |  |  |  | 37.51
DAVIS 1102 | 62041102 | 6.46 |  |  |  | 6.46
DAVIS 1103 | 62041103 | 5.85 |  |  |  | 5.85
DAVIS 1104 | 62041104 | 5.72 |  |  |  | 5.72
DAVIS 1105 | 62041105 | 8.02 |  |  |  | 8.02
DAVIS 1106 | 62041106 | 42.71 |  |  |  | 42.71
DAVIS 1107 | 62041107 | 84.37 |  |  |  | 84.37
DAVIS 1108 | 62041108 | 3.34 |  |  |  | 3.34
DAVIS 1109 | 62041109 | 4.45 |  |  |  | 4.45
DAVIS 1110 | 62041110 | 1.83 |  |  |  | 1.83
DAVIS 1111 | 62041111 | 7.24 |  |  |  | 7.24
DAVIS 1112 | 62041112 | 46.6 |  |  |  | 46.6
DAYTON ROAD 0401 | 102940401 | 2.11 |  |  |  | 2.11
DEEPWATER 1105 | 63621105 | 4.12 |  |  |  | 4.12
DEEPWATER 1106 | 63621106 | 0.06 |  |  |  | 0.06
DEEPWATER 1107 | 63621107 | 28.7 |  |  |  | 28.7
DEEPWATER 1108 | 63621108 | 0.09 |  |  |  | 0.09
DEEPWATER 1109 | 63621109 | 4.17 |  |  |  | 4.17
DEER CREEK PH 0401 | 158450401 | 1.12 | 1.12 |  |  | 0
DEL MAR 1103 | 152581103 | 13.01 |  |  |  | 13.01
DEL MAR 1104 | 152581104 | 0 |  |  |  | 0
DEL MAR 2105 | 152582105 | 13.85 |  |  |  | 13.85
DEL MAR 2106 | 152582106 | 3.18 |  |  |  | 3.18
DEL MAR 2109 | 152582109 | 6.88 |  | 2.03 |  | 4.85
DEL MAR 2110 | 152582110 | 1.77 |  |  |  | 1.77
DEL MONTE 1101 | 182221101 | 14.88 |  | 0.49 |  | 14.39
DEL MONTE 2102 | 182222102 | 16.27 |  | 0.66 |  | 15.61
DEL MONTE 2103 | 182222103 | 36.72 |  | 12.3 |  | 24.42
DEL MONTE 2104 | 182222104 | 59.25 |  | 43.85 |  | 15.4
DEL MONTE 2105 | 182222105 | 20.14 |  | 1.04 |  | 19.1
DELEVAN 1101 | 69551101 | 0.6 |  |  |  | 0.6
DELEVAN 1102 | 69551102 | 0.61 |  |  |  | 0.61
DESCHUTES 1101 | 103351101 | 130.44 | 7.48 | 99.43 |  | 23.53
DESCHUTES 1104 | 103351104 | 112.8 |  | 60.22 |  | 52.58
DEVILS DEN 1101 | 253451101 | 44.8 |  |  |  | 44.8
DEVILS DEN 1102 | 253451102 | 33.33 |  |  |  | 33.33
DIAMOND SPRINGS 1103 | 152261103 | 53.26 | 10.2 | 22.95 |  | 20.11
DIAMOND SPRINGS 1104 | 152261104 | 18.15 | 7.56 | 4.89 |  | 5.7
DIAMOND SPRINGS 1105 | 152261105 | 131.88 | 75.04 | 48.36 |  | 8.48
DIAMOND SPRINGS 1106 | 152261106 | 120.12 |  | 109.72 |  | 10.4
DIAMOND SPRINGS 1107 | 152261107 | 57.33 | 34.14 | 17.88 |  | 5.31
DINUBA 1102 | 254091102 | 22.52 |  |  |  | 22.52
DINUBA 1104 | 254091104 | 85.42 |  |  |  | 85.42
DINUBA 1105 | 254091105 | 99.83 |  |  |  | 99.83
DINUBA 1106 | 254091106 | 10.29 |  |  |  | 10.29
DIVIDE 1101 | 182571101 | 15.49 |  |  |  | 15.49
DIVIDE 1102 | 182571102 | 47.79 |  |  |  | 47.79
DIVIDE 1103 | 182571103 | 21.03 |  | 2.38 |  | 18.65
DIXON 1102 | 62061102 | 10.84 |  |  |  | 10.84
DIXON 1103 | 62061103 | 126.63 |  |  |  | 126.63
DIXON 1104 | 62061104 | 11.67 |  |  |  | 11.67
DIXON 1105 | 62061105 | 23.75 |  |  |  | 23.75
DIXON 1106 | 62061106 | 10.06 |  |  |  | 10.06
DIXON LANDING 2101 | 14722101 | 10.74 |  |  |  | 10.74
DIXON LANDING 2102 | 14722102 | 10.86 |  |  |  | 10.86
DIXON LANDING 2103 | 14722103 | 2.81 |  |  |  | 2.81
DIXON LANDING 2105 | 14722105 | 1.68 |  |  |  | 1.68
DIXON LANDING 2109 | 14722109 | 10.59 |  |  |  | 10.59
DIXON LANDING 2111 | 14722111 | 0.13 |  |  |  | 0.13
DOBBINS 1101 | 153741101 | 81.65 | 26.57 | 54.01 |  | 1.07
DOLAN RD 1102 | 182381102 | 0.45 |  |  |  | 0.45
DOLAN ROAD 1101 | 182381101 | 69.09 |  | 2.77 |  | 66.32
DOLAN ROAD 1103 | 182381103 | 3 |  |  |  | 3
DOLAN ROAD 1104 | 182381104 | 5.06 |  |  |  | 5.06
DOS PALOS 1101 | 254041101 | 75.66 |  |  |  | 75.66
DOS PALOS 1102 | 254041102 | 0.21 |  |  |  | 0.21
DRUM 1101 | 152321101 | 18.36 | 18.32 | 0.04 |  | 0
DUMBARTON 1102 | 14471102 | 16.47 |  |  |  | 16.47
DUMBARTON 1103 | 14471103 | 1.48 |  |  |  | 1.48
DUMBARTON 1104 | 14471104 | 13.19 |  |  |  | 13.19
DUMBARTON 1106 | 14471106 | 7.25 |  |  |  | 7.25
DUMBARTON 1107 | 14471107 | 10.35 |  |  |  | 10.35
DUMBARTON 1108 | 14471108 | 3.94 |  |  |  | 3.94
DUMBARTON 1109 | 14471109 | 3.71 |  |  |  | 3.71
DUMBARTON 1110 | 14471110 | 6.95 |  |  |  | 6.95
DUMBARTON 2111 | 14472111 | 6.41 |  |  |  | 6.41
DUNBAR 1101 | 43071101 | 53.4 | 26.42 | 2.62 |  | 24.36
DUNBAR 1102 | 43071102 | 62.11 | 7.2 | 42.28 |  | 12.63
DUNBAR 1103 | 43071103 | 60.09 | 20.67 | 14.76 |  | 24.66
DUNLAP 1102 | 254061102 | 55.46 |  | 55.46 |  | 0
DUNLAP 1103 | 254061103 | 71.32 |  | 71.32 |  | 0
DUNNIGAN 1101 | 63811101 | 78.06 |  |  |  | 78.06
EAST GRAND 0401 | 22570401 | 4.71 |  |  |  | 4.71
EAST GRAND 0404 | 22570404 | 3.82 |  |  |  | 3.82
EAST GRAND 1101 | 22571101 | 7.95 |  |  |  | 7.95
EAST GRAND 1102 | 22571102 | 2.21 |  |  |  | 2.21
EAST GRAND 1103 | 22571103 | 1.51 |  |  |  | 1.51
EAST GRAND 1104 | 22571104 | 15.54 |  |  |  | 15.54
EAST GRAND 1105 | 22571105 | 5.55 |  |  |  | 5.55
EAST GRAND 1106 | 22571106 | 3.7 |  |  |  | 3.7
EAST GRAND 1107 | 22571107 | 13.53 |  |  |  | 13.53
EAST GRAND 1108 | 22571108 | 3.86 |  |  |  | 3.86
EAST GRAND 1109 | 22571109 | 2.08 |  |  |  | 2.08
EAST GRAND 1110 | 22571110 | 3.34 |  |  |  | 3.34
EAST GRAND 1111 | 22571111 | 0.88 |  |  |  | 0.88
EAST GRAND 1114 | 22571114 | 0 |  |  |  | 0
EAST GRAND 1115 | 22571115 | 0 |  |  |  | 0
EAST MARYSVILLE 1105 | 152331105 | 39.25 |  |  |  | 39.25
EAST MARYSVILLE 1107 | 152331107 | 8.01 |  |  |  | 8.01
EAST MARYSVILLE 1108 | 152331108 | 67.82 |  |  |  | 67.82
EAST NICOLAUS 1101 | 152151101 | 68.88 |  |  |  | 68.88
EAST NICOLAUS 1102 | 152151102 | 58.28 |  |  |  | 58.28
EAST NICOLAUS 1103 | 152151103 | 93.3 |  |  |  | 93.3
EAST QUINCY 1101 | 102551101 | 17.43 | 1.69 | 2.06 |  | 13.68
EAST STOCKTON 0401 | 163130401 | 8.35 |  |  |  | 8.35
EAST STOCKTON 0402 | 163130402 | 9.76 |  |  |  | 9.76
EAST STOCKTON 1101 | 163131101 | 14.59 |  |  |  | 14.59
EAST STOCKTON 1102 | 163131102 | 16.09 |  |  |  | 16.09
ECHO SUMMIT 1101 | 158031101 | 14.7 |  | 5.9 | 0.04 | 8.76
EDENVALE 1101 | 82951101 | 9.68 |  |  |  | 9.68
EDENVALE 1102 | 82951102 | 5.72 |  | 0.52 |  | 5.2
EDENVALE 1103 | 82951103 | 0.31 |  |  |  | 0.31
EDENVALE 2105 | 82952105 | 37.05 |  | 2.32 |  | 34.73
EDENVALE 2106 | 82952106 | 16.89 |  |  |  | 16.89
EDENVALE 2107 | 82952107 | 0.07 |  |  |  | 0.07
EDENVALE 2108 | 82952108 | 2.87 |  |  |  | 2.87
EDENVALE 2109 | 82952109 | 2.47 |  |  |  | 2.47
EDENVALE 2110 | 82952110 | 0 |  |  |  | 0
EDENVALE 2112 | 82952112 | 1.33 |  |  |  | 1.33
EDENVALE 2113 | 82952113 | 2.42 |  | 0.02 |  | 2.4
EDES 1101 | 13681101 | 8.54 |  |  |  | 8.54
EDES 1103 | 13681103 | 12.44 |  |  |  | 12.44
EDES 1105 | 13681105 | 3.78 |  |  |  | 3.78
EDES 1110 | 13681110 | 7.49 |  |  |  | 7.49
EDES 1111 | 13681111 | 4.22 |  |  |  | 4.22
EDES 1112 | 13681112 | 17.11 | 0.58 | 14.67 |  | 1.86
EDES 1113 | 13681113 | 4.47 |  |  |  | 4.47
EDES 1114 | 13681114 | 10.4 |  |  |  | 10.4
EEL RIVER 1102 | 192381102 | 144.59 |  | 40.02 |  | 104.57
EEL RIVER 1103 | 192381103 | 59.35 |  | 3.2 |  | 56.15
EIGHT MILE 2101 | 163912101 | 72.61 |  |  |  | 72.61
EIGHT MILE 2102 | 163912102 | 29.37 |  |  |  | 29.37
EIGHT MILE 2103 | 163912103 | 0 |  |  |  | 0
EIGHT MILE 2104 | 163912104 | 1.36 |  |  |  | 1.36
EIGHT MILE 2105 | 163912105 | 0.49 |  |  |  | 0.49
EIGHT MILE 2106 | 163912106 | 30.16 |  |  |  | 30.16
EL CAPITAN 0004 | 253880004 | 0.01 |  |  |  | 0.01
EL CAPITAN 1102 | 253881102 | 16.59 |  |  |  | 16.59
EL CAPITAN 1103 | 253881103 | 69.97 |  |  |  | 69.97
EL CAPITAN 1104 | 253881104 | 47.15 |  |  |  | 47.15
EL CAPITAN 1105 | 253881105 | 4.84 |  |  |  | 4.84
EL CAPITAN 1106 | 253881106 | 14.32 |  |  |  | 14.32
EL CAPITAN 2109 | 253882109 | 4.48 |  |  |  | 4.48
EL CAPITAN 2110 | 253882110 | 14.69 |  |  |  | 14.69
EL CERRITO G 1101 | 12501101 | 10.12 |  |  |  | 10.12
EL CERRITO G 1102 | 12501102 | 7.8 |  |  |  | 7.8
EL CERRITO G 1103 | 12501103 | 9.05 |  |  |  | 9.05
EL CERRITO G 1104 | 12501104 | 7.85 |  |  |  | 7.85
EL CERRITO G 1105 | 12501105 | 31.68 | 5.58 | 18.89 |  | 7.21
EL CERRITO G 1106 | 12501106 | 4.65 |  |  |  | 4.65
EL CERRITO G 1107 | 12501107 | 3.59 |  |  |  | 3.59
EL CERRITO G 1108 | 12501108 | 14.41 |  | 0 |  | 14.41
EL CERRITO G 1109 | 12501109 | 8 |  |  |  | 8
EL CERRITO G 1110 | 12501110 | 10.16 |  | 0.69 |  | 9.47
EL CERRITO G 1111 | 12501111 | 12.63 |  | 0.2 |  | 12.43
EL CERRITO G 1112 | 12501112 | 24.55 | 1.65 | 0.35 |  | 22.55
EL CERRITO G 1113 | 12501113 | 11.39 |  | 0.1 |  | 11.29
EL CERRITO G 1114 | 12501114 | 6.77 |  |  |  | 6.77
EL DORADO PH 2101 | 152762101 | 138.06 | 102.15 | 25.45 | 0.73 | 9.73
EL DORADO PH 2102 | 152762102 | 33.96 | 33.96 |  |  | 0
EL NIDO 1101 | 252451101 | 57.51 |  |  |  | 57.51
EL NIDO 1102 | 252451102 | 59.45 |  |  |  | 59.45
EL NIDO 1103 | 252451103 | 59.98 |  |  |  | 59.98
EL NIDO 1104 | 252451104 | 86.58 |  |  |  | 86.58
EL PATIO 1101 | 82921101 | 0 |  |  |  | 0
EL PATIO 1102 | 82921102 | 0.98 |  |  |  | 0.98
EL PATIO 1103 | 82921103 | 13.12 |  |  |  | 13.12
EL PATIO 1104 | 82921104 | 11.87 |  |  |  | 11.87
EL PATIO 1105 | 82921105 | 6.94 |  |  |  | 6.94
EL PATIO 1107 | 82921107 | 15.62 |  |  |  | 15.62
EL PATIO 1108 | 82921108 | 6.72 |  |  |  | 6.72
EL PATIO 1109 | 82921109 | 10.55 |  |  |  | 10.55
EL PATIO 1111 | 82921111 | 0.77 |  |  |  | 0.77
EL PATIO 1112 | 82921112 | 19.44 |  |  |  | 19.44
EL PATIO 1113 | 82921113 | 4.75 |  |  |  | 4.75
EL PATIO 1114 | 82921114 | 0.6 |  |  |  | 0.6
EL PATIO 1116 | 82921116 | 8.73 |  |  |  | 8.73
EL PATIO 1117 | 82921117 | 4.17 |  |  |  | 4.17
EL PATIO 1118 | 82921118 | 10.88 |  |  |  | 10.88
EL PATIO 1119 | 82921119 | 8.25 |  |  |  | 8.25
EL PECO 1102 | 253981102 | 52.17 |  |  |  | 52.17
EL PECO 1105 | 253981105 | 101.89 |  |  |  | 101.89
EL PECO 1106 | 253981106 | 38.58 |  |  |  | 38.58
ELECTRA 1101 | 162161101 | 85.08 |  | 81.56 |  | 3.52
ELECTRA 1102 | 162161102 | 19.54 |  | 16.97 |  | 2.57
ELK 1101 | 42981101 | 106.63 |  | 73.18 |  | 33.45
ELK CREEK 1101 | 102781101 | 172.65 |  | 79.1 |  | 93.55
ELK HILLS 1104 | 252441104 | 57.39 |  |  |  | 57.39
ELK HILLS 1106 | 252441106 | 21.37 |  |  |  | 21.37
EMBARCADERO (Z) 1112 | 22871112 | 0 |  |  |  | 0
EMBARCADERO (Z) 1113 | 22871113 | 0.32 |  |  |  | 0.32
EMBARCADERO (Z) 1114 | 22871114 | 0 |  |  |  | 0
EMBARCADERO (Z) 1115 | 22871115 | 0.24 |  |  |  | 0.24
EMBARCADERO (Z) 1116 | 22871116 | 1.05 |  |  |  | 1.05
EMBARCADERO (Z) 1118 | 22871118 | 0.08 |  |  |  | 0.08
EMBARCADERO (Z) 1120 | 22871120 | 0.32 |  |  |  | 0.32
EMBARCADERO (Z) 1122 | 22871122 | 0.01 |  |  |  | 0.01
EMBARCADERO (Z) 1123 | 22871123 | 0.36 |  |  |  | 0.36
EMERALD LAKE 0401 | 24080401 | 13.09 | 2.09 | 6.87 |  | 4.13
EMERALD LAKE 0402 | 24080402 | 6.56 |  | 6.56 |  | 0
ERTA 0403 | 83510403 | 2.98 |  |  |  | 2.98
ERTA 0404 | 83510404 | 6.52 |  |  |  | 6.52
ESQUON 1101 | 102171101 | 69.97 |  |  |  | 69.97
ESQUON 1102 | 102171102 | 50.49 |  |  |  | 50.49
ESQUON 1103 | 102171103 | 20.35 |  |  |  | 20.35
ESTUDILLO 0401 | 13480401 | 4.74 |  | 0.79 |  | 3.95
EUREKA A 1103 | 192121103 | 10.42 |  |  |  | 10.42
EUREKA A 1106 | 192121106 | 1.81 |  |  |  | 1.81
EUREKA A 1107 | 192121107 | 4.5 |  |  |  | 4.5
EUREKA E 1101 | 192331101 | 13.29 |  |  |  | 13.29
EUREKA E 1104 | 192331104 | 26.88 |  | 0.03 |  | 26.85
EUREKA E 1105 | 192331105 | 7.24 |  |  |  | 7.24
EVERGREEN 2101 | 82012101 | 2.53 |  |  |  | 2.53
EVERGREEN 2102 | 82012102 | 10.73 |  |  |  | 10.73
EVERGREEN 2103 | 82012103 | 19.17 |  |  |  | 19.17
EVERGREEN 2104 | 82012104 | 3.54 |  |  |  | 3.54
EVERGREEN 2105 | 82012105 | 4.63 |  |  |  | 4.63
FAIRHAVEN 1103 | 192451103 | 9.43 |  |  |  | 9.43
FAIRHAVEN 1104 | 192451104 | 3.32 |  |  |  | 3.32
FAIRMOUNT 0401 | 12650401 | 5.6 |  | 1.33 |  | 4.27
FAIRMOUNT 0402 | 12650402 | 5.07 |  |  |  | 5.07
FAIRVIEW 2206 | 13432206 | 14.25 |  |  |  | 14.25
FAIRVIEW 2207 | 13432207 | 50.47 |  | 20.92 |  | 29.55
FAIRVIEW 2208 | 13432208 | 10 |  |  |  | 10
FAIRWAY 1103 | 182061103 | 6.79 |  |  |  | 6.79
FAIRWAY 1104 | 182061104 | 22.91 |  |  |  | 22.91
FAIRWAY 1106 | 182061106 | 5.5 |  |  |  | 5.5
FAIRWAY 1107 | 182061107 | 19 |  |  |  | 19
FAIRWAY 1108 | 182061108 | 11.41 |  |  |  | 11.41
FAMOSO 1101 | 252461101 | 39.07 |  |  |  | 39.07
FAMOSO 1102 | 252461102 | 27.37 |  |  |  | 27.37
FAMOSO 1103 | 252461103 | 32.96 |  |  |  | 32.96
FAMOSO 1105 | 252461105 | 10.04 |  |  |  | 10.04
FAMOSO 1107 | 252461107 | 18.81 |  |  |  | 18.81
FELLOWS 2103 | 254242103 | 26.76 |  |  |  | 26.76
FELLOWS 2104 | 254242104 | 77.9 |  |  |  | 77.9
FIGARDEN 2102 | 254552102 | 23.69 |  |  |  | 23.69
FIGARDEN 2103 | 254552103 | 5.48 |  |  |  | 5.48
FIGARDEN 2104 | 254552104 | 1.81 |  |  |  | 1.81
FIGARDEN 2105 | 254552105 | 12.63 |  |  |  | 12.63
FIGARDEN 2107 | 254552107 | 5.43 |  |  |  | 5.43
FIGARDEN 2108 | 254552108 | 4.96 |  |  |  | 4.96
FIGARDEN 2109 | 254552109 | 3.9 |  |  |  | 3.9
FIGARDEN 2110 | 254552110 | 15.8 |  |  |  | 15.8
FIGARDEN 2111 | 254552111 | 4.81 |  |  |  | 4.81
FIGARDEN 2112 | 254552112 | 31.03 |  |  |  | 31.03
FIGARDEN 2113 | 254552113 | 11.42 |  |  |  | 11.42
FIREBAUGH 1101 | 253471101 | 92.25 |  |  |  | 92.25
FIREBAUGH 1102 | 253471102 | 52.69 |  |  |  | 52.69
FIREBAUGH 1103 | 253471103 | 75.36 |  |  |  | 75.36
FITCH MOUNTAIN 1111 | 42751111 | 30.49 |  | 0.29 |  | 30.2
FITCH MOUNTAIN 1112 | 42751112 | 0.01 |  |  |  | 0.01
FITCH MOUNTAIN 1113 | 42751113 | 145.6 | 30.76 | 46.39 |  | 68.45
FLINT 1101 | 152531101 | 18.33 |  | 6.33 |  | 12
FLINT 1102 | 152531102 | 0.12 |  | 0.12 |  | 0
FLORENCE 0401 | 12690401 | 4.28 |  | 0.82 |  | 3.46
FMC 1105 | 83871105 | 16.57 |  |  |  | 16.57
FMC 1108 | 83871108 | 1.35 |  |  |  | 1.35
FMC 1109 | 83871109 | 1.02 |  |  |  | 1.02
FMC 1111 | 83871111 | 1.56 |  |  |  | 1.56
FOOTHILL 1101 | 182951101 | 39.49 |  | 18.83 |  | 20.66
FOOTHILL 1102 | 182951102 | 18.11 |  | 8.48 |  | 9.63
FORESTHILL 1101 | 152181101 | 64.53 | 64.48 | 0.05 |  | 0
FORESTHILL 1102 | 152181102 | 29.48 | 21.71 | 7.77 |  | 0
FORT BRAGG A 1101 | 42761101 | 81.06 |  | 70.39 |  | 10.67
FORT BRAGG A 1102 | 42761102 | 81.62 |  | 66.03 |  | 15.59
FORT BRAGG A 1103 | 42761103 | 2.71 |  | 0.07 |  | 2.64
FORT BRAGG A 1104 | 42761104 | 38.88 |  | 24.89 |  | 13.99
FORT ORD 1101 | 182401101 | 16.86 |  |  |  | 16.86
FORT ORD 2105 | 182402105 | 7.39 |  |  |  | 7.39
FORT ORD 2106 | 182402106 | 24.22 |  | 2.2 |  | 22.02
FORT ORD 2107 | 182402107 | 19.41 |  | 3.78 |  | 15.63
FORT ORD 2108 | 182402108 | 0.9 |  |  |  | 0.9
FORT ROSS 1121 | 42851121 | 93.69 | 21.97 | 70.01 |  | 1.71
FORT SEWARD 1121 | 192321121 | 48.08 |  | 36.14 |  | 11.94
FORT SEWARD 1122 | 192321122 | 21.83 |  | 17.43 |  | 4.4
FRANKLIN 1101 | 13921101 | 9.2 |  | 1.27 |  | 7.93
FRANKLIN 1102 | 13921102 | 4.41 |  |  |  | 4.41
FRANKLIN 1103 | 13921103 | 12.4 |  |  |  | 12.4
FRANKLIN 1104 | 13921104 | 14.67 |  | 7.41 |  | 7.26
FREMONT 1103 | 14351103 | 4.37 |  |  |  | 4.37
FREMONT 1104 | 14351104 | 21.61 |  | 1.08 |  | 20.53
FREMONT 1107 | 14351107 | 15.13 |  |  |  | 15.13
FREMONT 1108 | 14351108 | 4.88 |  |  |  | 4.88
FREMONT 1109 | 14351109 | 13.63 |  |  |  | 13.63
FREMONT 1110 | 14351110 | 10.36 |  |  |  | 10.36
FREMONT 1112 | 14351112 | 0.18 |  |  |  | 0.18
FRENCH CAMP 1101 | 163291101 | 15.5 |  |  |  | 15.5
FRENCH CAMP 1102 | 163291102 | 87 |  |  |  | 87
FRENCH CAMP 1103 | 163291103 | 1.23 |  |  |  | 1.23
FRENCH CAMP 1104 | 163291104 | 5.61 |  |  |  | 5.61
FRENCH GULCH 1101 | 103381101 | 15.98 |  | 15.98 |  | 0
FRENCH GULCH 1102 | 103381102 | 18.73 |  | 18.63 |  | 0.1
FROGTOWN 1701 | 163451701 | 71.73 | 6.65 | 63.84 |  | 1.24
FROGTOWN 1702 | 163451702 | 230.42 |  | 205 |  | 25.42
FRUITLAND 1141 | 192311141 | 26.4 |  | 23.43 |  | 2.97
FRUITLAND 1142 | 192311142 | 67.15 |  | 57.05 | 0.03 | 10.07
FRUITVALE 1101 | 253391101 | 3.34 |  |  |  | 3.34
FRUITVALE 1103 | 253391103 | 12.63 |  |  |  | 12.63
FRUITVALE 1104 | 253391104 | 11.22 |  |  |  | 11.22
FRUITVALE 1105 | 253391105 | 3.41 |  |  |  | 3.41
FRUITVALE 1106 | 253391106 | 9.5 |  |  |  | 9.5
FRUITVALE 1108 | 253391108 | 9.13 |  |  |  | 9.13
FULTON 1101 | 42561101 | 6.7 |  |  |  | 6.7
FULTON 1102 | 42561102 | 61.63 | 1.64 | 26.31 |  | 33.68
FULTON 1103 | 42561103 | 0.01 |  |  |  | 0.01
FULTON 1104 | 42561104 | 8.47 |  | 0.41 |  | 8.06
FULTON 1105 | 42561105 | 41.6 |  |  |  | 41.6
FULTON 1106 | 42561106 | 4.89 |  |  |  | 4.89
FULTON 1107 | 42561107 | 48.31 | 35.17 | 0.01 |  | 13.13
GABILAN 1101 | 182331101 | 72.7 |  | 4.55 |  | 68.15
GABILAN 1102 | 182331102 | 9.77 |  |  |  | 9.77
GALLO 1101 | 254901101 | 0.72 |  |  |  | 0.72
GALLO 1102 | 254901102 | 0.08 |  |  |  | 0.08
GANSNER 1101 | 103021101 | 44.06 | 3 | 30.42 |  | 10.64
GANSO 1103 | 254541103 | 39.42 |  |  |  | 39.42
GANSO 1104 | 254541104 | 37.38 |  |  |  | 37.38
GARBERVILLE 1101 | 192221101 | 161.52 |  | 82.19 |  | 79.33
GARBERVILLE 1102 | 192221102 | 136.61 |  | 122.01 |  | 14.6
GARBERVILLE 1103 | 192221103 | 2.24 |  | 0.48 |  | 1.76
GARCIA 0401 | 43040401 | 2.46 |  | 2.46 |  | 0
GARDNER 0401 | 254930401 | 0.02 |  |  |  | 0.02
GATES 1101 | 253931101 | 15.24 |  |  |  | 15.24
GATES 1102 | 253931102 | 41.79 |  |  |  | 41.79
GATES 1104 | 253931104 | 25.54 |  |  |  | 25.54
GATES 1105 | 253931105 | 39.31 |  |  |  | 39.31
GATES 1106 | 253931106 | 44.6 |  |  |  | 44.6
GATES 1107 | 253931107 | 2.52 |  |  |  | 2.52
GATES 1108 | 253931108 | 2.57 |  |  |  | 2.57
GATES 1109 | 253931109 | 0.3 |  |  |  | 0.3
GATES 1110 | 253931110 | 43.24 |  |  |  | 43.24
GERBER 1101 | 103391101 | 40 |  |  |  | 40
GERBER 1102 | 103391102 | 85.04 |  |  |  | 85.04
GEYSERVILLE 1101 | 42891101 | 138.39 |  | 70.28 |  | 68.11
GEYSERVILLE 1102 | 42891102 | 118.66 | 20.31 | 33.86 |  | 64.49
GIFFEN 1102 | 253151102 | 41.33 |  |  |  | 41.33
GIFFEN 1103 | 253151103 | 50.44 |  |  |  | 50.44
GIFFEN 1106 | 253151106 | 2.17 |  |  |  | 2.17
GIFFEN 1107 | 253151107 | 2.65 |  |  |  | 2.65
GILL 0401 | 13550401 | 3.25 |  |  |  | 3.25
GILL 0402 | 13550402 | 3.92 |  |  |  | 3.92
GIRVAN 1101 | 103401101 | 106.5 | 42.25 | 58.87 |  | 5.38
GIRVAN 1102 | 103401102 | 76.13 | 33.58 | 10.82 |  | 31.73
GLENN 1101 | 102601101 | 137.02 |  | 0.26 |  | 136.76
GLENWOOD 0404 | 24090404 | 6.06 |  |  |  | 6.06
GLENWOOD 0405 | 24090405 | 5.74 |  |  |  | 5.74
GLENWOOD 0406 | 24090406 | 2.31 |  |  |  | 2.31
GLENWOOD 1101 | 24091101 | 5.42 |  |  |  | 5.42
GLENWOOD 1102 | 24091102 | 7.17 |  |  |  | 7.17
GOLDTREE 1105 | 182581105 | 14.64 |  | 6.84 |  | 7.8
GOLDTREE 1107 | 182581107 | 3.53 |  | 0.94 |  | 2.59
GOLDTREE 1108 | 182581108 | 21.57 |  | 3.45 |  | 18.12
GONZALES 1101 | 182131101 | 25.94 |  | 3.89 |  | 22.05
GONZALES 1102 | 182131102 | 0.72 |  |  |  | 0.72
GONZALES 1103 | 182131103 | 6.69 |  |  |  | 6.69
GONZALES 1104 | 182131104 | 54.29 |  | 0.74 |  | 53.55
GOOSE LAKE 1101 | 254201101 | 0.54 |  |  |  | 0.54
GOOSE LAKE 1103 | 254201103 | 74.16 |  |  |  | 74.16
GOOSE LAKE 1106 | 254201106 | 66.48 |  |  |  | 66.48
GOOSE LAKE 2104 | 254202104 | 47.72 |  |  |  | 47.72
GRAND ISLAND 2223 | 62462223 | 96.76 |  |  |  | 96.76
GRAND ISLAND 2224 | 62462224 | 63.62 |  |  |  | 63.62
GRAND ISLAND 2225 | 62462225 | 65.18 |  |  |  | 65.18
GRAND ISLAND 2226 | 62462226 | 20.89 |  |  |  | 20.89
GRAND ISLAND 2227 | 62462227 | 157.79 |  |  |  | 157.79
GRANT 1102 | 14381102 | 4.42 |  |  |  | 4.42
GRANT 1103 | 14381103 | 4.19 |  |  |  | 4.19
GRANT 1104 | 14381104 | 19.29 |  |  |  | 19.29
GRANT 1105 | 14381105 | 13.96 |  |  |  | 13.96
GRANT 1106 | 14381106 | 17.02 |  |  |  | 17.02
GRANT 1107 | 14381107 | 5.37 |  |  |  | 5.37
GRANT 1108 | 14381108 | 22.69 |  |  |  | 22.69
GRASS VALLEY 1101 | 152031101 | 18.82 | 2.31 | 13.78 |  | 2.73
GRASS VALLEY 1102 | 152031102 | 5.79 |  | 0.06 |  | 5.73
GRASS VALLEY 1103 | 152031103 | 87.67 |  | 86.04 |  | 1.63
GRAYS FLAT 0401 | 102530401 | 10.63 |  | 10.63 |  | 0
GREEN VALLEY 2101 | 83192101 | 155.9 | 32.68 | 7.64 |  | 115.58
GREEN VALLEY 2102 | 83192102 | 45.84 |  |  |  | 45.84
GREEN VALLEY 2103 | 83192103 | 68.74 |  |  |  | 68.74
GREEN VALLEY 2104 | 83192104 | 30.18 |  |  |  | 30.18
GREENBRAE 1101 | 43091101 | 1.82 |  |  |  | 1.82
GREENBRAE 1102 | 43091102 | 13.42 | 5.73 |  |  | 7.69
GREENBRAE 1103 | 43091103 | 7.41 |  | 0.75 |  | 6.66
GREENBRAE 1104 | 43091104 | 18.38 |  | 0.18 |  | 18.2
GUALALA 1111 | 42841111 | 37.83 |  | 33.18 |  | 4.65
GUALALA 1112 | 42841112 | 47.39 |  | 42.92 |  | 4.47
GUERNSEY 1101 | 252661101 | 43.38 |  |  |  | 43.38
GUERNSEY 1102 | 252661102 | 41.59 |  |  |  | 41.59
GUERNSEY 1103 | 252661103 | 31.65 |  |  |  | 31.65
GUERNSEY 1104 | 252661104 | 29.96 |  |  |  | 29.96
GUERNSEY 1105 | 252661105 | 2.17 |  |  |  | 2.17
GUERNSEY 1106 | 252661106 | 36.97 |  |  |  | 36.97
GUERNSEY 1108 | 252661108 | 2.17 |  |  |  | 2.17
GUSTINE 1101 | 163111101 | 79.66 |  |  |  | 79.66
GUSTINE 1102 | 163111102 | 137.4 |  |  |  | 137.4
HALF MOON BAY 1101 | 24101101 | 47.06 | 12.56 | 12.37 |  | 22.13
HALF MOON BAY 1102 | 24101102 | 48.04 | 5.57 | 2.86 |  | 39.61
HALF MOON BAY 1103 | 24101103 | 166.4 | 1.42 | 122.3 |  | 42.68
HALSEY 1101 | 152241101 | 68.69 |  | 68.69 |  | 0
HALSEY 1102 | 152241102 | 59.63 |  | 49.36 |  | 10.27
HAMILTON A 1101 | 102121101 | 37.39 |  |  |  | 37.39
HAMILTON A 1102 | 102121102 | 43.6 |  |  |  | 43.6
HAMILTON BRANCH 1101 | 102361101 | 34.47 |  | 24.32 |  | 10.15
HAMMER 1101 | 163301101 | 5.5 |  |  |  | 5.5
HAMMER 1102 | 163301102 | 2.76 |  |  |  | 2.76
HAMMER 1103 | 163301103 | 3.75 |  |  |  | 3.75
HAMMER 1104 | 163301104 | 10.64 |  |  |  | 10.64
HAMMER 1105 | 163301105 | 10.83 |  |  |  | 10.83
HAMMER 1106 | 163301106 | 7.23 |  |  |  | 7.23
HAMMER 1108 | 163301108 | 6.01 |  |  |  | 6.01
HAMMER 1109 | 163301109 | 3.85 |  |  |  | 3.85
HAMMONDS 1101 | 253401101 | 35.11 |  |  |  | 35.11
HAMMONDS 1102 | 253401102 | 44.27 |  |  |  | 44.27
HAMMONDS 1104 | 253401104 | 66.3 |  |  |  | 66.3
HARDING 0401 | 163310401 | 1.01 |  |  |  | 1.01
HARDING 0402 | 163310402 | 3.86 |  |  |  | 3.86
HARDING 0403 | 163310403 | 1.54 |  |  |  | 1.54
HARDING 0404 | 163310404 | 2.7 |  |  |  | 2.7
HARDING 0405 | 163310405 | 2.9 |  |  |  | 2.9
HARDING 0406 | 163310406 | 3.16 |  |  |  | 3.16
HARDWICK 1101 | 253711101 | 71.93 |  |  |  | 71.93
HARDWICK 1102 | 253711102 | 97.84 |  |  |  | 97.84
HARRIS 1108 | 192431108 | 32.62 |  | 1.71 |  | 30.91
HARRIS 1109 | 192431109 | 49.85 |  | 14.29 |  | 35.56
HARTER 1102 | 152851102 | 4.39 |  |  |  | 4.39
HARTER 1104 | 152851104 | 7.24 |  |  |  | 7.24
HARTER 1105 | 152851105 | 23.51 |  |  |  | 23.51
HARTER 1106 | 152851106 | 2.12 |  |  |  | 2.12
HARTER 1107 | 152851107 | 10.23 |  |  |  | 10.23
HARTLEY 1101 | 43211101 | 72.18 |  | 34.7 |  | 37.48
HARTLEY 1102 | 43211102 | 27.56 |  | 4.06 |  | 23.5
HATTON 1101 | 182291101 | 32.97 | 2.67 | 17.71 |  | 12.59
HATTON 1102 | 182291102 | 22.45 |  | 11.39 |  | 11.06
HAYWARD O 0401 | 12240401 | 3.3 |  |  |  | 3.3
HAYWARD O 0402 | 12240402 | 3.71 |  |  |  | 3.71
HENRIETTA 1104 | 252681104 | 36 |  |  |  | 36
HENRIETTA 1106 | 252681106 | 45.91 |  |  |  | 45.91
HENRIETTA 1108 | 252681108 | 22.66 |  |  |  | 22.66
HENRIETTA 1110 | 252681110 | 86.11 |  |  |  | 86.11
HERDLYN 1102 | 163741102 | 76.17 |  |  |  | 76.17
HERDLYN 1103 | 163741103 | 99.21 |  |  |  | 99.21
HICKS 1108 | 83431108 | 12.13 |  |  |  | 12.13
HICKS 1109 | 83431109 | 14.97 |  |  |  | 14.97
HICKS 1110 | 83431110 | 8 |  |  |  | 8
HICKS 1111 | 83431111 | 21.87 |  |  |  | 21.87
HICKS 1112 | 83431112 | 4.43 |  |  |  | 4.43
HICKS 1113 | 83431113 | 19.24 |  |  |  | 19.24
HICKS 1114 | 83431114 | 9.51 |  |  |  | 9.51
HICKS 1115 | 83431115 | 15.41 |  | 0.05 |  | 15.36
HICKS 1116 | 83431116 | 34.25 |  | 13.95 |  | 20.3
HICKS 2101 | 83432101 | 42.38 | 2.24 | 10.16 |  | 29.98
HICKS 2102 | 83432102 | 3.9 |  |  |  | 3.9
HICKS 2103 | 83432103 | 21.55 | 5.28 | 2.09 |  | 14.18
HICKS 2105 | 83432105 | 9.68 |  |  |  | 9.68
HICKS 2111 | 83432111 | 4.57 |  |  |  | 4.57
HIGGINS 1103 | 152691103 | 148.33 |  | 143.51 |  | 4.82
HIGGINS 1104 | 152691104 | 87.96 |  | 72.5 |  | 15.46
HIGGINS 1107 | 152691107 | 32.53 |  | 17.87 |  | 14.66
HIGGINS 1108 | 152691108 | 0.02 |  |  |  | 0.02
HIGGINS 1109 | 152691109 | 86.65 |  | 82.85 |  | 3.8
HIGGINS 1110 | 152691110 | 57.25 |  | 48.9 |  | 8.35
HIGHLANDS 1101 | 43361101 | 0.03 |  | 0.03 |  | 0
HIGHLANDS 1102 | 43361102 | 64.29 | 10.7 | 29.29 |  | 24.3
HIGHLANDS 1103 | 43361103 | 123.89 |  | 110.34 |  | 13.55
HIGHLANDS 1104 | 43361104 | 29.23 |  | 11.91 |  | 17.32
HIGHWAY 1101 | 42651101 | 11.19 |  |  |  | 11.19
HIGHWAY 1102 | 42651102 | 19.88 |  |  |  | 19.88
HIGHWAY 1103 | 42651103 | 6.3 |  |  |  | 6.3
HIGHWAY 1104 | 42651104 | 9.56 |  |  |  | 9.56
HIGHWAY 1105 | 42651105 | 1.04 |  |  |  | 1.04
HIGHWAY 1106 | 42651106 | 15.26 |  |  |  | 15.26
HILLSDALE 0401 | 24110401 | 7.46 |  |  |  | 7.46
HILLSDALE 0402 | 24110402 | 8.02 |  |  |  | 8.02
HILLSDALE 0403 | 24110403 | 3.27 |  |  |  | 3.27
HILLSDALE 0404 | 24110404 | 5.69 |  |  |  | 5.69
HILLSDALE 0405 | 24110405 | 5.9 |  |  |  | 5.9
HOLLISTER 2101 | 182492101 | 25.56 |  |  |  | 25.56
HOLLISTER 2102 | 182492102 | 108.31 |  | 27.73 |  | 80.58
HOLLISTER 2103 | 182492103 | 13.55 |  |  |  | 13.55
HOLLISTER 2104 | 182492104 | 122.85 |  | 6.34 |  | 116.51
HOLLISTER 2105 | 182492105 | 164.92 |  | 64.36 |  | 100.56
HOLLISTER 2106 | 182492106 | 39.29 |  | 8.09 |  | 31.2
HOLLYWOOD 0401 | 13170401 | 5.36 |  | 2.78 |  | 2.58
HONCUT 1101 | 103211101 | 115.13 |  |  |  | 115.13
HONCUT 1102 | 103211102 | 149.07 |  | 2.57 |  | 146.5
HOOPA 1101 | 192401101 | 136.98 | 4.88 | 99.7 |  | 32.4
HOPLAND 1101 | 42251101 | 130.72 |  | 81.59 |  | 49.13
HORSESHOE 1101 | 152571101 | 36.25 |  | 4.93 |  | 31.32
HORSESHOE 1102 | 152571102 | 14.83 |  |  |  | 14.83
HORSESHOE 1103 | 152571103 | 5.24 |  |  |  | 5.24
HORSESHOE 1104 | 152571104 | 11.65 |  | 1.97 |  | 9.68
HORSESHOE 1105 | 152571105 | 2.27 |  |  |  | 2.27
HORSESHOE 1106 | 152571106 | 15.3 |  |  |  | 15.3
HUMBOLDT BAY 1101 | 192341101 | 12.9 |  |  |  | 12.9
HUMBOLDT BAY 1102 | 192341102 | 41.57 |  | 6.33 |  | 35.24
HUNTERS POINT (P) 1101 | 22331101 | 3.73 |  |  |  | 3.73
HUNTERS POINT (P) 1102 | 22331102 | 8.28 |  |  |  | 8.28
HUNTERS POINT (P) 1103 | 22331103 | 5.78 |  |  |  | 5.78
HUNTERS POINT (P) 1104 | 22331104 | 3.62 |  |  |  | 3.62
HUNTERS POINT (P) 1105 | 22331105 | 10.4 |  |  |  | 10.4
HUNTERS POINT (P) 1106 | 22331106 | 1.53 |  |  |  | 1.53
HUNTERS POINT (P) 1107 | 22331107 | 5.26 |  |  |  | 5.26
HUNTERS POINT (P) 1108 | 22331108 | 5.72 |  |  |  | 5.72
HUNTERS POINT (P) 1109 | 22331109 | 1.61 |  |  |  | 1.61
HURON 1106 | 253161106 | 17.05 |  |  |  | 17.05
HURON 1107 | 253161107 | 0.34 |  |  |  | 0.34
HURON 1108 | 253161108 | 10.15 |  |  |  | 10.15
HURON 1109 | 253161109 | 0.34 |  |  |  | 0.34
HURON 1112 | 253161112 | 13.8 |  |  |  | 13.8
HURON 1116 | 253161116 | 19.73 |  |  |  | 19.73
IGNACIO 1101 | 42481101 | 11.63 | 0.5 | 5.72 |  | 5.41
IGNACIO 1102 | 42481102 | 8.52 |  |  |  | 8.52
IGNACIO 1103 | 42481103 | 2.77 |  | 0.62 |  | 2.15
IGNACIO 1104 | 42481104 | 57.17 |  | 6.33 |  | 50.84
IGNACIO 1105 | 42481105 | 20.2 |  | 4.75 |  | 15.45
INDIAN FLAT 1104 | 252691104 | 16.12 |  | 16.12 |  | 0
INDUSTRIAL ACRES 0411 | 182300411 | 2.02 |  |  |  | 2.02
INDUSTRIAL ACRES 0412 | 182300412 | 9.79 |  |  |  | 9.79
INDUSTRIAL ACRES 0413 | 182300413 | 3.71 |  |  |  | 3.71
INDUSTRIAL ACRES 0415 | 182300415 | 1.43 |  |  |  | 1.43
IONE 1101 | 163881101 | 28.99 |  | 14.89 |  | 14.1
JACINTO 1101 | 102851101 | 77.3 |  |  |  | 77.3
JACINTO 1102 | 102851102 | 80.77 |  |  |  | 80.77
JACOBS CORNER 1101 | 254771101 | 62.36 |  |  |  | 62.36
JACOBS CORNER 1102 | 254771102 | 51.45 |  |  |  | 51.45
JAMESON 1101 | 63801101 | 0.01 |  |  |  | 0.01
JAMESON 1102 | 63801102 | 20.16 |  | 8 |  | 12.16
JAMESON 1103 | 63801103 | 10.84 |  | 2.19 |  | 8.65
JAMESON 1104 | 63801104 | 0.08 |  |  |  | 0.08
JAMESON 1105 | 63801105 | 63.85 |  | 16.19 |  | 47.66
JANES CREEK 1101 | 192391101 | 29.32 |  |  |  | 29.32
JANES CREEK 1102 | 192391102 | 6.26 |  |  |  | 6.26
JANES CREEK 1103 | 192391103 | 42.51 |  |  |  | 42.51
JANES CREEK 1104 | 192391104 | 2.57 |  |  |  | 2.57
JARVIS 1101 | 13501101 | 13.72 |  | 0.58 |  | 13.14
JARVIS 1103 | 13501103 | 3.42 |  |  |  | 3.42
JARVIS 1104 | 13501104 | 4.42 |  |  |  | 4.42
JARVIS 1105 | 13501105 | 6.84 |  |  |  | 6.84
JARVIS 1106 | 13501106 | 4.78 |  |  |  | 4.78
JARVIS 1108 | 13501108 | 17.68 |  | 0.7 |  | 16.98
JARVIS 1109 | 13501109 | 4.15 |  |  |  | 4.15
JARVIS 1110 | 13501110 | 5.96 |  |  |  | 5.96
JARVIS 1111 | 13501111 | 18.99 | 0.91 | 0.03 |  | 18.05
JARVIS 1112 | 13501112 | 7.24 |  |  |  | 7.24
JERSEY ISLAND 0401 | 18320401 | 2.88 |  |  |  | 2.88
JESSUP 1101 | 103441101 | 79.63 | 0.2 | 63.69 |  | 15.74
JESSUP 1102 | 103441102 | 86.62 |  | 53.34 |  | 33.28
JESSUP 1103 | 103441103 | 38.12 |  | 3.92 |  | 34.2
JOLON 1102 | 182981102 | 105.89 |  | 65.47 |  | 40.42
JOLON 1103 | 182981103 | 18.57 |  | 12.51 |  | 6.06
JUDAH 0401 | 22400401 | 3.69 |  |  |  | 3.69
JUDAH 0402 | 22400402 | 2.14 |  |  |  | 2.14
KANAKA 1101 | 103221101 | 72.46 | 45.63 | 26.47 |  | 0.36
KEARNEY 1104 | 252701104 | 73.13 |  |  |  | 73.13
KEARNEY 1106 | 252701106 | 39.27 |  |  |  | 39.27
KEARNEY 1110 | 252701110 | 50.46 |  |  |  | 50.46
KEARNEY 1113 | 252701113 | 0.63 |  |  |  | 0.63
KEARNEY 1114 | 252701114 | 13.36 |  |  |  | 13.36
KERCKHOFF 1101 | 252561101 | 34.21 |  | 34.21 |  | 0
KERMAN 1101 | 252711101 | 145.36 |  |  |  | 145.36
KERMAN 1102 | 252711102 | 58.45 |  |  |  | 58.45
KERMAN 1103 | 252711103 | 56.38 |  |  |  | 56.38
KERMAN 1104 | 252711104 | 65.97 |  |  |  | 65.97
KERMAN 1106 | 252711106 | 75.66 |  |  |  | 75.66
KERMAN 1108 | 252711108 | 28.11 |  |  |  | 28.11
KERN OIL 1103 | 252721103 | 11.39 |  |  |  | 11.39
KERN OIL 1104 | 252721104 | 39.14 |  |  |  | 39.14
KERN OIL 1106 | 252721106 | 44.03 |  | 1.31 |  | 42.72
KERN OIL 1107 | 252721107 | 21.16 |  |  |  | 21.16
KERN OIL 1108 | 252721108 | 7.69 |  |  |  | 7.69
KERN OIL 1109 | 252721109 | 11.24 |  |  |  | 11.24
KERN OIL 1110 | 252721110 | 8.55 |  |  |  | 8.55
KERN OIL 1112 | 252721112 | 0.07 |  |  |  | 0.07
KERN OIL 1114 | 252721114 | 21.52 |  |  |  | 21.52
KERN OIL 1116 | 252721116 | 4.59 |  |  |  | 4.59
KERN POWER 2101 | 255262101 | 1.99 |  |  |  | 1.99
KERN POWER 2102 | 255262102 | 4.35 |  |  |  | 4.35
KERN POWER 2103 | 255262103 | 12.51 |  |  |  | 12.51
KERN POWER 2104 | 255262104 | 5.06 |  |  |  | 5.06
KERN POWER 2105 | 255262105 | 12.54 |  |  |  | 12.54
KESWICK 1101 | 103451101 | 51.27 | 47.91 | 3.31 |  | 0.05
KETTLEMAN HILLS 1101 | 252731101 | 38.7 |  |  |  | 38.7
KETTLEMAN HILLS 2104 | 252732104 | 34.6 |  |  |  | 34.6
KING CITY 1101 | 182031101 | 6.91 |  |  |  | 6.91
KING CITY 1102 | 182031102 | 21.54 |  |  |  | 21.54
KING CITY 1103 | 182031103 | 27.78 |  | 17.75 |  | 10.03
KING CITY 1104 | 182031104 | 14.02 |  |  |  | 14.02
KING CITY 1105 | 182031105 | 3.09 |  |  |  | 3.09
KING CITY 1106 | 182031106 | 71.72 |  |  |  | 71.72
KING CITY 1107 | 182031107 | 0.02 |  |  |  | 0.02
KING CITY 1108 | 182031108 | 0.02 |  |  |  | 0.02
KINGSBURG 1102 | 252241102 | 15.54 |  |  |  | 15.54
KINGSBURG 1108 | 252241108 | 41.31 |  |  |  | 41.31
KINGSBURG 1110 | 252241110 | 86.22 |  |  |  | 86.22
KINGSBURG 1111 | 252241111 | 81.82 |  |  |  | 81.82
KINGSBURG 1112 | 252241112 | 14.15 |  |  |  | 14.15
KINGSBURG 1113 | 252241113 | 51.34 |  |  |  | 51.34
KINGSBURG 1114 | 252241114 | 18.59 |  |  |  | 18.59
KINGSBURG 1116 | 252241116 | 113.79 |  |  |  | 113.79
KIRKER 2103 | 14452103 | 8.01 |  |  |  | 8.01
KIRKER 2104 | 14452104 | 17.21 |  | 4.01 |  | 13.2
KIRKER 2105 | 14452105 | 9.31 |  |  |  | 9.31
KIRKER 2106 | 14452106 | 16.23 |  |  |  | 16.23
KIRKER 2107 | 14452107 | 8.05 |  |  |  | 8.05
KIRKER 2108 | 14452108 | 9.57 |  |  |  | 9.57
KIRKER 2109 | 14452109 | 8.62 |  |  |  | 8.62
KNIGHTS LANDING 1101 | 62721101 | 45.1 |  |  |  | 45.1
KNIGHTS LANDING 1102 | 62721102 | 118.89 |  |  |  | 118.89
KONOCTI 1102 | 43311102 | 145.87 | 64.06 | 61.13 |  | 20.68
KONOCTI 1108 | 43311108 | 33.04 |  | 20.4 |  | 12.64
LAKEVIEW 1102 | 253411102 | 52.33 |  |  |  | 52.33
LAKEVIEW 1103 | 253411103 | 22.68 |  |  |  | 22.68
LAKEVIEW 1106 | 253411106 | 36.9 |  |  |  | 36.9
LAKEVIEW 1107 | 253411107 | 26.06 |  |  |  | 26.06
LAKEVILLE 1101 | 43371101 | 19.67 |  |  |  | 19.67
LAKEVILLE 1102 | 43371102 | 50.36 | 0.07 | 18.06 |  | 32.23
LAKEVILLE 1105 | 43371105 | 4.22 |  |  |  | 4.22
LAKEWOOD 1101 | 13531101 | 0.72 |  |  |  | 0.72
LAKEWOOD 1102 | 13531102 | 9.57 |  | 0.1 |  | 9.47
LAKEWOOD 1103 | 13531103 | 2.57 |  |  |  | 2.57
LAKEWOOD 1104 | 13531104 | 11.74 |  |  |  | 11.74
LAKEWOOD 2107 | 13532107 | 33.31 |  | 7.77 |  | 25.54
LAKEWOOD 2108 | 13532108 | 0.53 |  |  |  | 0.53
LAKEWOOD 2109 | 13532109 | 7.27 | 0.42 |  |  | 6.85
LAKEWOOD 2110 | 13532110 | 22.68 |  |  |  | 22.68
LAKEWOOD 2111 | 13532111 | 2.29 |  |  |  | 2.29
LAKEWOOD 2112 | 13532112 | 8.9 |  |  |  | 8.9
LAKEWOOD 2223 | 13532223 | 9.13 |  |  |  | 9.13
LAKEWOOD 2224 | 13532224 | 31.47 | 0.82 |  |  | 30.65
LAKEWOOD 2225 | 13532225 | 3.34 |  |  |  | 3.34
LAKEWOOD 2226 | 13532226 | 8 |  |  |  | 8
LAKEWOOD 2227 | 13532227 | 7.89 | 0.03 |  |  | 7.86
LAMMERS 1101 | 162771101 | 9.67 |  |  |  | 9.67
LAMMERS 1102 | 162771102 | 3.55 |  |  |  | 3.55
LAMMERS 1103 | 162771103 | 9.36 |  |  |  | 9.36
LAMMERS 1105 | 162771105 | 1.79 |  |  |  | 1.79
LAMMERS 1106 | 162771106 | 2.29 |  |  |  | 2.29
LAMMERS 1107 | 162771107 | 9.14 |  |  |  | 9.14
LAMMERS 1108 | 162771108 | 1.11 |  |  |  | 1.11
LAMONT 1102 | 253911102 | 69.13 |  | 3.49 |  | 65.64
LAMONT 1103 | 253911103 | 26.85 |  |  |  | 26.85
LAMONT 1104 | 253911104 | 53.32 |  | 1.43 |  | 51.89
LAMONT 1105 | 253911105 | 37.1 |  |  |  | 37.1
LAMONT 1106 | 253911106 | 22.49 |  |  |  | 22.49
LAMONT 1107 | 253911107 | 46.12 |  |  |  | 46.12
LARKIN (Y) 1107 | 22801107 | 2.36 |  |  |  | 2.36
LARKIN (Y) 1108 | 22801108 | 0.11 |  |  |  | 0.11
LARKIN (Y) 1109 | 22801109 | 0.3 |  |  |  | 0.3
LARKIN (Y) 1110 | 22801110 | 0.99 |  |  |  | 0.99
LARKIN (Y) 1111 | 22801111 | 0.12 |  |  |  | 0.12
LARKIN (Y) 1119 | 22801119 | 1.72 |  |  |  | 1.72
LARKIN (Y) 1120 | 22801120 | 2.1 |  |  |  | 2.1
LARKIN (Y) 1127 | 22801127 | 1.53 |  |  |  | 1.53
LARKIN (Y) 1128 | 22801128 | 0.11 |  |  |  | 0.11
LARKIN (Y) 1135 | 22801135 | 1.65 |  |  |  | 1.65
LARKIN (Y) 1136 | 22801136 | 1.29 |  |  |  | 1.29
LARKIN (Y) 1137 | 22801137 | 0.01 |  |  |  | 0.01
LARKIN (Y) 1138 | 22801138 | 1.48 |  |  |  | 1.48
LARKIN (Y) 1140 | 22801140 | 0.08 |  |  |  | 0.08
LARKIN (Y) 1141 | 22801141 | 0.03 |  |  |  | 0.03
LAS GALLINAS A 1103 | 42991103 | 5.28 |  |  |  | 5.28
LAS GALLINAS A 1104 | 42991104 | 12.95 |  | 0.28 |  | 12.67
LAS GALLINAS A 1105 | 42991105 | 21.48 | 8.41 | 2.85 |  | 10.22
LAS GALLINAS A 1106 | 42991106 | 15.83 | 0.02 | 1.16 |  | 14.65
LAS GALLINAS A 1107 | 42991107 | 8.05 |  | 0.02 |  | 8.03
LAS PALMAS 1101 | 254921101 | 0.27 |  |  |  | 0.27
LAS POSITAS 2103 | 14402103 | 2.99 |  |  |  | 2.99
LAS POSITAS 2104 | 14402104 | 11.37 |  |  |  | 11.37
LAS POSITAS 2105 | 14402105 | 3.76 |  |  |  | 3.76
LAS POSITAS 2106 | 14402106 | 16.19 |  |  |  | 16.19
LAS POSITAS 2107 | 14402107 | 11.24 |  |  |  | 11.24
LAS POSITAS 2108 | 14402108 | 19.96 |  | 6.85 |  | 13.11
LAS POSITAS 2109 | 14402109 | 13.26 |  |  |  | 13.26
LAS POSITAS 2110 | 14402110 | 19.65 |  |  |  | 19.65
LAS PULGAS 0401 | 24120401 | 8.88 |  | 1.97 |  | 6.91
LAS PULGAS 0402 | 24120402 | 2.57 |  |  |  | 2.57
LAS PULGAS 0403 | 24120403 | 7.84 |  |  |  | 7.84
LAS PULGAS 0404 | 24120404 | 4.05 |  |  |  | 4.05
LATHROP 0402 | 163030402 | 0.04 |  |  |  | 0.04
LAURELES 1111 | 182371111 | 106.2 | 5.72 | 99.39 |  | 1.09
LAURELES 1112 | 182371112 | 43.16 |  | 33.05 |  | 10.11
LAWNDALE 0401 | 22440401 | 4.73 |  |  |  | 4.73
LAWNDALE 0402 | 22440402 | 4.75 |  |  |  | 4.75
LAWRENCE 1102 | 83421102 | 0.08 |  |  |  | 0.08
LAWRENCE 1103 | 83421103 | 0.23 |  |  |  | 0.23
LAWRENCE 1104 | 83421104 | 9.34 |  |  |  | 9.34
LAWRENCE 1105 | 83421105 | 1.07 |  |  |  | 1.07
LAWRENCE 1106 | 83421106 | 2.77 |  |  |  | 2.77
LAWRENCE 1107 | 83421107 | 4.63 |  |  |  | 4.63
LAWRENCE 1108 | 83421108 | 0.86 |  |  |  | 0.86
LAWRENCE 1109 | 83421109 | 1.96 |  |  |  | 1.96
LAWRENCE 1110 | 83421110 | 4.92 |  |  |  | 4.92
LAWRENCE 1111 | 83421111 | 3.71 |  |  |  | 3.71
LAWRENCE 1112 | 83421112 | 11.06 |  |  |  | 11.06
LAWRENCE 1113 | 83421113 | 5.65 |  |  |  | 5.65
LAYTONVILLE 1101 | 42681101 | 79.53 |  | 51.72 |  | 27.81
LAYTONVILLE 1102 | 42681102 | 125.38 | 3.39 | 107.15 |  | 14.84
LE GRAND 1104 | 255361104 | 56.91 |  |  |  | 56.91
LE GRAND 1106 | 255361106 | 59.89 |  |  |  | 59.89
LE GRAND 1110 | 255361110 | 91.79 |  |  |  | 91.79
LE GRAND 1112 | 255361112 | 68.74 |  |  |  | 68.74
LEMOORE 1101 | 253601101 | 41.55 |  |  |  | 41.55
LEMOORE 1102 | 253601102 | 11.54 |  |  |  | 11.54
LEMOORE 1103 | 253601103 | 14.43 |  |  |  | 14.43
LEMOORE 1104 | 253601104 | 49.88 |  |  |  | 49.88
LEMOORE 1105 | 253601105 | 12.03 |  |  |  | 12.03
LERDO 1110 | 253491110 | 11.91 |  |  |  | 11.91
LERDO 1111 | 253491111 | 36.22 |  |  |  | 36.22
LERDO 1112 | 253491112 | 23.94 |  |  |  | 23.94
LERDO 1113 | 253491113 | 38.51 |  |  |  | 38.51
LERDO 1114 | 253491114 | 9.9 |  |  |  | 9.9
LERDO 1115 | 253491115 | 15.88 |  |  |  | 15.88
LERDO 1116 | 253491116 | 42.26 |  |  |  | 42.26
LINCOLN 1101 | 153701101 | 50.24 |  | 16.09 |  | 34.15
LINCOLN 1102 | 153701102 | 9.58 |  |  |  | 9.58
LINCOLN 1104 | 153701104 | 136.5 |  | 33.43 |  | 103.07
LINCOLN 1105 | 153701105 | 32.24 |  |  |  | 32.24
LINCOLN 2108 | 153702108 | 1.63 |  |  |  | 1.63
LINCOLN 2109 | 153702109 | 0.86 |  |  |  | 0.86
LINDEN 1101 | 162071101 | 34.75 |  |  |  | 34.75
LINDEN 1103 | 162071103 | 60.06 |  |  |  | 60.06
LINDEN 1104 | 162071104 | 56 |  |  |  | 56
LIVE OAK 1101 | 153771101 | 28.43 |  |  |  | 28.43
LIVE OAK 1102 | 153771102 | 25.68 |  |  |  | 25.68
LIVE OAK 1104 | 153771104 | 112.27 |  |  |  | 112.27
LIVERMORE 1101 | 12141101 | 6.04 |  |  |  | 6.04
LIVERMORE 1102 | 12141102 | 4.22 |  |  |  | 4.22
LIVERMORE 1103 | 12141103 | 4.61 |  |  |  | 4.61
LIVERMORE 1104 | 12141104 | 8.63 |  |  |  | 8.63
LIVINGSTON 1101 | 252261101 | 103.25 |  |  |  | 103.25
LIVINGSTON 1102 | 252261102 | 13.62 |  |  |  | 13.62
LIVINGSTON 1104 | 252261104 | 50.61 |  |  |  | 50.61
LIVINGSTON 1105 | 252261105 | 88.76 |  |  |  | 88.76
LIVINGSTON 1106 | 252261106 | 55.35 |  |  |  | 55.35
LLAGAS 2101 | 83182101 | 101.98 |  | 21.37 |  | 80.61
LLAGAS 2102 | 83182102 | 12.63 |  |  |  | 12.63
LLAGAS 2103 | 83182103 | 16.71 |  |  |  | 16.71
LLAGAS 2104 | 83182104 | 30.02 |  | 2.68 |  | 27.34
LLAGAS 2105 | 83182105 | 17.55 | 0.12 | 0.46 |  | 16.97
LLAGAS 2106 | 83182106 | 32.26 |  | 1.18 |  | 31.08
LLAGAS 2107 | 83182107 | 22.28 | 3.63 | 2.64 |  | 16.01
LOCKEFORD 2101 | 163682101 | 90.85 |  |  |  | 90.85
LOCKEFORD 2102 | 163682102 | 242.45 |  |  |  | 242.45
LOCKHEED NO 2 1103 | 83001103 | 0.52 |  |  |  | 0.52
LOCKHEED NO 2 1106 | 83001106 | 0.37 |  |  |  | 0.37
LOCKHEED NO 2 1107 | 83001107 | 0.77 |  |  |  | 0.77
LOCKHEED NO 2 1108 | 83001108 | 1.25 |  |  |  | 1.25
LODI 1101 | 162111101 | 44.39 |  |  |  | 44.39
LODI 1102 | 162111102 | 97.07 |  |  |  | 97.07
LOGAN CREEK 2101 | 103142101 | 163.28 |  |  |  | 163.28
LOGAN CREEK 2102 | 103142102 | 240.91 |  | 3.48 |  | 237.43
LOGAN CREEK 2103 | 103142103 | 3.17 |  |  |  | 3.17
LOGAN CREEK 2199 | 103142199 | 0.03 |  |  |  | 0.03
LONE TREE 2101 | 13232101 | 1.15 |  |  |  | 1.15
LONE TREE 2102 | 13232102 | 16.62 |  |  |  | 16.62
LONE TREE 2105 | 13232105 | 21.8 |  | 10.71 |  | 11.09
LOS ALTOS 1103 | 82241103 | 6.79 |  |  |  | 6.79
LOS ALTOS 1104 | 82241104 | 12.93 |  |  |  | 12.93
LOS ALTOS 1105 | 82241105 | 1.81 |  |  |  | 1.81
LOS ALTOS 1106 | 82241106 | 9.93 |  |  |  | 9.93
LOS ALTOS 1107 | 82241107 | 2.96 |  |  |  | 2.96
LOS COCHES 1101 | 182151101 | 24.47 |  | 2.29 |  | 22.18
LOS COCHES 1102 | 182151102 | 28.95 |  |  |  | 28.95
LOS GATOS 1101 | 82021101 | 20.95 |  | 11.8 |  | 9.15
LOS GATOS 1102 | 82021102 | 6.1 |  | 1.1 |  | 5
LOS GATOS 1106 | 82021106 | 70.61 | 67.35 | 2.43 |  | 0.83
LOS GATOS 1107 | 82021107 | 93.96 | 80.52 | 12.66 |  | 0.78
LOS GATOS 1108 | 82021108 | 6.17 | 1.13 | 3.28 |  | 1.76
LOS MOLINOS 1101 | 103481101 | 55.79 |  | 0.19 |  | 55.6
LOS MOLINOS 1102 | 103481102 | 49.36 |  |  |  | 49.36
LOS OSITOS 2101 | 182082101 | 33.71 |  |  |  | 33.71
LOS OSITOS 2102 | 182082102 | 51.57 |  | 2.48 |  | 49.09
LOS OSITOS 2103 | 182082103 | 177.64 |  | 44.31 |  | 133.33
LOST HILLS 1101 | 254281101 | 0.01 |  |  |  | 0.01
LOW GAP 1101 | 192411101 | 72.3 |  | 70.59 |  | 1.71
LOYOLA 0401 | 82160401 | 8.28 |  |  |  | 8.28
LOYOLA 0403 | 82160403 | 8.84 |  |  |  | 8.84
LOYOLA 1101 | 82161101 | 19.35 |  |  |  | 19.35
LOYOLA 1102 | 82161102 | 50.86 |  | 0.02 |  | 50.84
LUCERNE 1103 | 43351103 | 52.89 |  | 26.64 |  | 26.25
LUCERNE 1106 | 43351106 | 47.64 |  | 36.79 |  | 10.85
MABURY 1101 | 82191101 | 4.18 |  |  |  | 4.18
MABURY 1103 | 82191103 | 7.89 |  |  |  | 7.89
MABURY 1104 | 82191104 | 13.71 |  |  |  | 13.71
MABURY 1105 | 82191105 | 0.85 |  |  |  | 0.85
MABURY 1106 | 82191106 | 15.05 |  |  |  | 15.05
MADERA 1102 | 252761102 | 0.02 |  |  |  | 0.02
MADERA 1104 | 252761104 | 14.64 |  |  |  | 14.64
MADERA 1106 | 252761106 | 8.71 |  |  |  | 8.71
MADERA 1112 | 252761112 | 12.27 |  |  |  | 12.27
MADERA 1114 | 252761114 | 9.68 |  |  |  | 9.68
MADERA 1116 | 252761116 | 2.89 |  |  |  | 2.89
MADERA 1118 | 252761118 | 9.02 |  |  |  | 9.02
MADERA 1119 | 252761119 | 126.08 |  |  |  | 126.08
MADISON 1103 | 63171103 | 72.69 |  |  |  | 72.69
MADISON 1105 | 63171105 | 84.8 |  | 0.35 |  | 84.45
MADISON 2101 | 63172101 | 166.84 |  | 5.25 |  | 161.59
MAGUNDEN 1101 | 252771101 | 19.48 |  |  |  | 19.48
MAGUNDEN 1104 | 252771104 | 5.18 |  |  |  | 5.18
MAGUNDEN 1105 | 252771105 | 13.72 |  |  |  | 13.72
MAGUNDEN 1106 | 252771106 | 16.02 |  |  |  | 16.02
MAGUNDEN 1108 | 252771108 | 30.66 |  | 3.93 |  | 26.73
MAGUNDEN 2108 | 252772108 | 45.23 |  |  |  | 45.23
MAGUNDEN 2109 | 252772109 | 14.41 |  |  |  | 14.41
MAINE PRAIRIE 0401 | 68670401 | 0.06 |  |  |  | 0.06
MALAGA 1101 | 254251101 | 3.55 |  |  |  | 3.55
MALAGA 1102 | 254251102 | 55.39 |  |  |  | 55.39
MALAGA 1103 | 254251103 | 20.18 |  |  |  | 20.18
MALAGA 1104 | 254251104 | 15.37 |  |  |  | 15.37
MALAGA 1105 | 254251105 | 0.64 |  |  |  | 0.64
MALAGA 1106 | 254251106 | 9.25 |  |  |  | 9.25
MALAGA 1107 | 254251107 | 2.65 |  |  |  | 2.65
MALAGA 1108 | 254251108 | 20.04 |  |  |  | 20.04
MALAGA 1109 | 254251109 | 3.31 |  |  |  | 3.31
MALAGA 1110 | 254251110 | 15.38 |  |  |  | 15.38
MALAGA 1111 | 254251111 | 8.89 |  |  |  | 8.89
MANCHESTER 1101 | 253921101 | 11.83 |  |  |  | 11.83
MANCHESTER 1102 | 253921102 | 13.62 |  |  |  | 13.62
MANCHESTER 1103 | 253921103 | 7.17 |  |  |  | 7.17
MANCHESTER 1104 | 253921104 | 3.97 |  |  |  | 3.97
MANCHESTER 1105 | 253921105 | 9.04 |  |  |  | 9.04
MANCHESTER 1106 | 253921106 | 14.91 |  |  |  | 14.91
MANCHESTER 1107 | 253921107 | 8.68 |  |  |  | 8.68
MANCHESTER 1108 | 253921108 | 14.64 |  |  |  | 14.64
MANCHESTER 1109 | 253921109 | 15.79 |  |  |  | 15.79
MANCHESTER 1110 | 253921110 | 14.46 |  |  |  | 14.46
MANCHESTER 1111 | 253921111 | 14.44 |  |  |  | 14.44
MANCHESTER 1112 | 253921112 | 15.95 |  |  |  | 15.95
MANTECA 1701 | 162611701 | 6.15 |  |  |  | 6.15
MANTECA 1702 | 162611702 | 14.06 |  |  |  | 14.06
MANTECA 1703 | 162611703 | 15.7 |  |  |  | 15.7
MANTECA 1704 | 162611704 | 7.55 |  |  |  | 7.55
MANTECA 1705 | 162611705 | 34.85 |  |  |  | 34.85
MANTECA 1706 | 162611706 | 7.49 |  |  |  | 7.49
MANTECA 1707 | 162611707 | 7.94 |  |  |  | 7.94
MANTECA 1708 | 162611708 | 9.7 |  |  |  | 9.7
MAPLE 0401 | 13520401 | 3.66 |  |  |  | 3.66
MAPLE CREEK 1101 | 192101101 | 32.8 |  | 9.28 |  | 23.52
MARICOPA 1101 | 254211101 | 38.36 |  |  |  | 38.36
MARICOPA 1102 | 254211102 | 37.75 |  |  |  | 37.75
MARINA (F) 0401 | 22780401 | 0.53 |  |  |  | 0.53
MARINA (F) 0402 | 22780402 | 0.48 |  |  |  | 0.48
MARINA (F) 0403 | 22780403 | 0.04 |  |  |  | 0.04
MARINA (F) 0404 | 22780404 | 0.37 |  |  |  | 0.37
MARINA (F) 0405 | 22780405 | 0.14 |  |  |  | 0.14
MARINA (F) 0407 | 22780407 | 1.42 |  |  |  | 1.42
MARINA (F) 0408 | 22780408 | 0.52 |  |  |  | 0.52
MARINA (F) 1101 | 22781101 | 0 |  |  |  | 0
MARINA (F) 1102 | 22781102 | 0 |  |  |  | 0
MARINA (F) 1103 | 22781103 | 0.2 |  |  |  | 0.2
MARIPOSA 2101 | 254452101 | 257.85 | 75.47 | 177.45 |  | 4.93
MARIPOSA 2102 | 254452102 | 257.9 | 56.8 | 188.16 |  | 12.94
MARIPOSA REMOTE 0001 | 257010001 | 0.01 |  | 0.01 |  | 0
MARTELL 1101 | 163011101 | 82.53 |  | 70.23 |  | 12.3
MARTELL 1102 | 163011102 | 12.11 |  | 6.88 |  | 5.23
MARTELL 1103 | 163011103 | 29.39 |  | 20.31 |  | 9.08
MARYSVILLE 1102 | 152011102 | 7.44 |  |  |  | 7.44
MARYSVILLE 1103 | 152011103 | 12.03 |  |  |  | 12.03
MARYSVILLE 1104 | 152011104 | 5.54 |  |  |  | 5.54
MARYSVILLE 1105 | 152011105 | 8.6 |  |  |  | 8.6
MARYSVILLE 1106 | 152011106 | 3.53 |  |  |  | 3.53
MARYSVILLE 1107 | 152011107 | 8.52 |  |  |  | 8.52
MARYSVILLE 1108 | 152011108 | 51.56 |  |  |  | 51.56
MAXWELL 1102 | 62881102 | 60.09 |  |  |  | 60.09
MAXWELL 1105 | 62881105 | 88.64 |  | 3.9 |  | 84.74
MAXWELL 1106 | 62881106 | 29.6 |  |  |  | 29.6
MC ARTHUR 1101 | 103491101 | 178.95 |  | 64.9 |  | 114.05
MC ARTHUR 1102 | 103491102 | 30.19 |  | 1.08 |  | 29.11
MC CALL 1101 | 254121101 | 95.02 |  |  |  | 95.02
MC CALL 1102 | 254121102 | 25.11 |  |  |  | 25.11
MC CALL 1103 | 254121103 | 17.18 |  |  |  | 17.18
MC CALL 1104 | 254121104 | 16.64 |  |  |  | 16.64
MC CALL 1105 | 254121105 | 15.14 |  |  |  | 15.14
MC CALL 1106 | 254121106 | 76.93 |  |  |  | 76.93
MC CALL 1107 | 254121107 | 100.02 |  |  |  | 100.02
MC CALL 1108 | 254121108 | 56.04 |  |  |  | 56.04
MC FARLAND 1101 | 253181101 | 14.15 |  |  |  | 14.15
MC FARLAND 1102 | 253181102 | 42.12 |  |  |  | 42.12
MC FARLAND 1104 | 253181104 | 37.95 |  |  |  | 37.95
MC FARLAND 1105 | 253181105 | 19.83 |  |  |  | 19.83
MC KEE 1103 | 83531103 | 21.98 |  | 0.58 |  | 21.4
MC KEE 1104 | 83531104 | 15.57 |  |  |  | 15.57
MC KEE 1105 | 83531105 | 8.32 |  |  |  | 8.32
MC KEE 1106 | 83531106 | 15.19 |  |  |  | 15.19
MC KEE 1107 | 83531107 | 38.03 |  | 2.68 |  | 35.35
MC KEE 1108 | 83531108 | 10.44 |  | 0.66 |  | 9.78
MC KEE 1109 | 83531109 | 1.77 |  |  |  | 1.77
MC KEE 1110 | 83531110 | 1.67 |  |  |  | 1.67
MC KEE 1111 | 83531111 | 26.63 |  | 8.7 |  | 17.93
MC KEE 1112 | 83531112 | 16.68 |  |  |  | 16.68
MC MULLIN 1104 | 254411104 | 62.11 |  |  |  | 62.11
MC MULLIN 1105 | 254411105 | 57.86 |  |  |  | 57.86
MC MULLIN 1106 | 254411106 | 93.72 |  |  |  | 93.72
MCKITTRICK 1101 | 252781101 | 52.72 |  |  |  | 52.72
MEADOW LANE 2102 | 14302102 | 0.01 |  |  |  | 0.01
MEADOW LANE 2103 | 14302103 | 21.46 |  |  |  | 21.46
MEADOW LANE 2104 | 14302104 | 4.17 |  |  |  | 4.17
MEADOW LANE 2105 | 14302105 | 14.37 |  |  |  | 14.37
MEADOW LANE 2106 | 14302106 | 23.43 | 0.74 | 0.11 |  | 22.58
MEADOW LANE 2107 | 14302107 | 8.44 |  |  |  | 8.44
MEADOW LANE 2108 | 14302108 | 23.89 |  |  |  | 23.89
MEADOW LANE 2109 | 14302109 | 0.58 |  |  |  | 0.58
MEADOW LANE 2110 | 14302110 | 6.57 |  |  |  | 6.57
MENDOCINO 1101 | 42951101 | 74.59 | 13.37 | 18.76 |  | 42.46
MENDOCINO 1102 | 42951102 | 0.05 |  |  |  | 0.05
MENDOTA 1101 | 252311101 | 1.61 |  |  |  | 1.61
MENDOTA 1102 | 252311102 | 103.48 |  |  |  | 103.48
MENDOTA 1103 | 252311103 | 15.79 |  |  |  | 15.79
MENDOTA 1104 | 252311104 | 62.33 |  |  |  | 62.33
MENLO 0401 | 24130401 | 6.41 |  |  |  | 6.41
MENLO 0402 | 24130402 | 7.55 |  |  |  | 7.55
MENLO 0403 | 24130403 | 8.26 |  |  |  | 8.26
MENLO 0404 | 24130404 | 8.17 |  |  |  | 8.17
MENLO 1101 | 24131101 | 1.51 |  |  |  | 1.51
MENLO 1102 | 24131102 | 63.69 | 0.01 | 28.25 |  | 35.43
MENLO 1103 | 24131103 | 56.98 |  | 39.73 |  | 17.25
MENLO 1104 | 24131104 | 16.79 |  |  |  | 16.79
MERCED 1108 | 252801108 | 69.46 |  |  |  | 69.46
MERCED 1114 | 252801114 | 58.04 |  |  |  | 58.04
MERCED 1116 | 252801116 | 77.62 |  |  |  | 77.62
MERCED 2101 | 252802101 | 29.94 |  |  |  | 29.94
MERCED 2102 | 252802102 | 25.96 |  |  |  | 25.96
MERCED FALLS 1102 | 252811102 | 153.29 |  | 93.43 |  | 59.86
MERIDIAN 1101 | 62541101 | 57.74 |  |  |  | 57.74
MERIDIAN 1102 | 62541102 | 71.9 |  |  |  | 71.9
MESA 1101 | 182821101 | 81.81 | 11.14 | 37.25 |  | 33.42
MESA 1102 | 182821102 | 3.69 |  |  |  | 3.69
MESA 1103 | 182821103 | 75.79 |  | 9.98 |  | 65.81
MESA 1104 | 182821104 | 41.29 |  |  |  | 41.29
METTLER 1109 | 163701109 | 20.37 |  |  |  | 20.37
METTLER 1110 | 163701110 | 38.04 |  |  |  | 38.04
MIDDLE RIVER 1101 | 162091101 | 31.34 |  |  |  | 31.34
MIDDLE RIVER 1102 | 162091102 | 32.09 |  |  |  | 32.09
MIDDLE RIVER 1103 | 162091103 | 28.53 |  |  |  | 28.53
MIDDLETOWN 1101 | 43141101 | 105.9 | 80.67 | 9.22 |  | 16.01
MIDDLETOWN 1102 | 43141102 | 56.08 | 0.04 | 38.32 |  | 17.72
MIDDLETOWN 1103 | 43141103 | 35.5 | 6.14 | 13.98 |  | 15.38
MIDWAY 1101 | 252611101 | 60.33 |  |  |  | 60.33
MIDWAY 1102 | 252611102 | 52.66 |  |  |  | 52.66
MIDWAY 1103 | 252611103 | 30.61 |  |  |  | 30.61
MIDWAY 1104 | 252611104 | 36.82 |  |  |  | 36.82
MILLBRAE 0401 | 22690401 | 2.82 |  |  |  | 2.82
MILLBRAE 0403 | 22690403 | 4.9 |  |  |  | 4.9
MILLBRAE 0404 | 22690404 | 7.08 |  |  |  | 7.08
MILLBRAE 1101 | 22691101 | 3.98 |  |  |  | 3.98
MILLBRAE 1102 | 22691102 | 4.76 |  |  |  | 4.76
MILLBRAE 1103 | 22691103 | 0.18 |  |  |  | 0.18
MILLBRAE 1104 | 22691104 | 15.9 |  |  |  | 15.9
MILLBRAE 1105 | 22691105 | 0.26 |  |  |  | 0.26
MILLBRAE 1106 | 22691106 | 3.71 |  |  |  | 3.71
MILLBRAE 1107 | 22691107 | 4.77 |  |  |  | 4.77
MILLBRAE 1108 | 22691108 | 14.15 |  |  |  | 14.15
MILPITAS 1101 | 82831101 | 4.1 |  |  |  | 4.1
MILPITAS 1103 | 82831103 | 0.07 |  |  |  | 0.07
MILPITAS 1104 | 82831104 | 1.04 |  |  |  | 1.04
MILPITAS 1105 | 82831105 | 4.73 |  | 0.07 |  | 4.66
MILPITAS 1106 | 82831106 | 3.14 |  |  |  | 3.14
MILPITAS 1108 | 82831108 | 13.3 |  | 0.02 |  | 13.28
MILPITAS 1109 | 82831109 | 49.48 |  | 29.94 |  | 19.54
MILPITAS 2110 | 82832110 | 10.37 |  |  |  | 10.37
MILPITAS 2111 | 82832111 | 1.8 |  |  |  | 1.8
MILPITAS 2112 | 82832112 | 0.87 |  |  |  | 0.87
MILPITAS 2113 | 82832113 | 0.12 |  |  |  | 0.12
MILPITAS 2114 | 82832114 | 0.17 |  |  |  | 0.17
MIRA VISTA 0401 | 12330401 | 8.69 |  |  |  | 8.69
MIRA VISTA 0403 | 12330403 | 7.1 |  |  |  | 7.1
MIRABEL 1101 | 42091101 | 51.35 | 19.95 | 8.95 |  | 22.45
MIRABEL 1102 | 42091102 | 57.6 | 31.89 | 4.82 |  | 20.89
MISSION (X) 0401 | 22010401 | 1.63 |  |  |  | 1.63
MISSION (X) 1102 | 22011102 | 0.17 |  |  |  | 0.17
MISSION (X) 1108 | 22011108 | 5.24 |  |  |  | 5.24
MISSION (X) 1109 | 22011109 | 1.13 |  |  |  | 1.13
MISSION (X) 1110 | 22011110 | 5.72 |  |  |  | 5.72
MISSION (X) 1113 | 22011113 | 2.63 |  |  |  | 2.63
MISSION (X) 1116 | 22011116 | 3.02 |  |  |  | 3.02
MISSION (X) 1118 | 22011118 | 0.6 |  |  |  | 0.6
MISSION (X) 1124 | 22011124 | 0.71 |  |  |  | 0.71
MISSION (X) 1125 | 22011125 | 0.97 |  |  |  | 0.97
MISSION (X) 1127 | 22011127 | 0.47 |  |  |  | 0.47
MISSION (X) 1128 | 22011128 | 0.77 |  |  |  | 0.77
MIWUK 1701 | 163661701 | 76.12 | 74.58 | 1.54 |  | 0
MIWUK 1702 | 163661702 | 74.53 | 71.89 | 2.64 |  | 0
MOLINO 1101 | 42571101 | 90.26 | 7.16 | 26.47 |  | 56.63
MOLINO 1102 | 42571102 | 161.09 | 90.1 | 19.53 |  | 51.46
MOLINO 1103 | 42571103 | 77.75 |  |  |  | 77.75
MOLINO 1104 | 42571104 | 61.22 |  | 2.38 |  | 58.84
MONARCH 0401 | 162300401 | 3.2 |  |  |  | 3.2
MONARCH 0402 | 162300402 | 2.84 |  |  |  | 2.84
MONARCH 0403 | 162300403 | 4.61 |  |  |  | 4.61
MONROE 1104 | 43301104 | 5.21 |  |  |  | 5.21
MONROE 1105 | 43301105 | 10.67 |  |  |  | 10.67
MONROE 1106 | 43301106 | 13.49 |  |  |  | 13.49
MONROE 2102 | 43302102 | 4.86 |  |  |  | 4.86
MONROE 2103 | 43302103 | 11.52 | 0.45 |  |  | 11.07
MONROE 2107 | 43302107 | 10.36 | 0.61 |  |  | 9.75
MONTAGUE 2101 | 83892101 | 0.87 |  |  |  | 0.87
MONTAGUE 2102 | 83892102 | 0.81 |  |  |  | 0.81
MONTAGUE 2103 | 83892103 | 0.94 |  |  |  | 0.94
MONTAGUE 2104 | 83892104 | 0.84 |  |  |  | 0.84
MONTAGUE 2105 | 83892105 | 0.78 |  |  |  | 0.78
MONTAGUE 2106 | 83892106 | 0 |  |  |  | 0
MONTAGUE 2108 | 83892108 | 0.93 |  |  |  | 0.93
MONTAGUE 2109 | 83892109 | 0.81 |  |  |  | 0.81
MONTE RIO 1111 | 42811111 | 63.88 | 43.76 | 13.32 |  | 6.8
MONTE RIO 1112 | 42811112 | 19.68 | 19.68 |  |  | 0
MONTE RIO 1113 | 42811113 | 61.04 | 61.04 |  |  | 0
MONTICELLO 1101 | 43051101 | 123.11 |  | 107.78 |  | 15.33
MORAGA 1101 | 13801101 | 25.72 | 16.41 | 4.79 |  | 4.52
MORAGA 1102 | 13801102 | 13.3 | 2.91 | 2.1 |  | 8.29
MORAGA 1103 | 13801103 | 17.44 | 0.12 | 2 |  | 15.32
MORAGA 1104 | 13801104 | 21.15 | 0.01 | 13.63 |  | 7.51
MORAGA 1105 | 13801105 | 19.72 | 6.87 | 0.81 |  | 12.04
MORGAN HILL 2104 | 83242104 | 20.9 |  | 5.74 |  | 15.16
MORGAN HILL 2105 | 83242105 | 82.09 | 14.1 | 35.87 |  | 32.12
MORGAN HILL 2106 | 83242106 | 39.06 |  | 0.12 |  | 38.94
MORGAN HILL 2108 | 83242108 | 13.09 |  |  |  | 13.09
MORGAN HILL 2109 | 83242109 | 26.36 |  | 2.45 |  | 23.91
MORGAN HILL 2110 | 83242110 | 32.65 |  | 2.22 |  | 30.43
MORGAN HILL 2111 | 83242111 | 72.48 | 16.46 | 35 |  | 21.02
MORMON 1101 | 163211101 | 62.42 |  |  |  | 62.42
MORMON 1102 | 163211102 | 87.99 |  |  |  | 87.99
MORMON 1103 | 163211103 | 23.44 |  |  |  | 23.44
MORRO BAY 1101 | 183011101 | 46.06 | 0.49 | 4.88 |  | 40.69
MORRO BAY 1102 | 183011102 | 57.81 | 4.03 | 17.91 |  | 35.87
MOSHER 2104 | 163722104 | 0.01 |  |  |  | 0.01
MOSHER 2107 | 163722107 | 3.13 |  |  |  | 3.13
MOSHER 2108 | 163722108 | 1.88 |  |  |  | 1.88
MOSHER 2110 | 163722110 | 2.21 |  |  |  | 2.21
MOSHER 2111 | 163722111 | 17.44 |  |  |  | 17.44
MOUNTAIN QUARRIES 2101 | 152282101 | 223.64 | 22.68 | 200 |  | 0.96
MOUNTAIN VIEW 1102 | 82031102 | 14.28 |  |  |  | 14.28
MOUNTAIN VIEW 1103 | 82031103 | 2.86 |  |  |  | 2.86
MOUNTAIN VIEW 1104 | 82031104 | 7.76 |  |  |  | 7.76
MOUNTAIN VIEW 1105 | 82031105 | 9.51 |  |  |  | 9.51
MOUNTAIN VIEW 1106 | 82031106 | 7.34 |  |  |  | 7.34
MOUNTAIN VIEW 1107 | 82031107 | 19.28 |  |  |  | 19.28
MOUNTAIN VIEW 1108 | 82031108 | 14.67 |  |  |  | 14.67
MOUNTAIN VIEW 1109 | 82031109 | 9.97 |  |  |  | 9.97
MOUNTAIN VIEW 1110 | 82031110 | 9.36 |  |  |  | 9.36
MOUNTAIN VIEW 1111 | 82031111 | 1.74 |  |  |  | 1.74
MOUNTAIN VIEW 1112 | 82031112 | 0.97 |  |  |  | 0.97
MOUNTAIN VIEW 1113 | 82031113 | 3.99 |  |  |  | 3.99
MOUNTAIN VIEW 1114 | 82031114 | 6.63 |  |  |  | 6.63
MT EDEN 1101 | 13761101 | 6.7 |  |  |  | 6.7
MT EDEN 1102 | 13761102 | 6.58 |  |  |  | 6.58
MT EDEN 1103 | 13761103 | 13.07 |  |  |  | 13.07
MT EDEN 1104 | 13761104 | 14 |  |  |  | 14
MT EDEN 1105 | 13761105 | 7.04 |  |  |  | 7.04
MT EDEN 1106 | 13761106 | 6.73 |  |  |  | 6.73
MT EDEN 1107 | 13761107 | 6.07 |  |  |  | 6.07
MT EDEN 1108 | 13761108 | 23.46 |  |  |  | 23.46
MT EDEN 1109 | 13761109 | 16.98 |  |  |  | 16.98
MT EDEN 1110 | 13761110 | 3.22 |  |  |  | 3.22
MT EDEN 1111 | 13761111 | 3.24 |  |  |  | 3.24
MT EDEN 1112 | 13761112 | 16.45 |  |  |  | 16.45
MT EDEN 1113 | 13761113 | 2.64 |  |  |  | 2.64
MT EDEN 1114 | 13761114 | 3.58 |  |  |  | 3.58
NAPA 1102 | 42021102 | 32.45 |  | 0.27 |  | 32.18
NAPA 1103 | 42021103 | 14.85 |  |  |  | 14.85
NAPA 1105 | 42021105 | 15.53 |  |  |  | 15.53
NAPA 1106 | 42021106 | 1.24 |  |  |  | 1.24
NAPA 1109 | 42021109 | 11.66 |  |  |  | 11.66
NAPA 1110 | 42021110 | 13.28 |  |  |  | 13.28
NAPA 1112 | 42021112 | 51.86 |  | 19.24 |  | 32.62
NARROWS 2101 | 153132101 | 61.45 |  | 61.45 |  | 0
NARROWS 2102 | 153132102 | 117.57 |  | 93.54 |  | 24.03
NARROWS 2104 | 153132104 | 0 |  | 0 |  | 0
NARROWS 2105 | 153132105 | 196.33 |  | 176.75 |  | 19.58
NARROWS PH 1151 | 153131151 | 0.2 |  | 0.2 |  | 0
NEW HOPE 1101 | 162081101 | 38.35 |  |  |  | 38.35
NEW HOPE 1102 | 162081102 | 50.59 |  |  |  | 50.59
NEWARK 12KV 1101 | 12221101 | 1.44 |  |  |  | 1.44
NEWARK 12KV 1102 | 12221102 | 8.4 |  |  |  | 8.4
NEWARK 12KV 1103 | 12221103 | 18.1 |  |  |  | 18.1
NEWARK 12KV 1104 | 12221104 | 0.37 |  |  |  | 0.37
NEWARK 12KV 1105 | 12221105 | 1.54 |  |  |  | 1.54
NEWARK 12KV 1106 | 12221106 | 18.36 |  |  |  | 18.36
NEWARK 12KV 1107 | 12221107 | 21.46 |  |  |  | 21.46
NEWARK 12KV 1108 | 12221108 | 0.95 |  |  |  | 0.95
NEWARK 21KV 2102 | 12232102 | 2.68 |  |  |  | 2.68
NEWARK 21KV 2103 | 12232103 | 17.79 |  |  |  | 17.79
NEWARK 21KV 2104 | 12232104 | 4.99 |  |  |  | 4.99
NEWARK 21KV 2105 | 12232105 | 2.51 |  |  |  | 2.51
NEWARK 21KV 2107 | 12232107 | 7.02 |  |  |  | 7.02
NEWARK 21KV 2108 | 12232108 | 4.82 |  |  |  | 4.82
NEWARK 21KV 2109 | 12232109 | 0 |  |  |  | 0
NEWARK 21KV 2110 | 12232110 | 3.19 |  |  |  | 3.19
NEWARK 21KV 2111 | 12232111 | 0 |  |  |  | 0
NEWBURG 1131 | 192151131 | 39.09 |  | 5.67 |  | 33.42
NEWBURG 1132 | 192151132 | 22.27 |  | 1.29 |  | 20.98
NEWBURG 1133 | 192151133 | 16.92 |  | 2.38 |  | 14.54
NEWHALL 1109 | 254461109 | 66.55 |  |  |  | 66.55
NEWHALL 1111 | 254461111 | 53.93 |  |  |  | 53.93
NEWMAN 1101 | 162741101 | 36.53 |  |  |  | 36.53
NEWMAN 1102 | 162741102 | 9.51 |  |  |  | 9.51
NEWMAN 1105 | 162741105 | 42.69 |  |  |  | 42.69
NEWMAN 1106 | 162741106 | 32.51 |  |  |  | 32.51
NORCO 1101 | 254691101 | 39.26 |  |  |  | 39.26
NORCO 1102 | 254691102 | 7.67 |  |  |  | 7.67
NORD 1103 | 103071103 | 18.51 |  |  |  | 18.51
NORD 1104 | 103071104 | 50.35 |  |  |  | 50.35
NORD 1105 | 103071105 | 6.99 |  |  |  | 6.99
NORD 1106 | 103071106 | 10.83 |  |  |  | 10.83
NORIEGA 0401 | 22510401 | 1.55 |  |  |  | 1.55
NORIEGA 0402 | 22510402 | 1.76 |  |  |  | 1.76
NORTECH 2107 | 82462107 | 0.11 |  |  |  | 0.11
NORTECH 2109 | 82462109 | 3.15 |  |  |  | 3.15
NORTECH 2110 | 82462110 | 9.47 |  |  |  | 9.47
NORTECH 2111 | 82462111 | 0.71 |  |  |  | 0.71
NORTH BRANCH 1101 | 163231101 | 88.31 |  | 62.34 |  | 25.97
NORTH DUBLIN 2101 | 14052101 | 1.87 |  | 1.4 |  | 0.47
NORTH DUBLIN 2103 | 14052103 | 21.69 |  | 18.65 |  | 3.04
NORTH TOWER 1102 | 42041102 | 18.7 |  |  |  | 18.7
NORTH TOWER 1103 | 42041103 | 13.04 |  |  |  | 13.04
NORTH TOWER 1104 | 42041104 | 19.71 |  |  |  | 19.71
NORTH TOWER 1108 | 42041108 | 13.3 |  |  |  | 13.3
NORTH TOWER 2101 | 42042101 | 4.42 |  | 0.52 |  | 3.9
NORTH TOWER 2104 | 42042104 | 4.21 |  |  |  | 4.21
NOTRE DAME 1101 | 102041101 | 1.6 |  |  |  | 1.6
NOTRE DAME 1102 | 102041102 | 10.61 |  |  |  | 10.61
NOTRE DAME 1103 | 102041103 | 7.85 |  | 0.57 |  | 7.28
NOTRE DAME 1104 | 102041104 | 35.86 | 17.95 | 9.74 |  | 8.17
NOVATO 1101 | 42211101 | 7.33 |  | 1.2 |  | 6.13
NOVATO 1102 | 42211102 | 0.59 |  |  |  | 0.59
NOVATO 1103 | 42211103 | 2.95 |  |  |  | 2.95
NOVATO 1104 | 42211104 | 24.36 |  | 3.45 |  | 20.91
OAK 0401 | 12600401 | 5.41 |  | 3.45 |  | 1.96
OAK PARK 0401 | 163270401 | 2.48 |  |  |  | 2.48
OAK PARK 0402 | 163270402 | 0.5 |  |  |  | 0.5
OAKHURST 1101 | 254421101 | 91.78 | 2.56 | 88.37 |  | 0.85
OAKHURST 1102 | 254421102 | 16.32 | 1.17 | 11.32 |  | 3.83
OAKHURST 1103 | 254421103 | 125.45 | 80.93 | 41.88 |  | 2.64
OAKLAND C 1108 | 12011108 | 2.04 |  |  |  | 2.04
OAKLAND C 1109 | 12011109 | 3.28 |  |  |  | 3.28
OAKLAND C 1110 | 12011110 | 1.25 |  |  |  | 1.25
OAKLAND C 1112 | 12011112 | 1.16 |  |  |  | 1.16
OAKLAND C 1113 | 12011113 | 3.36 |  |  |  | 3.36
OAKLAND C 1114 | 12011114 | 3.27 |  |  |  | 3.27
OAKLAND C 1115 | 12011115 | 1.24 |  |  |  | 1.24
OAKLAND C 1116 | 12011116 | 2.47 |  |  |  | 2.47
OAKLAND C 1117 | 12011117 | 2.97 |  |  |  | 2.97
OAKLAND C 1118 | 12011118 | 3.32 |  |  |  | 3.32
OAKLAND C 1119 | 12011119 | 0.43 |  |  |  | 0.43
OAKLAND C 1120 | 12011120 | 2.96 |  |  |  | 2.96
OAKLAND C 1121 | 12011121 | 1.91 |  |  |  | 1.91
OAKLAND C 1132 | 12011132 | 1.22 |  |  |  | 1.22
OAKLAND C 1133 | 12011133 | 0.03 |  |  |  | 0.03
OAKLAND C 1134 | 12011134 | 1.4 |  |  |  | 1.4
OAKLAND D 0406 | 12040406 | 3.19 |  |  |  | 3.19
OAKLAND D 0407 | 12040407 | 0.33 |  |  |  | 0.33
OAKLAND D 0408 | 12040408 | 4.08 |  |  |  | 4.08
OAKLAND D 0410 | 12040410 | 2.75 |  |  |  | 2.75
OAKLAND D 1101 | 12041101 | 0.16 |  |  |  | 0.16
OAKLAND D 1102 | 12041102 | 2.85 |  |  |  | 2.85
OAKLAND D 1103 | 12041103 | 0.34 |  |  |  | 0.34
OAKLAND D 1104 | 12041104 | 5.93 |  |  |  | 5.93
OAKLAND D 1105 | 12041105 | 8.27 |  |  |  | 8.27
OAKLAND D 1106 | 12041106 | 8.78 |  |  |  | 8.78
OAKLAND D 1107 | 12041107 | 2.51 |  |  |  | 2.51
OAKLAND D 1110 | 12041110 | 5.47 |  |  |  | 5.47
OAKLAND D 1111 | 12041111 | 7.81 |  |  |  | 7.81
OAKLAND D 1112 | 12041112 | 10.64 | 1.95 | 0.41 |  | 8.28
OAKLAND D 1115 | 12041115 | 2.74 |  |  |  | 2.74
OAKLAND D 1116 | 12041116 | 2.81 |  |  |  | 2.81
OAKLAND D 1117 | 12041117 | 0.5 |  |  |  | 0.5
OAKLAND D 1130 | 12041130 | 6.44 |  |  |  | 6.44
OAKLAND D 1131 | 12041131 | 7.74 |  |  |  | 7.74
OAKLAND D 1132 | 12041132 | 2.79 |  |  |  | 2.79
OAKLAND D 1133 | 12041133 | 2.97 |  |  |  | 2.97
OAKLAND D 1134 | 12041134 | 5.07 |  |  |  | 5.07
OAKLAND D 1202 | 12041202 | 0.24 |  |  |  | 0.24
OAKLAND I 0401 | 12080401 | 3.23 |  |  |  | 3.23
OAKLAND I 0402 | 12080402 | 5.11 |  |  |  | 5.11
OAKLAND J 0401 | 12090401 | 4.63 |  |  |  | 4.63
OAKLAND J 0403 | 12090403 | 6.3 |  |  |  | 6.3
OAKLAND J 0408 | 12090408 | 4.57 |  |  |  | 4.57
OAKLAND J 0409 | 12090409 | 3 |  |  |  | 3
OAKLAND J 1101 | 12091101 | 10.41 |  |  |  | 10.41
OAKLAND J 1102 | 12091102 | 18.3 |  | 6.01 |  | 12.29
OAKLAND J 1103 | 12091103 | 2.78 |  |  |  | 2.78
OAKLAND J 1104 | 12091104 | 6.84 |  |  |  | 6.84
OAKLAND J 1105 | 12091105 | 20.26 |  | 1.52 |  | 18.74
OAKLAND J 1106 | 12091106 | 18.02 |  | 1.89 |  | 16.13
OAKLAND J 1108 | 12091108 | 9.25 |  |  |  | 9.25
OAKLAND J 1109 | 12091109 | 0.04 |  |  |  | 0.04
OAKLAND J 1110 | 12091110 | 2.08 |  |  |  | 2.08
OAKLAND J 1111 | 12091111 | 4.67 |  |  |  | 4.67
OAKLAND J 1112 | 12091112 | 5.51 |  |  |  | 5.51
OAKLAND J 1114 | 12091114 | 0 |  |  |  | 0
OAKLAND J 1115 | 12091115 | 3.9 |  |  |  | 3.9
OAKLAND J 1116 | 12091116 | 23.48 |  | 0.48 |  | 23
OAKLAND J 1117 | 12091117 | 13.12 |  |  |  | 13.12
OAKLAND J 1118 | 12091118 | 13.87 |  | 0.31 |  | 13.56
OAKLAND K 1101 | 12101101 | 7.27 | 1.09 | 1.47 |  | 4.71
OAKLAND K 1102 | 12101102 | 14.94 | 14.94 |  |  | 0
OAKLAND K 1103 | 12101103 | 10.68 | 1.13 | 4.84 |  | 4.71
OAKLAND K 1104 | 12101104 | 14.89 | 9.56 | 5.33 |  | 0
OAKLAND L 1101 | 12111101 | 5.82 |  |  |  | 5.82
OAKLAND L 1102 | 12111102 | 1.28 |  |  |  | 1.28
OAKLAND L 1103 | 12111103 | 4.69 |  |  |  | 4.69
OAKLAND L 1105 | 12111105 | 2.48 |  |  |  | 2.48
OAKLAND L 1106 | 12111106 | 0.35 |  |  |  | 0.35
OAKLAND L 1107 | 12111107 | 1.47 |  |  |  | 1.47
OAKLAND L 1108 | 12111108 | 0 |  |  |  | 0
OAKLAND X 0401 | 12540401 | 5.5 |  |  |  | 5.5
OAKLAND X 0402 | 12540402 | 1.77 |  |  |  | 1.77
OAKLAND X 1101 | 12541101 | 5.29 |  | 0.5 |  | 4.79
OAKLAND X 1102 | 12541102 | 6.37 |  |  |  | 6.37
OAKLAND X 1103 | 12541103 | 7.68 |  |  |  | 7.68
OAKLAND X 1104 | 12541104 | 13.22 | 10.71 | 1.35 |  | 1.16
OAKLAND X 1105 | 12541105 | 19.38 |  | 2.51 |  | 16.87
OAKLAND X 1106 | 12541106 | 22.88 | 4.14 | 10.81 |  | 7.93
OAKLAND X 1107 | 12541107 | 12.92 |  |  |  | 12.92
OAKLAND X 1109 | 12541109 | 7.1 |  |  |  | 7.1
OAKLAND X 1110 | 12541110 | 0.43 |  |  |  | 0.43
OAKLAND X 1111 | 12541111 | 1.03 |  |  |  | 1.03
OAKLAND X 1112 | 12541112 | 3.93 |  |  |  | 3.93
OAKLAND X 1114 | 12541114 | 5.08 |  |  |  | 5.08
OAKLAND X 1115 | 12541115 | 12.61 |  |  |  | 12.61
OCEAN 0401 | 22580401 | 3.7 |  |  |  | 3.7
OCEAN 0402 | 22580402 | 2.96 |  |  |  | 2.96
OCEANO 1102 | 182601102 | 54.18 |  | 37.12 |  | 17.06
OCEANO 1103 | 182601103 | 11.37 |  | 1.11 |  | 10.26
OCEANO 1104 | 182601104 | 112.15 | 6.75 | 78.81 |  | 26.59
OCEANO 1105 | 182601105 | 23.59 |  | 0.66 |  | 22.93
OCEANO 1106 | 182601106 | 29.36 |  | 1.96 |  | 27.4
OCEANO 1108 | 182601108 | 11.07 |  |  |  | 11.07
OILFIELDS 1102 | 182391102 | 39.1 |  |  |  | 39.1
OILFIELDS 1103 | 182391103 | 144.71 |  | 116.94 |  | 27.77
OLD RIVER 1101 | 252821101 | 41.99 |  |  |  | 41.99
OLD RIVER 1102 | 252821102 | 49.41 |  |  |  | 49.41
OLD RIVER 1103 | 252821103 | 35.34 |  |  |  | 35.34
OLD RIVER 1104 | 252821104 | 58.21 |  |  |  | 58.21
OLD RIVER 1105 | 252821105 | 15.44 |  |  |  | 15.44
OLEMA 1101 | 42291101 | 123.11 | 15.44 | 55.47 |  | 52.2
OLETA 1101 | 163541101 | 116.76 | 4.66 | 84.68 |  | 27.42
OLETA 1102 | 163541102 | 98.63 |  | 56.04 |  | 42.59
OLIVEHURST 1101 | 152901101 | 21.81 |  |  |  | 21.81
OLIVEHURST 1102 | 152901102 | 6.02 |  |  |  | 6.02
OLIVEHURST 1103 | 152901103 | 47.14 |  |  |  | 47.14
OLIVEHURST 1104 | 152901104 | 11.38 |  |  |  | 11.38
OLIVEHURST 1105 | 152901105 | 53.94 |  |  |  | 53.94
OREGON TRAIL 1102 | 103521102 | 49.03 |  | 44.69 |  | 4.34
OREGON TRAIL 1103 | 103521103 | 112.31 |  | 109.37 |  | 2.94
OREGON TRAIL 1104 | 103521104 | 73.39 |  | 60.53 |  | 12.86
ORICK 1101 | 192261101 | 7.98 |  |  |  | 7.98
ORICK 1102 | 192261102 | 23.29 |  |  |  | 23.29
ORINDA 0401 | 12350401 | 5.37 | 0.1 | 3.37 |  | 1.9
ORINDA 0402 | 12350402 | 6.61 | 3.19 | 3.16 |  | 0.26
ORLAND B 1101 | 102701101 | 29.28 |  |  |  | 29.28
ORLAND B 1102 | 102701102 | 20.04 |  |  |  | 20.04
ORLAND B 1103 | 102701103 | 94.38 |  |  |  | 94.38
ORO FINO 1101 | 103031101 | 31.74 | 31.74 |  |  | 0
ORO FINO 1102 | 103031102 | 109.38 | 83.12 | 26.26 |  | 0
ORO LOMA 1102 | 255371102 | 1.07 |  |  |  | 1.07
ORO LOMA 1103 | 255371103 | 1.1 |  |  |  | 1.1
ORO LOMA 1106 | 255371106 | 72.81 |  |  |  | 72.81
ORO LOMA 1108 | 255371108 | 55.53 |  |  |  | 55.53
ORO LOMA 1115 | 255371115 | 73.78 |  |  |  | 73.78
ORO LOMA 1116 | 255371116 | 24.7 |  |  |  | 24.7
ORO LOMA 1117 | 255371117 | 50.2 |  |  |  | 50.2
ORO LOMA 1118 | 255371118 | 42.74 |  |  |  | 42.74
OROSI 1101 | 252841101 | 50.36 |  |  |  | 50.36
OROSI 1102 | 252841102 | 34.84 |  | 0.8 |  | 34.04
OROSI 1103 | 252841103 | 37.72 |  |  |  | 37.72
OROSI 1104 | 252841104 | 55.84 |  |  |  | 55.84
OROVILLE 0402 | 102520402 | 1.58 |  |  |  | 1.58
OROVILLE 0403 | 102520403 | 2.03 |  |  |  | 2.03
OROVILLE 1101 | 102521101 | 23.53 |  |  |  | 23.53
OROVILLE 1102 | 102521102 | 6.28 |  |  |  | 6.28
OROVILLE 1103 | 102521103 | 10.36 |  |  |  | 10.36
OROVILLE 1104 | 102521104 | 9.87 |  |  |  | 9.87
ORTIGA 1105 | 254311105 | 42.41 |  |  |  | 42.41
ORTIGA 1106 | 254311106 | 53.7 |  |  |  | 53.7
OTTER 1101 | 182941101 | 26.95 | 14.55 | 7.09 |  | 5.31
OTTER 1102 | 182941102 | 53.79 | 4.38 | 48.32 |  | 1.09
PACIFIC GROVE 0421 | 182440421 | 3.34 |  |  |  | 3.34
PACIFIC GROVE 0422 | 182440422 | 6.89 |  | 0.13 |  | 6.76
PACIFIC GROVE 0423 | 182440423 | 1.68 |  |  |  | 1.68
PACIFIC GROVE 0424 | 182440424 | 8.97 |  |  |  | 8.97
PACIFIC PIPE GRAPEVI 1101 | 255441101 | 0.02 |  |  |  | 0.02
PACIFICA 1101 | 22811101 | 9.23 | 0.07 | 0.74 |  | 8.42
PACIFICA 1102 | 22811102 | 20.1 | 1.34 | 1.38 |  | 17.38
PACIFICA 1103 | 22811103 | 14.13 | 0.19 | 0.77 |  | 13.17
PACIFICA 1104 | 22811104 | 7.18 |  | 0.7 |  | 6.48
PALMER 1101 | 183031101 | 62.6 |  | 39.46 |  | 23.14
PALO SECO 0401 | 13180401 | 4.73 |  | 4.71 |  | 0.02
PANAMA 2101 | 253422101 | 38.65 |  |  |  | 38.65
PANAMA 2102 | 253422102 | 32.89 |  |  |  | 32.89
PANOCHE 1101 | 253671101 | 24.31 |  |  |  | 24.31
PANOCHE 1102 | 253671102 | 42.59 |  |  |  | 42.59
PANOCHE 1103 | 253671103 | 122.18 |  | 44.24 |  | 77.94
PANORAMA 1101 | 103461101 | 39.18 |  | 12.98 |  | 26.2
PANORAMA 1102 | 103461102 | 84.44 |  | 29.99 |  | 54.45
PARADISE 1103 | 102831103 | 36.04 | 18.47 | 14.79 |  | 2.78
PARADISE 1104 | 102831104 | 31 | 20.97 | 1.32 |  | 8.71
PARADISE 1105 | 102831105 | 48.1 | 45.54 |  |  | 2.56
PARADISE 1106 | 102831106 | 8.84 | 8.3 |  |  | 0.54
PARKWAY 1101 | 42051101 | 7.12 |  |  |  | 7.12
PARKWAY 1102 | 42051102 | 0 |  |  |  | 0
PARKWAY 1103 | 42051103 | 6.7 |  |  |  | 6.7
PARLIER 1102 | 252291102 | 10.97 |  |  |  | 10.97
PARLIER 1103 | 252291103 | 40.84 |  |  |  | 40.84
PARLIER 1104 | 252291104 | 49.86 |  |  |  | 49.86
PARLIER 1105 | 252291105 | 21.42 |  |  |  | 21.42
PARSONS 0401 | 13660401 | 1.32 |  |  |  | 1.32
PARSONS 0402 | 13660402 | 3.43 |  |  |  | 3.43
PASO ROBLES 1101 | 182611101 | 6.57 |  |  |  | 6.57
PASO ROBLES 1102 | 182611102 | 6.41 |  |  |  | 6.41
PASO ROBLES 1103 | 182611103 | 60.48 |  | 38.53 |  | 21.95
PASO ROBLES 1104 | 182611104 | 65.55 |  | 37.15 |  | 28.4
PASO ROBLES 1106 | 182611106 | 11.46 |  |  |  | 11.46
PASO ROBLES 1107 | 182611107 | 37.7 |  | 0.26 |  | 37.44
PASO ROBLES 1108 | 182611108 | 12.43 |  |  |  | 12.43
PAUL SWEET 2101 | 83252101 | 28.44 |  |  |  | 28.44
PAUL SWEET 2102 | 83252102 | 18 | 3.7 | 0.73 |  | 13.57
PAUL SWEET 2103 | 83252103 | 16.87 |  |  |  | 16.87
PAUL SWEET 2104 | 83252104 | 38.37 | 17.2 |  |  | 21.17
PAUL SWEET 2105 | 83252105 | 40.87 | 6.8 | 0.8 |  | 33.27
PAUL SWEET 2106 | 83252106 | 51.86 | 30.65 | 5.23 |  | 15.98
PAUL SWEET 2107 | 83252107 | 49.49 | 4.04 | 4.24 |  | 41.21
PAUL SWEET 2108 | 83252108 | 20.72 |  |  |  | 20.72
PAUL SWEET 2109 | 83252109 | 23.6 | 0.85 | 2.02 |  | 20.73
PEABODY 2102 | 63642102 | 7.01 |  |  |  | 7.01
PEABODY 2104 | 63642104 | 6.76 |  |  |  | 6.76
PEABODY 2105 | 63642105 | 61.12 |  |  |  | 61.12
PEABODY 2106 | 63642106 | 1.08 |  | 0.39 |  | 0.69
PEABODY 2107 | 63642107 | 194.05 |  |  |  | 194.05
PEABODY 2108 | 63642108 | 3.02 |  | 0.34 |  | 2.68
PEABODY 2109 | 63642109 | 3.63 |  |  |  | 3.63
PEABODY 2112 | 63642112 | 3.45 |  |  |  | 3.45
PEABODY 2113 | 63642113 | 9.73 |  | 1.02 |  | 8.71
PEACHTON 1101 | 103241101 | 68.89 |  |  |  | 68.89
PEACHTON 1102 | 103241102 | 67.67 |  |  |  | 67.67
PEACHTON 1103 | 103241103 | 60.88 |  |  |  | 60.88
PEASE 1101 | 153751101 | 6.84 |  |  |  | 6.84
PEASE 1102 | 153751102 | 3.98 |  |  |  | 3.98
PEASE 1103 | 153751103 | 97.44 |  |  |  | 97.44
PEASE 1104 | 153751104 | 62.57 |  |  |  | 62.57
PEASE 1105 | 153751105 | 8.24 |  |  |  | 8.24
PENNGROVE 1101 | 43471101 | 41.73 |  | 20.09 |  | 21.64
PENRYN 1103 | 152561103 | 80.22 |  | 67.15 |  | 13.07
PENRYN 1105 | 152561105 | 91.41 |  | 33.91 |  | 57.5
PENRYN 1106 | 152561106 | 25.83 |  | 0.81 |  | 25.02
PENRYN 1107 | 152561107 | 83.96 |  | 35.97 |  | 47.99
PENTLAND 1101 | 255311101 | 0.02 |  |  |  | 0.02
PEORIA 1701 | 163781701 | 84.58 |  | 77.43 |  | 7.15
PEORIA 1704 | 163781704 | 118.03 |  | 58.71 |  | 59.32
PEORIA 1705 | 163781705 | 70.02 |  | 57.46 |  | 12.56
PERRY 1101 | 183071101 | 83.71 | 7.18 | 58.34 |  | 18.19
PETALUMA A 0411 | 42120411 | 3.06 |  |  |  | 3.06
PETALUMA A 0413 | 42120413 | 2.37 |  |  |  | 2.37
PETALUMA C 1101 | 42631101 | 0.51 |  |  |  | 0.51
PETALUMA C 1102 | 42631102 | 4.21 |  |  |  | 4.21
PETALUMA C 1105 | 42631105 | 10.67 |  |  |  | 10.67
PETALUMA C 1106 | 42631106 | 9 |  |  |  | 9
PETALUMA C 1108 | 42631108 | 118.47 |  | 75.79 |  | 42.68
PETALUMA C 1109 | 42631109 | 66.6 |  | 48.74 |  | 17.86
PETALUMA C 1110 | 42631110 | 0.25 |  |  |  | 0.25
PETROL 1101 | 252541101 | 0.03 |  |  |  | 0.03
PHILO 1101 | 42601101 | 96.11 |  | 76.49 |  | 19.62
PHILO 1102 | 42601102 | 105.92 |  | 88.3 |  | 17.62
PIERCY 2109 | 83912109 | 19.9 |  |  |  | 19.9
PIERCY 2110 | 83912110 | 27.42 |  | 19.66 |  | 7.76
PIERCY 2111 | 83912111 | 0.91 |  |  |  | 0.91
PIKE CITY 1101 | 152201101 | 34.03 | 34.03 |  |  | 0
PIKE CITY 1102 | 152201102 | 9.52 | 9.52 |  |  | 0
PINE GROVE 1101 | 163751101 | 71.79 |  | 71.79 |  | 0
PINE GROVE 1102 | 163751102 | 176.13 | 85.35 | 90.78 |  | 0
PINECREST 0401 | 163160401 | 3.15 | 1.12 | 1.95 |  | 0.08
PINEDALE 2101 | 252852101 | 1.43 |  |  |  | 1.43
PINEDALE 2102 | 252852102 | 2.76 |  |  |  | 2.76
PINEDALE 2103 | 252852103 | 1.98 |  |  |  | 1.98
PINEDALE 2105 | 252852105 | 1.76 |  |  |  | 1.76
PINEDALE 2106 | 252852106 | 5.43 |  |  |  | 5.43
PINEDALE 2107 | 252852107 | 1.59 |  |  |  | 1.59
PINEDALE 2109 | 252852109 | 7.14 |  |  |  | 7.14
PINEDALE 2110 | 252852110 | 0.19 |  |  |  | 0.19
PINEDALE 2111 | 252852111 | 0.75 |  |  |  | 0.75
PIPER BANK 0401 | 18120401 | 1.56 |  |  |  | 1.56
PIT NO 1 1101 | 103721101 | 52.88 |  | 29.54 |  | 23.34
PIT NO 3 2101 | 103732101 | 48.49 |  | 47.46 |  | 1.03
PIT NO 5 1101 | 101321101 | 23.62 |  | 23.62 |  | 0
PIT NO 7 1101 | 103501101 | 2.84 |  | 2.84 |  | 0
PITTSBURG 0401 | 12160401 | 1.04 |  |  |  | 1.04
PITTSBURG 0402 | 12160402 | 1.87 |  |  |  | 1.87
PLACER 1101 | 152461101 | 7.71 |  | 1.26 |  | 6.45
PLACER 1102 | 152461102 | 2.12 |  | 1.86 |  | 0.26
PLACER 1103 | 152461103 | 29.53 |  | 12.08 |  | 17.45
PLACER 1104 | 152461104 | 13.39 |  | 0.52 |  | 12.87
PLACERVILLE 1109 | 153081109 | 11.05 |  | 10.76 |  | 0.29
PLACERVILLE 1110 | 153081110 | 34.41 | 0.73 | 32.66 |  | 1.02
PLACERVILLE 1111 | 153081111 | 16.69 |  | 14.73 |  | 1.96
PLACERVILLE 1112 | 153081112 | 29.78 |  | 27.54 |  | 2.24
PLACERVILLE 2106 | 153082106 | 273.51 | 179.49 | 93.76 |  | 0.26
PLAINFIELD 1101 | 63441101 | 33.73 |  |  |  | 33.73
PLAINFIELD 1105 | 63441105 | 51.66 |  |  |  | 51.66
PLAINFIELD 1106 | 63441106 | 32.79 |  |  |  | 32.79
PLEASANT GROVE 2103 | 152442103 | 1.88 |  |  |  | 1.88
PLEASANT GROVE 2104 | 152442104 | 2.42 |  |  |  | 2.42
PLEASANT GROVE 2107 | 152442107 | 0.02 |  |  |  | 0.02
PLEASANT GROVE 2108 | 152442108 | 2.1 |  |  |  | 2.1
PLEASANT GROVE 2110 | 152442110 | 34.64 |  |  |  | 34.64
PLUMAS 1101 | 153731101 | 32.33 |  |  |  | 32.33
PLUMAS 1102 | 153731102 | 5.63 |  |  |  | 5.63
PLUMAS 2106 | 153732106 | 31.95 |  |  |  | 31.95
PLUMAS 2107 | 153732107 | 39.77 |  |  |  | 39.77
PLYMOUTH 0401 | 22680401 | 4.7 |  |  |  | 4.7
POINT ARENA 1101 | 43381101 | 66.15 |  | 44.25 |  | 21.9
POINT MORETTI 1101 | 82931101 | 53.94 | 29.9 | 17.32 |  | 6.72
POINT PINOLE 1101 | 14261101 | 20.99 |  |  |  | 20.99
POINT PINOLE 1102 | 14261102 | 14.06 |  |  |  | 14.06
POINT PINOLE 1103 | 14261103 | 0.01 |  |  |  | 0.01
PORTOLA 0401 | 22610401 | 2.45 |  |  |  | 2.45
PORTOLA 0402 | 22610402 | 3.5 |  |  |  | 3.5
POSO MOUNTAIN 2101 | 253642101 | 59.33 |  | 48.76 |  | 10.57
POSO MOUNTAIN 2103 | 253642103 | 20.45 |  | 18.43 |  | 2.02
POSO MOUNTAIN 2104 | 253642104 | 12.55 |  | 8.03 |  | 4.52
POTRERO PP (A) 1101 | 22031101 | 7.2 |  |  |  | 7.2
POTRERO PP (A) 1102 | 22031102 | 0.48 |  |  |  | 0.48
POTRERO PP (A) 1103 | 22031103 | 1.8 |  |  |  | 1.8
POTRERO PP (A) 1104 | 22031104 | 0.3 |  |  |  | 0.3
POTRERO PP (A) 1105 | 22031105 | 1.52 |  |  |  | 1.52
POTRERO PP (A) 1107 | 22031107 | 0.9 |  |  |  | 0.9
POTRERO PP (A) 1108 | 22031108 | 3.5 |  |  |  | 3.5
POTRERO PP (A) 1109 | 22031109 | 5.2 |  |  |  | 5.2
POTRERO PP (A) 1110 | 22031110 | 6.49 |  |  |  | 6.49
POTRERO PP (A) 1112 | 22031112 | 0.93 |  |  |  | 0.93
POTRERO PP (A) 1113 | 22031113 | 1.74 |  |  |  | 1.74
POTRERO PP (A) 1114 | 22031114 | 0.07 |  |  |  | 0.07
POTRERO PP (A) 1115 | 22031115 | 0.84 |  |  |  | 0.84
POTRERO PP (A) 1116 | 22031116 | 2.21 |  |  |  | 2.21
POTRERO PP (A) 1117 | 22031117 | 4.93 |  |  |  | 4.93
POTRERO PP (A) 1118 | 22031118 | 4.29 |  |  |  | 4.29
POTRERO PP (A) 1119 | 22031119 | 2.51 |  |  |  | 2.51
POTRERO PP (A) 1121 | 22031121 | 0.17 |  |  |  | 0.17
POTTER VALLEY P H 1104 | 42281104 | 18.84 | 0.11 | 4.57 |  | 14.16
POTTER VALLEY P H 1105 | 42281105 | 73.4 | 4.64 | 43.35 |  | 25.41
PRUNEDALE 1107 | 182961107 | 46.88 |  |  |  | 46.88
PRUNEDALE 1110 | 182961110 | 79.81 |  | 0.24 |  | 79.57
PUEBLO 1102 | 43291102 | 8.99 |  |  | 0.09 | 8.9
PUEBLO 1103 | 43291103 | 8.1 |  |  |  | 8.1
PUEBLO 1104 | 43291104 | 50.91 |  | 28.41 | 0.05 | 22.45
PUEBLO 1105 | 43291105 | 70.1 |  | 20.73 | 0.05 | 49.32
PUEBLO 2101 | 43292101 | 11.6 |  |  |  | 11.6
PUEBLO 2102 | 43292102 | 98.08 | 21.14 | 0.74 |  | 76.2
PUEBLO 2103 | 43292103 | 77.46 | 37.61 | 8.1 |  | 31.75
PURISIMA 1101 | 182971101 | 58.3 |  | 17.62 |  | 40.68
PUTAH CREEK 1102 | 63681102 | 50.82 |  | 26.6 |  | 24.22
PUTAH CREEK 1103 | 63681103 | 36.51 |  | 3.76 |  | 32.75
PUTAH CREEK 1105 | 63681105 | 83.61 |  | 1.78 |  | 81.83
RACETRACK 1703 | 163761703 | 62.12 | 1.46 | 54.53 |  | 6.13
RACETRACK 1704 | 163761704 | 45.38 |  | 45.38 |  | 0
RADUM 1101 | 13151101 | 1.62 |  |  |  | 1.62
RADUM 1102 | 13151102 | 1.15 |  |  |  | 1.15
RADUM 1105 | 13151105 | 11.8 | 1.14 | 1.9 |  | 8.76
RAINBOW 1103 | 254441103 | 16.9 |  |  |  | 16.9
RAINBOW 1105 | 254441105 | 23.72 |  |  |  | 23.72
RAINBOW 1106 | 254441106 | 122.11 |  |  |  | 122.11
RALSTON 1101 | 24141101 | 14.47 | 0.41 | 8.52 |  | 5.54
RALSTON 1102 | 24141102 | 10.74 |  | 3.77 |  | 6.97
RANCHERS COTTON 1000 | 254801000 | 0.01 |  |  |  | 0.01
RANCHERS COTTON 1101 | 254801101 | 14.12 |  |  |  | 14.12
RANDOLPH 0401 | 22590401 | 0 |  |  |  | 0
RANDOLPH 0402 | 22590402 | 1.27 |  |  |  | 1.27
RANDOLPH 0403 | 22590403 | 3.12 |  |  |  | 3.12
RAWSON 1103 | 103531103 | 39.98 |  | 2.75 |  | 37.23
RED BLUFF 1101 | 103541101 | 74.44 |  | 47.63 |  | 26.81
RED BLUFF 1102 | 103541102 | 1.48 |  |  |  | 1.48
RED BLUFF 1103 | 103541103 | 37.99 |  | 16.8 |  | 21.19
RED BLUFF 1104 | 103541104 | 93.4 |  | 66.12 |  | 27.28
RED BLUFF 1105 | 103541105 | 37.7 |  | 13.6 |  | 24.1
REDBUD 1101 | 43191101 | 66.17 | 19.24 | 21.65 |  | 25.28
REDBUD 1102 | 43191102 | 58.39 | 0.65 | 27.84 |  | 29.9
REDWOOD CITY 0402 | 24160402 | 1.25 |  |  |  | 1.25
REDWOOD CITY 0403 | 24160403 | 2.15 |  |  |  | 2.15
REDWOOD CITY 0404 | 24160404 | 1.61 |  |  |  | 1.61
REDWOOD CITY 0405 | 24160405 | 3.35 |  |  |  | 3.35
REDWOOD CITY 0406 | 24160406 | 6.58 |  |  |  | 6.58
REDWOOD CITY 0408 | 24160408 | 5.6 |  |  |  | 5.6
REDWOOD CITY 0409 | 24160409 | 4.91 |  |  |  | 4.91
REDWOOD CITY 0410 | 24160410 | 5.42 |  |  |  | 5.42
REDWOOD CITY 1101 | 24161101 | 1.94 |  |  |  | 1.94
REDWOOD CITY 1102 | 24161102 | 1.63 |  |  |  | 1.63
REDWOOD CITY 1103 | 24161103 | 1.59 |  |  |  | 1.59
REDWOOD CITY 1104 | 24161104 | 0.98 |  |  |  | 0.98
REDWOOD CITY 1105 | 24161105 | 7.26 |  |  |  | 7.26
REEDLEY 1101 | 252341101 | 26.41 |  |  |  | 26.41
REEDLEY 1104 | 252341104 | 82.43 |  | 1.69 |  | 80.74
REEDLEY 1106 | 252341106 | 123.19 |  |  |  | 123.19
REEDLEY 1110 | 252341110 | 42.16 |  |  |  | 42.16
REEDLEY 1112 | 252341112 | 89.86 |  | 0.78 |  | 89.08
RENFRO 2101 | 254572101 | 31.34 |  |  |  | 31.34
RENFRO 2102 | 254572102 | 4.41 |  |  |  | 4.41
RENFRO 2103 | 254572103 | 25.47 |  |  |  | 25.47
RENFRO 2105 | 254572105 | 10.08 |  |  |  | 10.08
RENFRO 2107 | 254572107 | 6.74 |  |  |  | 6.74
RESEARCH 2101 | 14692101 | 7.79 |  |  |  | 7.79
RESEARCH 2102 | 14692102 | 20.7 | 2.17 |  |  | 18.53
RESERVATION ROAD 1101 | 182731101 | 36.95 |  | 29.08 |  | 7.87
RESERVATION ROAD 1102 | 182731102 | 58.33 |  | 19.69 |  | 38.64
RESERVE OIL 1101 | 254181101 | 2.19 |  |  |  | 2.19
RICE 1101 | 62831101 | 53.25 |  |  |  | 53.25
RICE 1102 | 62831102 | 62.18 |  |  |  | 62.18
RICE 1103 | 62831103 | 77.94 |  |  |  | 77.94
RICE 1104 | 62831104 | 32.94 |  |  |  | 32.94
RICHMOND Q 0401 | 12520401 | 5.95 |  |  |  | 5.95
RICHMOND Q 0402 | 12520402 | 3.61 |  |  |  | 3.61
RICHMOND R 1118 | 13471118 | 2.97 |  |  |  | 2.97
RICHMOND R 1119 | 13471119 | 3.58 |  |  |  | 3.58
RICHMOND R 1120 | 13471120 | 2.97 |  |  |  | 2.97
RICHMOND R 1121 | 13471121 | 4.47 |  |  |  | 4.47
RICHMOND R 1122 | 13471122 | 3.86 |  |  |  | 3.86
RICHMOND R 1123 | 13471123 | 1.33 |  |  |  | 1.33
RICHMOND R 1124 | 13471124 | 6.75 |  |  |  | 6.75
RICHMOND R 1125 | 13471125 | 4.61 |  |  |  | 4.61
RICHMOND R 1126 | 13471126 | 13.05 |  |  |  | 13.05
RICHMOND R 1127 | 13471127 | 20.27 |  |  |  | 20.27
RICHMOND R 1128 | 13471128 | 7.55 |  |  |  | 7.55
RICHMOND R 1129 | 13471129 | 13.87 |  |  |  | 13.87
RICHMOND R 1130 | 13471130 | 15.96 |  |  |  | 15.96
RIDGE 0401 | 12840401 | 2.66 |  | 2.66 |  | 0
RIDGE 0402 | 12840402 | 2.4 |  | 1.75 |  | 0.65
RINCON 1101 | 43321101 | 38.12 | 16.46 | 5.75 |  | 15.91
RINCON 1102 | 43321102 | 19.26 | 0.01 | 2.61 |  | 16.64
RINCON 1103 | 43321103 | 47.95 | 40.61 | 4.37 |  | 2.97
RINCON 1104 | 43321104 | 11.53 | 1.92 |  |  | 9.61
RIO BRAVO 1101 | 252861101 | 20.93 |  |  |  | 20.93
RIO BRAVO 1102 | 252861102 | 36.79 |  |  |  | 36.79
RIO BRAVO 1103 | 252861103 | 26.97 |  |  |  | 26.97
RIO BRAVO 1104 | 252861104 | 8.61 |  |  |  | 8.61
RIO BRAVO 1106 | 252861106 | 62.94 |  |  |  | 62.94
RIO DELL 1101 | 192251101 | 19.46 |  |  |  | 19.46
RIO DELL 1102 | 192251102 | 73.38 |  | 49.2 | 0.76 | 23.42
RIPON 1701 | 163801701 | 64.88 |  |  |  | 64.88
RIPON 1702 | 163801702 | 24.67 |  |  |  | 24.67
RIPON 1703 | 163801703 | 83.43 |  |  |  | 83.43
RIPON 1704 | 163801704 | 9.74 |  |  |  | 9.74
RISING RIVER 1101 | 103551101 | 58.65 |  | 43.52 |  | 15.13
RIVER ROCK 1101 | 255251101 | 0.02 |  |  |  | 0.02
RIVERBANK 1711 | 163191711 | 36.14 |  |  |  | 36.14
RIVERBANK 1712 | 163191712 | 54.39 |  |  |  | 54.39
RIVERBANK 1713 | 163191713 | 54.12 |  |  |  | 54.12
RIVERBANK 1714 | 163191714 | 33.84 |  |  |  | 33.84
RIVERBANK 1715 | 163191715 | 92.48 |  |  |  | 92.48
RIVERBANK 1716 | 163191716 | 26.89 |  |  |  | 26.89
ROB ROY 2104 | 83692104 | 159.83 | 39.36 | 62.04 |  | 58.43
ROB ROY 2105 | 83692105 | 66.26 | 26.89 | 11.33 |  | 28.04
ROCKLIN 1101 | 152061101 | 4.72 |  |  |  | 4.72
ROCKLIN 1102 | 152061102 | 18.66 |  |  |  | 18.66
ROCKLIN 1103 | 152061103 | 5.11 |  |  |  | 5.11
ROCKLIN 1104 | 152061104 | 3.3 |  |  |  | 3.3
ROSEDALE 1101 | 254761101 | 12.1 |  |  |  | 12.1
ROSEDALE 2102 | 254762102 | 3.72 |  |  |  | 3.72
ROSSMOOR 1101 | 14161101 | 30.55 | 2.13 | 10.74 |  | 17.68
ROSSMOOR 1102 | 14161102 | 1.45 | 0.45 |  |  | 1
ROSSMOOR 1103 | 14161103 | 2.58 |  |  |  | 2.58
ROSSMOOR 1104 | 14161104 | 19.43 |  | 0.3 |  | 19.13
ROSSMOOR 1105 | 14161105 | 4.27 |  |  |  | 4.27
ROSSMOOR 1106 | 14161106 | 16.09 | 0.58 | 2.84 |  | 12.67
ROSSMOOR 1107 | 14161107 | 10.51 | 0.03 |  |  | 10.48
ROSSMOOR 1108 | 14161108 | 13.12 | 1.97 | 3.14 |  | 8.01
ROSSMOOR 1109 | 14161109 | 13.98 | 6.35 | 1.14 |  | 6.49
ROUGH AND READY ISLA 1102 | 163081102 | 54.28 |  |  |  | 54.28
ROUND MOUNTAIN 1101 | 109001101 | 0.02 |  | 0.02 |  | 0
RUSS RANCH 1101 | 192471101 | 0.22 |  |  |  | 0.22
RUSSELL (SMUD) 2101 | 63142101 | 5.14 |  |  |  | 5.14
RUSSELL 0401 | 13310401 | 3.41 |  |  |  | 3.41
RUSSELL 0402 | 13310402 | 3.34 |  |  |  | 3.34
SALINAS 1101 | 182011101 | 8.27 |  |  |  | 8.27
SALINAS 1102 | 182011102 | 21.22 |  |  |  | 21.22
SALINAS 1103 | 182011103 | 10.8 |  |  |  | 10.8
SALINAS 1104 | 182011104 | 31.51 |  |  |  | 31.51
SALINAS 1105 | 182011105 | 10.9 |  |  |  | 10.9
SALINAS 1106 | 182011106 | 18.61 |  |  |  | 18.61
SALINAS 1107 | 182011107 | 7.19 |  |  |  | 7.19
SALINAS 1108 | 182011108 | 2.73 |  |  |  | 2.73
SALINAS 1109 | 182011109 | 20.41 |  |  |  | 20.41
SALMON CREEK 1101 | 43161101 | 47.28 | 7.21 | 14.96 |  | 25.11
SALT SPRINGS 2101 | 163692101 | 21.96 |  | 17.07 | 1.36 | 3.53
SALT SPRINGS 2102 | 163692102 | 51.97 | 42.09 | 9.81 |  | 0.07
SAN ARDO 1101 | 182191101 | 56.61 |  | 2.67 |  | 53.94
SAN ARDO 1102 | 182191102 | 124.26 |  |  |  | 124.26
SAN BENITO 2101 | 182742101 | 48.3 |  | 4.28 |  | 44.02
SAN BENITO 2102 | 182742102 | 12.95 |  |  |  | 12.95
SAN BENITO 2103 | 182742103 | 0.59 |  |  |  | 0.59
SAN BENITO 2104 | 182742104 | 51.43 |  | 26.66 |  | 24.77
SAN BERNARD 1101 | 253191101 | 41.93 |  | 1.17 |  | 40.76
SAN BERNARD 1102 | 253191102 | 11.98 |  |  |  | 11.98
SAN BERNARD 1104 | 253191104 | 9.26 |  |  |  | 9.26
SAN BRUNO 0401 | 22700401 | 3.61 |  |  |  | 3.61
SAN BRUNO 0402 | 22700402 | 3.11 |  |  |  | 3.11
SAN BRUNO 0403 | 22700403 | 5.03 |  |  |  | 5.03
SAN CARLOS 0401 | 24180401 | 1.65 |  |  |  | 1.65
SAN CARLOS 0402 | 24180402 | 4.29 |  |  |  | 4.29
SAN CARLOS 0403 | 24180403 | 6.92 |  |  |  | 6.92
SAN CARLOS 0404 | 24180404 | 8.75 |  |  |  | 8.75
SAN CARLOS 0405 | 24180405 | 8.18 |  |  |  | 8.18
SAN CARLOS 0406 | 24180406 | 6.54 |  |  |  | 6.54
SAN CARLOS 1101 | 24181101 | 1.46 |  |  |  | 1.46
SAN CARLOS 1102 | 24181102 | 0.46 |  |  |  | 0.46
SAN CARLOS 1103 | 24181103 | 16.49 |  | 3.82 |  | 12.67
SAN CARLOS 1104 | 24181104 | 22.03 |  | 10.61 |  | 11.42
SAN JOAQUIN #2 1103 | 252521103 | 79.88 | 10.31 | 69.57 |  | 0
SAN JOAQUIN #3 1101 | 252531101 | 24.33 | 22.76 | 1.57 |  | 0
SAN JOAQUIN #3 1102 | 252531102 | 11.39 | 5.46 | 5.94 |  | -0.01
SAN JOAQUIN #3 1103 | 252531103 | 56.28 | 30.39 | 25.89 |  | 0
SAN JOAQUIN 1106 | 252361106 | 52.04 |  |  |  | 52.04
SAN JOAQUIN 1108 | 252361108 | 41.1 |  |  |  | 41.1
SAN JOAQUIN 1112 | 252361112 | 42.24 |  |  |  | 42.24
SAN JOSE A 0403 | 82250403 | 3.98 |  |  |  | 3.98
SAN JOSE A 0404 | 82250404 | 1.66 |  |  |  | 1.66
SAN JOSE A 0405 | 82250405 | 1.83 |  |  |  | 1.83
SAN JOSE A 0407 | 82250407 | 1.83 |  |  |  | 1.83
SAN JOSE A 0408 | 82250408 | 2.39 |  |  |  | 2.39
SAN JOSE A 0410 | 82250410 | 4.56 |  |  |  | 4.56
SAN JOSE A 1109 | 82251109 | 0.62 |  |  |  | 0.62
SAN JOSE A 1110 | 82251110 | 9.02 |  |  |  | 9.02
SAN JOSE A 1111 | 82251111 | 0.12 |  |  |  | 0.12
SAN JOSE A 1112 | 82251112 | 10.55 |  |  |  | 10.55
SAN JOSE B 1101 | 82261101 | 0.16 |  |  |  | 0.16
SAN JOSE B 1102 | 82261102 | 0.26 |  |  |  | 0.26
SAN JOSE B 1104 | 82261104 | 0.48 |  |  |  | 0.48
SAN JOSE B 1105 | 82261105 | 8.63 |  |  |  | 8.63
SAN JOSE B 1106 | 82261106 | 0.7 |  |  |  | 0.7
SAN JOSE B 1107 | 82261107 | 9.06 |  |  |  | 9.06
SAN JOSE B 1108 | 82261108 | 8.07 |  |  |  | 8.07
SAN JOSE B 1109 | 82261109 | 0.38 |  |  |  | 0.38
SAN JOSE B 1110 | 82261110 | 13.27 |  |  |  | 13.27
SAN JOSE B 1111 | 82261111 | 0.08 |  |  |  | 0.08
SAN JOSE B 1112 | 82261112 | 12.52 |  |  |  | 12.52
SAN JOSE B 1113 | 82261113 | 0.1 |  |  |  | 0.1
SAN JOSE B 1114 | 82261114 | 0.68 |  |  |  | 0.68
SAN JOSE B 1115 | 82261115 | 0.78 |  |  |  | 0.78
SAN JOSE B 1116 | 82261116 | 5 |  |  |  | 5
SAN JOSE B 1117 | 82261117 | 3.63 |  |  |  | 3.63
SAN JUSTO 1101 | 183181101 | 55.93 |  | 37.23 |  | 18.7
SAN LEANDRO U 1101 | 13111101 | 3.89 |  |  |  | 3.89
SAN LEANDRO U 1102 | 13111102 | 12.39 |  |  |  | 12.39
SAN LEANDRO U 1103 | 13111103 | 1.93 |  |  |  | 1.93
SAN LEANDRO U 1104 | 13111104 | 6.25 |  |  |  | 6.25
SAN LEANDRO U 1105 | 13111105 | 7.75 |  |  |  | 7.75
SAN LEANDRO U 1106 | 13111106 | 12.37 |  |  |  | 12.37
SAN LEANDRO U 1107 | 13111107 | 15.01 |  |  |  | 15.01
SAN LEANDRO U 1108 | 13111108 | 8.49 |  |  |  | 8.49
SAN LEANDRO U 1109 | 13111109 | 19.8 | 0.86 | 11.57 |  | 7.37
SAN LEANDRO U 1110 | 13111110 | 18.9 |  |  |  | 18.9
SAN LEANDRO U 1111 | 13111111 | 2.29 |  |  |  | 2.29
SAN LEANDRO U 1112 | 13111112 | 3.96 |  |  |  | 3.96
SAN LEANDRO U 1113 | 13111113 | 7.11 |  |  |  | 7.11
SAN LEANDRO U 1114 | 13111114 | 29.07 |  | 9.53 |  | 19.54
SAN LEANDRO U 1115 | 13111115 | 1.47 |  |  |  | 1.47
SAN LEANDRO U 1116 | 13111116 | 3.8 |  |  |  | 3.8
SAN LEANDRO U 1151 | 13111151 | 5.95 |  |  |  | 5.95
SAN LORENZO 0401 | 13460401 | 4.37 |  |  |  | 4.37
SAN LUIS OBISPO 1101 | 182631101 | 36.78 | 10.18 | 15.4 |  | 11.2
SAN LUIS OBISPO 1102 | 182631102 | 13.44 |  | 0.58 |  | 12.86
SAN LUIS OBISPO 1103 | 182631103 | 38.96 |  | 20.21 |  | 18.75
SAN LUIS OBISPO 1104 | 182631104 | 82.39 | 21.32 | 36.56 |  | 24.51
SAN LUIS OBISPO 1105 | 182631105 | 11.79 |  | 1.43 |  | 10.36
SAN LUIS OBISPO 1107 | 182631107 | 50.34 | 24.62 | 21.75 |  | 3.97
SAN LUIS OBISPO 1108 | 182631108 | 10.03 |  | 1.61 |  | 8.42
SAN MATEO 0404 | 24190404 | 5.08 |  |  |  | 5.08
SAN MATEO 0407 | 24190407 | 3.59 |  |  |  | 3.59
SAN MATEO 0408 | 24190408 | 5.63 |  |  |  | 5.63
SAN MATEO 0409 | 24190409 | 3.13 |  |  |  | 3.13
SAN MATEO 0410 | 24190410 | 5.15 |  |  |  | 5.15
SAN MATEO 2101 | 24192101 | 7.25 |  |  |  | 7.25
SAN MATEO 2102 | 24192102 | 13.01 |  |  |  | 13.01
SAN MIGUEL 1104 | 182661104 | 144.71 |  | 23.74 |  | 120.97
SAN MIGUEL 1105 | 182661105 | 20.16 |  | 1.39 |  | 18.77
SAN MIGUEL 1106 | 182661106 | 74.23 |  | 37.82 |  | 36.41
SAN MIGUEL 1107 | 182661107 | 5.74 |  |  |  | 5.74
SAN PABLO 1105 | 14371105 | 19.47 |  |  |  | 19.47
SAN PABLO 1106 | 14371106 | 0.65 |  |  |  | 0.65
SAN RAFAEL 1101 | 42011101 | 27.43 | 12.24 | 1.2 |  | 13.99
SAN RAFAEL 1102 | 42011102 | 4.85 |  |  |  | 4.85
SAN RAFAEL 1103 | 42011103 | 5.9 |  |  |  | 5.9
SAN RAFAEL 1104 | 42011104 | 24.9 | 1.88 | 9.71 |  | 13.31
SAN RAFAEL 1105 | 42011105 | 23.01 |  | 1.62 |  | 21.39
SAN RAFAEL 1106 | 42011106 | 21.1 |  | 2.8 |  | 18.3
SAN RAFAEL 1107 | 42011107 | 29.14 | 18.24 | 2.98 |  | 7.92
SAN RAFAEL 1108 | 42011108 | 29.46 | 26.37 | 0.44 |  | 2.65
SAN RAFAEL 1109 | 42011109 | 26.32 |  | 9.79 |  | 16.53
SAN RAFAEL 1110 | 42011110 | 13.14 | 7.93 |  |  | 5.21
SAN RAMON 2101 | 14232101 | 1.08 |  | 0.61 |  | 0.47
SAN RAMON 2102 | 14232102 | 2.33 |  | 1.52 |  | 0.81
SAN RAMON 2103 | 14232103 | 2.76 | 0 |  |  | 2.76
SAN RAMON 2104 | 14232104 | 20.65 |  |  |  | 20.65
SAN RAMON 2105 | 14232105 | 3.44 |  |  |  | 3.44
SAN RAMON 2106 | 14232106 | 5.09 | 0.45 |  |  | 4.64
SAN RAMON 2107 | 14232107 | 27.43 | 14.33 | 0.17 |  | 12.93
SAN RAMON 2108 | 14232108 | 17.31 | 16.38 |  |  | 0.93
SAN RAMON 2110 | 14232110 | 0.1 |  |  |  | 0.1
SAN RAMON 2111 | 14232111 | 9.43 |  |  |  | 9.43
SAN RAMON 2114 | 14232114 | 1.61 |  |  |  | 1.61
SAN RAMON 2116 | 14232116 | 0 |  |  |  | 0
SAN RAMON 2117 | 14232117 | 1.67 |  | 0.56 |  | 1.11
SAN RAMON 2118 | 14232118 | 0.82 |  |  |  | 0.82
SAN RAMON 2119 | 14232119 | 3.02 |  | 0.59 |  | 2.43
SAND CREEK 1103 | 254601103 | 150.17 |  | 148.46 |  | 1.71
SANGER 1104 | 252351104 | 9.61 |  |  |  | 9.61
SANGER 1106 | 252351106 | 8.57 |  |  |  | 8.57
SANGER 1108 | 252351108 | 81.22 |  |  |  | 81.22
SANGER 1110 | 252351110 | 29.33 |  |  |  | 29.33
SANGER 1112 | 252351112 | 11.54 |  |  |  | 11.54
SANGER 1114 | 252351114 | 63.07 |  |  |  | 63.07
SANGER 1116 | 252351116 | 6.36 |  |  |  | 6.36
SANGER 1118 | 252351118 | 29.51 |  |  |  | 29.51
SANTA MARIA 1105 | 182671105 | 28.85 |  |  |  | 28.85
SANTA MARIA 1106 | 182671106 | 18.94 |  |  |  | 18.94
SANTA MARIA 1107 | 182671107 | 4.93 |  |  |  | 4.93
SANTA MARIA 1108 | 182671108 | 93.89 | 43.73 | 28.52 |  | 21.64
SANTA MARIA 1109 | 182671109 | 46.46 |  |  |  | 46.46
SANTA MARIA 1110 | 182671110 | 52.56 |  |  |  | 52.56
SANTA MARIA 1111 | 182671111 | 15.6 |  |  |  | 15.6
SANTA MARIA 1112 | 182671112 | 10.45 |  |  |  | 10.45
SANTA NELLA 1101 | 254051101 | 38.53 |  |  |  | 38.53
SANTA NELLA 1104 | 254051104 | 52.32 |  |  |  | 52.32
SANTA RITA 1102 | 253541102 | 89.22 |  |  |  | 89.22
SANTA RITA 1105 | 253541105 | 61.38 |  |  |  | 61.38
SANTA ROSA A 1101 | 42151101 | 4.52 |  |  |  | 4.52
SANTA ROSA A 1102 | 42151102 | 12.08 |  |  |  | 12.08
SANTA ROSA A 1103 | 42151103 | 10.95 |  |  |  | 10.95
SANTA ROSA A 1104 | 42151104 | 56.15 | 37.51 | 5.24 |  | 13.4
SANTA ROSA A 1105 | 42151105 | 9.38 |  |  |  | 9.38
SANTA ROSA A 1106 | 42151106 | 10 |  |  |  | 10
SANTA ROSA A 1107 | 42151107 | 8.43 | 2.88 |  |  | 5.55
SANTA ROSA A 1108 | 42151108 | 6.81 |  | 0.14 |  | 6.67
SANTA ROSA A 1109 | 42151109 | 5.92 |  |  |  | 5.92
SANTA ROSA A 1110 | 42151110 | 22.39 |  |  |  | 22.39
SANTA ROSA A 1111 | 42151111 | 26.1 |  | 5.67 |  | 20.43
SANTA ROSA A 1112 | 42151112 | 12.64 |  |  |  | 12.64
SANTA TERESA 2101 | 82962101 | 0.43 |  |  |  | 0.43
SANTA YNEZ 1101 | 182721101 | 58.86 | 14.55 | 14.07 |  | 30.24
SANTA YNEZ 1102 | 182721102 | 33.83 | 4.99 | 9.01 |  | 19.83
SANTA YNEZ 1104 | 182721104 | 84.8 | 4.59 | 37.72 |  | 42.49
SARANAP 0401 | 13560401 | 2.46 |  |  |  | 2.46
SARATOGA 1103 | 83371103 | 10.48 |  | 4.59 |  | 5.89
SARATOGA 1104 | 83371104 | 18.12 |  | 2.92 |  | 15.2
SARATOGA 1105 | 83371105 | 16.72 |  | 10.1 |  | 6.62
SARATOGA 1106 | 83371106 | 26.76 | 1.38 | 14.05 |  | 11.33
SARATOGA 1107 | 83371107 | 45.44 | 20.53 | 13.94 |  | 10.97
SARATOGA 1108 | 83371108 | 18.57 |  |  |  | 18.57
SARATOGA 1109 | 83371109 | 25.33 |  |  |  | 25.33
SARATOGA 1110 | 83371110 | 19.99 |  |  |  | 19.99
SARATOGA 1111 | 83371111 | 23.93 |  |  |  | 23.93
SARATOGA 1112 | 83371112 | 8.44 |  |  |  | 8.44
SARATOGA 1113 | 83371113 | 25.66 |  |  |  | 25.66
SARATOGA 1114 | 83371114 | 21.11 |  |  |  | 21.11
SARATOGA 1115 | 83371115 | 13.81 |  | 2.82 |  | 10.99
SAUSALITO 0401 | 42490401 | 2.01 |  |  |  | 2.01
SAUSALITO 0402 | 42490402 | 2.94 |  |  |  | 2.94
SAUSALITO 1101 | 42491101 | 6.74 |  | 1.25 |  | 5.49
SAUSALITO 1102 | 42491102 | 17.99 |  | 9.11 |  | 8.88
SCE MCFARLAND 1101 | 258111101 | 0.5 |  |  |  | 0.5
SCE REFUGIO 1701 | 188071701 | 0.08 | 0.08 |  |  | 0
SCE TEHACHAPI 1101 | 258131101 | 1.44 |  | 1.44 |  | 0
SCE TEJON TIE 1101 | 258191101 | 0.06 |  | 0.06 |  | 0
SCE VEGAS 1701 | 188881701 | 0.17 | 0.17 |  |  | 0
SCHINDLER 1104 | 252891104 | 0.01 |  |  |  | 0.01
SCHINDLER 1105 | 252891105 | 41.86 |  |  |  | 41.86
SCHINDLER 1107 | 252891107 | 1.43 |  |  |  | 1.43
SCHINDLER 1108 | 252891108 | 2.31 |  |  |  | 2.31
SCHINDLER 1109 | 252891109 | 1.67 |  |  |  | 1.67
SCHINDLER 1110 | 252891110 | 48.18 |  |  |  | 48.18
SCHINDLER 1111 | 252891111 | 41.63 |  |  |  | 41.63
SCHINDLER 1112 | 252891112 | 49.22 |  |  |  | 49.22
SCHINDLER 1114 | 252891114 | 58.36 |  |  |  | 58.36
SCHINDLER 1116 | 252891116 | 25.73 |  |  |  | 25.73
SEACLIFF 0401 | 83500401 | 9.16 | 6.52 | 1.23 |  | 1.41
SEACLIFF 0402 | 83500402 | 1.57 | 0.07 | 0.01 |  | 1.49
SEMITROPIC 1104 | 252901104 | 15.83 |  |  |  | 15.83
SEMITROPIC 1106 | 252901106 | 27.34 |  |  |  | 27.34
SEMITROPIC 1108 | 252901108 | 11.78 |  |  |  | 11.78
SEMITROPIC 1110 | 252901110 | 50.12 |  |  |  | 50.12
SEMITROPIC 1112 | 252901112 | 26.73 |  |  |  | 26.73
SERRAMONTE 1103 | 22861103 | 13.16 |  |  |  | 13.16
SERRAMONTE 1104 | 22861104 | 12.65 |  |  |  | 12.65
SF E 0401 | 22070401 | 3.52 |  |  |  | 3.52
SF E 0405 | 22070405 | 2.2 |  |  |  | 2.2
SF E 0406 | 22070406 | 1.47 |  |  |  | 1.47
SF E 0407 | 22070407 | 0.94 |  |  |  | 0.94
SF E 0408 | 22070408 | 2.68 |  |  |  | 2.68
SF E 0409 | 22070409 | 1.8 |  |  |  | 1.8
SF E 0410 | 22070410 | 1.87 |  |  |  | 1.87
SF E 1101 | 22071101 | 1.12 |  |  |  | 1.12
SF E 1103 | 22071103 | 3.14 |  |  |  | 3.14
SF E 1105 | 22071105 | 2.42 |  |  |  | 2.42
SF E 1107 | 22071107 | 3.75 |  |  |  | 3.75
SF G 0401 | 22090401 | 0.67 |  |  |  | 0.67
SF G 0402 | 22090402 | 1.56 |  |  |  | 1.56
SF G 0403 | 22090403 | 0.71 |  |  |  | 0.71
SF G 0404 | 22090404 | 0.96 |  |  |  | 0.96
SF G 0405 | 22090405 | 1.47 |  |  |  | 1.47
SF G 0406 | 22090406 | 1.28 |  |  |  | 1.28
SF G 0407 | 22090407 | 1.36 |  |  |  | 1.36
SF G 0408 | 22090408 | 1.28 |  |  |  | 1.28
SF G 0409 | 22090409 | 0.91 |  |  |  | 0.91
SF G 0410 | 22090410 | 0.58 |  |  |  | 0.58
SF G 0412 | 22090412 | 1.1 |  |  |  | 1.1
SF G 0413 | 22090413 | 0.98 |  |  |  | 0.98
SF G 0414 | 22090414 | 0.89 |  |  |  | 0.89
SF G 1101 | 22091101 | 1.02 |  |  |  | 1.02
SF G 1102 | 22091102 | 0.56 |  |  |  | 0.56
SF H 0401 | 22100401 | 4.61 |  |  |  | 4.61
SF H 0402 | 22100402 | 4.08 |  |  |  | 4.08
SF H 0403 | 22100403 | 1.06 |  |  |  | 1.06
SF H 0404 | 22100404 | 2.72 |  |  |  | 2.72
SF H 0405 | 22100405 | 2.46 |  |  |  | 2.46
SF H 1101 | 22101101 | 6.42 |  |  |  | 6.42
SF H 1102 | 22101102 | 6.91 |  |  |  | 6.91
SF H 1103 | 22101103 | 8.63 |  |  |  | 8.63
SF H 1104 | 22101104 | 0.65 |  |  |  | 0.65
SF H 1105 | 22101105 | 14.84 |  |  |  | 14.84
SF H 1106 | 22101106 | 7.93 |  |  |  | 7.93
SF H 1107 | 22101107 | 3.78 |  |  |  | 3.78
SF H 1108 | 22101108 | 13.42 |  |  |  | 13.42
SF H 1109 | 22101109 | 4.69 |  |  |  | 4.69
SF H 1110 | 22101110 | 13.13 |  |  |  | 13.13
SF H 1111 | 22101111 | 3.9 |  |  |  | 3.9
SF J 0402 | 22220402 | 0.87 |  |  |  | 0.87
SF J 0404 | 22220404 | 0.52 |  |  |  | 0.52
SF J 0406 | 22220406 | 0.52 |  |  |  | 0.52
SF J 0407 | 22220407 | 0 |  |  |  | 0
SF J 0409 | 22220409 | 0.15 |  |  |  | 0.15
SF J 1108 | 22221108 | 0 |  |  |  | 0
SF K 0401 | 22130401 | 2.48 |  |  |  | 2.48
SF K 0402 | 22130402 | 3.31 |  |  |  | 3.31
SF K 0403 | 22130403 | 2.49 |  |  |  | 2.49
SF K 0404 | 22130404 | 0.97 |  |  |  | 0.97
SF K 0405 | 22130405 | 2.81 |  |  |  | 2.81
SF K 0406 | 22130406 | 1.73 |  |  |  | 1.73
SF K 0407 | 22130407 | 1.28 |  |  |  | 1.28
SF K 0408 | 22130408 | 1.35 |  |  |  | 1.35
SF K 0409 | 22130409 | 2.39 |  |  |  | 2.39
SF K 0410 | 22130410 | 2.03 |  |  |  | 2.03
SF K 0411 | 22130411 | 2.27 |  |  |  | 2.27
SF K 1101 | 22131101 | 6.74 |  |  |  | 6.74
SF L 0401 | 22260401 | 2.47 |  |  |  | 2.47
SF L 0402 | 22260402 | 0 |  |  |  | 0
SF L 0403 | 22260403 | 0.25 |  |  |  | 0.25
SF L 0404 | 22260404 | 0.81 |  |  |  | 0.81
SF L 0405 | 22260405 | 2.3 |  |  |  | 2.3
SF L 0406 | 22260406 | 2.14 |  |  |  | 2.14
SF L 0407 | 22260407 | 0.55 |  |  |  | 0.55
SF L 0408 | 22260408 | 2.4 |  |  |  | 2.4
SF L 0409 | 22260409 | 0.15 |  |  |  | 0.15
SF L 1101 | 22261101 | 2.38 |  |  |  | 2.38
SF L 1102 | 22261102 | 7.95 |  |  |  | 7.95
SF L 1103 | 22261103 | 1.97 |  |  |  | 1.97
SF M 0401 | 22270401 | 3.73 |  |  |  | 3.73
SF M 0402 | 22270402 | 1.97 |  |  |  | 1.97
SF M 0403 | 22270403 | 3.69 |  |  |  | 3.69
SF M 0404 | 22270404 | 3.57 |  |  |  | 3.57
SF M 0405 | 22270405 | 2.35 |  |  |  | 2.35
SF M 0406 | 22270406 | 2.91 |  |  |  | 2.91
SF N 0401 | 22280401 | 3.13 |  |  |  | 3.13
SF N 0402 | 22280402 | 1.01 |  |  |  | 1.01
SF N 0403 | 22280403 | 2.47 |  |  |  | 2.47
SF N 0405 | 22280405 | 1.07 |  |  |  | 1.07
SF N 0406 | 22280406 | 0.8 |  |  |  | 0.8
SF N 0408 | 22280408 | 3.12 |  |  |  | 3.12
SF N 1101 | 22281101 | 0.27 |  |  |  | 0.27
SF N 1102 | 22281102 | 6.09 |  |  |  | 6.09
SHADY GLEN 1101 | 152431101 | 41.09 |  | 34.74 |  | 6.35
SHADY GLEN 1102 | 152431102 | 51.78 | 24.1 | 25.89 |  | 1.79
SHAFTER 1101 | 253651101 | 0.03 |  |  |  | 0.03
SHAFTER 1102 | 253651102 | 27.52 |  |  |  | 27.52
SHAFTER 1103 | 253651103 | 39.63 |  |  |  | 39.63
SHAFTER 1104 | 253651104 | 9.62 |  |  |  | 9.62
SHAFTER 1111 | 253651111 | 24.34 |  |  |  | 24.34
SHAFTER 1112 | 253651112 | 47.89 |  |  |  | 47.89
SHARON 1101 | 255331101 | 1.54 |  |  |  | 1.54
SHEPHERD 2109 | 252062109 | 4.35 |  |  |  | 4.35
SHEPHERD 2110 | 252062110 | 8.38 |  |  |  | 8.38
SHEPHERD 2111 | 252062111 | 69.07 |  | 29.52 |  | 39.55
SHEPHERD 2112 | 252062112 | 7.75 |  |  |  | 7.75
SHINGLE SPRINGS 1103 | 153651103 | 13.67 | 4.6 | 3.1 |  | 5.97
SHINGLE SPRINGS 1104 | 153651104 | 59.85 | 37.11 | 6.66 |  | 16.08
SHINGLE SPRINGS 2105 | 153652105 | 32.74 | 26.05 | 4.37 |  | 2.32
SHINGLE SPRINGS 2108 | 153652108 | 29.67 | 7.21 | 7.76 |  | 14.7
SHINGLE SPRINGS 2109 | 153652109 | 209.66 | 107.69 | 101.33 |  | 0.64
SHINGLE SPRINGS 2110 | 153652110 | 65.17 | 55.44 | 7.37 |  | 2.36
SILVER 0401 | 22670401 | 5.04 |  |  |  | 5.04
SILVERADO 2102 | 43432102 | 108.6 | 32.79 | 24.65 |  | 51.16
SILVERADO 2103 | 43432103 | 32.58 | 10.77 | 0.03 |  | 21.78
SILVERADO 2104 | 43432104 | 139.18 | 75.02 | 36.32 |  | 27.84
SILVERADO 2105 | 43432105 | 63.59 | 34.9 | 1.72 |  | 26.97
SISQUOC 1101 | 182811101 | 26.81 |  |  |  | 26.81
SISQUOC 1102 | 182811102 | 115.23 | 31.2 | 19.57 |  | 64.46
SISQUOC 1103 | 182811103 | 50.1 | 22.64 | 2.79 |  | 24.67
SISQUOC 1104 | 182811104 | 32.55 |  |  |  | 32.55
SKAGGS ISLAND 1101 | 43341101 | 0.05 |  |  |  | 0.05
SMARTVILLE 1101 | 153791101 | 16.07 |  | 15.75 |  | 0.32
SMUD 0401 | 158050401 | 0.01 |  | 0.01 |  | 0
SMYRNA 1101 | 253551101 | 43.48 |  |  |  | 43.48
SMYRNA 1102 | 253551102 | 66.66 |  |  |  | 66.66
SMYRNA 1104 | 253551104 | 44.55 |  |  |  | 44.55
SMYRNA 1105 | 253551105 | 51.92 |  |  |  | 51.92
SMYRNA 1106 | 253551106 | 46.54 |  |  |  | 46.54
SNEATH LANE 1101 | 22721101 | 9.42 |  | 2.26 |  | 7.16
SNEATH LANE 1102 | 22721102 | 10.53 |  | 1.24 |  | 9.29
SNEATH LANE 1106 | 22721106 | 11.62 |  | 2.62 |  | 9
SNEATH LANE 1107 | 22721107 | 10.47 |  | 0.91 |  | 9.56
SO. CAL. EDISON #3 1101 | 258861101 | 9.49 | 6.73 | 2.6 |  | 0.16
SO. CAL. EDISON 1001 | 258881001 | 2.02 |  |  |  | 2.02
SOBRANTE 1101 | 14671101 | 21.39 |  | 14.97 |  | 6.42
SOBRANTE 1102 | 14671102 | 27.62 | 1.26 | 26 |  | 0.36
SOBRANTE 1103 | 14671103 | 11.36 | 1.82 | 7.69 |  | 1.85
SOLANO 0402 | 13140402 | 6.32 |  |  |  | 6.32
SOLEDAD 2101 | 182052101 | 41.49 |  | 17.33 |  | 24.16
SOLEDAD 2102 | 182052102 | 48.97 |  | 11.6 |  | 37.37
SOLEDAD 2104 | 182052104 | 25.09 |  | 1.22 |  | 23.87
SOLEDAD 2105 | 182052105 | 47.73 |  | 4.47 |  | 43.26
SONOMA 1102 | 42721102 | 18.14 | 6.02 |  |  | 12.12
SONOMA 1103 | 42721103 | 25.42 | 12.68 |  |  | 12.74
SONOMA 1104 | 42721104 | 55.43 |  | 19.63 |  | 35.8
SONOMA 1105 | 42721105 | 63.43 | 3.47 | 10.14 |  | 49.82
SONOMA 1106 | 42721106 | 11.14 | 0.88 |  |  | 10.26
SONOMA 1107 | 42721107 | 51.96 |  | 3.87 |  | 48.09
SOQUEL 0402 | 83300402 | 6.58 |  |  |  | 6.58
SOTO 0402 | 13260402 | 2.04 |  |  |  | 2.04
SPAULDING 1101 | 152251101 | 23.94 | 1.19 | 19.15 | 0.37 | 3.23
SPENCE 1102 | 182201102 | 33.47 |  | 2.36 |  | 31.11
SPENCE 1103 | 182201103 | 12.37 |  |  |  | 12.37
SPENCE 1104 | 182201104 | 52.34 |  | 9.04 |  | 43.3
SPENCE 1105 | 182201105 | 7.18 |  |  |  | 7.18
SPRING GAP 1702 | 162831702 | 42.35 | 39.7 | 0.77 |  | 1.88
STAFFORD 1101 | 43201101 | 15.35 |  | 2.27 |  | 13.08
STAFFORD 1102 | 43201102 | 37.35 | 1.54 | 19.66 |  | 16.15
STAGG 1101 | 162421101 | 19.59 |  |  |  | 19.59
STAGG 1103 | 162421103 | 6.06 |  |  |  | 6.06
STAGG 1105 | 162421105 | 12.07 |  |  |  | 12.07
STAGG 1106 | 162421106 | 1.86 |  |  |  | 1.86
STAGG 2104 | 162422104 | 24.45 |  |  |  | 24.45
STAGG 2105 | 162422105 | 4.5 |  |  |  | 4.5
STAGG 2106 | 162422106 | 5.45 |  |  |  | 5.45
STAGG 2107 | 162422107 | 6.04 |  |  |  | 6.04
STAGG 2108 | 162422108 | 5.83 |  |  |  | 5.83
STANISLAUS 1701 | 162821701 | 74.89 | 22.65 | 51.99 |  | 0.25
STANISLAUS 1702 | 162821702 | 85 | 78.35 | 6.66 |  | -0.01
STELLING 1102 | 83481102 | 0.69 |  |  |  | 0.69
STELLING 1103 | 83481103 | 2.85 |  |  |  | 2.85
STELLING 1104 | 83481104 | 11.01 |  |  |  | 11.01
STELLING 1105 | 83481105 | 0.4 |  |  |  | 0.4
STELLING 1106 | 83481106 | 0 |  |  |  | 0
STELLING 1107 | 83481107 | 8.19 |  |  |  | 8.19
STELLING 1108 | 83481108 | 31.72 |  |  |  | 31.72
STELLING 1109 | 83481109 | 16.57 |  | 0.88 |  | 15.69
STELLING 1110 | 83481110 | 49.26 | 10.28 | 21.86 |  | 17.12
STELLING 1111 | 83481111 | 26.77 |  |  |  | 26.77
STELLING 1112 | 83481112 | 2.19 |  |  |  | 2.19
STELLING 1113 | 83481113 | 17.16 |  |  |  | 17.16
STILLWATER 1101 | 103561101 | 35.17 |  | 34.41 |  | 0.76
STILLWATER 1102 | 103561102 | 78.34 |  | 78.24 |  | 0.1
STOCKDALE 1105 | 254071105 | 5.05 |  |  |  | 5.05
STOCKDALE 1106 | 254071106 | 5.6 |  |  |  | 5.6
STOCKDALE 1108 | 254071108 | 3.84 |  |  |  | 3.84
STOCKDALE 1109 | 254071109 | 4.48 |  |  |  | 4.48
STOCKDALE 1110 | 254071110 | 6.31 |  |  |  | 6.31
STOCKDALE 1111 | 254071111 | 8.66 |  |  |  | 8.66
STOCKDALE 2105 | 254072105 | 5.01 |  |  |  | 5.01
STOCKDALE 2106 | 254072106 | 8.97 |  |  |  | 8.97
STOCKDALE 2107 | 254072107 | 1.84 |  |  |  | 1.84
STOCKDALE 2108 | 254072108 | 2.96 |  |  |  | 2.96
STOCKDALE 2109 | 254072109 | 8.53 |  |  |  | 8.53
STOCKDALE 2110 | 254072110 | 8.78 |  |  |  | 8.78
STOCKDALE 2111 | 254072111 | 2.87 |  |  |  | 2.87
STOCKDALE 2112 | 254072112 | 30.1 |  |  |  | 30.1
STOCKDALE 2113 | 254072113 | 15.7 |  |  |  | 15.7
STOCKDALE 2114 | 254072114 | 10.47 |  |  |  | 10.47
STOCKDALE 2115 | 254072115 | 0.45 |  |  |  | 0.45
STOCKTON A 0404 | 162370404 | 5.17 |  |  |  | 5.17
STOCKTON A 0405 | 162370405 | 0.39 |  |  |  | 0.39
STOCKTON A 0406 | 162370406 | 3.25 |  |  |  | 3.25
STOCKTON A 0410 | 162370410 | 6.31 |  |  |  | 6.31
STOCKTON A 1101 | 162371101 | 4.12 |  |  |  | 4.12
STOCKTON A 1102 | 162371102 | 6.47 |  |  |  | 6.47
STOCKTON A 1103 | 162371103 | 0.21 |  |  |  | 0.21
STOCKTON A 1104 | 162371104 | 15.88 |  |  |  | 15.88
STOCKTON A 1105 | 162371105 | 12.35 |  |  |  | 12.35
STOCKTON A 1106 | 162371106 | 16.95 |  |  |  | 16.95
STOCKTON A 1107 | 162371107 | 11.28 |  |  |  | 11.28
STOCKTON A 1108 | 162371108 | 9.3 |  |  |  | 9.3
STOCKTON A 1109 | 162371109 | 11.9 |  |  |  | 11.9
STOCKTON A 1110 | 162371110 | 10.08 |  |  |  | 10.08
STOCKTON A 1111 | 162371111 | 0.07 |  |  |  | 0.07
STOCKTON ACRES 0401 | 163220401 | 2.87 |  |  |  | 2.87
STOCKTON ACRES 0402 | 163220402 | 3.01 |  |  |  | 3.01
STONE 1101 | 83701101 | 19.95 |  |  |  | 19.95
STONE 1104 | 83701104 | 5.55 |  |  |  | 5.55
STONE 1107 | 83701107 | 11.97 |  |  |  | 11.97
STONE 1108 | 83701108 | 4.39 |  |  |  | 4.39
STONE 1109 | 83701109 | 8.25 |  |  |  | 8.25
STONE 1110 | 83701110 | 11.83 |  |  |  | 11.83
STONE CORRAL 1108 | 252921108 | 76.2 |  | 1.87 |  | 74.33
STONE CORRAL 1109 | 252921109 | 16.52 |  |  |  | 16.52
STONE CORRAL 1110 | 252921110 | 62.6 |  | 2.01 |  | 60.59
STOREY 1104 | 254611104 | 75.54 |  |  |  | 75.54
STOREY 1105 | 254611105 | 14.36 |  |  |  | 14.36
STOREY 1106 | 254611106 | 13.49 |  |  |  | 13.49
STOREY 1107 | 254611107 | 19.08 |  |  |  | 19.08
STOREY 1108 | 254611108 | 72.24 |  |  |  | 72.24
STOREY 1109 | 254611109 | 177.3 |  |  |  | 177.3
STOREY 1111 | 254611111 | 29.65 |  |  |  | 29.65
STROUD 1101 | 253661101 | 31.94 |  |  |  | 31.94
STROUD 1102 | 253661102 | 34.26 |  |  |  | 34.26
STROUD 1104 | 253661104 | 31.17 |  |  |  | 31.17
STUART 0401 | 13840401 | 2.94 |  |  |  | 2.94
STUART 0402 | 13840402 | 2.12 |  |  |  | 2.12
STUART 0403 | 13840403 | 3.12 |  |  |  | 3.12
STUART 0404 | 13840404 | 1.07 |  |  |  | 1.07
STUART 0405 | 13840405 | 2.8 |  |  |  | 2.8
STUART 0406 | 13840406 | 2.94 |  |  |  | 2.94
SUISUN 1101 | 62131101 | 6.17 |  |  |  | 6.17
SUISUN 1102 | 62131102 | 9.81 |  |  |  | 9.81
SUISUN 1103 | 62131103 | 2.73 |  |  |  | 2.73
SUISUN 1104 | 62131104 | 4.83 |  |  |  | 4.83
SUISUN 1105 | 62131105 | 5.37 |  |  |  | 5.37
SUISUN 1106 | 62131106 | 4.99 |  |  |  | 4.99
SUISUN 1107 | 62131107 | 9.67 |  |  |  | 9.67
SUISUN 1108 | 62131108 | 6.59 |  |  |  | 6.59
SUISUN 1109 | 62131109 | 8.06 |  |  |  | 8.06
SUISUN 1110 | 62131110 | 2.91 |  |  |  | 2.91
SUISUN 1111 | 62131111 | 0.63 |  |  |  | 0.63
SUISUN 1112 | 62131112 | 2.85 |  |  |  | 2.85
SULLIVAN 0402 | 22850402 | 3.2 |  |  |  | 3.2
SUMMIT 1101 | 152591101 | 15.19 |  | 7.2 | 2.05 | 5.94
SUMMIT 1102 | 152591102 | 5.04 |  | 5.04 |  | 0
SUNOL 1101 | 14241101 | 55.43 | 9.57 | 23.58 |  | 22.28
SWIFT 2102 | 83392102 | 2.95 |  | 0.35 |  | 2.6
SWIFT 2106 | 83392106 | 21.28 |  |  |  | 21.28
SWIFT 2107 | 83392107 | 11.89 |  | 1.89 |  | 10
SWIFT 2108 | 83392108 | 4.92 |  |  |  | 4.92
SWIFT 2109 | 83392109 | 5.46 |  | 0.15 |  | 5.31
SWIFT 2110 | 83392110 | 86.24 |  | 81.31 |  | 4.93
SWIFT 2111 | 83392111 | 8.58 |  |  |  | 8.58
SYCAMORE CREEK 1101 | 102971101 | 4.78 |  |  |  | 4.78
SYCAMORE CREEK 1102 | 102971102 | 7.55 |  |  |  | 7.55
SYCAMORE CREEK 1103 | 102971103 | 3.14 |  |  |  | 3.14
SYCAMORE CREEK 1104 | 102971104 | 8.13 |  |  |  | 8.13
SYCAMORE CREEK 1105 | 102971105 | 15.13 |  |  |  | 15.13
SYCAMORE CREEK 1107 | 102971107 | 6.01 |  |  |  | 6.01
SYCAMORE CREEK 1109 | 102971109 | 13.42 |  | 0.13 |  | 13.29
SYCAMORE CREEK 1110 | 102971110 | 8.42 |  |  |  | 8.42
SYCAMORE CREEK 1111 | 102971111 | 64.8 | 27.37 | 24.9 |  | 12.53
TAFT 1101 | 252081101 | 14.18 |  |  |  | 14.18
TAFT 1102 | 252081102 | 0.05 |  |  |  | 0.05
TAFT 1103 | 252081103 | 27.46 |  |  |  | 27.46
TAFT 1104 | 252081104 | 11.2 |  |  |  | 11.2
TAFT 1106 | 252081106 | 7.13 |  |  |  | 7.13
TAFT 1108 | 252081108 | 9.21 |  |  |  | 9.21
TAMARACK 1101 | 152291101 | 19.55 |  | 18.66 | 0.13 | 0.76
TAMARACK 1102 | 152291102 | 7.85 |  |  | 0.31 | 7.54
TAR FLAT 0401 | 163240401 | 3.62 | 0 | 3.15 |  | 0.47
TAR FLAT 0402 | 163240402 | 6.7 | 0.88 | 4.52 |  | 1.3
TARAVAL 0401 | 22500401 | 1.82 |  |  |  | 1.82
TARAVAL 0402 | 22500402 | 3.04 |  |  |  | 3.04
TARAVAL 0403 | 22500403 | 3.47 |  |  |  | 3.47
TASSAJARA 2103 | 14662103 | 19.56 | 0.18 | 0.3 |  | 19.08
TASSAJARA 2104 | 14662104 | 9.65 | 1.57 | 4.36 |  | 3.72
TASSAJARA 2106 | 14662106 | 2.92 |  | 0.35 |  | 2.57
TASSAJARA 2107 | 14662107 | 8.52 |  |  |  | 8.52
TASSAJARA 2108 | 14662108 | 24.1 | 1.7 |  |  | 22.4
TASSAJARA 2109 | 14662109 | 4.02 |  | 2.89 |  | 1.13
TASSAJARA 2112 | 14662112 | 18.54 | 6.79 | 3.56 |  | 8.19
TASSAJARA 2113 | 14662113 | 4.93 | 3.82 |  |  | 1.11
TECUYA 1101 | 254511101 | 0.04 |  |  |  | 0.04
TEJON 1102 | 252931102 | 60.73 |  | 36.83 |  | 23.9
TEJON 1103 | 252931103 | 32.57 |  | 2.96 |  | 29.61
TEJON 1105 | 252931105 | 31.29 |  |  |  | 31.29
TEJON 1106 | 252931106 | 36 |  |  |  | 36
TEJON 1107 | 252931107 | 0.54 |  |  |  | 0.54
TEMBLOR 1104 | 252551104 | 49.26 |  |  |  | 49.26
TEMBLOR 2103 | 252552103 | 30.3 |  |  |  | 30.3
TEMPLETON 2108 | 183052108 | 36.13 |  | 5.36 |  | 30.77
TEMPLETON 2109 | 183052109 | 211.96 |  |  |  | 211.96
TEMPLETON 2110 | 183052110 | 173.1 | 33.51 | 93.84 |  | 45.75
TEMPLETON 2111 | 183052111 | 63.83 | 0.88 | 45.94 |  | 17.01
TEMPLETON 2112 | 183052112 | 37.82 |  | 2.6 |  | 35.22
TEMPLETON 2113 | 183052113 | 323.88 | 53.34 | 143.01 |  | 127.53
TEMPORARY CARBONA 1101 | 169951101 | 0.64 |  |  |  | 0.64
TEMPORARY CARBONA 1102 | 169951102 | 3.44 |  |  |  | 3.44
TEMPORARY CARBONA 1104 | 169951104 | 31.68 |  |  |  | 31.68
TEMPORARY CARBONA 1105 | 169951105 | 1.64 |  |  |  | 1.64
TERMINOUS 1102 | 163021102 | 22.68 |  |  |  | 22.68
TERMINOUS 1103 | 163021103 | 40.02 |  |  |  | 40.02
TEVIS 2101 | 255322101 | 23.77 |  |  |  | 23.77
TEVIS 2102 | 255322102 | 2.27 |  |  |  | 2.27
TEVIS 2103 | 255322103 | 3.28 |  |  |  | 3.28
TEVIS 2104 | 255322104 | 18.2 |  |  |  | 18.2
TEVIS 2105 | 255322105 | 1.97 |  |  |  | 1.97
TEXACO EMIDIO 1101 | 255421101 | 0.02 |  |  |  | 0.02
TIDEWATER 2104 | 14652104 | 26 |  |  |  | 26
TIDEWATER 2105 | 14652105 | 14.06 |  |  |  | 14.06
TIDEWATER 2106 | 14652106 | 35.95 |  | 3.68 |  | 32.27
TIDEWATER 2107 | 14652107 | 21.72 |  |  |  | 21.72
TIDEWATER 2108 | 14652108 | 9.6 |  |  |  | 9.6
TIDEWATER 2109 | 14652109 | 30.53 |  |  |  | 30.53
TIDEWATER 2110 | 14652110 | 10.17 |  |  |  | 10.17
TIGER CREEK 0201 | 161380201 | 3.77 | 1.73 | 2.04 |  | 0
TIVY VALLEY 1106 | 252941106 | 26.82 |  |  |  | 26.82
TIVY VALLEY 1107 | 252941107 | 174.29 |  | 116.36 |  | 57.93
TOCALOMA 0241 | 43150241 | 0.05 |  | 0.05 |  | 0
TOKAY 1101 | 168881101 | 12.31 |  |  |  | 12.31
TRACY 0402 | 162880402 | 2.91 |  |  |  | 2.91
TRACY 0405 | 162880405 | 3.24 |  |  |  | 3.24
TRACY 1102 | 162881102 | 27.77 |  |  |  | 27.77
TRACY 1103 | 162881103 | 4.42 |  |  |  | 4.42
TRACY 1104 | 162881104 | 4.73 |  |  |  | 4.73
TRACY 1105 | 162881105 | 4.74 |  |  |  | 4.74
TRACY 1106 | 162881106 | 36.57 |  |  |  | 36.57
TRACY 1107 | 162881107 | 6.14 |  |  |  | 6.14
TRACY 1109 | 162881109 | 5.11 |  |  |  | 5.11
TRACY 1110 | 162881110 | 9.14 |  |  |  | 9.14
TRACY 1111 | 162881111 | 7.23 |  |  |  | 7.23
TRACY 1112 | 162881112 | 4.69 |  |  |  | 4.69
TRES PINOS 1111 | 183221111 | 32.91 |  | 0.11 |  | 32.8
TRES VIAS 1101 | 103251101 | 68.6 |  |  |  | 68.6
TRIDAM POWERHOUSE 2101 | 168152101 | 0.05 | 0.05 |  |  | 0
TRIMBLE 1103 | 83801103 | 2.73 |  |  |  | 2.73
TRIMBLE 1104 | 83801104 | 0.41 |  |  |  | 0.41
TRIMBLE 1105 | 83801105 | 1.44 |  |  |  | 1.44
TRIMBLE 1106 | 83801106 | 0.65 |  |  |  | 0.65
TRIMBLE 1107 | 83801107 | 1.05 |  |  |  | 1.05
TRIMBLE 1110 | 83801110 | 0.34 |  |  |  | 0.34
TRIMBLE 2114 | 83802114 | 0 |  |  |  | 0
TRIMBLE 2115 | 83802115 | 0.31 |  |  |  | 0.31
TRIMBLE 2116 | 83802116 | 3.38 |  |  |  | 3.38
TRIMBLE 2118 | 83802118 | 0.39 |  |  |  | 0.39
TRINIDAD 1101 | 192231101 | 26.53 |  |  |  | 26.53
TRINIDAD 1102 | 192231102 | 24.19 |  |  | 0.25 | 23.94
TUDOR 1101 | 153711101 | 31.73 |  |  |  | 31.73
TUDOR 1102 | 153711102 | 23.15 |  |  |  | 23.15
TULARE LAKE 1104 | 252951104 | 14.58 |  |  |  | 14.58
TULARE LAKE 1106 | 252951106 | 52.18 |  |  |  | 52.18
TULARE LAKE 1108 | 252951108 | 48.76 |  |  |  | 48.76
TULE POWER HOUSE 1101 | 258591101 | 4.07 |  | 4.07 |  | 0
TULUCAY 1101 | 42301101 | 19.94 |  | 3.77 |  | 16.17
TUPMAN 1103 | 254561103 | 45.02 |  |  |  | 45.02
TUPMAN 1104 | 254561104 | 53.33 |  |  |  | 53.33
TUPMAN 1105 | 254561105 | 17.69 |  |  |  | 17.69
TUPMAN 1106 | 254561106 | 36.62 |  |  |  | 36.62
TWISSELMAN 1101 | 254401101 | 0.02 |  |  |  | 0.02
TWISSELMAN 1102 | 254401102 | 49.23 |  |  |  | 49.23
TWISSELMAN 1104 | 254401104 | 0.02 |  |  |  | 0.02
TWISSELMAN 2105 | 254402105 | 88.97 |  |  |  | 88.97
TYLER 1103 | 103571103 | 6.41 |  |  |  | 6.41
TYLER 1104 | 103571104 | 25.49 |  |  |  | 25.49
TYLER 1105 | 103571105 | 111.8 |  | 60.18 |  | 51.62
UKIAH 1111 | 42771111 | 32 |  | 7.84 |  | 24.16
UKIAH 1113 | 42771113 | 15.84 |  | 7.5 |  | 8.34
UKIAH 1114 | 42771114 | 103.63 |  | 53.83 |  | 49.8
UKIAH 1115 | 42771115 | 50.62 |  | 35.13 |  | 15.49
UPPER LAKE 1101 | 42871101 | 79.83 | 1.44 | 41.6 |  | 36.79
VACA DIXON 1101 | 63591101 | 50.46 |  | 22.5 |  | 27.96
VACA DIXON 1102 | 63591102 | 1.96 |  |  |  | 1.96
VACA DIXON 1103 | 63591103 | 126.78 |  |  |  | 126.78
VACA DIXON 1104 | 63591104 | 7.49 |  |  |  | 7.49
VACA DIXON 1105 | 63591105 | 49.72 |  | 1.4 |  | 48.32
VACA DIXON 1106 | 63591106 | 11.11 |  |  |  | 11.11
VACA DIXON 1109 | 63591109 | 2.13 |  |  |  | 2.13
VACAVILLE 1102 | 63601102 | 1 |  |  |  | 1
VACAVILLE 1103 | 63601103 | 11.13 |  |  |  | 11.13
VACAVILLE 1104 | 63601104 | 15.09 |  | 12.86 |  | 2.23
VACAVILLE 1105 | 63601105 | 2.87 |  |  |  | 2.87
VACAVILLE 1106 | 63601106 | 1.76 |  |  |  | 1.76
VACAVILLE 1107 | 63601107 | 1.91 |  |  |  | 1.91
VACAVILLE 1108 | 63601108 | 51.98 |  | 29.74 |  | 22.24
VACAVILLE 1109 | 63601109 | 5.64 |  | 0.81 |  | 4.83
VACAVILLE 1110 | 63601110 | 2.36 |  |  |  | 2.36
VACAVILLE 1111 | 63601111 | 13.03 |  | 10.12 |  | 2.91
VACAVILLE 1112 | 63601112 | 3.33 |  | 0.19 |  | 3.14
VALLEJO B 0411 | 42450411 | 7.07 |  |  |  | 7.07
VALLEJO B 0413 | 42450413 | 6.46 |  |  |  | 6.46
VALLEJO B 0414 | 42450414 | 8.29 |  |  |  | 8.29
VALLEJO B 0415 | 42450415 | 7.61 |  |  |  | 7.61
VALLEJO B 1101 | 42451101 | 16.3 |  |  |  | 16.3
VALLEJO B 1102 | 42451102 | 2.49 |  |  |  | 2.49
VALLEJO C 0401 | 42550401 | 2.8 |  |  |  | 2.8
VALLEY HOME 1702 | 162981702 | 56.27 |  |  |  | 56.27
VALLEY HOME 1703 | 162981703 | 127.51 |  |  |  | 127.51
VALLEY HOME 1704 | 162981704 | 39.28 |  |  |  | 39.28
VALLEY VIEW 1103 | 14341103 | 18.13 | 0.59 |  |  | 17.54
VALLEY VIEW 1105 | 14341105 | 14.15 |  | 3.98 |  | 10.17
VALLEY VIEW 1106 | 14341106 | 21.32 | 1.97 | 6.78 |  | 12.57
VASCO 1101 | 13751101 | 2.56 |  |  |  | 2.56
VASCO 1102 | 13751102 | 88.13 |  | 45.63 |  | 42.5
VASCO 1103 | 13751103 | 14.67 |  |  |  | 14.67
VASONA 1101 | 83771101 | 9.94 |  |  |  | 9.94
VASONA 1102 | 83771102 | 15.36 |  | 0.12 |  | 15.24
VASONA 1103 | 83771103 | 15.52 |  |  |  | 15.52
VASONA 1104 | 83771104 | 3.73 |  |  |  | 3.73
VASONA 1105 | 83771105 | 11.62 |  |  |  | 11.62
VASONA 1108 | 83771108 | 10.93 |  |  |  | 10.93
VICTOR 1101 | 163281101 | 18.26 |  |  |  | 18.26
VICTOR 1102 | 163281102 | 87.15 |  |  |  | 87.15
VIEJO 2201 | 182852201 | 17.32 |  | 14.59 |  | 2.73
VIEJO 2202 | 182852202 | 46.34 |  | 14.57 |  | 31.77
VIEJO 2203 | 182852203 | 22.78 |  | 3.04 |  | 19.74
VIEJO 2204 | 182852204 | 24.57 |  | 4.39 |  | 20.18
VIERRA 1701 | 162701701 | 9.72 |  |  |  | 9.72
VIERRA 1702 | 162701702 | 6.9 |  |  |  | 6.9
VIERRA 1703 | 162701703 | 5.61 |  |  |  | 5.61
VIERRA 1706 | 162701706 | 6.88 |  |  |  | 6.88
VIERRA 1707 | 162701707 | 48.43 |  |  |  | 48.43
VINA 1101 | 103581101 | 56.34 |  |  |  | 56.34
VINEYARD 2104 | 14502104 | 3.86 |  |  |  | 3.86
VINEYARD 2105 | 14502105 | 3.93 |  |  |  | 3.93
VINEYARD 2106 | 14502106 | 5.5 |  |  |  | 5.5
VINEYARD 2107 | 14502107 | 13.89 |  | 3 |  | 10.89
VINEYARD 2108 | 14502108 | 13.41 | 5.17 |  |  | 8.24
VINEYARD 2109 | 14502109 | 4.72 |  |  |  | 4.72
VINEYARD 2110 | 14502110 | 11.21 |  | 5.91 |  | 5.3
VIRGINIA 0401 | 13780401 | 4.02 |  |  |  | 4.02
VOLTA 1101 | 102541101 | 149.13 | 6.23 | 140.75 |  | 2.15
VOLTA 1102 | 102541102 | 129.61 | 86.85 | 41.93 |  | 0.83
Valley Springs 1101 | 168891101 | 2.14 |  |  |  | 2.14
WAHTOKE 1106 | 254531106 | 13.92 |  |  |  | 13.92
WAHTOKE 1107 | 254531107 | 19.14 |  |  |  | 19.14
WAHTOKE 1108 | 254531108 | 108.42 |  |  |  | 108.42
WAHTOKE 1109 | 254531109 | 6.95 |  |  |  | 6.95
WAHTOKE 1110 | 254531110 | 16.19 |  |  |  | 16.19
WAHTOKE 1111 | 254531111 | 29.93 |  |  |  | 29.93
WALDO 0401 | 13350401 | 5.7 |  | 1.6 |  | 4.1
WALDO 0402 | 13350402 | 5.17 |  | 2.97 |  | 2.2
WALL 0401 | 13740401 | 5.38 |  |  |  | 5.38
WALNUT CREEK 0403 | 12200403 | 0.51 |  |  |  | 0.51
WALNUT CREEK 0404 | 12200404 | 6.44 |  |  |  | 6.44
WARD 0401 | 12980401 | 4.52 |  |  |  | 4.52
WASCO 1101 | 252961101 | 12.15 |  |  |  | 12.15
WASCO 1102 | 252961102 | 7.71 |  |  |  | 7.71
WASCO 1104 | 252961104 | 9.94 |  |  |  | 9.94
WATERLOO 1101 | 163151101 | 58 |  |  |  | 58
WATERLOO 1102 | 163151102 | 21.72 |  |  |  | 21.72
WATERSHED 0402 | 24240402 | 1.19 | 0.02 |  |  | 1.17
WATSONVILLE 0411 | 83330411 | 2.31 |  |  |  | 2.31
WATSONVILLE 0413 | 83330413 | 1.22 |  |  |  | 1.22
WATSONVILLE 0414 | 83330414 | 1.28 |  |  |  | 1.28
WATSONVILLE 2101 | 83332101 | 102.59 |  |  |  | 102.59
WEBER 1101 | 163481101 | 3.23 |  |  |  | 3.23
WEBER 1102 | 163481102 | 31.75 |  |  |  | 31.75
WEBER 1103 | 163481103 | 1.8 |  |  |  | 1.8
WEBER 1105 | 163481105 | 20.89 |  |  |  | 20.89
WEBER 1107 | 163481107 | 0.04 |  |  |  | 0.04
WEBER 1108 | 163481108 | 0.44 |  |  |  | 0.44
WEBER 1109 | 163481109 | 53.12 |  |  |  | 53.12
WEBER 1110 | 163481110 | 12.68 |  |  |  | 12.68
WEBER 1111 | 163481111 | 19.87 |  |  |  | 19.87
WEBER 1112 | 163481112 | 0.03 |  |  |  | 0.03
WEBER 1113 | 163481113 | 2.12 |  |  |  | 2.12
WEBER 1114 | 163481114 | 9.8 |  |  |  | 9.8
WEBER 1115 | 163481115 | 14.66 |  |  |  | 14.66
WEEDPATCH 1101 | 252971101 | 20.32 |  |  |  | 20.32
WEEDPATCH 1102 | 252971102 | 18.17 |  |  |  | 18.17
WEEDPATCH 1103 | 252971103 | 18.05 |  |  |  | 18.05
WEEDPATCH 1105 | 252971105 | 0.96 |  |  |  | 0.96
WEEDPATCH 1106 | 252971106 | 64.45 |  |  |  | 64.45
WEIMAR 1101 | 152491101 | 78.71 |  | 78.71 |  | 0
WEIMAR 1102 | 152491102 | 36.6 |  | 36.6 |  | 0
WELLFIELD 1102 | 254291102 | 37.87 |  |  |  | 37.87
WELLFIELD 1103 | 254291103 | 0.32 |  |  |  | 0.32
WELLFIELD 1104 | 254291104 | 5.27 |  |  |  | 5.27
WEST FRESNO 1101 | 253731101 | 16 |  |  |  | 16
WEST FRESNO 1102 | 253731102 | 4.16 |  |  |  | 4.16
WEST FRESNO 1103 | 253731103 | 5.9 |  |  |  | 5.9
WEST FRESNO 1104 | 253731104 | 16.63 |  |  |  | 16.63
WEST FRESNO 1105 | 253731105 | 6.02 |  |  |  | 6.02
WEST FRESNO 1106 | 253731106 | 5.92 |  |  |  | 5.92
WEST FRESNO 1107 | 253731107 | 4.32 |  |  |  | 4.32
WEST FRESNO 1108 | 253731108 | 2.48 |  |  |  | 2.48
WEST FRESNO 1109 | 253731109 | 20.28 |  |  |  | 20.28
WEST FRESNO 1110 | 253731110 | 5.25 |  |  |  | 5.25
WEST FRESNO 1111 | 253731111 | 27.95 |  |  |  | 27.95
WEST FRESNO 1112 | 253731112 | 29.37 |  |  |  | 29.37
WEST LANE 1101 | 163621101 | 10.01 |  |  |  | 10.01
WEST LANE 1102 | 163621102 | 14.57 |  |  |  | 14.57
WEST LANE 1103 | 163621103 | 4.91 |  |  |  | 4.91
WEST POINT 1101 | 163201101 | 63.13 | 63.09 | 0.04 |  | 0
WEST POINT 1102 | 163201102 | 252.39 | 184.3 | 67.58 |  | 0.51
WEST SACRAMENTO 1104 | 63131104 | 11.92 |  |  |  | 11.92
WEST SACRAMENTO 1105 | 63131105 | 6.31 |  |  |  | 6.31
WEST SACRAMENTO 1106 | 63131106 | 2.85 |  |  |  | 2.85
WEST SACRAMENTO 1107 | 63131107 | 18.71 |  |  |  | 18.71
WEST SACRAMENTO 1108 | 63131108 | 8.73 |  |  |  | 8.73
WEST SACRAMENTO 1109 | 63131109 | 39.04 |  |  |  | 39.04
WEST SACRAMENTO 1110 | 63131110 | 8.4 |  |  |  | 8.4
WEST SACRAMENTO 1111 | 63131111 | 0.01 |  |  |  | 0.01
WESTLAKE 0401 | 22600401 | 0.81 |  |  |  | 0.81
WESTLAKE 0403 | 22600403 | 1.76 |  |  |  | 1.76
WESTLEY 1101 | 162671101 | 86.69 |  |  |  | 86.69
WESTLEY 1102 | 162671102 | 0.07 |  |  |  | 0.07
WESTLEY 1103 | 162671103 | 95.97 |  | 0.43 |  | 95.54
WESTPARK 1101 | 253701101 | 11.34 |  |  |  | 11.34
WESTPARK 1102 | 253701102 | 3.75 |  |  |  | 3.75
WESTPARK 1103 | 253701103 | 16.92 |  |  |  | 16.92
WESTPARK 1104 | 253701104 | 10.4 |  |  |  | 10.4
WESTPARK 1105 | 253701105 | 2.29 |  |  |  | 2.29
WESTPARK 1106 | 253701106 | 2.76 |  |  |  | 2.76
WESTPARK 1107 | 253701107 | 5.37 |  |  |  | 5.37
WESTPARK 1108 | 253701108 | 19.8 |  |  |  | 19.8
WESTPARK 1109 | 253701109 | 9.84 |  |  |  | 9.84
WESTPARK 1110 | 253701110 | 12.99 |  |  |  | 12.99
WESTPARK 1111 | 253701111 | 5.22 |  |  |  | 5.22
WESTPARK 1112 | 253701112 | 6.91 |  |  |  | 6.91
WHEATLAND 1101 | 152811101 | 0 |  |  |  | 0
WHEATLAND 1102 | 152811102 | 30.05 |  |  |  | 30.05
WHEATLAND 1104 | 152811104 | 113.44 |  |  |  | 113.44
WHEATLAND 1105 | 152811105 | 74.76 |  | 10.65 |  | 64.11
WHEELER RIDGE 1101 | 253481101 | 73.76 |  |  |  | 73.76
WHEELER RIDGE 1102 | 253481102 | 34.37 |  |  |  | 34.37
WHEELER RIDGE 1103 | 253481103 | 38.83 |  |  |  | 38.83
WHISMAN 1101 | 83631101 | 5.09 |  |  |  | 5.09
WHISMAN 1102 | 83631102 | 1.76 |  |  |  | 1.76
WHISMAN 1103 | 83631103 | 2.67 |  |  |  | 2.67
WHISMAN 1104 | 83631104 | 0 |  |  |  | 0
WHISMAN 1105 | 83631105 | 0.96 |  |  |  | 0.96
WHISMAN 1106 | 83631106 | 7.12 |  |  |  | 7.12
WHISMAN 1107 | 83631107 | 0.13 |  |  |  | 0.13
WHISMAN 1108 | 83631108 | 7.33 |  |  |  | 7.33
WHISMAN 1110 | 83631110 | 1.99 |  |  |  | 1.99
WHISMAN 1111 | 83631111 | 2.2 |  |  |  | 2.2
WHITMORE 1101 | 103601101 | 90.96 | 31.87 | 59.09 |  | 0
WHITNEY 0402 | 13240402 | 1.85 |  |  |  | 1.85
WILDWOOD 1101 | 103611101 | 32.18 |  | 32.18 |  | 0
WILKINS SLOUGH 1101 | 62771101 | 52.44 |  |  |  | 52.44
WILKINS SLOUGH 1102 | 62771102 | 62.19 |  |  |  | 62.19
WILKINS SLOUGH 1103 | 62771103 | 34.46 |  |  |  | 34.46
WILLIAMS 1101 | 62051101 | 32.67 |  |  |  | 32.67
WILLIAMS 1102 | 62051102 | 98.73 |  |  |  | 98.73
WILLITS 1102 | 42661102 | 11.27 |  | 4.79 |  | 6.48
WILLITS 1103 | 42661103 | 154.71 | 49.97 | 91.44 |  | 13.3
WILLITS 1104 | 42661104 | 96.02 | 50.93 | 36.44 |  | 8.65
WILLOW CREEK 1101 | 192171101 | 56.6 | 25.95 | 20.11 |  | 10.54
WILLOW CREEK 1102 | 192171102 | 9.56 | 5.31 | 4.25 |  | 0
WILLOW CREEK 1103 | 192171103 | 76.19 | 0.54 | 74.5 |  | 1.15
WILLOW PASS 1101 | 13911101 | 7.07 |  | 1.12 |  | 5.95
WILLOW PASS 1102 | 13911102 | 5.1 |  |  |  | 5.1
WILLOW PASS 2107 | 13912107 | 3.08 |  | 0.66 |  | 2.42
WILLOW PASS 2108 | 13912108 | 21.22 |  | 0.23 |  | 20.99
WILLOWS A 1101 | 102741101 | 4.28 |  |  |  | 4.28
WILLOWS A 1103 | 102741103 | 9.85 |  |  |  | 9.85
WILLOWS A 1104 | 102741104 | 9.39 |  |  |  | 9.39
WILSON 1101 | 254301101 | 16.5 |  |  |  | 16.5
WILSON 1102 | 254301102 | 30.38 |  |  |  | 30.38
WILSON 1103 | 254301103 | 115.45 |  |  |  | 115.45
WINDSOR 1101 | 43501101 | 6.4 |  |  |  | 6.4
WINDSOR 1102 | 43501102 | 14.67 |  |  |  | 14.67
WINDSOR 1103 | 43501103 | 11.24 |  | 1.98 |  | 9.26
WINTERS 1101 | 63321101 | 12.9 |  |  |  | 12.9
WINTERS 1102 | 63321102 | 35.49 |  |  |  | 35.49
WISE 1101 | 152271101 | 13.61 |  | 5.77 |  | 7.84
WISE 1102 | 152271102 | 119.01 |  | 114.01 |  | 5
WISHON 1101 | 251511101 | 7.59 | 3.48 | 4.12 |  | -0.01
WOLFE 1104 | 83671104 | 6.79 |  |  |  | 6.79
WOLFE 1105 | 83671105 | 7.29 |  |  |  | 7.29
WOLFE 1106 | 83671106 | 9.13 |  |  |  | 9.13
WOLFE 1107 | 83671107 | 10.63 |  |  |  | 10.63
WOLFE 1109 | 83671109 | 8.89 |  |  |  | 8.89
WOLFE 1110 | 83671110 | 2.02 |  |  |  | 2.02
WOLFE 1113 | 83671113 | 17.29 |  |  |  | 17.29
WOLFE 1114 | 83671114 | 2.92 |  |  |  | 2.92
WOOD 0401 | 13380401 | 3.32 |  | 0.17 |  | 3.15
WOODACRE 1101 | 43021101 | 38.41 | 22.83 | 7.8 |  | 7.78
WOODACRE 1102 | 43021102 | 31.02 | 19.29 | 11.36 |  | 0.37
WOODLAND 1101 | 62031101 | 7.2 |  |  |  | 7.2
WOODLAND 1102 | 62031102 | 13.5 |  |  |  | 13.5
WOODLAND 1103 | 62031103 | 1.23 |  |  |  | 1.23
WOODLAND 1104 | 62031104 | 5.86 |  |  |  | 5.86
WOODLAND 1105 | 62031105 | 2.7 |  |  |  | 2.7
WOODLAND 1106 | 62031106 | 28.09 |  |  |  | 28.09
WOODLAND 1107 | 62031107 | 11.16 |  |  |  | 11.16
WOODLAND 1108 | 62031108 | 21.22 |  |  |  | 21.22
WOODLAND 1109 | 62031109 | 10.68 |  |  |  | 10.68
WOODLAND 1110 | 62031110 | 10.9 |  |  |  | 10.9
WOODLAND 1111 | 62031111 | 0.25 |  |  |  | 0.25
WOODLAND 1112 | 62031112 | 12.85 |  |  |  | 12.85
WOODLAND 1113 | 62031113 | 20.88 |  |  |  | 20.88
WOODSIDE 1101 | 24251101 | 61.87 | 42.65 | 0.49 |  | 18.73
WOODSIDE 1102 | 24251102 | 17.02 |  | 0.06 |  | 16.96
WOODSIDE 1104 | 24251104 | 44.13 | 7.16 | 13 |  | 23.97
WOODSIDE 1105 | 24251105 | 6.33 |  |  |  | 6.33
WOODWARD 2101 | 255292101 | 25.84 |  |  |  | 25.84
WOODWARD 2102 | 255292102 | 1.47 |  |  |  | 1.47
WOODWARD 2104 | 255292104 | 2.76 |  |  |  | 2.76
WOODWARD 2105 | 255292105 | 0.36 |  |  |  | 0.36
WOODWARD 2106 | 255292106 | 0.29 |  |  |  | 0.29
WOODWARD 2107 | 255292107 | 9.48 |  |  |  | 9.48
WOODWARD 2108 | 255292108 | 92.13 |  | 18.51 |  | 73.62
WOODWARD 2109 | 255292109 | 1.83 |  |  |  | 1.83
WRIGHT 1110 | 254641110 | 87.64 |  |  |  | 87.64
WYANDOTTE 1102 | 102911102 | 39.19 |  | 4.33 |  | 34.86
WYANDOTTE 1103 | 102911103 | 67.04 | 38.68 | 15.28 |  | 13.08
WYANDOTTE 1105 | 102911105 | 25.68 | 0.68 | 16.11 |  | 8.89
WYANDOTTE 1106 | 102911106 | 94.31 |  | 0.55 |  | 93.76
WYANDOTTE 1107 | 102911107 | 154.94 | 9.92 | 101.39 |  | 43.63
WYANDOTTE 1109 | 102911109 | 117.8 |  | 52.17 |  | 65.63
WYANDOTTE 1110 | 102911110 | 39.32 |  | 12.63 |  | 26.69
YOSEMITE 0401 | 22490401 | 3.55 |  |  |  | 3.55
YOSEMITE 0402 | 22490402 | 2.4 |  |  |  | 2.4
YOSEMITE 0403 | 22490403 | 0 |  |  |  | 0
ZACA 1101 | 182681101 | 26.18 | 1.3 | 16.63 |  | 8.25
ZACA 1102 | 182681102 | 80.28 | 22.35 | 40.6 |  | 17.33
ZAMORA 1105 | 63191105 | 45.61 |  |  |  | 45.61
ZAMORA 1106 | 63191106 | 52.81 |  |  |  | 52.81
ZAMORA 1107 | 63191107 | 76.92 |  |  |  | 76.92
|  |  | 6926.27 | 18133.67
25059.94