## ET-WD-Details
Count | Count Excl MEDs | HFTD | RFW/HWW | REGION | TL Area | kV Cls | kV | SAP FL | LINE NO | FACILITY | YEAR | Date Out | Time Out | MED | ET Wire Down | Auto Reclose Disabled | Durn (hr:min) | Durn (mins) | Date In | Time In | Out Cls | Cause Category | Cause Detail | Secondary Cause | Comments | CAP | REGION | TOTL | Customers Affected | CESO/ Event | CMIN/ Event | SAIFI Contr | SAIDI Contr | CAIDI | System Customer Count | Fault Type | Fault Estimate | AUTO / EFO / SCHD | Outage Mode | HFTD | County | Division | LAT | LONG | Actual Location | Weather | Conductor | ET-GIS Location | ET-GIS Location | ET-GIS Location | Conductor Rating
1 | 0 | Tier 2 |  | NORTH COAST | NORTH | 69 | 60 | ETL.7490 | 60145 | MAPLE CREEK-HOOPA | 2023 | 2023-01-04 07:16 | 44930.3028 | YES | YES | No | 1900-01-02 10:43 | 4963 | 2023-01-07 17:59 | 44933.7493 | C | Tree | Tree-failure | NONE | Relayed – 1/4/23, 0716 Maple Creek-Hoopa 60kV line relayed and tested NG. SUS Russ Ranch(1), Willow Creek(CESO=2,483;CMIN=xxxx) and Hoopa(CESO=1,618;CMIN=30,661,100). Weather storm. Protection reports A-C fault near STR 002/006. 0720 Maple Creek to Willow Creek section manually tested NG. 1300 Willow Creek and Hoopa restored by temporary generation. No estimated return. 1/7/23, 1759 Maple Creek-Hoopa 60kV line returned to service after crew repaired conductor down at pole 2/6. This restores transmission service to Russ Ranch, Willow Creek and Hoopa. DO given OK to restore load. INT-16519 | NONE | NORTH COAST | INT-16519 | 4101 | 4101 | 31540082 | 0.00072259 | 5.5573 | 7690.8271 | 5675418 | A-C | 002/006 | AUTO | Single Mode | Tier 2 | Humboldt | Humboldt | 40.7894 | -123.8378 | Maple Creek-Hoopa 60kV Line STR 002/006 | Storm | 4/0 ACAR | Lat: 40.78936, Long: -123.83780 |  |  | SN=330;SE=364;WN=432;WE=454
2 | 0 | Tier 3 |  | NORTH COAST | NORTH | 69 | 60 | ETL.7550 | 60151 | MENDOCINO-WILLITS-FORT BRAGG | 2023 | 2023-01-04 07:22 | 44930.3069 | YES | YES | No | 0.26389 | 380 | 2023-01-04 13:42 | 44930.5708 | F | Equipment Failure | Equip Fail-conductor | NONE | Relayed – 1/4/23, 0548 Mendocino-Willits-Fort Bragg 60kV line relayed and improperly did not test. No customer interruption. Weather storm. Line is in a tier 2/3 HFTD. Protection reports A-C fault near STR 010/006. 0555 Line manually tested OK. 0556 line returned normal. Patrol found 1 phase of downed conductor between 010/000 and 010/001. 1342 Mendocino-Willits-Fort Bragg 60kV line returned to service after crews repaired 1 phase of down conductor. INT-16521 | NONE | NORTH COAST | INT-16521 | 0 | 0 | 0 | 0 | 0 | 0 | 5675418 | A-C | 010/006 | AUTO | Single Mode | Tier 3 | Mendocino | Humboldt | 39.3471 | -123.3066 | Mendocino-Willits-Fort Bragg 60kV line between 001/000 and 001/001 | Storm | 397.5 AAC | Lat: 39.34714, Long: -123.30664 |  |  | SN=440;SE=514;WN=666;WE=711
3 | 0 | Non-HFTD |  | NORTH COAST | NORTH | 69 | 60 | ETL.7850 | 60184 | RIO DELL JCT-BRIDGEVILLE | 2023 | 2023-01-04 09:33 | 44930.3979 | YES | YES | No | 1900-01-01 08:21 | 3381 | 2023-01-06 17:54 | 44932.7458 | F | Tree | Tree-failure | COND | Relayed – 1/4/23, 0933 Rio Dell JCT-Bridgeville 60kV line relayed and tested OK. MOM Carlotta(1,129) and Humboldt Redwood(1). Weather storm. Protection reports B-C fault near STR 031/006. 0934 Bridgeville to Carlotta section relayed and tested OK. No customer interruption. 0946 Rio Dell JCT to Carlotta section relayed and tested NG while switching to restore the line normal. SUS Carlotta(CESO=964;CMIN=107,004) and Humboldt Redwood(1). No estimated return. 1/5/23, 1558 Line patrol found tree across all three conductors between poles 021/009 and 032/000. 1/6/23, 1754 Rio Dell JCT-Bridgeville 60kV line returned to service after crew removed tree from line and repaired three phases of down conductor between poles 021/009 and 032/000. INT-16528 | NONE | NORTH COAST | INT-16528 | 1129 | 964 | 107004 | 0.00016986 | 0.018854 | 111 | 5675418 | B-C | 031/006 | AUTO | Single Mode | Non-HFTD | Humboldt | Humboldt | 40.5352 | -124.0415 | Rio Dell JCT-Humboldt 60kV line STR 021/009 | Storm | 4/0 AAC | Lat: 40.53517, Long: -124.04147 |  |  | SN=328;SE=372;WN=443;WE=473
4 | 0 | Tier 2 |  | NORTH COAST | NORTH | 69 | 60 | ETL.6980 | 60430 | FORT ROSS-GUALALA | 2023 | 2023-01-04 10:55 | 44930.4549 | YES | YES | No | 1900-01-04 08:36 | 7716 | 2023-01-09 19:31 | 44935.8132 | C | Tree | Tree-failure | COND | Relayed – 1/4/23, 1055 Fort Ross-Gualala 60kV line relayed and tested NG. MOM Gualala(423). SUS Annapolis(CESO=111;CMIN=1,198,444). Weather storm. Protection reports A-B-C fault near STR 053/008. 1208 Fort Ross to Annapolis section manually tested OK, restoring Annapolis. 1419 Fort Ross to Annapolis section relayed and tested NG. SUS Annapolis. Estimated return 1/8/23 due to safety issues of crew getting to location from adverse weather. 1/9/23, 1931 Fort Ross-Gualala 60kV line manually tested OK, restoring Annapolis, after crews repaired 2 phases of wire down at structure 31/12, repaired single phase of wire down at structures 35/3, 35/4 and 35/6 & replaced structure 35/2 and repaired 2 phases of wire down. INT-16538 | NONE | NORTH COAST | INT-16538 | 111 | 111 | 1198444 | 1.9558e-05 | 0.21116 | 10796.7928 | 5675418 | A-B-C | 053/008 | AUTO | Single Mode | Tier 2 | Sonoma | Sonoma | 38.5909 | -123.3024 | Fort Ross-Gualala 60kV line STRs 031/012, 035/003, 035/004, 035/006, 035/002 | Storm | 715 AAC | Lat: 38.59086, Long: -123.30243 |  |  | SN=703;SE=802;WN=972;WE=1039
5 | 0 | Non-HFTD |  | NORTH COAST | NORTH | 69 | 60 | ETL.6220 | 60010 | BRIDGEVILLE-GARBERVILLE | 2023 | 2023-01-04 13:06 | 44930.5458 | YES | YES | No | 1899-12-31 07:42 | 1902 | 2023-01-05 20:48 | 44931.8667 | F | Tree | Tree-failure | COND | Relayed – 1/4/23, 1306 Bridgeville-Garberville 60kV line relayed and tested NG. On the trouble, Garberville SVC separated. SUS Fruitland(CESO=1,143;CMIN=76,581) and Fort Seward(CESO=335;CMIN=22,445). Weather storm. 1413 Garberville to Fruitland line section manually tested OK, restoring Fruitland and Fort Seward. 1518 Garberville SVC returned to service. No estimated return. Protection reports A-B-C-G fault near STR 016/001. 1605, Line patrol found tree in the line with 3 phases of down conductor between poles 015/010 and 016/001. Poles 016/000 needs to be reframed and 016/003 has broken insulators. 1/5/23, 2047 Bridgeville to Fruitland line section manually tested OK after crews reframed 16/0, repaired floating conductor at 16/3, and put up wire at 15/10 and 16/1. 2048 Line return to normal service. INT-16542 | NONE | NORTH COAST | INT-16542 | 1478 | 1478 | 99026 | 0.00026042 | 0.017448 | 67 | 5675418 | A-B-C-G | 016/001 | AUTO | Single Mode | Non-HFTD | Humboldt | Humboldt | 40.2884 | -123.7414 | Bridgeville-Garberville 60kV line STRs 016/000, 016/001, 016/003, 015/010 | Storm | 4/0 ACSR | Lat: 40.28837, Long: -123.74143 |  |  | SN=330;SE=364;WN=432;WE=454
6 | 0 | Tier 3 |  | SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 60 | ETL.7590 | 60156 | MONTA VISTA-BURNS | 2023 | 2023-01-04 13:36 | 44930.5667 | YES | YES | No | 1900-01-01 06:32 | 3272 | 2023-01-06 20:08 | 44932.8389 | F | Tree | Tree-failure | COND | Relayed – 1/4/23, 1336 Monta Vista-Burns 60kV line relayed and tested NG. On the trouble, Burns-Lone Star #1 and #2-60kV lines de-energized. SUS Big Basin(CESO=4,072;CMIN=13,323,584), Point Moretti(CESO=1,060;CMIN=3,476,800), Crusher(1) and Cemex(1). Weather storm. Protection reports A-B-C fault near STR 013/104. 1420 T-line troubleman confirmed three phases of downed conductor one span between poles 011/093 and 011/094 on Monta Vista-Burns 60kV line caused by fallen tree top. 1/5/23, 1359 Crew is continuing with repair at 11/93-11/94. ETOR is now unknown as there is a report of additional wire down at another location (008/073-009/074) -patrol to confirm has been initiated. Helicopter for full line patrols has not been able to get up at this time – there looks to be a window of opportunity from 1500-1600. 2021 Monta Vista-Burns 60kV line (Monta Vista to Big Basin section) cleared for crew to repair three phases of downed conductor one span between poles 11/93 and 11/94 damaged by downed tree top. Estimated return 01/05/23. Multiple locations of wires down on line. 1/6/23, 1951 Monta Vista-Burns 60kV line (Monta Vista-Big Basin section) manually tested OK. 2008 Line restored, restoring Big Basin. 2011 Burns energized, restoring Burns. 2016 Burns-Lone Star #2-60kV line returned to service restoring Point Moretti and Crusher. 2103 Burns-Lone Star #1-60kV line returned to service restoring transmission service to Cemex (1). INT-16543 | NONE | SOUTH BAY AND CENTRAL COAST | INT-16543-1 | 4072 | 4072 | 13323584 | 0.00071748 | 2.3476 | 3272 | 5675418 | A-B-C | 013/104 | AUTO | Common Mode-initiating | Tier 3 | Santa Cruz | Central Coast | 37.1694 | -122.1658 | Monta Vista-Burns 60kV line STRs 008/073-009/074 | Storm | 397.5 AAC | Lat: 37.16936, Long: -122.16582 |  |  | SN=440;SE=514;WN=666;WE=711
7 | 0 | Tier 2 |  | NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | ETL.8410 | 60244 | ELK-GUALALA | 2023 | 2023-01-04 14:48 | 44930.6167 | YES | YES | No | 1900-01-01 02:18 | 3018 | 2023-01-06 17:06 | 44932.7125 | F | Tree | Tree-failure | COND | Relayed - 1/4/23, 1448 Elk-Gualala 60kV line relayed and tested NG. SUS Point Arena(CESO=909;CMIN=2,743,362), Garcia(CESO=9;CMIN=27,162) and Gualala(CESO=3,782;CMIN=11,414,076). Weather storm. Protection reports A-B-C fault near STR 056/002. Line patrol found tree in the line and 3 phases of down conductor between structure 054/003 and 054/004. No estimated return. 1/6/23, 1706 Elk-Gualala 60kV line, (Point arena to Gualala section) returned to service restoring Garcia (9) and Gualala (3782) after crew removed tree from line and repaired three phases of downed conductor between poles 54/3 and 54/4 on Garcia to Gualala section. INT-16546 | NONE | NORTH VALLEY AND SIERRA | INT-16546 | 4700 | 4700 | 14184600 | 0.00082813 | 2.4993 | 3018 | 5675418 | A-B-C | 056/002 | AUTO | Single Mode | Tier 2 | Mendocino | Humboldt | 38.9078 | -123.6612 | Elk-Gualala 60kV line between STRs 054/003 and 054/004 | Storm | 397.5 AAC | Lat: 38.90775, Long: -123.66117 |  |  | SN=440;SE=514;WN=666;WE=711
8 | 0 | Tier 2 |  | NORTH COAST | NORTH | 69 | 60 | ETL.2060 | 60389 | FORT BRAGG-ELK | 2023 | 2023-01-04 14:59 | 44930.6243 | YES | YES | No | 1899-12-31 18:59 | 2579 | 2023-01-06 09:58 | 44932.4153 | F | Tree | Tree-failure | COND | Relayed – 1/4/23, 1459 Fort Bragg-Elk 60kV line (Elk to Big River section) relayed and tested NG. On the trouble, Big River 60kV SVC tripped. MOM Big River(2,613). Weather storm. No estimated return. Protection reports A-B-C fault near STR 004/001. 1745, Line patrol found broken pole 004/010 and wire down between pole 004/009 and 004/011. 1/6/23, 0955 Crew replaced pole 4/10 and repaired conductor between poles 4/9 and 4/10. 0955 Fort Bragg-Elk 60kV Line (Big River-Elk section) tested OK. 0958 Fort Bragg-Elk 60kV Line restored normal. INT-16547 | NONE | NORTH COAST | INT-16547 | 2613 | 0 | 0 | 0 | 0 | 0 | 5675418 | A-B-C | 004/001 | AUTO | Single Mode | Tier 2 | Mendocino | Humboldt | 39.1895 | -123.7453 | Fort Bragg-Elk 60kV line STRs 004/009 to 004/011 | Storm | 397.5 AAC | Lat: 39.18950, Long: -123.74527 |  |  | SN=440;SE=514;WN=666;WE=711
9 | 0 | Tier 2 |  | BAY AREA | NORTH | 69 | 60 | ETL.7180 | 60113 | IGNACIO-BOLINAS #2 | 2023 | 2023-01-04 16:35 | 44930.691 | YES | YES | No | 1899-12-31 21:16 | 2716 | 2023-01-06 13:51 | 44932.5771 | F | Equipment Failure | Equip Fail-structure-line | COND | Relayed - 1/4/23, 1635 Ignacio-Bolinas #2-60kV line relayed and tested NG. SUS Tocaloma(1) and Olema(CESO=2,225;CMIN=). Weather storm. Protection reports A-G fault near STR 025/277. 1646 Ignacio to Tocaloma line section manually tested NG. 1651 Bolinas to Tocaloma line section manually tested OK, restoring Olema. 1957 Bolinas to Tocaloma section relayed and did not test. Sustained interruption to Olema. Estimated return 01/05/23. 1/5/23, Line patrol found downed center phase conductor between STR 013/158 and 013/159 and NG cross arm at pole 023/266 and a blown jumper at pole 023/269. 1/6/23, 1351 Ignacio-Bolinas #2-60kV line (Stafford JCT to Tocaloma JCT section) tested OK after crew repaired downed conductor between 13/158 and 1/159, restoring transmission service to Tocaloma and Olema. Bolimas-Olema JCT will be cleared to repair issues once safe. INT-16549 | NONE | BAY AREA | INT-16549 | 2225 | 2225 | 6043100 | 0.00039204 | 1.0648 | 2716 | 5675418 | A-G | 025/277 | AUTO | Single Mode | Tier 2 | Marin | North Bay | 38.0668 | -122.7174 | Ignacio-Bolinas #2 STRs 013/158 to 013/159 | Storm | 715 AAC | Lat: 38.06682, Long: -122.71738 |  |  | SN=703;SE=802;WN=972;WE=1039
10 | 0 | Non-HFTD |  | SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 60 | ETL.8310 | 60231 | WATSONVILLE-SALINAS | 2023 | 2023-01-04 19:04 | 44930.7944 | YES | YES | No | 1899-12-31 18:37 | 2557 | 2023-01-06 13:41 | 44932.5701 | F | Tree | Tree-failure | COND | Relayed – 1/4/23, 1904 Watsonville-Salinas 60kV line relayed and tested OK, but remained open-ended at Watsonville CB 42. SUS Granite Rock(1) and Brigatano(1). Weather storm. Line is in tier 2/3 HFTD. Protection reports C-G fault near STR 001/033. 1/5/23, 0853 Salinas to Brigatano JCT section manually tested OK restoring Granite Rock (1) and Brigatano (1).Switching in progress to clear Watsonville to Granite Rock JCT section for crew to remove tree from line between poles 1/33 and 1/34, repair downed conductors and replace NG insulators. 1/6/23, 1333 Watsonville-Salinas 60kV line manually tested OK, after crew replaced NG insulators at structure 1/33. 1341 Line restored normal. From trouble on 01/04/23 at 1918. INT-16558 | NONE | SOUTH BAY AND CENTRAL COAST | INT-16558 | 2 | 0 | 0 | 0 | 0 | 0 | 5675418 | C-G | 001/033 | AUTO | Single Mode | Non-HFTD | Monterey | Central Coast | 36.8788 | -121.7548 | Watsonville-Salinas 60kV line COND/INSL between STRs 001/033 and 001/034 | Storm | 3/0 CU | Lat: 36.87881, Long: -121.75480 |  |  | SN=359;SE=406;WN=482;WE=515
11 | 0 | Tier 3 |  | NORTH COAST | NORTH | 69 | 60 | ETL.6979 | 60429 | MONTE RIO-FORT ROSS | 2023 | 2023-01-04 19:51 | 44930.8271 | YES | YES | No | 1899-12-31 02:07 | 1567 | 2023-01-05 21:58 | 44931.9153 | F | Tree | Tree-failure | COND | Relayed – 1/4/23, 1951 Monte Rio-Fort Ross 60kV line relayed and tested NG. On the trouble, Salmon Creek 60kV tap de-energized. SUS Fort Ross(CESO=642;CMIN=1,006,014) and Salmon Creek(CESO=1,820;CMIN=2,851,940). Weather storm. No estimated return. Protection reports A-B fault near STR 017/002. 1/5/23, 2158 Monte Rio-Fort Ross 60kV line manually tested OK after crew repaired three phases of downed conductor between poles 17/2 and 17/3. Salmon Creek 60kV tap energized. INT-16562 | NONE | NORTH COAST | INT-16562 | 2462 | 2462 | 3857954 | 0.0004338 | 0.67977 | 1567 | 5675418 | A-B | 017/002 | AUTO | Single Mode | Tier 3 | Sonoma | Sonoma | 38.4784 | -123.0545 | Monte Rio-Fort Ross 60kV line COND between STRs 017/002, 017/003 | Storm | 4/0 AAC | Lat: 38.47839, Long: -123.05445 |  |  | SN=328;SE=372;WN=443;WE=473
12 | 0 | Non-HFTD |  | NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | ETL.7980 | 60198 | SMARTVILLE-MARYSVILLE | 2023 | 2023-01-04 23:57 | 44930.9979 | YES | YES | No | 1899-12-31 20:45 | 2685 | 2023-01-06 20:42 | 44932.8625 | F | Work Procedure Error | Work Procedure-not following prescribed procedures | PROC | Relayed – 1/4/23, 2357 Smartville-Marysville 60kV line relayed and tested OK on Marysville, but remained open-ended at Smartville. SUS Yuba(1). MOM Browns Valley(605). Weather storm. Line is in tier 2/3 HFTD. Protection reports A-B-C-G fault near STR 006/128. 1/5/23, 0937 Smartville-Marysville 60kV line, (Browns Valley to Yuba Goldfield JCT section) manually tested OK restoring transmission service to Yuba Goldfields (1) after foot patrol completed with on the line section with no trouble found. 1/6/23, 2042 Smartville-Yuba Gold Field section manually tested OK. 2043 Line returned to service normal after crew repaired broken poles 4/74 to 4/78 and associated conductor. INT-16575 | NONE | NORTH VALLEY AND SIERRA | INT-16575 | 605 | 0 | 0 | 0 | 0 | 0 | 5675418 | A-B-C-G | 006/128 | AUTO | Single Mode | Non-HFTD | Yuba | Sierra | 39.2005 | -121.3714 | Smartville-Marysville 60kV line COND/STRs 004/74 to 004/078 | Storm | 1/0 CU | Lat: 39.20054, Long: -121.37139 |  |  | SN=243;SE=311;WN=358;WE=382
13 | 0 | Tier 2 |  | NORTH COAST | NORTH | 115 | 115 | ETL.1110 | 10018 | BRIDGEVILLE-COTTONWOOD | 2023 | 2023-01-04 23:59 | 44930.9993 | YES | YES | No | 1900-01-01 21:55 | 4195 | 2023-01-07 21:54 | 44933.9125 | F | Tree | Tree-failure | COND | Relayed - 1/4/23, 2359 Bridgeville-Cottonwood 115kV line relayed and tested NG. SUS Wildwood(CESO=139;CMIN=2,085), Forest Glen(1) and Low Gap(1). Weather storm. Protection reports A-C-G fault near STR 059/433. 0107 Cottonwood to Low Gap section manually tested NG. 0110 Cottonwood to Wildwood JCT manually tested OK, restoring Wildwood. 0117 Bridgeville to Low Gap JCT section manually tested OK, restored Low Gap. 1414 Low Gap to Wildwood section cleared for crew to remove tree in the line between structures 059/432 to 059/433 and repair NG insulator at structure 059/432. Estimated return 01/06/23. INT-16576 | NONE | NORTH COAST | INT-16576 | 139 | 139 | 2085 | 2.4492e-05 | 0.00036737 | 15 | 5675418 | A-C-G | 059/433 | AUTO | Single Mode | Tier 2 | Trinity | Humboldt | 40.3716 | -123.3593 | Bridgeville-Cottonwood 60kV line COND between STRs 059/432 and 059/433 | Storm | 397.5 ACSR | Lat: 40.37164, Long: -123.35932 |  |  | SN=538;SE=602;WN=712;WE=757
14 | 0 | Tier 2 | HWW | NORTH COAST | NORTH | 69 | 60 | ETL.2060 | 60389 | FORT BRAGG-ELK | 2023 | 2023-01-07 06:34 | 44933.2736 | YES | YES | No | 0.3 | 432 | 2023-01-07 13:46 | 44933.5736 | F | Tree | Tree-failure | NONE | Relayed – 1/7/23, 0634 Fort Bragg-Elk 60kV line relayed and tested NG. SUS Big River(CESO=2,542;CMIN=35,588). Weather wind. Protection reports B-G fault near STR 021/001. 1346 Line returned to service after crew repaired downed conductor at pole 21/1. INT-16585 | NONE | NORTH COAST | INT-16585 | 2542 | 2542 | 35588 | 0.0004479 | 0.0062706 | 14 | 5675418 | B-G | 021/001 | AUTO | Single Mode | Tier 2 | Mendocino | Humboldt | 39.3935 | -123.801 | Fort Bragg-Elk 60kV line conductor at pole 021/001 | Wind | 397.5 AAC | Lat: 39.39355, Long: -123.80098 |  |  | SN=440;SE=514;WN=666;WE=711
15 | 0 | Non-HFTD |  | NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | ETL.7710 | 60168 | NICOLAUS-WILKINS SLOUGH | 2023 | 2023-01-07 19:39 | 44933.8187 | YES | YES | No | 0.69236 | 997 | 2023-01-08 12:16 | 44934.5111 | F | Tree | Tree-failure | COND | Relayed – 1/7/23, 1939 Nicolaus-Wilkins Slough 60kV line relayed and tested NG. SUS District 1001 Metering(1) and Carnack(1). Weather storm. Protection reports C-G fault near STR 002/038. 2137 Nicolaus-Knights Landing JCT section manually tested OK restoring District 1001 metering. 1/8/23, Troubleman found 2 phases down between structures 000/013 and 000/016 due to tree falling through the line. 1/8/23, 1216 Nicolaus-Wilkins Slough 60kV line returned to service after crew repaired a downed conductor between structures 0/13 and 0/15, restoring Carnack. From trouble on 01/07/23 at 1939. INT-16590 | NONE | NORTH VALLEY AND SIERRA | INT-16590 | 2 | 0 | 0 | 0 | 0 | 0 | 5675418 | C-G | 002/038 | AUTO | Single Mode | Non-HFTD | Sutter | SIerra | 38.9011 | -121.5436 | Nicolaus-Wilkins Slough 60kV line COND between 000/013 and 000/015 | Storm | 2/0 CU | Lat: 38.90107, Long: -121.54363 |  |  | SN=281;SE=326;WN=415;WE=443
16 | 0 | Non-HFTD |  | NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | ETL.7700 | 60167 | NICOLAUS-PLAINFIELD | 2023 | 2023-01-07 23:39 | 44933.9854 | YES | YES | No | 1900-01-02 20:36 | 5556 | 2023-01-11 20:15 | 44937.8438 | C | Equipment Failure | Equip Fail-conductor | PROC | Relayed – 1/7/23, 2339 Nicolaus-Plainfield JCT 60kV line relayed and tested NG. No customer interruption. Weather storm. Protection reports A-B-C fault near STR 016/271. 1/11/23, 2015 Nicolaus-Plainfield 60kV line returned to service after crew repaired down conductor between poles 16/275 and 17/277, leaning pole 17/284, replaced pole 16/276 and reframed pole 17/281. INT-16595 | NONE | NORTH VALLEY AND SIERRA | INT-16595 | 0 | 0 | 0 | 0 | 0 | 0 | 5675418 | A-B-C | 016/271 | AUTO | Single Mode | Non-HFTD | Yolo | Sacramento | 38.734 | -121.6863 | Nicolaus-Plainfield 60kV line COND between 016/275 and 017/277, 017/284, and 017/281 | Storm | 1/0 CU | Lat: 38.73402, Long: -121.68631 |  |  | SN=243;SE=311;WN=358;WE=382
17 | 0 | Tier 3 |  | BAY AREA | NORTH | 69 | 60 | ETL.7140 | 60109 | IGNACIO-BOLINAS #1 | 2023 | 2023-01-07 23:45 | 44933.9896 | YES | YES | No | 1900-01-01 19:00 | 4020 | 2023-01-10 18:45 | 44936.7812 | F | Tree | Tree-failure | COND | Relayed – 1/7/23, 2345 Ignacio-Bolinas #1-60kV line relayed and tested NG. SUS Woodacre(CESO=4,154;CMIN=2,546,416) and Bolinas(CESO=3,438;CMIN=939,877). Weather storm. Protection reports A-B fault near STR 003/042. 1/10/23, 1845 Ignacio-Bolinas #1-60kV line (Ignacio to Woodacre section) returned to service after crew replaced NG pole 4/44 damaged by the storm. From trouble on 01/07/23 at 2345. INT-16601 | NONE | BAY AREA | INT-16601 | 7602 | 7602 | 3486293 | 0.0013395 | 0.61428 | 458.6021 | 5675418 | A-B | 003/042 | AUTO | Single Mode | Tier 3 | Marin | North Bay | 38.0483 | -122.5988 | Ignacio-Bolinas #1 STR 004/044 | Storm | 715 AAC | Lat: 38.04832, Long: -122.59881 |  |  | SN=802;SE=846;WN=972;WE=1039
18 | 0 | Non-HFTD |  | CENTRAL VALLEY | NORTH | 69 | 60 | ETL.8070 | 60427 | SUTTER HOME SW STA-STAGG | 2023 | 2023-01-07 23:47 | 44933.991 | YES | YES | No | 0.96319 | 1387 | 2023-01-08 22:54 | 44934.9542 |  | Weather | Weather-rain | STRU | Relayed - 1/07/23, 2347 Sutter Home SW STA-Stagg 60kV line relayed and tested NG. Sustained Interruption to Constellation (1) and Terminous (623). Weather storm. INT-16605. 1011 Sutter Home SW STA-Stagg 60kV line (Sebastiani JCT section) manually tested OK restoring transmission service to Terminus (623) and Constellations (1). 1/8/23, 2243 Sutter Home SW STA-Stagg 60kV line (Sutter Home to Constellation section) returned to service after crews replaced broken poles 13/236, 13/237 and 13/238. 2254 Line returned to normal servcie. | NONE | CENTRAL VALLEY | INT-16605 | 318 | 318 | 275070 | 5.6031e-05 | 0.048467 | 865 | 5675418 | A-B-G | 014/258A | AUTO | Single Mode | Non-HFTD | San Joaquin | Stockton | 38.1379 | -121.4073 | Sutter Home SW STA-Stagg 60kV line CONDs STRs 013/237-013/239 | Storm | 715 AAC | Lat: 38.13789, Long: -121.40731 |  |  | SN=631;SE=742;WN=972;WE=1039
19 | 0 | Non-HFTD |  | NORTH VALLEY AND SIERRA | NORTH | 115 | 115 | ETL.1140 | 10021 | BRIGHTON-DAVIS | 2023 | 2023-01-07 23:50 | 44933.9931 | YES | YES | No | 1900-01-02 16:08 | 5288 | 2023-01-11 15:58 | 44937.6653 | C | Weather | Weather-rain | STRU | Relayed – 1/7/23, 2350 Brighton-Davis 115kV line relayed and tested NG. SUS Barker Slough(1). Weather storm. Protection reports C-G fault near STR 028/320. 1/8/23, 0730 Brighton-Davis 115kV line (Brighton to Barker Slough) energized, restoring Barker Slough. 0735 Barker Slough to Davis cleared for crew to repair storm damage. Estimated return 01/09/32. 1/11/23, 1558 Brighton-Davis 115kV line (Barker Slough to Davis section) returned to service after crew replaced NG down poles 27/313 to 28/324. From trouble on 01/07/23 at 2350.INT-16603 | NONE | NORTH VALLEY AND SIERRA | INT-16603 | 1 | 0 | 0 | 0 | 0 | 0 | 5675418 | C-G | 028/320 | AUTO | Single Mode | Non-HFTD | Yolo | Sacramento | 38.5461 | -121.7286 | Brighton-Davis 115kV line CONDs between STR 027/313 & 028/324 | Storm | 715 AAC | Lat: 38.54606, Long: -121.72859 |  |  | SN=631;SE=742;WN=972;WE=1039
20 | 0 | Non-HFTD |  | CENTRAL VALLEY | NORTH | 69 | 60 | ETL.7450 | 60140 | LOCKEFORD-LODI #3 | 2023 | 2023-01-07 23:55 | 44933.9965 | YES | YES | No | 0.70278 | 1012 | 2023-01-08 16:47 | 44934.6993 | F | Weather | Weather-rain | COND | Relayed – 1/7/23, 2355 Lockeford-Lodi #3-60kV line relayed and tested NG. SUS Mettler(CESO=1,458;CMIN=692,550). Weather lightning. Protection reports B-C fault near STR 002/052. 0750 Lockeford-Lodi #3-60kV line (Lodi to Lodi JCT section) manually tested OK restoring Mettler (1458). 1/8/23, 0752 Lockeford-Lodi #3-60kV line (Lockeford to Harney Lane section) manually tested OK. Lodi JCT to Harney Lane section cleared for crew to repair three to four spans of downed conductor on the line section. 1/8/23, 1647 Lockeford-Lodi #3-60kV line (Lodi JCT to Harney Lane section) returned to service after crew repaired downed conductor between poles 2/52 and 2/53, damaged by the storm. INT-16609 | NONE | CENTRAL VALLEY | INT-16609 | 1458 | 1458 | 692550 | 0.0002569 | 0.12203 | 475 | 5675418 | B-C | 002/052 | AUTO | Single Mode | Non-HFTD | San Joaquin | Stockton | 38.1015 | -121.2047 | Lockeford-Lodi #3 60kV line CONDs between STR 002/052 and 002/053 | Storm | 715 AAC | Lat: 38.10147, Long: -121.20474 |  |  | SN=631;SE=742;WN=972;WE=1039
21 | 0 | Non-HFTD |  | CENTRAL VALLEY | NORTH | 69 | 60 | ETL.8068 | 60426 | SUTTER HOME SW STA-LOCKEFORD-LODI | 2023 | 2023-01-08 00:01 | 44934.0007 | YES | YES | No | 0.60347 | 869 | 2023-01-08 14:30 | 44934.6042 | F | Tree | Tree-failure | COND | Relayed – 1/8/23, 0001 Sutter Home SW STA-Lockeford-Lodi 60kV line relayed and tested NG. On the trouble, Sutter Home-Sutter Home SW STA 60kV line de-energized. SUS Sutter Home Winery(1), New Hope(CESO=877;CMIN=) and Colony(CESO=1,085;CMIN=). Weather lightning. Protection reports A-B fault near STR 001/013. 1025 Sutter Home SW STA to Colony section manually tested OK, restoring New Hope and Colony. 1042 Sutter Home-Sutter Home SW STA 60kV line energized, restoring Sutter Home Winery. 1430 Lockeford to Colony section returned to service after crew removed downed tree between structures 1/16 and 1/17. Line returned normal. INT-16608 | NONE | CENTRAL VALLEY | INT-16608-1 | 1962 | 1962 | 1224288 | 0.0003457 | 0.21572 | 624 | 5675418 | B-C | 002/052 | AUTO | Common Mode-initiating | Non-HFTD | San Joaquin | Stockton | 38.1538 | -121.2117 | Sutter Home SW STA-Lockeford-Lodi 60kV line CONDs between 001/016 and 001/017 | Lightning | 4/0 AAC | Lat: 38.15375, Long: -121.21175 |  |  | SN=356;SE=409;WN=443;WE=473
22 | 0 | Tier 2 |  | NORTH COAST | NORTH | 69 | 60 | ETL.7820 | 60181 | POTTER VALLEY-WILLITS | 2023 | 2023-01-08 04:09 | 44934.1729 | YES | YES | No | 0.54583 | 786 | 2023-01-08 17:15 | 44934.7188 | F | Tree | Tree-failure | NONE | Relayed – 1/8/23, 0409 Potter Valley-Willits 60kV line relayed and tested NG. No customer interruption. Weather storm. Protection reports A-B fault near STR 003/000. 1715 Line returned to service after crews repaired 3 phases of down conductor between 003/002 and 003/003. INT-16620 | NONE | NORTH COAST | INT-16620 | 0 | 0 | 0 | 0 | 0 | 0 | 5675418 | A-B | 003/000 | AUTO | Single Mode | Tier 2 | Mendocino | Humboldt | 39.3829 | -123.2271 | Potter Valley-Willits 60kV line COND between STRs 003/002 and 003/003 | Storm | 1/0 ACSR | Lat: 39.38294, Long: -123.22713 |  |  | SN=222;SE=245;WN=287;WE=303
23 | 0 | Tier 3 |  | NORTH COAST | NORTH | 69 | 60 | ETL.7490 | 60145 | MAPLE CREEK-HOOPA | 2023 | 2023-01-08 23:06 | 44934.9625 | YES | YES | No | 1900-01-01 13:17 | 3677 | 2023-01-11 12:23 | 44937.516 | F | Tree | Tree-failure | COND | Relayed – 1/8/23, 2306 Maple Creek-Hoopa 60kV line relayed, Maple Creek to Willow Creek section tested OK, Willow Creek to Hoopa tested NG. No customer interruption. Weather storm. Protection reports A-B-C fault near STR 020/014. 1/11/23, 1223 Maple Creek-Hoopa 60kV line returned to service restoring transmission service to Hoopa (2044) after crew repaired (3) phases of downed conductor between poles 21/10 and 22/0. INT-16631 | NONE | NORTH COAST | INT-16631 | 2044 | 2044 | 7515788 | 0.00036015 | 1.3243 | 3677 | 5675418 | B-C-G | 001/026 | AUTO | Single Mode | Tier 3 | Humboldt | Humboldt | 40.9715 | -123.6423 | Maple Creek-Hoopa 60kV Line CONDs 021/010 to 022/000 | Storm | 4/0 ACAR | Lat: 40.97147, Long: -123.64229 |  |  | SN=330;SE=364;WN=432;WE=454
24 | 0 | Tier 2 | HWW | NORTH COAST | NORTH | 69 | 60 | ETL.6980 | 60430 | FORT ROSS-GUALALA | 2023 | 2023-01-09 00:49 | 44935.034 | YES | YES | No | 0.82083 | 1182 | 2023-01-09 20:31 | 44935.8549 | F | Tree | Tree-failure | NONE | Relayed - 1/9/23, 0049 Elk-Gualala 60kV line relayed and tested NG. On the trouble, Fort Ross-Gualala 60kV line (Annapolis to Gualala section) de-energized. 0052 Elk-Gualala 60kV line manually tested OK. SUS Annapolis(CESO=229;CMIN=270,678). MOM Point Arena(909), Garcia(9) and Gualala(3,782). Weather storm. Protection reports A-C fault near STR 045/009. 1931 Fort Ross-Gualala 60kV line manually tested OK, restoring Annapolis, after crews removed a tree at structure 48/3, repaired 2 phases of wire down at structure 31/12, repaired single phase of wire down at structures 35/3, 35/4 and 35/6 and replaced structure 35/2 and repaired 2 phases of wire down. 2031 Line returned normal. INT-16633 | NONE | NORTH COAST | INT-16633-2 | 229 | 229 | 270678 | 4.0349e-05 | 0.047693 | 1182 | 5675418 | NA | NA | AUTO | Dependent Mode | Tier 2 | Sonoma | Sonoma | 38.5909 | -123.3024 | Fort Ross-Gualala 60kV line CONDs 031/012, 035/003 to 035/006 | Storm | 715 AAC | Lat: 38.59086, Long: -123.30243 |  |  | SN=631;SE=742;WN=972;WE=1039
25 | 0 | Non-HFTD | HWW | SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 60 | ETL.6420 | 60033 | COBURN-OIL FIELDS #2 | 2023 | 2023-01-09 15:04 | 44935.6278 | YES | YES | YES | 1900-01-02 18:25 | 5425 | 2023-01-13 09:29 | 44939.3951 | X | Disaster | Disaster-flood | STRU | Relayed – 1/9/23, 1504 Coburn-Oil Fields #2-60kV line relayed and did not test. SUS San Ardo(CESO=810;CMIN=7,290). Weather storm. Protection reports A-B-C fault near STR 004/091. Line Patrol found pole 4/88 washed away. 1509 San Ardo to Oilfields section manually tested OK, restoring San Ardo. Estimated return 01/11/23. 1/13/23, 0929 Coburn-Oil Fields #2-60kV line (Coburn to San Ardo JCT section) returned to service after crew replaced pole 4/88 that was damaged by local flooding. INT-16644 | NONE | SOUTH BAY AND CENTRAL COAST | INT-16644 | 810 | 810 | 7290 | 0.00014272 | 0.0012845 | 9 | 5675418 | A-B-C | 004/091 | AUTO | Single Mode | Non-HFTD | Monterey | Central Coast | 36.2247 | -121.1004 | Coburn-Oil Fields #2 60kV line STR 004/088 | Storm | 715 AAC | Lat: 36.22467, Long: -121.10045 |  |  | SN=703;SE=802;WN=972;WE=1039
26 | 0 | Tier 3 |  | SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 60 | ETL.6240 | 60012 | BURNS-LONE STAR #2 | 2023 | 2023-01-10 01:57 | 44936.0813 | YES | YES | No | 1899-12-31 15:16 | 2356 | 2023-01-11 17:13 | 44937.7174 | F | Tree | Tree-failure | COND | Relayed – 1/10/23, 0157 Burns-Lone Star #2-60kV line relayed and locked out. SUS Crusher(1). Weather storm. Protection reports A-G fault near STR 003/066. 1/11/23, 1713 Burns-Lone Star #2-60kV line returned to service after crew repaired wire down between 2/63 and 2/64, restoring Crusher. From trouble on 01/10/23 at 0157. INT-16647 | NONE | SOUTH BAY AND CENTRAL COAST | INT-16647 | 1 | 0 | 0 | 0 | 0 | 0 | 5675418 | A-G | 003/066 | AUTO | Single Mode | Tier 3 | Santa Cruz | Central Coast | 37.0658 | -122.1545 | Burns-Lone Star #2 60kV line CONDs between STR 002/063 and 002/064 | Storm | 4/0 AAC | Lat: 37.06578, Long: -122.15453 |  |  | SN=328;SE=372;WN=443;WE=473
27 | 0 | Tier 2 |  | SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 60 | ETL.6710 | 60064 | DEL MONTE-VIEJO | 2023 | 2023-01-10 00:04 | 44936.0028 | YES | YES | No | 1899-12-31 00:44 | 1484 | 2023-01-11 00:48 | 44937.0333 | F | Tree | Tree-failure | STRU | Relayed – 1/10/23, 0204 Del Monte-Viejo 60kV line relayed and tested OK, but tested NG on Viejo end. MOM Navy Lab(1) and Hatton(4,752). Weather storm. Protection reports A-B-C fault near STR 006/041. 1/11/23, 0048 Del Monte-Viejo 60kV line (Hatton to Viejo section) returned to service after crews rehung wire down between pole 5/137 to 5/140 and straighten leaning pole 5/139 and 5/137. Cause found to be tree failed into line. INT-16646 | NONE | SOUTH BAY AND CENTRAL COAST | INT-16646 | 4753 | 0 | 0 | 0 | 0 | 0 | 5675418 | A-B-C | 006/041 | AUTO | Single Mode | Tier 2 | Monterey | Central Coast | 36.563 | -121.9113 | Del Monte-Viejo 60kV line CONDs between STRs 005/137 to 005/140 | Storm | 397.5 AAC | Lat: 36.56303, Long: -121.91128 |  |  | SN=440;SE=514;WN=666;WE=711
28 | 0 | Non-HFTD |  | SOUTH BAY AND CENTRAL COAST | SOUTH | 115 | 115 | ETL.1520 | 10066 | EL PATIO-SAN JOSE A | 2023 | 2023-01-10 02:20 | 44936.0972 | YES | YES | No | 1900-01-06 14:10 | 10930 | 2023-01-17 16:30 | 44943.6875 | C | Tree | Tree-failure | STRU | Relayed – 1/10/23, 0220 El Patio-San Jose "A" 115kV line relayed and did not test. No customer interruption. Protection reports B-C fault near STR 001/012. Weather storm. 0227 Line manually tested NG. Caused by damage to multiple structures. Estimated return 01/13/23. 1/17/23, 1630 El Patio-San Jose “A” 115kV line returned to service after crews replace tower 3/30, new poles at 2/27A, 2/28A, 2/29A, new wire and hardware from Poles 2/29A-3/31 and 2/24B-3/31. INT-16648 | NONE | SOUTH BAY AND CENTRAL COAST | INT-16648 | 0 | 0 | 0 | 0 | 0 | 0 | 5675418 | B-C | 001/012 | AUTO | Single Mode | Non-HFTD | Santa Clara | San Jose | 37.3145 | -121.9047 | El Patio-San Jose A 115kV CONDs, STRs 003/030, 002/027A-002/003/031 | Storm | 2-715 AAC | Lat: 37.31453, Long: -121.90465 |  |  | SN=1406;SE=1604;WN=1944;WE=2078
29 | 0 | Tier 2 |  | NORTH COAST | NORTH | 69 | 60 | ETL.7850 | 60184 | RIO DELL JCT-BRIDGEVILLE | 2023 | 2023-01-10 03:58 | 44936.1653 | YES | YES | No | 1899-12-31 15:52 | 2392 | 2023-01-11 19:50 | 44937.8264 | F | Tree | Tree-failure | COND | Relayed – 1/10/23, 0358 Rio Dell JCT-Bridgeville 60kV line relayed and tested NG. SUS Carlotta(CESO=1,133;CMIN=15,862) and Humboldt Redwood Co-generator (offline). Weather storm. Protection reports C-G fault near STR 037/006. 0411 Rio Dell JCT to Carlotta section energized restoring Carlotta and Humboldt Redwood Co-generator. Estimated return 01/11/23. Patrol found fallen tree between structure 038/005 and 038/006, one transmission phase down and two broken distribution arms. 1/11/23, 1950 Rio Dell JCT-Bridgeville 60kV line (Bridgeville to Carlotta section) returned to service after crews removed tree and repaired 1 phase of down conductor between structure 38/5 and 38/6. INT-16661 | NONE | NORTH COAST | INT-16661 | 1133 | 1133 | 15862 | 0.00019963 | 0.0027949 | 14 | 5675418 | C-G | 037/006 | AUTO | Single Mode | Tier 2 | Humboldt | Humboldt | 40.4697 | -123.817 | Rio Dell JCT-Humboldt 60kV line COND STRs 038/005, 038/006 | Storm | 4/0 AAC | Lat: 40.46971, Long: -123.81696 |  |  | SN=328;SE=372;WN=443;WE=473
30 | 0 | Non-HFTD |  | SOUTH BAY AND CENTRAL COAST | SOUTH | 115 | 115 | ETL.2460 | 10173 | MESA-SISQUOC | 2023 | 2023-01-10 06:39 | 44936.2771 | YES | YES | No | 1900-01-05 06:56 | 9056 | 2023-01-16 13:35 | 44942.566 | X | Disaster | Disaster-flood | STRU | Relayed – 1/10/23, 0639 Mesa-Sisquoc 115kV line relayed and tested NG. No customer interruption. Weather storm. Estimated return 01/11/23. Protection reports A-G fault near STR 004/075. 1/16/23, 1335 Mesa-Sisquoc 115kV line returned to service normal after crew replaced NG poles 2/37C, 2/38, 2/39A, NG insulators at pole 2/40 and repaired NG conductor at pole 2/41.From trouble on 01/10/23 at 0639. INT-16675 | NONE | SOUTH BAY AND CENTRAL COAST | INT-16675 | 0 | 0 | 0 | 0 | 0 | 0 | 5675418 | A-G | 004/075 | AUTO | Single Mode | Non-HFTD | San Luis Obispo | Los Padres | 34.9911 | -120.4351 | Mesa-Sisquoc 115kV line STRs/COND 002/037C to 002/041 | Storm | 1113 AAC | Lat: 34.99111, Long: -120.43505 |  |  | SN=920;SE=1055;WN=1287;WE=1378
31 | 0 | Non-HFTD |  | SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 60 | ETL.7930 | 60192 | SALINAS-LAURELES | 2023 | 2023-01-10 08:18 | 44936.3458 | YES | YES | No | 0.49306 | 710 | 2023-01-10 20:08 | 44936.8389 | F | Tree | Tree-failure | NONE | Relayed - 1/10/23, 0818 Salinas-Laureles 60kV line relayed and tested NG. On the trouble, Laureles-Otter 60kV line de-energized. Salinas to Reservation Road section tested OK. MOM Reservation Road(3,811). SUS Laureles(CESO=3,521;CMIN=2,566,809) and Otter(CESO=1,114;CMIN=812,106). Weather storm. 2001 Salinas-Laureles 60kV line (Salinas to Reservation Road section) de-energized. SUS Reservation Road(CESO=6,865;CMIN=41,190). 2008 Salinas-Laureles 60kV line manually tested OK, restoring Reservation Road and Laureles, after crew repaired 1 span wire down at A17/379 due to downed tree. 2010 Laureles-Otter 60kV line energized, restoring Otter. INT-16677 | NONE | SOUTH BAY AND CENTRAL COAST | INT-16677-1 | 10386 | 10386 | 2607999 | 0.00183 | 0.45953 | 251.1072 | 5675418 | C-G | 018/348 | AUTO | Dependent Mode-initiating | Non-HFTD | Monterey | Central Coast | 36.5845 | -121.8592 | Salinas-Laureles STR A017/379 | Storm | 3/0 CU | Lat: 36.58447, Long: -121.85916 |  |  | SN=325;SE=377;WN=482;WE=515
32 | 0 | Non-HFTD |  | NORTH VALLEY AND SIERRA | NORTH | 115 | 115 | ETL.2170 | 10143 | MADISON-VACA | 2023 | 2023-01-10 21:14 | 44936.8847 | YES | YES | No | 1899-12-31 00:14 | 1454 | 2023-01-11 21:28 | 44937.8944 | F | Equipment Failure | Equip Fail-structure-line | NONE | Relayed – 1/10/23, 2114 Madison-Vaca 115kV line relayed and tested NG. SUS Madison(CESO=3,819;CMIN=351,348). Weather storm. 2248 Madison restored on alternate power source. No estimated return. Protection reports A-B-C fault near STR 002/041. 1/11/23, 2053 Madison-Vaca 115kV line (Madison to Fulton JCT section) returned to service after crew replaced damage pole 001/029 and 1 phase of down conductor. 2128 Line return normal. INT-16682 | NONE | NORTH VALLEY AND SIERRA | INT-16682 | 3819 | 3819 | 351348 | 0.0006729 | 0.061907 | 92 | 5675418 | A-B-C | 002/041 | AUTO | Single Mode | Non-HFTD | Yolo | Sacramento | 38.6483 | -121.9619 | Madison-Vaca STR 001/029 | Storm | 3/0 CU | Lat: 38.64831, Long: -121.96192 |  |  | SN=325;SE=377;WN=482;WE=515
33 | 0 | Tier 2 |  | NORTH COAST | NORTH | 69 | 60 | ETL.8170 | 60217 | TRINITY-MAPLE CREEK | 2023 | 2023-01-10 21:37 | 44936.9007 | YES | YES | YES | 1900-01-12 19:25 | 19885 | 2023-01-24 17:02 | 44950.7097 | X | Disaster | Disaster-flood | STRU | Forced – 1/10/23, 2137 Trinity-Maple Creek 60kV line (Trinity to Big Bar section) forced out of service due to leaning pole 8/13, caused by landslide. No customer interruption. No estimated return. 1/24/23, 1702 Trinity-Maple Creek 60kV line (Trinity to Big Bar section) returned to service after crew replaced NG structures 8/12, 8/13, added 2 new poles and repaired downed conductors in between NG structures due to landslide. T23-003316 | NONE | NORTH VALLEY AND SIERRA | T23-003316 | 0 | 0 | 0 | 0 | 0 | 0 | 5675418 | NA | NA | EFO | Emergency Forced Outage | Tier 2 | Trinity | Humboldt | 40.7619 | -123.0691 | Trinity-Maple Creek 60kV line STRs, CONDs 008/012, 008/013 | Storm | 4/0 ACSR | Lat: 40.76193, Long: -123.06914 |  |  | SN=303;SE=340;WN=432;WE=454
34 | 1 | Non-HFTD |  | SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 60 | ETL.7320 | 60127 | KING CITY-COBURN #1 | 2023 | 2023-01-11 00:13 | 44937.009 | No | YES | YES | 1900-01-12 18:54 | 19854 | 2023-01-24 19:07 | 44950.7965 | C | Equipment Failure | Equip Fail-structure-line | NONE | Relayed – 1/11/23, 0013 King City-Coburn #1-60kV line relayed and did not test. SUS Jolon(CESO=628;CMIN=12,560) and Los Ositos(CESO=5,800;CMIN=168,200). Weather storm. Protection reports C-G fault near STR 004/074. 0021 Line manually tested NG. 0026 King City to Los Ositos JCT section tested NG. 0033 King City to Jolon JCT manually tested OK, restoring Jolon. 0042 Soledad to Los Ositos JCT manually tested OK, restoring Los Ositos. Estimated return 01/14/23. 1/25/23, 1907 King City-Coburn #1-60kV line (Coburn to Orchard JCT section) returned to service after crew replaced NG poles 6/97 and 6/98, repaired downed conductor and replaced NG insulators between poles 6/97 and 7/99. INT-16684 | NONE | SOUTH BAY AND CENTRAL COAST | INT-16684 | 6428 | 6428 | 180760 | 0.0011326 | 0.03185 | 28.1207 | 5675418 | A-B-C | 002/041 | AUTO | Single Mode | Non-HFTD | Monterey | Central Coast | 36.2535 | -121.1715 | King City-Coburn #1 CONDs, STRs 006/097, 006/097 | Storm | 397.5 AAC | Lat: 36.25350, Long: -121.17155 |  |  | SN=440;SE=514;WN=666;WE=711
35 | 2 | Non-HFTD |  | SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 60 | ETL.7330 | 60128 | KING CITY-COBURN #2 | 2023 | 2023-01-11 01:01 | 44937.0424 | No | YES | No | 1900-01-13 20:11 | 21371 | 2023-01-25 21:12 | 44951.8833 | C | Equipment Failure | Equip Fail-structure-line | NONE | Relayed – 1/11/23, 0101 King City-Coburn #2-60kV line relayed and tested NG. On the trouble, King City-Coburn #1-60kV line (King City to Jolon JCT section) de-energized. MOM Los Coches(219). SUS King City(CESO=5,537;CMIN=943,220) and Jolon(CESO=628;CMIN=104,876). Weather storm. Protection reports C-G fault near STR 003/050. 0344 King City-Coburn #2-60kV line (Coburn to King City section) manually tested OK. 0347 King City restored. 0348 King City-Coburn #1-60kV line (King City to Jolon section) energized, restoring Jolon. Estimated return 01/14/23. 1/25/23, 2112 King City-Coburn #2-60kV line (Coburn JCT to Teague JCT section) (trouble) returned to service after crew repaired conductor at poles A5/83ABC, A5/84ABC, & A5/86; replaced pole A5/84 and removed pole A5/85. INT-16685 | NONE | SOUTH BAY AND CENTRAL COAST | INT-16685 | 6384 | 6165 | 1048096 | 0.0010863 | 0.18467 | 170.0075 | 5675418 | A-B-C | 002/041 | AUTO | Single Mode | Non-HFTD | Monterey | Central Coast | 36.2544 | -121.1678 | King City-Coburn #2 CONDs, STRs A5/83ABC, A5/84ABC, & A5/86; replaced pole A5/84 and removed pole A5/85 | Storm | 397.5 AAC | Lat: 36.25435, Long: -121.16778 |  |  | SN=440;SE=514;WN=666;WE=711
36 | 3 | Tier 2 |  | NORTH COAST | NORTH | 69 | 60 | ETL.8410 | 60244 | ELK-GUALALA | 2023 | 2023-01-11 23:38 | 44937.9847 | No | YES | No | 0.69653 | 1003 | 2023-01-12 16:21 | 44938.6813 | F | Tree | Tree-failure | STRU | Relayed – 1/11/23, 2338 Elk-Gualala 60kV line relayed and tested NG. SUS Point Arena(CESO=845;CMIN=5,070). Weather storm. Protection reports B-C fault near STR 063/002. 2344 Elk to Garcia section manually tested OK, restoring Point Arena. No estimated return. 1/12/23, 1621 Elk-Gualala 60kV line manually tested OK, restoring transmission service to Garcia (9) after crew removed tree and repaired one phase of damaged conductor between poles 60/2 and 60/3. INT-16697 | NONE | NORTH COAST | INT-16697 | 845 | 845 | 5070 | 0.00014889 | 0.00089333 | 6 | 5675418 | B-C | 063/002 | AUTO | Single Mode | Tier 2 | Mendocino | Humboldt | 38.857 | -123.5834 | Elk-Gualala 60kV line STR, CONDs 060/002, 060/003 | Storm | 397.5 AAC | Lat: 38.85704, Long: -123.58337 |  |  | SN=440;SE=514;WN=666;WE=711
37 | 4 | Non-HFTD |  | NORTH COAST | NORTH | 69 | 60 | ETL.6810 | 60075 | ESSEX JCT-ORICK | 2023 | 2023-01-12 06:39 | 44938.2771 | No | YES | No | 0.34583 | 498 | 2023-01-12 14:57 | 44938.6229 | F | Tree | Tree-failure | COND | Relayed - 1/12/23, 0639 Essex JCT-Orick 60kV line relayed and tested NG, Essex JCT to Trinidad section tested OK. MOM Trinidad(1,500). SUS Orick(CESO=337;CMIN=171,664). Weather storm. Protection reports B-C fault near STR 021/002A. 1036 Trinidad JCT to Big Lagoon section manually tested OK. 1456 Essex JCT to Big Lagoon section forced out of service to operate Big Lagoon SW 77 dead. 1457 Line manually tested OK, restoring Orick, after crew repaired 3 phases of conductor and re-sagged conductor between poles 020/007A and 020/008. MOM Trinidad. INT-16702 | NONE | NORTH COAST | INT-16702 | 1837 | 337 | 171664 | 5.9379e-05 | 0.030247 | 509.3887 | 5675418 | B-C | 021/002A | AUTO | Single Mode | Non-HFTD | Humboldt | Humboldt | 41.1678 | -124.1006 | Essex JCT-Orick 60kV CONDs STR 020/007A, 020/008 | Storm | 2/0 CU | Lat: 41.16781, Long: -124.10060 |  |  | SN=310;SE=350;WN=415;WE=443
38 | 4 | Tier 3 |  | NORTH COAST | NORTH | 69 | 60 | ETL.6220 | 60010 | BRIDGEVILLE-GARBERVILLE | 2023 | 2023-01-14 07:00 | 44940.2917 | YES | YES | No | 0.57222 | 824 | 2023-01-14 20:44 | 44940.8639 | F | Tree | Tree-failure | COND | Relayed – 1/14/23, 0700 Bridgeville-Garberville 60kV line relayed and tested NG. 0704 Fruitland JCT to Garberville section manually tested OK. MOM Fruitland(335) and Fort Seward(1,143). Weather storm. Protection reports A-G fault near STR 010/000. 2044 Line returned normal after crews repaired one phase of downed transmission conductor and two phases of downed distribution conductor on Bridgeville to Fruitland JCT section between poles 9/17 and 10/0. INT-16716 | NONE | NORTH COAST | INT-16716 | 1478 | 0 | 0 | 0 | 0 | 0 | 5675418 | A-G | 010/000 | AUTO | Single Mode | Tier 3 | Humboldt | Humboldt | 40.3669 | -123.731 | Bridgeville-Garberville 60kV line COND 009/017 and 010/000 | Storm | 4/0 ACSR | Lat: 40.36686, Long: -123.73101 |  |  | SN=303;SE=340;WN=432;WE=454
39 | 4 | Tier 3 |  | SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 60 | ETL.6710 | 60064 | DEL MONTE-VIEJO | 2023 | 2023-01-14 09:58 | 44940.4153 | YES | YES | No | 0.95347 | 1373 | 2023-01-15 08:51 | 44941.3688 | F | Tree | Tree-failure | STRU | Relayed – 1/14/23, 0958 Del Monte-Viejo 60kV line relayed and tested NG. Hatton to Viejo section tested OK via automatics. MOM Hatton(4,752). SUS Navy Lab(1). Weather storm. Protection reports A-B-C fault near STR 002/045. 1210 Del Monte to Viejo JCT section manually tested OK, restoring Navy Lab. 1427 Viejo JCT to Hatton section cleared to repair downed conductor between structures 2/50 to 2/53 and replace NG pole 2/51. Estimated return 01/15/23. 1/15/23, 0847 Del Monte-Viejo 60kV line (Viejo JCT to Hatton section) returned to service after crews repair downed conductor between structures 2/50 and 2/53, and replace NG pole 2/51. 0851 Line returned normal. Caused by tree failure. INT-16725 | NONE | SOUTH BAY AND CENTRAL COAST | INT-16725 | 4752 | 0 | 0 | 0 | 0 | 0 | 5675418 | C-G | 001/041 | AUTO | Single Mode | Tier 3 | Monterey | Central Coast | 36.5814 | -121.8738 | Del Monte-Viejo 60kV line CONDs between STRs 002/050 and 002/053 | Storm | 715 AAC | Lat: 36.58143, Long: -121.87378 |  |  | SN=703;SE=802;WN=972;WE=1039
40 | 5 | Non-HFTD |  | NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | ETL.6440 | 60035 | COLEMAN-RED BLUFF | 2023 | 2023-02-01 06:12 | 44958.2583 | No | YES | YES | 0.4875 | 702 | 2023-02-01 17:54 | 44958.7458 | F | Equipment Failure | Equip Fail-insulator-line | HDWR | Relayed - 2/1/23, 0612 Coleman-Red Bluff 60kV line relayed and did not test due to automatic reclosing disabled for wildfire mitigation. 0616 Line manually tested NG. SUS Dairyville(CESO=713;CMIN=12,834), Vina(CESO=400;CMIN=48,800) and Los Molinos(CESO=2,379;CMIN=183,183). Weather clear. Protection reports B-G fault near STR 033/609. 0625 Coleman to Los Molinos section manually tested NG. 0630 Coleman to Dairyville section manually tested OK, restoring Dairyville. 0729 Gerber to Los Molinos JCT section manually tested OK, restoring Los Molinos. 0803 Vina transferred to alternate source, restoring Vina. 1224 to 1754 Dairyville to Los Molinos section cleared, to repair one phase of downed conductor between poles 31/574 and 31/575 and opportunity repair Los Molinos SW 37. 2/1/23, 1754 Coleman-Red Bluff 60kV line (Dairyville to Los Molinos section) returned to service after crew repaired one phase of downed conductor between poles 31/574 and 31/575 and opportunity repair Los Molinos SW 37. No cause found for conductor broken off at insulator. INT-16775 | NONE | NORTH VALLEY AND SIERRA | INT-16775 | 3492 | 3492 | 244817 | 0.00061529 | 0.043136 | 70.108 | 5675418 | B-G | 033/609 | AUTO | Single Mode | Non-HFTD | Tehama | North Valley | 39.9768 | -122.0589 | Coleman-Red Bluff 60kV line INSL STR 031/574 | Clear | 1/0 CU | Lat: 39.97677 , Long: -122.05893 |  |  | SN=243;SE=282;WN=358;WE=382
41 | 6 | Non-HFTD |  | NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | ETL.6150 | 60001 | ALMENDRA JCT-NICOLAUS | 2023 | 2023-02-12 05:54 | 44969.2458 | No | YES | No | 0.32361 | 466 | 2023-02-12 13:40 | 44969.5694 | F | External Contact | Ext Cont-car pole | COND | Relayed - 2/12/23, 0554 Almendra JCT-Nicolaus 60kV line relayed and tested OK. MOM Barry(679) and Tudor(503). Weather clear. Line is not in a tier 2/3 HFTD/HFRA. Protection reports C-G fault near STR 020/406. 0559 Line forced out of service due to single phasing condition. SUS Barry(CESO=679;CMIN=216,974) and Tudor(CESO=503;CMIN=134,022). 1024 Almendra JCT to Barry section manually tested OK, restoring transmission service to Barry. 1340 Line restored normal, restoring transmission service to Tudor after crew repaired one phase of downed conductor at pole 20/406 caused by car pole. | NONE | NORTH VALLEY AND SIERRA | INT-16792 | 1182 | 1182 | 350996 | 0.00020827 | 0.061845 | 296.9509 | 5675418 | C-G | 020/406 | AUTO | Single Mode | Non-HFTD | Sutter | Sierra | 38.9298 | -121.6064 | Almendra JCT-Nicolaus 60kV line STR 020/406 | Clear | 2/0 CU | Lat: 38.92979, Long: -121.60644 |  |  | SN=281;SE=326;WN=415;WE=443
42 | 7 | Non-HFTD |  | CENTRAL VALLEY | CENTRAL | 69 | 70 | ETL.8970 | 70115 | COPUS-OLD RIVER | 2023 | 2023-02-15 13:45 | 44972.5729 | No | YES | No | 0.23819 | 343 | 2023-02-15 19:28 | 44972.8111 | F | Equipment Failure | Equip Fail-conductor | NONE | Relayed - 2/15/23, 1345 Copus-Old RIver 70kV line relayed and tested NG. On the trouble, Maricopa-Copus 70kV line de-energized. SUS Copus(CESO=215;CMIN=3,440), South Kern(1), Gardner(CESO=1;CMIN=16), Maricopa West(1), Basic School(1) and Pentland(1). Weather clear. Line is not in a tier 2/3 HFTD/HFRA. Protection reports A-B-G fault near STR 008/143. 1400 Maricopa-Copus 70kV line energized, restoring Gardner, Maricopa West, Basic School, Pentland and Copus. 1612 South Kern JCT to San Emidio JCT cleared to repair one phase of downed conductor between poles 012/213 and 012/214. 1641 Copus to South Kern JCT manually tested OK, restoring transmission service to South Kern. 1642 Old RIver to San Emidio JCT section manually tested OK. 1928 South Kern JCT to San Emidio JCT section returned to service after crew completed repairs. No cause found. | NONE | CENTRAL VALLEY | INT-16795-1 | 216 | 216 | 3456 | 3.8059e-05 | 0.00060894 | 16 | 5675418 | A-B-G | 008/143 | AUTO | Dependent Mode-initiating | Non-HFTD | Kern | Kern | 35.1085 | -119.2027 | Copus-Old River 70kV line COND between 012/213 and 012/214 | Clear | 3/0 AAC | Lat: 35.10850, Long: -119.20268 |  |  | SN=308;SE=354;WN=381;WE=407
43 | 7 | Tier 2 |  | BAY AREA | NORTH | 69 | 60 | ETL.7140 | 60109 | IGNACIO-BOLINAS #1 | 2023 | 2023-02-21 14:24 | 44978.6 | YES | YES | YES | 0.97083 | 1398 | 2023-02-22 13:42 | 44979.5708 | F | Tree | Tree-failure | COND | Relayed - 2/21/23, 1424 Ignacio-Bolinas #1-60kV line relayed and did not test due to automatic reclosing disabled for wildfire mitigation. 1426 Line manually tested NG. SUS Woodacre(CESO=3,906;CMIN=355,446). Weather wind. Line is in a HFRA and tier 2/3 HFTD. Protection reports A-C fault near STR 014/148, 1431 Ignacio to Woodacre section manually tested OK restoring Woodacre. Estimated return 02/22/23. 2/22/23, 1342 Ignacio-Bolinas 60kV line (Bolinas to Woodacre section) returned to service after crew repaired two phases of downed conductor between poles 13/147 and 13/148. | NONE | BAY AREA | INT-16815 | 3906 | 3906 | 355446 | 0.00068823 | 0.062629 | 91 | 5675418 | A-C | 014/148 | AUTO | Single Mode | Tier 2 | Marin | North Bay | 37.9412 | -122.7057 | Ignacio-Bolinas #1 60kV line COND between 014/147 and 014/148 | Wind | 2 CU | Lat: 37.94121, Long: -122.70569 |  |  | SN=201;SE=227;WN=266;WE=284
44 | 7 | Non-HFTD |  | BAY AREA | SOUTH | 69 | 60 | ETL.6560 | 60048 | COOLEY LANDING-LOS ALTOS | 2023 | 2023-02-21 14:45 | 44978.6146 | YES | YES | YES | 0.76458 | 1101 | 2023-02-22 09:06 | 44979.3792 | F | Weather | Weather-wind | NONE | Relayed - 2/21/23, 1445 Cooley Landing-Los Altos 60kV line relayed and did not test by design. SUS Northrup. Weather wind. Line is in a HFRA and tier 2/3 HFTD. Protection reports C-G fualt near STR 013/081. 2331 line cleared for crew to repair downed conductor between poles 4/20 and 4/21 on Westinghouse 60kV tap. Estimated return 02/22/23. 2/22/23, 0906 Cooley Landing-Los Altos 60kV line returned to service after crew repaired and re-strung conductor between poles 004/21 and 004/20, restoring Northrup. M&C SUPV: High winds caused conductor to contact tower multiple times and then the conductor ultimately failed. | NONE | SOUTH BAY AND CENTRAL COAST | INT-16818 | 1 | 0 | 0 | 0 | 0 | 0 | 5675418 | C-G | 019/116 | AUTO | Single Mode | Non-HFTD | Santa Clara | De Anza | 37.4263 | -122.0697 | Cooley Landing-Los Altos 60kV COND between 004/020 and 004/021 | Wind | 4/0 CU | Lat: 37.42633, Long: -122.06973 |  |  | SN=415;SE=470;WN=560;WE=598
45 | 7 | Non-HFTD |  | CENTRAL VALLEY | CENTRAL | 69 | 70 | ETL.8460 | 70004 | ARCO-TULARE LAKE | 2023 | 2023-02-21 17:49 | 44978.7424 | YES | YES | No | 0.78333 | 1128 | 2023-02-22 12:37 | 44979.5257 | F | Equipment Failure | Equip Fail-structure-line | NONE | Relayed - 2/21/23, 1749 Arco-Tulare Lake 70kV line relayed and tested NG. On the trouble, Badger Hill and Las Perillas Co-generators separated. MOM Tulare Lake(722). SUS Lost Hills(1). Weather wind. Line is not in a HFRA or tier 2/3 HFTD. 2138 Arco to Las Perillas JCT returned to service restoring Badger Hill and Las Perillas Co-generators (offline) and Lost Hills. Estimated return 02/22/23. Protection reports A-B-C-G fault near STR 007/117. 2/22/23, 1237 Arco-Tulare Lake 70kV line (Las Perillas to Tulare Lake section) returned to service after crew replaced NG poles 008/128, 008/129, 007/118, repaired wire down between poles 008/124 and 008/125 and 2 spans of down conductor at pole 007/118. High wind in area; structures failed. | NONE | CENTRAL VALLEY | INT-16822 | 722 | 0 | 0 | 0 | 0 | 0 | 5675418 | A-B-C-G | 007/117 | AUTO | Single Mode | Non-HFTD | Kings | Fresno | 35.8907 | -119.9155 | Arco-Tulare Lake 70kV line 008/124 and 008/125 and 2 spans of down conductor at pole 007/118 | Wind | 3/0 AAC | Lat: 35.89066, Long: -119.91550 |  |  | SN=308;SE=354;WN=381;WE=407
46 | 7 | Non-HFTD |  | CENTRAL VALLEY | CENTRAL | 115 | 115 | ETL.2580 | 10185 | MIDSUN-MIDWAY | 2023 | 2023-02-21 22:36 | 44978.9417 | YES | YES | No | 1899-12-31 19:15 | 2595 | 2023-02-23 17:51 | 44980.7438 | F | Equipment Failure | Equip Fail-structure-line | NONE | Relayed - 2/21/23, 2236 Midsun-Midway 115kV line (Midsun to Cymric JCT section) relayed and tested NG. SUS Cymric Co-generator (offline) and Texaco North Midway(1). 2243 Line manually tested NG. Weather wind. Line is not in a HFRA or tier 2/3 HFTD. Protection reports A-B-C fault near STR 016/177. 2/23/23, 1751 Midsun-Midway 115kV line (Midsun SW STA to Cymric JCT section) returned to service restoring Cymric Co-gen (offline) and Texaco North Midway (1) after crews replaced NG poles 16/177, 16/178, 16/179/ 16/180, 16/181, 16/182, 16/183, and 16/184 damaged by storm. | NONE | CENTRAL VALLEY | INT-16828 | 0 | 0 | 0 | 0 | 0 | 0 | 5675418 | A-B-C | 016/177 | AUTO | Single Mode | Non-HFTD | Kern | Kern | 35.2801 | -119.6248 | Midsun-Midway 115kV line poles 16/177, 16/178, 16/179/ 16/180, 16/181, 16/182, 16/183, and 16/184 damaged by storm. | Wind | 715 AAC | Lat: 35.28006, Long: -119.62477 |  |  | SN=631;SE=742;WN=972;WE=1039
47 | 8 | Tier 2 |  | NORTH COAST | NORTH | 69 | 60 | ETL.7130 | 60108 | HUMBOLDT-MAPLE CREEK | 2023 | 2023-02-22 06:56 | 44979.2889 | No | YES | YES | 0.51667 | 744 | 2023-02-22 19:20 | 44979.8056 | F | Tree | Tree-failure | COND | Relayed - 2/22/23, 0656 Humboldt-Maple Creek 60kV line relayed and did not test due to automatic reclosing disabled for wildfire mitigation. On the trouble, Trinity-Maple Creek 60kV line open-ended at Maple Creek and Maple Creek Hoopa 60kV line de-energized. 0702 Humboldt-Maple Creek 60kV line manually tested NG. 0705 Trinity-Maple Creek 60kV line returned to service restoring Maple Creek. 0706 Maple Creek-Hoopa 60kV line returned to service restoring Russ ranch, Willow Creek and Hoopa. SUS Maple Creek(CESO=149;CMIN=1,490), Willow Creek(CESO=2,350;CMIN=23,500), Hoopa(CESO=2,085;CMIN=20,850) and Russ Ranch(CESO=2;CMIN=20). Weather storm. Lines are in a HFRA and tier 2/3 HFTD. Protection reports A-B fault near STR 006/007. 0706 all customers restored. 1920 Humboldt-Maple Creek 60kV line returned to service after crew repaired damaged conductors between structures 007/003 and 007/004 and removed a downed tree in the area. | NONE | NORTH COAST | INT-16829-1 | 4586 | 4586 | 45860 | 0.00080805 | 0.0080805 | 10 | 5675418 | A-B | 006/007 | AUTO | Dependent Mode-initiating | Tier 2 | Humboldt | Humboldt | 40.7587 | -123.9968 | Humboldt-Maple Creek 60kV line CONDs between 007/003 and 007/004 | Storm | 4/0 AAC | Lat: 40.75875, Long: -123.99681 |  |  | SN=328;SE=372;WN=443;WE=473
48 | 8 | Tier 2 |  | NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | ETL.7710 | 60168 | NICOLAUS-WILKINS SLOUGH | 2023 | 2023-02-24 01:22 | 44981.0569 | YES | YES | No | 0.61736 | 889 | 2023-02-24 16:11 | 44981.6743 | F | Equipment Failure | Equip Fail-conductor | NONE | Relayed - 2/24/23, 0122 Nicolaus-Wilkins Slough 60kV line relayed and tested NG. SUS Carnac(1) and District 1001 Metering. Weather storm. Line is in a HFRA and tier 2/3 HFTD. Protection reports B-C fault near STR 001/027. 0932 Nicolaus to District 1500 section manually tested OK, restoring District 1001 and District 1500 (Carnack). 1611 DIST 1500 JCT to DIST 2047 JCT section returned to service after crews repair 2 phases of wire down between 019/137 and 019/138. | NONE | NORTH VALLEY AND SIERRA | INT-16864 | 0 | 0 | 0 | 0 | 0 | 0 | 5675418 | B-C | 001/027 | AUTO | Single Mode | Non-HFTD | Yolo | Sacramento | 38.749 | -121.6926 | Nicolaus-Wilkins Slough 60kV line between 019/137 and 019/138. | Storm | 6 CU | Lat: 38.74905, Long: -121.69268 |  |  | SN=100;SE=115;WN=144;WE=153
49 | 8 | Non-HFTD |  | NORTH COAST | NORTH | 69 | 60 | ETL.7820 | 60181 | POTTER VALLEY-WILLITS | 2023 | 2023-02-24 03:51 | 44981.1604 | YES | YES | YES | 1899-12-31 10:04 | 2044 | 2023-02-25 13:55 | 44982.5799 | F | Tree | Tree-failure | COND | Relayed - 2/24/23, 0351 Potter Valley-Willits 60kV line relayed and did not test due to automatic reclosing disabled for wildfire mitigation. No customer interruption. Weather storm. Line is in a HFRA and tier 2/3 HFTD. Protection reports A-C fault near STR 006/004. 0354 Line manually tested NG. 2/25/23, 1355 Potter Valley-Willits 60kV line manually tested OK after crew repaired one phase of downed conductor between structures 5/10 and 6/0 caused by tree failure. From trouble on 02/24/23 at 0351. | NONE | NORTH COAST | INT-16879 | 0 | 0 | 0 | 0 | 0 | 0 | 5675418 | A-C | 006/004 | AUTO | Single Mode | Tier 3 | Mendocino | Humboldt | 39.3848 | -123.2221 | Potter Valley-Willits 60kV line COND between STRs 005/010 and 006/000 | Storm | 1/0 ACSR | Lat: 39.38483, Long: -123.22212 |  |  | SN=222;SE=245;WN=287;WE=303
50 | 8 | Tier 3 |  | NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | ETL.6310 | 60019 | CASCADE-BENTON-DESCHUTES | 2023 | 2023-02-24 05:35 | 44981.2326 | YES | YES | YES | 0.5125 | 738 | 2023-02-24 17:53 | 44981.7451 | F | Equipment Failure | Equip Fail-conductor | NONE | Relayed - 2/24/23, 0535 Cascade-Benton-Deschutes 60kV line relayed and did not test due to automatic reclosing disabled for wildfire mitigation. SUS Oregon Trail(CESO=3,671;CMIN=851,672) and Wintu pumps(1). Weather storm. Protection reports A-C fault near STR 001/035. Comm issues and indication of 10kV on line, possible Distribution co-mingling with transmission. Line is in a HFRA and tier 2/3 HFTD. 0927 Cascade-Benton-Deschutes 60kV line manually tested OK from Cascade, after Wintu PP SW 65 was opened, restoring Oregon Trail. 1753 Cascade-Benton-Deschutes 60kV line (Wintu tap section) returned to service after crew repaired wire down between 1/23 and 1/24. | NONE | NORTH VALLEY AND SIERRA | INT-16889 | 3672 | 3672 | 851672 | 0.000647 | 0.15006 | 231.9368 | 5675418 | A-C | 001/035 | AUTO | Single Mode | Tier 2 | Shasta | North Valley | 40.6391 | -122.3319 | Cascade-Benton-Deschutes 60kV line COND between 0/23 and 1/24 | Storm | 4/0 AAC | Lat: 40.63909, Long: -122.33186 |  |  | SN=356;SE=409;WN=443;WE=473
51 | 8 | Tier 2 |  | NORTH COAST | NORTH | 69 | 60 | ETL.6880 | 60082 | FULTON-CALISTOGA | 2023 | 2023-02-24 05:58 | 44981.2486 | YES | YES | YES | 0.49097 | 707 | 2023-02-24 17:45 | 44981.7396 | F | Equipment Failure | Equip Fail-insulator-line | COND | Relayed - 2/24/23, 0558 Fulton-Calistoga 60kV line relayed and did not test due to automatic reclosing disabled for wildfire mitigation. SUS Calistoga(CESO=3,824;CMIN=1,300,160) and Middletown(CESO=4,642;CMIN=190,322). 0609 Line manually tested NG. Weather storm. Line is in a Tier 2/3 HFTD/HFRA. Protection reports B-C fault near :006/006. 0639 Middletown transferred to alternate source. 1138 Fulton to Calistoga JCT section manually tested OK, restoring Calistoga. 1342 to 1745 Cleared Middletown to Calistoga JCT section for crew to repair two phases of downed conductor at structure :7/8. | NONE | NORTH COAST | INT-16892 | 8466 | 8466 | 1490482 | 0.0014917 | 0.26262 | 176.055 | 5675418 | B-C | :006/006 | AUTO | Single Mode | Tier 3 | Lake | Humboldt | 38.6982 | -122.5974 | Fulton-Calistoga 60kV line STR :007/008 | Storm | 4/0 AAC | Lat: 38.69827, Long: -122.59739 |  |  | SN=328;SE=372;WN=443;WE=473
52 | 8 | Tier 3 |  | NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | ETL.6720 | 60065 | DESABLA-CENTERVILLE | 2023 | 2023-02-24 06:14 | 44981.2597 | YES | YES | YES | 1900-01-03 05:54 | 6114 | 2023-02-28 12:08 | 44985.5056 | C | Tree | Tree-failure | COND | Relayed - 2/24/23, 0614 DeSabla-Centerville 60kV line relayed and did not test due to automatic reclosing disabled for wildfire mitigation. SUS Orofino(CESO=4,733;CMIN= 9,234,173), Toadstown(offline), DeSabla PH(offline) and Forks of the Butte(offline). Weather storm. 0726 Line manually tested NG. Weather storm. Line is in a HFRA and tier 2/3 HFTD. Protection cannot report fault location due to comms failure. Estimated return 02/25/23. 2/28/23, 1208 DeSabla-Centerville 60kV line returned to service after crew repaired downed conductor at poles 1/20-1/21, 2/30-2/31 & 2/34-2/35, restoring transmissioon service to Toadtown PH, Oro Fino, Forks of the Butte and DeSabla. | NONE | NORTH VALLEY AND SIERRA | INT-16903 | 4733 | 4733 | 9234173 | 0.00083395 | 1.627 | 1951.0188 | 5675418 | Unknown | COMM Issues | AUTO | Single Mode | Tier 3 | Butte | North Valley | 39.8571 | -121.6286 | DeSabla-Centerville 60kV line CONDs 001/020-001/021, 002/030-002/031 & 002/034-002/035 | Storm | 350 AAC | Lat: 39.85710, Long: -121.62864 |  |  | SN=406;SE=474;WN=613;WE=655
53 | 8 | Tier 3 |  | NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | ETL.7300 | 60125 | KILARC-DESCHUTES | 2023 | 2023-02-24 06:34 | 44981.2736 | YES | YES | YES | 0.70069 | 1009 | 2023-02-24 23:23 | 44981.9743 | F | Equipment Failure | Equip Fail-conductor | NONE | Relayed - 2/24/23, 0634 Kilarc-Deschutes 60kV line relayed and did not test due to automatic reclosing disabled for wildfire mitigation. 0638 Line manually tested NG. SUS CAL Creek PH (offline), Cow Creek PH (offline), Bear Creek (offline), Whitmore(CESO=542;CMIN=835,764) and Mega Olsen (offline). Weather storm. Line is in a HFRA and tier 2/3 HFTD. Protection reports B-G fault near 001/028. 1218 TKO JCT to Deschutes section manually tested OK, restoring Cow Creek PH and Bear Creek Hydro. 2321 Kilarc-Deschutes 60kV line (Whitmore to TKO JCT section) manually tested OK after crew repaired wire down between structures 10/215 and 10/216. 2323 Kilarc to Whitmore section energized, restoring Whitmore and Mega Olsen co-generator. | NONE | NORTH VALLEY AND SIERRA | INT-16901 | 542 | 542 | 835764 | 9.55e-05 | 0.14726 | 1542 | 5675418 | B-G | 001/028 | AUTO | Single Mode | Tier 2 | Shasta | North Valley | 40.5812 | -122.0116 | Kilarc-Deschutes 60kV line COND between STRs 010/215 and 010/216 | Storm | 2 ACSR | Lat: 40.58119, Long: -122.01159 |  |  | SN=154;SE=173;WN=216;WE=228
54 | 8 | Tier 3 |  | CENTRAL VALLEY | CENTRAL | 69 | 70 | ETL.9340 | 70094 | WISHON-SAN JOAQUIN #3 | 2023 | 2023-02-24 19:36 | 44981.8167 | YES | YES | YES | 1900-01-01 15:42 | 3822 | 2023-02-27 11:18 | 44984.4708 | F | Weather | Weather-snow/ ice | COND | Relayed - 2/24/23, 1936 Wishon-San Joaquin #3-70kV line relayed and did not test due automatic reclosing disabled for wildfire mitigation. 1939 Line manually test NG. SUS San Joaquin #2 PH(CESO=1,056;CMIN=4,036,032), Crane Valley PH (offline) and San Joaquin #3 PH (offline). Weather storm. Line is in a HFRA and tier 2/3 HFTD. Protection reports 2/25/23, Update for Wishon-San Joaquin #3-70kV line trouble on 02/24/23 at 1936: 1518 A.G. Wishon PH #3 to San Joaquin PH #2 JCT section manually tested OK restoring San Joaquin #2 PH 70/12kV Distribution transformer and San Joaquin #2 PH (offline). San Joaquin #3 PH to San Joaquin #2 PH JCT section cleared for crew to repair two phases of downed conductor between poles 3/1 and 3/2. Estimated return 02/26/23. 2/27/23, 1118 Wishon-San Joaquin #3-70kV line returned to service normal after crews repaired downed conductor between structures 3/4 to 3/5. Caused by wire being pencilled from being annealled and snow load. DO notified OK to restore San Joaquin #2 PH. | NONE | CENTRAL VALLEY | INT-16938 | 1056 | 1056 | 4036032 | 0.00018607 | 0.71114 | 3822 | 5675418 | A-C | 001/001 | AUTO | Single Mode | Tier 3 | Madera | Yosemite | 37.21 | -119.4968 | Wishon-San Joaquin #3-70kV line COND between STRs 003/004 and 003/005 | Storm | 1 CU | Lat: 37.210005, Long: -119.496794 | SD |  | SN=243;SE=282;WN=358;WE=382
55 | 8 | Tier 2 |  | SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 70 | ETL.9210 | 70081 | TAFT-CUYAMA #2 | 2023 | 2023-02-24 21:27 | 44981.8938 | YES | YES | YES | 1900-01-02 00:27 | 4347 | 2023-02-27 21:54 | 44984.9125 | C | Equipment Failure | Equip Fail-structure-line | COND | Relayed - 2/24/23, 2127 Taft-Cuyama #2-70kV line relayed and did not test due to automatic reclosing disabled for wildfire mitigation. 2129 Line manually tested OK to Open Cuyama SW 35. SUS Cuyama #2-70/12kV transformer(CESO=400;CMIN=856,000). Weather storm. Line is in a HFRA and tier 2/3 HFTD. Protection reports B-G fault near STR 006/069. 2229 Taft-Cuyama #2-70kV line relayed and did not test due to automatic reclosing disabled for wildfire mitigation. 2/26/23, Update to Taft-Cuyama #2-70kV line trouble 02/24/23 at 2127. 0907 Cuyama #2-70/12kV transformer restored from alternate transmission source. 2/27/23, 2154 Taft-Cuyama #2-70kV line returned to service after crew repaired downed conductor between poles 7/73 to 7/74, 9/84 to 9/87, 10/92 to 10/93 and 10/96 to 11/97. Snow and wind in area, poles twisted. From trouble on 02/24/23 at 2229. | NONE | SOUTH BAY AND CENTRAL COAST | INT-16943 | 400 | 400 | 856000 | 7.0479e-05 | 0.15083 | 2140 | 5675418 | B-G | 006/069 | AUTO | Single Mode | Non-HFTD | San Luis Obispo | Kern | 35.0376 | -119.5186 | Taft-Cuyama #2-70kV line COND between STRs 7/73 to 7/74, 9/84 to 9/87, 10/92 to 10/93 and 10/96 to 11/97 | Storm | 2 ACSR | Lat: 35.03759, Long: -119.51861 |  |  | SN=154;SE=173;WN=216;WE=228
56 | 8 | Non-HFTD |  | SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 70 | ETL.9200 | 70080 | TAFT-CUYAMA #1 | 2023 | 2023-02-24 22:07 | 44981.9215 | YES | YES | YES | 1899-12-31 00:17 | 1457 | 2023-02-25 22:24 | 44982.9333 | F | Equipment Failure | Equip Fail-structure-line | COND | Relayed - 2/24/23, 2207 Taft-Cuyama #1-70kV line relayed and did not test due to automatic reclosing disabled for wildfire mitigation. 2208 Line manually tested NG. SUS Cuyama #1-70/12kV transformer(CESO=400;CMIN=) and Cuyama PV. Weather storm. Line is in a HFRA and tier 2/3 HFTD. Protection reports C-G fault near STR 016/148. 2/25/23, 2224 Taft-Cuyama #1-70kV line returned to service, restoring Cuyama #1-70/12kV transformer and Cuyama PV (offline) after crew repaired down conductor at pole 016/159. From trouble on 02/24/23 at 2207. | NONE | SOUTH BAY AND CENTRAL COAST | INT-16944 | 400 | 400 | 582800 | 7.0479e-05 | 0.10269 | 1457 | 5675418 | C-G | 016/148 | AUTO | Single Mode | Non-HFTD | Santa Barbara | Kern | 34.9396 | -119.6395 | Taft-Cuyama #1-70kV line COND at STR 016/159 | Storm | 4/0 AAC | Lat: 34.93957, Long: -119.63949 |  |  | SN=328;SE=372;WN=443;WE=473
57 | 8 | Non-HFTD |  | NORTH VALLEY AND SIERRA | NORTH | 69 | 70 | ETL.8640 | 70023 | EXCHEQUER-MARIPOSA | 2023 | 2023-02-25 06:53 | 44982.2868 | YES | YES | YES | 1899-12-31 08:24 | 1944 | 2023-02-26 15:17 | 44983.6368 | F | Equipment Failure | Equip Fail-conductor | NONE | Relayed - 2/25/23, 0653 Exchequer-Mariposa 70kV line open-ended at Mariposa. Mariposa 70kV CB 52 tripped and did not reclose with indication of single phasing condition on line. MOM Mariposa(7,171). Weather storm. Line is in a tier 2/3 HFTD/HFRA. No fault location available, communication issues. Reports open C phase. 0710 Exchequer 70kV CB 22 manually tripped de-energizing line ending single phasing condition. Line patrol found downed conductor between structures 11/0 and 10/10. Estimated return 02/26/23. 2/26/23, 1517 Exchequer-Mariposa 70kV line returned to service after crew repaired downed conductor between structures 10/10 and 11/0. | NONE | NORTH VALLEY AND SIERRA | INT-16953 | 7171 | 0 | 0 | 0 | 0 | 0 | 5675418 | Open C Phase | NA | AUTO | Single Mode | Tier 2 | Mariposa | Yosemite | 37.5024 | -120.1353 | Exchequer-Mariposa 70kV line COND between STRs 010/010 and 011/000 | Storm | 715 AAC | Lat: 37.50244, Long: -120.13527 |  |  | SN=631;SE=742;WN=972;WE=1039
58 | 8 | Tier 2 |  | NORTH COAST | NORTH | 69 | 60 | ETL.7850 | 60184 | RIO DELL JCT-BRIDGEVILLE | 2023 | 2023-02-27 08:04 | 44984.3361 | YES | YES | YES | 1899-12-31 13:11 | 2231 | 2023-02-28 21:15 | 44985.8854 | F | Equipment Failure | Equip Fail-connector/ hardware | COND | Relayed - 2/27/23, 0804 Rio Dell JCT-Bridgeville 60kV line relayed and did not test due to automatic reclosing disabled for wildfire mitigation. 0810 Line manually tested NG. SUS Carlotta(CESO=1,305;CMIN=9,135) and Humboldt Redwood (offline). Weather storm. Line is in a tier 2/3 HFTD/HFRA. Protection reports A-G fault near STR 032/002. 0811 Rio Dell JCT to Carlotta JCT section manually tested OK restoring Carlotta and Humboldt Redwood (offline). Caused by one phase of downed conductor between pole 32/5 and 32/6. Estimated return 02/28/23. 2/28/23, 2115 Rio Dell JCT-Bridgeville 60kV line (Bridgeville to Carlotta section) returned to service after crew repaired one span of wire down between 33/5 and 33/6 | NONE | NORTH COAST | INT-16983 | 1305 | 1305 | 9135 | 0.00022994 | 0.0016096 | 7 | 5675418 | A-G | 032/002 | AUTO | Single Mode | Tier 2 | Humboldt | Humboldt | 40.4865 | -123.8977 | Rio Dell JCT-Bridgeville 60kV line COND between 033/005 and 033/006 | Storm | 4/0 AAC | Lat: 40.48652, Long: -123.89776 |  |  | SN=328;SE=372;WN=443;WE=473
59 | 8 | Tier 2 |  | NORTH COAST | NORTH | 69 | 60 | ETL.7130 | 60108 | HUMBOLDT-MAPLE CREEK | 2023 | 2023-02-27 09:26 | 44984.3931 | YES | YES | YES | 1900-01-01 05:42 | 3222 | 2023-03-01 15:08 | 44986.6306 | F | Weather | Weather-lightning | HDWR | Relayed - 2/27/23, 0926 Humboldt-Maple Creek 60kV line relayed and did not test due to automatic reclosing disabled for wildfire mitigation. On the trouble, Maple Creek-Hoopa 60kV line de-energized and Trinity-Maple Creek 60kV line open-ended at Maple Creek. 0930 Humboldt-Maple Creek 60kV line manually tested NG. 0934 Trinity-Maple Creek 60kV line returned to service restoring Maple Creek. 0936 Humboldt-Maple Creek 60kV line manually tested NG. On the trouble, the Humboldt-Maple Creek 60kV line de-energized. 0936 Maple Creek to Willow Creek section manually tested OK restoring transmission service to Russ Ranch and Willow Creek. SUS Maple Creek(CESO=147;CMIN=1,176), Russ Ranch(CESO=2;CMIN=20), Willow Creek(CESO=2,373;CMIN=33,222) and Hoopa(CESO=1,413;CMIN=611,829). Weather storm. Line is in a tier 2/3 HFTD/HFRA. Protection reports A-G fault near STR 013/004. Caused by center phase wire down between structures 14/000 and 13/005 on Humboldt-Maple Creek 60kV line. Estimated return 2/28/23. No estimated return for Maple Creek-Hoopa 60kV line (Willow Creek to Hoopa section). 3/1/23, 1508 Humboldt-Maple Creek 60kV line returned to service after crew replaced center phase of conductor between 014/000 and 013/005. 3/2/23, 1254 Maple Creek-Hoopa 60kV line (Willow Creek to Hoopa section) manually tested OK and returned to service, restoring transmission service to Hoopa after crew repaired 3 spans of down conductor between poles 25/4, 25/6, 25/7 and 25/8. Unknown cause of wire down on Humboldt-Maple Creek line. Tree fell through line for Maple Creek-Hoopa WD. | NONE | NORTH COAST | INT-16990-1 | 0 | 0 | 0 | 0 | 0 | 0 | 5675418 | A-G | 013/004 | AUTO | Dependent Mode-initiating | Tier 2 | Humboldt | Humboldt | 40.7679 | -123.8762 | Humboldt-Maple Creek 60kV line COND between 014/000 and 013/005 | Storm | 2/0 CU | Lat: 40.76788, Long: -123.87624 |  |  | SN=310;SE=350;WN=415;WE=443
60 | 8 | Tier 2 |  | NORTH COAST | NORTH | 69 | 60 | ETL.7490 | 60145 | MAPLE CREEK-HOOPA | 2023 | 2023-02-27 09:26 | 44984.3931 | YES | YES | No | 1900-01-02 03:28 | 4528 | 2023-03-02 12:54 | 44987.5375 | C | Tree | Tree-failure | COND | Relayed - 2/27/23, 0926 Humboldt-Maple Creek 60kV line relayed and did not test due to automatic reclosing disabled for wildfire mitigation. On the trouble, Maple Creek-Hoopa 60kV line de-energized and Trinity-Maple Creek 60kV line open-ended at Maple Creek. 0930 Humboldt-Maple Creek 60kV line manually tested NG. 0934 Trinity-Maple Creek 60kV line returned to service restoring Maple Creek. 0936 Humboldt-Maple Creek 60kV line manually tested NG. On the trouble, the Humboldt-Maple Creek 60kV line de-energized. 0936 Maple Creek to Willow Creek section manually tested OK restoring transmission service to Russ Ranch and Willow Creek. SUS Maple Creek(CESO=;CMIN=), Russ Ranch(CESO=;CMIN=), Willow Creek(CESO=;CMIN=) and Hoopa(CESO=;CMIN=). Weather storm. Line is in a tier 2/3 HFTD/HFRA. Protection reports A-G fault near STR 013/004. Caused by center phase wire down between structures 14/000 and 13/005 on Humboldt-Maple Creek 60kV line. Estimated return 2/28/23. No estimated return for Maple Creek-Hoopa 60kV line (Willow Creek to Hoopa section). 3/1/23, 1508 Humboldt-Maple Creek 60kV line returned to service after crew replaced center phase of conductor between 014/000 and 013/005. 3/2/23, 1254 Maple Creek-Hoopa 60kV line (Willow Creek to Hoopa section) manually tested OK and returned to service, restoring transmission service to Hoopa after crew repaired 3 spans of down conductor between poles 25/4, 25/6, 25/7 and 25/8. Unknown cause of wire down on Humboldt-Maple Creek line. Tree fell through line for Maple Creek-Hoopa WD. | NONE | NORTH COAST | INT-16990-2 | 3788 | 3788 | 645071 | 0.00066744 | 0.11366 | 170.2932 | 5675418 | NA | NA | AUTO | Dependent Mode | Tier 3 | Humboldt | Humboldt | 41.0159 | -123.6469 | Maple Creek-Hoopa 60kV line COND between STRs 025/004 and 025/008 | Storm | 4/0 ACSR | Lat: 41.01590, Long: -123.64689 |  |  | SN=303;SE=340;WN=432;WE=454
61 | 8 | Tier 3 |  | NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | ETL.6760 | 60070 | DRUM-GRASS VALLEY-WEIMAR | 2023 | 2023-02-27 17:59 | 44984.7493 | YES | YES | YES | 1900-01-03 21:56 | 7076 | 2023-03-04 15:55 | 44989.6632 | C | Tree | Tree-failure | COND | Relayed - 2/27/23, 1759 Drum-Grass Valley-Weimar 60kV line relayed and did not test due to automatic reclosing disabled for wildfire mitigation. 1804 Line manually tested NG. SUS Shady Glen(CESO=2,202;CMIN=17,616), Bonnie Nook(1) and Cape Horn(1). Rollins PH separated on the trouble. Weather storm. Line is in a tier 2/3 HFTD/HFRA. Protection reports A-B-C-G fault near STR B024/552. 1809 Drum-Grass Valley-Weimar 60kV line (Drum to Shady Glen JCT section manually tested OK restoring Shady Glen, Bonnie Nook and Cape Horn. Estimated return 02/28/23. 3/1/23, T-line patrol reports Tree on conductor at the following structures: B21/467, B22/493, B22/502, B23/514, B23/518, B23/530 wire down between structure B23/531 & B23/532. 3/4/23, 1555 Drum-Grass Valley-Weimar 60kV line (Grass Valley to Rollins JCT section) returned to service after crew removed tree from structures B21/467, B22/493, B22/502, B23/514, B23/518, B23/530 and repaired down conductor between structures B23/531 and B23/532. | NONE | NORTH VALLEY AND SIERRA | INT-17004 | 2202 | 2202 | 1716 | 0.00038799 | 0.00030236 | 0.77929 | 5675418 | A-B-C-G | B024/552 | AUTO | Single Mode | Tier 3 | Nevada | Sierra | 39.1919 | -121.0125 | Drum-Grass Valley-Weimar 60kV line CONDs at STRs B021/467, B022/493, B022/502, B023/514, B023/518, B023/530, B023/531 & B023/532 | Storm | 397.5 AAC | Lat: 39.19188, Long: -121.01248 |  |  | SN=440;SE=514;WN=666;WE=711
62 | 8 | Tier 3 |  | NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | ETL.6480 | 60039 | COLGATE-CHALLENGE | 2023 | 2023-02-28 07:48 | 44985.325 | YES | YES | YES | 1900-01-01 10:29 | 3509 | 2023-03-02 18:17 | 44987.7618 | F | Tree | Tree-failure | COND | Relayed - 2/28/23, 0748 Colgate-Challenge 60kV line relayed and did not test due to automatic reclosing disabled for wildfire mitigation. 0750 Line manually tested NG. 0751 Colgate to Dobbins section manually tested OK. SUS Challenge(CESO=576;CMIN=554,224)and Dobbins(CESO=923;CMIN=17,537). Weather storm. Line is in a tier 2/3 HFTD/HFRA. Protection reports A-C fault near 005/104. 3/2/23, 1817 Colgate-Challenge 60kV line manually tested OK. D.O. given OK to restore customers at Challenge. Work completed by T-line: Repaired slack conductor at poles 5/104, 5/105 and 5/106, (2) phases of downed conductor at poles 005/099 to 005/101 and (8) spans of conductor with trees on line between structures 005/101 to 006/111. | NONE | NORTH VALLEY AND SIERRA | INT-17011 | 1499 | 1499 | 571761 | 0.00026412 | 0.10074 | 381.4283 | 5675418 | A-C | 005/104 | AUTO | Single Mode | Tier 3 | Yuba | Sierra | 39.3975 | -121.1671 | Colgate-Challenge 60kV line CONDs at STR 005/104, 005/105 and 005/106, 005/099 to 005/101 between structures 005/101 to 006/111 | Storm | 4/0 ACSR | Lat: 39.39753, Long: -121.16709 |  |  | SN=303;SE=340;WN=432;WE=454
63 | 8 | Tier 3 |  | NORTH COAST | NORTH | 69 | 60 | ETL.7820 | 60181 | POTTER VALLEY-WILLITS | 2023 | 2023-02-28 07:57 | 44985.3313 | YES | YES | YES | 1900-01-01 05:20 | 3200 | 2023-03-02 13:17 | 44987.5535 | F | Tree | Tree-failure | COND | Relayed - 2/28/23, 0757 Potter Valley-Willits 60kV line relayed and did not test due to automatic reclosing disabled for wildfire mitigation. 0759 Line manually tested NG. No customer interruption. Weather storm. Line is in a tier 2/3 HFTD/HFRA. Protection reports A-C fault near STR 004/007. 3/2/23, 1317 Line returned to service after crew repaired repaired multiple spans of wire down between poles 5/9 and 6/0. | NONE | NORTH COAST | INT-17012 | 0 | 0 | 0 | 0 | 0 | 0 | 5675418 | A-C | 004/007 | AUTO | Single Mode | Tier 3 | Mendocino | Humboldt | 39.3848 | -123.2221 | Potter Valley-Willits 60kV line COND between poles 005/009 and 006/000 | Storm | 1/0 ACSR | Lat: 39.38483, Long: -123.22212 |  |  | SN=222;SE=245;WN=287;WE=303
64 | 8 | Tier 3 |  | NORTH COAST | NORTH | 69 | 60 | ETL.6220 | 60010 | BRIDGEVILLE-GARBERVILLE | 2023 | 2023-02-28 11:24 | 44985.475 | YES | YES | YES | 1899-12-31 04:52 | 1732 | 2023-03-01 16:16 | 44986.6778 | F | Equipment Failure | Equip Fail-conductor | NONE | Relayed - 2/28/23, 1124 Bridgeville-Garberville 60kV line relayed and did not test due to automatic reclosing disabled for wildfire mitigation. 1126 Line tested NG. 1128 Bridgeville to Fort Seward section manually tested OK. 1129 Garberville to Fort Seward section manually tested NG. 1130 Fort Seward 60kV tap isolated. 1130 Garberville to Fort Seward JCT manually tested NG. SUS Fort Seward(CESO=335;CMIN=580,220). MOM Fruitland(1,143). Weather storm. Line is in a tier 2/3 HFTD/HFRA. Protection reports B-C fault near STR 026/003. 1544 Bridgeville to Fort Seward JCT section forced out of service to test Fort Seward 60kV tap with CB. 1548 Bridgeville to Fort Seward section manually tested OK, restoring transmission service to Fort Seward. Momentary interruption to Fruitland. Estimated return 03/01/23. 3/1/23, 1616 Bridgeville-Garberville 60kV line (Fort Seward JCT to Garberville section) returned to service after crew spliced one phase of conductor between structures 025/002 and 025/004. | NONE | NORTH COAST | INT-17019 | 1478 | 1732 | 580220 | 0.00030518 | 0.10223 | 335 | 5675418 | B-C | 026/003 | AUTO | Single Mode | Non-HFTD | Humboldt | Humboldt | 40.199 | -123.7078 | Bridgeville-Garberville 60kV line COND between STRs 025/002 and 025/004. | Storm | 4/0 ACSR | Lat: 40.19899, Long: -123.70786 |  |  | SN=303;SE=340;WN=432;WE=454
65 | 8 | Non-HFTD |  | NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | ETL.7560 | 60152 | WEIMAR #1 | 2023 | 2023-02-28 11:51 | 44985.4938 | YES | YES | No | 1899-12-31 06:43 | 1843 | 2023-03-01 18:34 | 44986.7736 | F | Equipment Failure | Equip Fail-conductor | NONE | Relayed - 2/28/23, 1151 Weimar #1 and Middle Fork #1-60kV lines relayed and tested NG. SUS Forest Hill(CESO=629;CMIN=2,896,754) and Ralston PH station service. Weather storm. Lines are in a tier 2/3 HFTD/HFRA. Protection reports A-C fault near STR 005/067. 1803 Weimar to Forest Hill JCT section manually tested NG after crew made repairs to sagging conductors between 2/40 and 2/41. Estimated return 03/01/23. 3/1/23, 1834 Middle Fork #1 and Weimar #1-60kV lines returned to service, restoring Forest Hill and Ralston PH station service after crew replaced 2 spans of downed conductor between structures 007/115 and 008/118. From trouble on 02/28/23 at 1151. | NONE | NORTH VALLEY AND SIERRA | INT-17022-1 | 629 | 629 | 2896754 | 0.00011083 | 0.5104 | 4605.333 | 5675418 | A-C | 005/067 | AUTO | Common Mode | Tier 3 | Placer | Sierra | 39.0191 | -120.8593 | Weimar #1 and Middle Fork #1-60kV lines COND between STRs 007/115 and 008/118 | Storm | 2 ACSR | Lat: 39.01907, Long: -120.85931 |  |  | SN=154;SE=173;WN=216;WE=228
66 | 8 | Tier 3 |  | NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | ETL.6760 | 60070 | DRUM-GRASS VALLEY-WEIMAR | 2023 | 2023-02-28 12:40 | 44985.5278 | YES | YES | YES | 1900-01-02 06:29 | 4709 | 2023-03-03 19:09 | 44988.7979 | C | Tree | Tree-failure | COND | Relayed - 2/28/23, 1240 Drum-Grass Valley-Weimar 60kV line (Drum to Shady Glen section) relayed and did not test due to automatic reclosing disabled for wildfire mitigation. 1257 Drum to Cape Horn section manually tested NG. SUS Shady Glen(CESO=2,852;CMIN=82,708), Bonnie Nook(CESO=895;CMIN=22,375) and Cape Horn(1). Weather storm. Line is in a tier 2/3 HFTD/HFRA. 1305 Drum to Bonnie Nook section manually tested OK, restoring Bonnie Nook. 1309 Weimar to Shady Glen to Cape Horn JCT section manually tested OK, restoring Shady Glen. 1312 Cape Horn restored. Estimated return Bonnie Nook to Cape Horn JCT section 03/01/23. 3/3/23, 1909 Drum-Grass Valley-Weimar 60kV line (Bonnie Nook to Cape Horn section) returned to service after crew replaced NG pole 12/279, repaired one phase of downed conductor between poles 11/265 & 11/266, repaired one phase of downed conductor at pole 11/265, one phase of downed conductor at pole 13/298 and removed tree from line at pole 7/175. | NONE | NORTH VALLEY AND SIERRA | INT-17030-2 | 3747 | 3747 | 105083 | 0.00066022 | 0.018515 | 28.0446 | 5675418 | A-C | 012/294 | AUTO | Single Mode | Tier 3 | Placer | Sierra | 39.1511 | -120.8988 | Drum-Grass Valley-Weimar 60kV line COND between poles 011/265 & 011/266, 011/265, 013/298, 007/175 | Storm | 2/0 CU | Lat: 39.15110, Long: -120.89881 |  |  | SN=310;SE=350;WN=415;WE=443
67 | 8 | Tier 3 |  | NORTH VALLEY AND SIERRA | NORTH | 115 | 115 | ETL.4393 | 10459 | DRUM-HIGGINS | 2023 | 2023-02-28 15:47 | 44985.6576 | YES | YES | YES | 1900-01-02 18:17 | 5417 | 2023-03-04 10:04 | 44989.4194 | C | Tree | Tree-failure | COND | Relayed - 2/28/23, 1547 Drum-Higgins 115kV line relayed and did not test due to automatic reclosing disabled for wildfire mitigation. 1550 Line tested NG. SUS Dutch Flat #1 PH (offline), Dutch Flat #2 PH (offline) and Chicago Park PH (offline). Weather storm. Line is in a tier 2/3 HFTD/HFRA. Protection reports A-B fault near STR 008/081. 3/4/23, 1004 Drum-Higgins 115kV line de-energized during restoration switching to close Dutch Flat #1 JCT 119 and Chicago Park JCT 137 dead. Sustained interruption to Dutch Flat #1 PH (offline), Dutch Flat #2 PH (offline) and Chicago Park PH (offline). 1053 Dutch Flat #1 JCT to Chicago Park JCT section manually tested OK after crew repaired 2 phases of down conductor between towers 7/72 and 7/73 and 1 phase of down conductor between towers 8/78 and 8/80, restoring Dutch Flat #1 PH (offline), Dutch Flat #2 PH (offline) and Chicago Park PH (offline). 1056 Drum-Higgins 115kV line (Dutch Flat #1 JCT to Chicago Park JCT section) returned to service. | NONE | NORTH VALLEY AND SIERRA | INT-17033 | 0 | 0 | 0 | 0 | 0 | 0 | 5675418 | A-B | 008/081 | AUTO | Single Mode | Tier 3 | Placer | Sierra | 39.1897 | -120.8598 | Drum-Higgins 115kV line COND between STRs 007/072 and 007/073 and COND between STRs 008/078 and 008/080 | Storm | 397.5 ACSR | Lat: 39.18972, Long: -120.85975 |  |  | SN=538;SE=602;WN=712;WE=757
68 | 8 | Tier 3 |  | NORTH VALLEY AND SIERRA | NORTH | 115 | 115 | ETL.1540 | 10068 | EL DORADO-MISSOURI FLAT #2 | 2023 | 2023-02-28 19:23 | 44985.8076 | YES | YES | YES | 1899-12-31 21:34 | 2734 | 2023-03-02 16:57 | 44987.7063 | F | Unknown | Unk-no patrol conducted | NONE | Relayed - 2/28/23, 1923 El Dorado-Missouri Flat #2-115kV line relayed and did not test due to automatic reclosing disabled for wildfire mitigation. 1928 Line manually tested NG. MOM Apple Hill(1,503) and Placerville(7,866). Weather storm. Line is in a tier 2/3 HFTD/HFRA. 2116 Line manually tested NG. Protection reports A-C fault near STR 003/024. 3/2/23, 1646 El Dorado-Missouri Flat #2-115kV line (Missouri Flat to Apple Hill JCT section) forced out of service to close Apple Hill JCT SW 329 dead. No customer interruption. 1650 Line manually tested OK after crew repaired wire down between tower 2/18 and 2/17. 1652 Line returned to service. 1657 Line restored normal. From trouble on 02/28/23 at 1923. | NONE | NORTH VALLEY AND SIERRA | INT-17038 | 9369 | 0 | 0 | 0 | 0 | 0 | 5675418 | B-C | 003/024 | AUTO | Single Mode | Tier 3 | El Dorado | Sierra | 38.7724 | -120.6526 | El Dorado-Missouri Flat #2-115kV line COND between 002/018 and 002/017 | Storm | 3/0 CU | Lat: 38.77237, Long: -120.65261 |  |  | SN=325;SE=377;WN=482;WE=515
69 | 9 | Non-HFTD |  | CENTRAL VALLEY | CENTRAL | 69 | 70 | ETL.8550 | 70113 | CARUTHERS-LEMOORE NAS-CAMDEN | 2023 | 2023-03-02 06:02 | 44987.2514 | No | YES | No | 0.34444 | 496 | 2023-03-02 14:18 | 44987.5958 | F | External Contact | Ext Cont-vandalism | COND | Relayed - 3/2/23, 0602 Caruthers-Lemoore NAS-Camden 70kV line relayed and tested NG. No customer interruption. Weather clear. Line is not in a tier 2/3 HFTD/HFRA. Protection reports A-G fualt near STR 046/007. 1418 Line returned to service after crew repaired one phase of downed conductor between poles 47/13 and 47/14A. Patrol suspects gunshot. CAP creation requested. | CAP Requested | CENTRAL VALLEY | INT-17051 | 0 | 0 | 0 | 0 | 0 | 0 | 5675418 | A-G | 046/007 | AUTO | Single Mode | Non-HFTD | Kings | Fresno | 36.3995 | -119.9051 | Caruthers-Lemoore NAS-Camden 70kV COND between STRs 047/013 and 047/014A | Clear | 1/0 CU | Lat: 36.39951, Long: -119.90505 |  |  | SN=243;SE=282;WN=358;WE=382
70 | 9 | Tier 2 |  | SOUTH BAY AND CENTRAL COAST | CENTRAL | 69 | 60 | ETL.6710 | 60064 | DEL MONTE-VIEJO | 2023 | 2023-03-09 18:46 | 44994.7819 | YES | YES | YES | 1899-12-31 07:11 | 1871 | 2023-03-11 01:57 | 44996.0813 | F | Tree | Tree-failure | STRU | Relayed - 3/9/23, 1846 Del Monte-Viejo 60kV line relayed and did not test due to automatic reclosing disabled for wildfire mitigation. SUS Navy Lab(1), Hatton(CESO=2,149;CMIN=147,356), Viejo(CESO=3,803;CMIN=7,165,770). Weather storm. Line is in a tier 2/3 HFTD/HFRA. Protection reports A-B-C fault near STR 005/129. 1857 Del Monte to Navy lab section manually tested OK, restoring transmission service to Navy Lab. 1930 Viejo to Hatton section manually tested NG. 1934 Del Monte to Navy Lab section forced out of service to closed Hatton SW 57 dead. 1939 Del Monte to Navy Lab section energized. MOM Navy Lab. 1940 Transmission service to Hatton restored. Estimated return for Viejo to Hatton section 03/10/23. 2146 Del Monte-Viejo 60kV line (Del Monte to Hatton section) relayed and did not test due to automatic reclosing disabled for wildfire mitigation. 2150 Del Monte to Hatton section manually tested OK. Momentary to Navy Lab and Hatton. Weather storm. Line is in a tier 2/3 HFTD/HFRA. 2202 Del Monte-Viejo 60kV line (Del Monte to Hatton section) relayed and did not test due to automatic reclosing disabled for wildfire mitigation. 2203 Del Monte to Hatton section manually tested OK. Momentary to Navy Lab and Hatton. Weather storm. Line is in a tier 2/3 HFTD/HFRA. 2321 Del Monte-Viejo (Del Monte to Hatton section) forced out of service to secure loose guy wires at pole 0/10. Sustained interruption to Navy Lab and Hatton. 2353 Del Monte to Hatton section returned to service restoring Navy Lab and Hatton after crew cut pole 0/10 guy wires in the clear. 3/11/23, 0157 Del Monte-Viejo 60kV line, (Del Monte to Hatton section) forced out of service to close Hatton SW 59 dead. 0200 Line manually tested OK after crew repaired downed conductor between poles 5/136 & 5/137. Momentary interruption to Navy Lab and Hatton. 0357 Line returned normal restoring transmission service to Viejo. From trouble on 03/09/23 at 1846. | NONE | SOUTH BAY AND CENTRAL COAST | INT-17092 | 5952 | 5952 | 7313126 | 0.0010487 | 1.2886 | 1228.6838 | 5675418 | A-B-C | 005/129 | AUTO | Single Mode | Tier 2 | Monterey | Central Coast | 36.5617 | -121.9114 | Del Monte-Viejo 60kV line COND between STRs 005/136, 005/137 | Storm | 397.5 AAC | Lat: 36.56174, Long: -121.91139 |  |  | SN=488;SE=554;WN=666;WE=711
71 | 9 | Tier 2 |  | NORTH COAST | NORTH | 69 | 60 | ETL.8170 | 60217 | TRINITY-MAPLE CREEK | 2023 | 2023-03-09 20:41 | 44994.8618 | YES | YES | YES | 1899-12-31 20:55 | 2695 | 2023-03-11 17:36 | 44996.7333 | F | Tree | Tree-failure | HDWR | Relayed - 3/9/23, 2041 Trinity-Maple Creek 60kV line relayed and did not test due to automatic reclosing disabled for wildfire mitigation. On the trouble Hyampom 60kV tap de-energized. MOM Big Bar, Grouse Creek, Big Creek, Hyampom and Ridge Cabin. Weather storm. Line is in tier 2/3 HFTD/HFRA. 2045 Line manually tested NG. 2048 Big Bar JCT to Maple Creek section manually tested OK, restoring Big Bar and Ridge Cabin. 2050 Hyampom 60kV tap energized, restoring Grouse Creek, Big Creek and Hyampom. Estimated return for Trinity to Big Bar JCT section 03/10/23. 3/11/23, 1736 Trinity-Maple Creek 60kV line (Trinity to Big Bar JCT section) manually tested OK after crew replaced three phases of NG conductor and removed downed tree between poles 1/10, 1/11 and reframed pole 1/11. From trouble on 03/09/23 at 2041. | NONE | NORTH COAST | INT-17096 | 0 | 0 | 0 | 0 | 0 | 0 | 5675418 | A-C | 001/010 | AUTO | Single Mode | Tier 2 | Trinity | Humboldt | 40.7287 | -122.9583 | Trinity-Maple Creek 60kV line COND between poles 001/010, 001/011 | Storm | 4/0 ACSR | Lat: 40.72866, Long: -122.95825 |  |  | SN=303;SE=340;WN=432;WE=454
72 | 9 | Tier 2 |  | NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | ETL.7640 | 60161 | MTN GATE JCT-CASCADE | 2023 | 2023-03-09 21:01 | 44994.8757 | YES | YES | YES | 0.81458 | 1173 | 2023-03-10 16:34 | 44995.6903 | F | Equipment Failure | Equip Fail-conductor | NONE | Relayed - 3/9/23, 2101 Mountain Gate JCT-Cascade 60kV line relayed and did not test due to automatic reclosing disabled for wildfire mitigation. On the trouble, Keswick CB 22 and Deschutes CB 12 tripped out of section Delta-Mountain Gate JCT 60kV line de-energized. SUS Mountain Gate(1) and Antler(CESO=879;CMIN=1,208,625). Weather storm. Line is in a tier 2/3 HFTD/HFRA. Protection reports A-C fault near STR 001/010. 2102 Keswick CB 22 closed via automatics. 2102 Deschutes CB 12 closed via automatics. 2110 Line manually tested NG. No estimated return. 3/10/23, 1634 Mountain Gate JCT-Cascade 60kV line manually tested OK restoring transmission service to Mountain Gate after crew repaired center phase wire down between structures 000/001 and 015/187. 1637 Delta-Mountain Gate JCT 60kV line energized restoring transmission service to Antler. From trouble on 03/09/23 at 2101. Burn spots found mid span but no clear vegetation contact. | NONE | NORTH VALLEY AND SIERRA | INT-17098-1 | 879 | 879 | 1208625 | 0.00015488 | 0.21296 | 1375 | 5675418 | A-C | 001/010 | AUTO | Dependent Mode-initiating | Tier 2 | Shasta | North Valley | 40.7442 | -122.3084 | Mountain Gate JCT-Cascade 60kV line COND between STRs 000/001 and 015/187 | Storm | 4/0 AAC | Lat: 40.74416, Long: -122.30840 |  |  | SN=297;SE=345;WN=443;WE=473
73 | 9 | Non-HFTD |  | SOUTH BAY AND CENTRAL COAST | CENTRAL | 69 | 60 | ETL.6700 | 60063 | DEL MONTE-MONTEREY | 2023 | 2023-03-09 21:18 | 44994.8875 | YES | YES | YES | 1899-12-31 07:41 | 1901 | 2023-03-11 04:59 | 44996.2076 | F | Tree | Tree-failure | COND | Relayed - 3/9/23, 2118 Del Monte-Monterey 60kV line and Monterey-Viejo 60kV line relayed and did not test due to automatic reclosing disabled for wildfire mitigation. SUS Viejo(CESO=3,803;CMIN=692,146) and Navy School(1). Weather storm. Line is in a tier 2/3 HFTD/HFRA. Protection reports A-B-C fault near STR 001/066. 3/11/23, 0459 Del Monte-Monterey 60kV line returned to service restoring Navy School Sub after crew repaired downed conductor between poles 001/054 to 001/056, replaced NG pole 001/056, removed SW 27 and installed jumpers at pole 001/157. From trouble on 03/09/23 at 2118. | NONE | SOUTH BAY AND CENTRAL COAST | INT-17100 | 3803 | 3803 | 692146 | 0.00067008 | 0.12196 | 182 | 5675418 | A-B-C | 001/066 | AUTO | Single Mode | Non-HFTD | Monterey | Central Coast | 36.5997 | -121.8761 | Del Monte-Monterey 60kV line COND between STRs 001/054 to 001/056, replaced NG pole 001/056, 001/157 | Storm | 715 AAC | Lat: 36.59970, Long: -121.87605 |  |  | SN=703;SE=802;WN=972;WE=1039
74 | 10 | Tier 2 |  | NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | ETL.7270 | 60122 | KESWICK-TRINITY | 2023 | 2023-03-10 02:27 | 44995.1021 | No | YES | YES | 1899-12-31 15:12 | 2352 | 2023-03-11 17:39 | 44996.7354 | F | Tree | Tree-failure | STRU | Relayed - 3/10/23, 0227 Keswick-Trinity 60kV line relayed and did not test due to automatic reclosing disabled for wildfire mitigation. SUS French Gulch(CESO=218;CMIN=2,180). Weather storm. Line is in a tier 2/3 HFTD/HFRA. 0236 Line manually tested NG. 0237 Keswick to French Gulch section manually tested OK, restoring French Gulch. Estimated return 03/11/23. Protection reports A-B-C fault near STR 025/418. 3/11/23, 1518 Keswick-Trinity 60kV line (French Gulch to Trinity section) returned to service after crews replaced three phases of downed conductor between poles 25/417 to 25/418 and 25/418 to 25/419, reframed poles 4/15, 4/18, 4/17, 4/19, 25/415, 25/419 and replaced NG pole 25/420. 1739 Line returned normal. From trouble on 03/10/23 at 0227. | NONE | NORTH VALLEY AND SIERRA | INT-17108 | 218 | 218 | 2180 | 3.8411e-05 | 0.00038411 | 10 | 5675418 | A-B-C | 025/418 | AUTO | Single Mode | Tier 2 | Trinity | North Valley | 40.7017 | -122.8519 | Keswick-Trinity 60kV line COND between STRs 025/417 to 025/418 and 025/418 to 025/419 | Storm | 2/0 CU | Lat: 40.70168, Long: -122.85186 |  |  | SN=281;SE=326;WN=415;WE=443
75 | 11 | Tier 2 |  | CENTRAL VALLEY | CENTRAL | 115 | 115 | ETL.2400 | 10166 | MELONES-RACETRACK | 2023 | 2023-03-11 14:45 | 44996.6146 | No | YES | YES | 1900-01-01 03:28 | 3088 | 2023-03-13 18:13 | 44998.759 | F | Weather | Weather-wind | STRU | Relayed - 3/11/23, 1445 Melones-Racetrack 115kV line relayed and did not test due to automatic reclosing disabled for wildfire mitigation. 1449 Line manually tested NG. SUS Racetrack(CESO=3,795;CMIN=356,730). Weather storm. Line is in a tier 2/3 HFTD/HFRA. Protection reports A-C fault near STR 001/009. 1620 Racetrack 115kV tap section manually tested OK restoring Racetrack. 1805 Melones SW STA to Racetrack section cleared for crew to repair downed poles 001/008 and 001/009. Estimated return 03/12/23. 3/13/23, 1802 Melones-Racetrack 115kV line (Melones to Racetrack section) returned to service after crew replaced downed poles 001/008 and 001/009 damaged by wind. 1813 Line restored normal. From trouble 03/11/23 at 1445. | NONE | CENTRAL VALLEY | INT-17118 | 3795 | 3795 | 356730 | 0.00066867 | 0.062855 | 94 | 5675418 | A-C | 001/009 | AUTO | Single Mode | Tier 2 | Tuolumne | Yosemite | 37.9254 | -120.5122 | Melones-Racetrack 115kV line STRs, CONDs 001/008 and 001/009 | Storm | 397.5 AAC | Lat: 37.92543, Long: -120.51223 |  |  | SN=440;SE=514;WN=666;WE=711
76 | 11 | Non-HFTD |  | CENTRAL VALLEY | CENTRAL | 69 | 70 | ETL.9010 | 70061 | MERCED-MERCED FALLS | 2023 | 2023-03-14 12:51 | 44999.5354 | YES | YES | YES | 0.59653 | 859 | 2023-03-15 03:10 | 45000.1319 | F | Weather | Weather-wind | STRU | Relayed - 3/14/23, 1251 Merced-Merced Falls 70kV line relayed and did not test. 1259 Line manually tested NG. No customer interruption. Weather storm. Line is not in a tier 2/3 HFTD/HFRA. Protection reports B-C fault near STR 010/001 Estimated return 03/15/23. 3/15/23, 0310 Merced-Merced Falls 70kV line returned to service after crew repaired downed poles 10/2, 10/3 and 10/4 damaged by high winds during storm. From trouble on 03/14/23 at 1251. | NONE | CENTRAL VALLEY | INT-17137 | 0 | 0 | 0 | 0 | 0 | 0 | 5675418 | B-C | 010/001 | AUTO | Single Mode | Non-HFTD | Merced | Yosemite | 37.4089 | -120.4527 | Merced-Merced Falls 70kV line STRs 010/002, 010/003 and 010/004 | Storm | 397.5 AAC | Lat: 37.40887, Long: -120.45272 |  |  | SN=440;SE=514;WN=666;WE=711
77 | 11 | Tier 2 |  | NORTH COAST | NORTH | 69 | 60 | ETL.7850 | 60184 | RIO DELL JCT-BRIDGEVILLE | 2023 | 2023-03-14 18:08 | 44999.7556 | YES | YES | YES | 0.95694 | 1378 | 2023-03-15 17:06 | 45000.7125 | F | Tree | Tree-failure | COND | Relayed - 3/14/23, 1808 Rio Dell JCT-Bridgeville 60kV line relayed and did not test due to automatic reclosing disabled for wildfire mitigation. 1810 Bridgeville to Carlotta section manually tested NG. 1813 Rio Dell JCT to Carlotta section manually tested OK. MOM Carlotta(1,129) and Humboldt Redwood at Carlotta(1). Weather storm. Line is in tier 2/3 HFTD/HFRA. Protection reports B-G fault near STR 036/001. Estimated return 03/15/23. 3/15/23, 1706 Rio Dell JCT-Bridgeville 60kV line (Bridgeville to Carlotta section) returned to service after crew spliced conductor at poles 36/0 and 35/11. From trouble on 03/14/23 at 1808. | NONE | NORTH COAST | INT-17145 | 1129 | 0 | 0 | 0 | 0 | 0 | 5675418 | B-G | 036/001 | AUTO | Single Mode | Tier 2 | Humboldt | Humboldt | 40.4655 | -123.8585 | Rio Dell JCT-Bridgeville 60kV line COND STRs 036/000 and 035/011 | Storm | 4/0 AAC | Lat: 40.46546, Long: -123.85851 |  |  | SN=297;SE=345;WN=443;WE=473
78 | 12 | Tier 3 |  | SOUTH BAY AND CENTRAL COAST | SOUTH | 115 | 115 | ETL.1710 | 10087 | GREEN VALLEY-CAMP EVERS | 2023 | 2023-03-15 05:09 | 45000.2146 | No | YES | YES | 1900-01-02 12:20 | 5060 | 2023-03-18 17:29 | 45003.7285 | C | Equipment Failure | Equip Fail-conductor | NONE | Relayed - 3/15/23, 0509 Green Valley-Camp Evers 115kV line relayed and did not test due to automatic reclosing disabled for wildfire mitigation. 0513 Line manually tested NG. No customer interruption. Weather clear. Line is in a tier 2/3 HFTD/HFRA. Protection reports A-B-C fault near STR 005/064. Estimated return 03/16/23. 3/18/23, 1729 Green Valley-Camp Evers 115kV line returned to service after crew repaired three phases of downed conductor between towers 6/77 and 6/78. From trouble on 03/15/23 at 0509. | NONE | SOUTH BAY AND CENTRAL COAST | INT-17147 | 0 | 0 | 0 | 0 | 0 | 0 | 5675418 | A-B-C | 005/064 | AUTO | Single Mode | Tier 3 | Santa Cruz | Central Coast | 36.9998 | -121.8685 | Green Valley-Camp Evers 115kV line COND STRs 006/077 and 006/078 | Storm | 715 AAC | Lat: 36.99980, Long: -121.86847 |  |  | SN=703;SE=802;WN=972;WE=1039
79 | 12 | Tier 3 |  | SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 60 | ETL.6230 | 60011 | BURNS-LONE STAR #1 | 2023 | 2023-03-21 12:39 | 45006.5271 | YES | YES | YES | 1900-01-03 10:59 | 6419 | 2023-03-25 23:38 | 45010.9847 | C | Tree | Tree-tree contact | COND | Relayed - 3/21/23, 1239 Burns-Lone Star #1-60kV line relayed and did not test. SUS Point Moretti(CESO=174;CMIN=1,066,910), Crusher(1) and CEMEX(1). Weather storm. Line is in a tier 2/3 HFTD/HFRA. Protection reports B-C fault near STR 013/106. 1243 Line manually tested NG. Estimated return 03/22/23. 3/25/23, 2338 Burns-Lone Star #1 line returned to service after crews repair one phase of downed conductor between poles 000/003 and 000/004 and replace NG insulator at pole 000/003. | NONE | SOUTH BAY AND CENTRAL COAST | INT-17172 | 174 | 174 | 1066910 | 3.0659e-05 | 0.18799 | 6131.6667 | 5675418 | B-C | 013/106 | AUTO | Single Mode | Tier 3 | Santa Cruz | Central Coast | 37.094 | -122.1445 | Burns-Lonestar #1 STRs 000/003, 000/004 | Rain | 4/0 AAC | Lat: 37.09399, Long: -122.14446 |  |  | SN=328;SE=372;WN=443;WE=473
80 | 12 | Non-HFTD |  | SOUTH BAY AND CENTRAL COAST | SOUTH | 115 | 115 | ETL.1710 | 10087 | GREEN VALLEY-CAMP EVERS | 2023 | 2023-03-21 13:04 | 45006.5444 | YES | YES | YES | 1900-01-01 09:59 | 3479 | 2023-03-23 23:03 | 45008.9604 | F | Tree | Tree-tree contact | STRU | Relayed - 3/21/23, 1304 Green Valley-Camp Evers 115kV line relayed and did not test. No customer interruption. Weather storm. Line is in tier 2/3 HFTD/HFRA. Protection reports B-C fault near STR 001/022. 1312 Line manually tested NG. Estimated return 03/22/23. 3/23/23, 2303 Green Valley-Camp Evers 115kV line returned to service after crew repaired downed conductors at poles 1/19 and 1/20, replaced NG poles 1/20 and 1/22, re-framed and replaced NG insulators on pole 1/21 and replaced NG insulators on pole 1/23. From trouble on 03/21/23 at 1304. | NONE | SOUTH BAY AND CENTRAL COAST | INT-17175 | 0 | 0 | 0 | 0 | 0 | 0 | 5675418 | B-C | 001/022 | AUTO | Single Mode | Non-HFTD | Santa Cruz | Central Coast | 36.9639 | -121.7694 | Green Valley-Camp Evers 115kV line COND, STRs, INSLs 001/019, 001/020, 001/021, 001/023 | Rain | 715 AAC | Lat: 36.96391, Long: -121.76941 |  |  | SN=703;SE=802;WN=972;WE=1039
81 | 12 | Tier 3 |  | SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 60 | ETL.7590 | 60156 | MONTA VISTA-BURNS | 2023 | 2023-03-21 13:05 | 45006.5451 | YES | YES | YES | 1900-01-02 08:40 | 4840 | 2023-03-24 21:45 | 45009.9062 | C | Tree | Tree-tree contact | STRU | Relayed - 3/21/23, 1305 Monta Vista-Burns 60kV line relayed and did not test. On the trouble, Burns 60kV bus and Burns-Lone Star #2-60kV line de-energized. SUS Big Basin(CESO=4,072;CMIN=) and Burns(CESO=35;CMIN=). Weather storm. Line is in a tier 2/3 HFTD/HFRA. Protection reports A-B-C fault near STR 008/067. 1311 Monta Vista to Big Basin section manually tested NG. Estimated return 03/22/23. 3/24/23, 2145 Monta Vista-Burns 60kV line returned to service restoring transmission service to Big Basin after crew replaced NG conductors and hardware between structures 8/69, 8/70 and 8/71. From trouble on 03/21/23 at 1305. 3/25/23, 2331 Burns 60kV bus returned to service restoring transmission service to Burns. 2333 Burns-Lone Star #2-60kV line returned to service. | NONE | SOUTH BAY AND CENTRAL COAST | INT-17172-4 | 4072 | 4072 | 19708480 | 0.00071748 | 3.4726 | 4840 | 5675418 | A-B-C | 008/067 | AUTO | Dependent Mode-initiating | Tier 3 | Santa Cruz | Central Coast | 37.213 | -122.1503 | Monta Vista-Burns 60kV line CONDs, STRs, HDWR 008/069, 008/070 and 008/071 | Storm | 397.5 AAC | Lat: 37.21301, Long: -122.15027 |  |  | SN=488;SE=554;WN=666;WE=711
82 | 13 | Non-HFTD |  | NORTH COAST | NORTH | 69 | 60 | ETL.6810 | 60075 | ESSEX JCT-ORICK | 2023 | 2023-03-27 13:58 | 45012.5819 | No | YES | YES | 1899-12-31 02:51 | 1611 | 2023-03-28 16:49 | 45013.7007 | F | Tree | Tree-tree contact | COND | Relayed - 3/27/23, 1358 Essex JCT-Orick 60kV line relayed and did not test. 1402 Essex JCT to Big Lagoon section manually tested OK. SUS Orick(CESO=356;CMIN=). Momentary interruption to Trinidad(1,500). Weather cloudy/windy. Line is in a tier 2/3 HFTD/HFRA. Protection reports A-B fault near STR 021/002A. 1728 Big Lagoon to Orick section cleared to repair sagging conductors at pole 21/002A and 1 phase of downed conductor between 23/7 and 23/8 caused by tree falling through the line. Estimated return 03/28/23. 3/28/23, 1649 Essex JCT-Orick 60kV line returned to service restoring Orick after crew repaired three phases of downed conductor two spans between poles 23/6, 23/7 and 23/8. Momentary interruption Trinidad (1,500). | NONE | NORTH COAST | INT-17203 | 1856 | 356 | 573516 | 6.2727e-05 | 0.10105 | 1611 | 5675418 | A-B | 021/002A | AUTO | Single Mode | Non-HFTD | Humboldt | Humboldt | 41.2101 | -124.1007 | Essex JCT-Orick 60kV line CONDs, STRs 023/006, 023/007 and 023/008 | Wind | 2/0 CU | Lat: 41.21007, Long: -124.10066 |  |  | SN=310;SE=350;WN=415;WE=443
83 | 14 | Non-HFTD |  | NORTH COAST | NORTH | 115 | 115 | ETL.7080 | 60103 | HUMBOLDT BAY-HUMBOLDT #1 | 2023 | 2023-03-27 22:35 | 45012.941 | No | YES | YES | 0.74028 | 1066 | 2023-03-28 16:21 | 45013.6813 | F | Tree | Tree-tree contact | COND | Relayed - 3/27/23, 2235 Humboldt Bay-Humboldt #1-115kV line relayed and did not test. No customer interruption. Weather storm. Line is in tier 2/3 HFTD/HFRA. Protection reports A-B-C fault near STR 006/031. 2242 Line manually tested line NG. Estimated return 03/28/23. 3/28/23, 1621 Humboldt-Humboldt Bay #1-115kV line returned to service after crew removed trees from line and repaired three phases of downed conductor at structure 6/31. | NONE | NORTH COAST | INT-17204 | 0 | 0 | 0 | 0 | 0 | 0 | 5675418 | A-B-C | 006/031 | AUTO | Dependent Mode-initiating | Non-HFTD | Humboldt | Humboldt | 40.7819 | -124.1117 | Humboldt Bay-Humboldt #1-115kV line STR 006/031 | Storm | 397.5 AAC | Lat: 40.78191, Long: -124.11169 |  |  | SN=440;SE=514;WN=666;WE=711
84 | 15 | Tier 3 |  | NORTH VALLEY AND SIERRA | NORTH | 115 | 115 | ETL.4220 | 10360 | WOODLEAF-PALERMO | 2023 | 2023-03-28 16:35 | 45013.691 | No | YES | YES | 1899-12-31 22:28 | 2788 | 2023-03-30 15:03 | 45015.6271 | F | Tree | Tree-failure | COND | Relayed - 3/28/23, 1635 Woodleaf-Palermo 115kV line relayed and did not test. SUS Sly Creek PH (offline), Woodleaf PH (offline), Deadwood PH (offline), Forbestown PH (offline) and Kanaka(CESO=1,627;CMIN=13,016). Weather storm. Line is in a tier 2/3 HFTD/HFRA. Protection reports A-G fault near STR 004/040. 1641 Line manually tested NG. 1644 Palermo to Kanaka JCT manually tested OK, restoring transmission service to Kanaka. No estimated return. 3/30/23, 1503 Sly Creek 115kV tap returned to service after crew repaired one phase of downed conductor between structures 0/4 and 0/5 restoring Sly Creek PH (offline) and Deadwood Creek PH (offline). From trouble on 03/28/23 at 1635. | NONE | NORTH VALLEY AND SIERRA | INT-17219 | 1627 | 1627 | 13016 | 0.00028667 | 0.0022934 | 8 | 5675418 | A-G | 004/040 | AUTO | Single Mode | Tier 3 | Butte | North Valley | 39.5768 | -121.1232 | Sly Creek 115kV Tap COND STRs 000/004 and 000/005 | Storm | 4/0 ACSR | Lat: 39.57684, Long: -121.12319 |  |  | SN=303;SE=340;WN=432;WE=454
85 | 16 | Non-HFTD |  | CENTRAL VALLEY | CENTRAL | 69 | 70 | ETL.8960 | 70056 | LOS BANOS-PACHECO | 2023 | 2023-04-14 05:25 | 45030.2257 | No | YES | YES | 0.89236 | 1285 | 2023-04-15 02:50 | 45031.1181 | F | Equipment Failure | Equip Fail-conductor | COND | Relayed - 4/14/23, 0525 Los Banos-Pacheco 70kV line relayed and did not test as directed by Operations. 0540 Line tested NG. SUS Dinosaur Point (offline) and Pacheco PP(1). Weather clear. Line is in a tier 2/3 HFTD/HFRA. Fault location not available due to electromechanical relays. Estimated return 04/15/23. 4/15/23, 0250 Los Banos-Pacheco 70kV line returned to service after crew replaced two phases of conductor between towers 081/356 and 081/357, restoring Dinosaur Point and Pacheco PP. From trouble on 04/14/23 at 0525. T-Line did an air patrol and found 1 Phase (Middle) broke (on Ground) 3” in the shoe (1113 ALUM). Crew repaired Middle Phase and Top Phase had loose wrap. Pictures and wire down report in the CAP 000125932201. Work was completed on LC 125908968 | 125932201 | CENTRAL VALLEY | INT-17272 | 0 | 0 | 0 | 0 | 0 | 0 | 5675418 | NA | NA | AUTO | Single Mode | Non-HFTD | Merced | Yosemite | 37.1317 | -121.0768 | Los Banos-Pacheco 70kV line between STRs 081/356 and 081/357 | Clear | 1113 AAC | Lat: 37.13172, Long: -121.07685 |  |  | SN=825;SE=975;WN=1287;WE=1378
86 | 17 | Tier 3 |  | NORTH COAST | NORTH | 69 | 60 | ETL.7550 | 60151 | MENDOCINO-WILLITS-FORT BRAGG | 2023 | 2023-05-02 08:26 | 45048.3514 | No | YES | YES | 1899-12-31 08:50 | 1970 | 2023-05-03 17:16 | 45049.7194 | F | Tree | Tree-3rd party | COND | Relayed - 5/2/23, 0826 Mendocino-Willits-Fort Bragg 60kV line relayed and did not test as directed by Operations. On the trouble, Fort Bragg-Elk, Philo JCT-Elk and Elk-Gualala 60kV lines de-energized. Sustained interruption to Fort Bragg, Philo, Elk, Point Arena, Garcia and Big River. Weather rain. Line is in tier 2/3 HFTD/HFRA. 1020 Philo JCT-Elk 60kV line energized restoring Philo. 1027 Elk restored. 1029 Ft Bragg-Elk 60kV line energized restoring Big River. 1038 Ft Bragg restored. 1128 Elk-Gualala 60kV line energized restoring Point Arena and Garcia. 1257 Line cleared for crew to repair downed conductor between structures 29/007 and 29/009 caused by third party tree crew. Estimated return 05/03/23. 5/3/23, 1716 Mendocino-Willits-Fort Bragg 60kV line returned to service after crew re-sagged downed conductors between structures 29/007 and 29/009, reframed wire and replaced insulators between structures 29/008 and 29/009, damaged by third party tree crew. From trouble on 05/02/23 at 0826. | NONE | NORTH COAST | INT-17311-1 | 15834 | 15834 | 2364723 | 0.0027899 | 0.41666 | 149.3446 | 5675418 | A-B-C | 025/008 | AUTO | Dependent Mode-initiating | Tier 2 | Mendocino | Humboldt | 39.3473 | -123.5979 | Mendocino-Willits-Fort Bragg 60kV line COND between STRs 029/007 and 029/009 | Clear | 715 AAC | Lat: 39.34730, Long: -123.59788 |  |  | SN=703;SE=802;WN=972;WE=1039
87 | 18 | Non-HFTD |  | NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | ETL.6610 | 60053 | CORTINA #4 | 2023 | 2023-05-25 21:48 | 45071.9083 | No | YES | No | 0.58681 | 845 | 2023-05-26 11:53 | 45072.4951 | F | Weather | Weather-lightning | COND | Relayed - 5/25/23, 2148 Cortina #4-60kV line relayed and tested NG. 2259 Cortina to Maxwell section tested OK. 2148 to 2259 Sustained interruption to Maxwell(CESO=1,178;CMIN=155,963). 2148 to 2301 Sustained interruption to Rice(CESO=1,310;CMIN=94,320). Weather lightning. Line is not in a tier 2/3 HFTD/HFRA. Protection reports A-B-C fault near STR B014/245. Estimated return 05/26/23. Troubleman bellieved cause to be lightning; confirmed by LDN. 5/26/23, 1153 Cortina #4 60kV line (Maxwell to Colusa Corners section) returned to service after crew repaired/replaced insulators and 2 phases of down wire at structure 015/249. From trouble on 05/25/23 at 2148. | NONE | NORTH VALLEY AND SIERRA | INT-17380 | 2488 | 2488 | 250283 | 0.00043838 | 0.044099 | 100.5961 | 5675418 | A-B-C | B014/245 | AUTO | Single Mode | Non-HFTD | Colusa | Sacramento | 39.2765 | -122.149 | Cortina #4-60kV line ET-WD STR 015/249 | Lightning | 397.5 AAC | Lat: 39.27648, Long: -122.14896 | 39.2765 | -122.149 | SN=440;SE=514;WN=666;WE=711
88 | 19 | Non-HFTD |  | CENTRAL VALLEY | CENTRAL | 69 | 70 | ETL.8970 | 70115 | COPUS-OLD RIVER | 2023 | 2023-05-28 08:54 | 45074.3708 | No | YES | No | 0.42083 | 606 | 2023-05-28 19:00 | 45074.7917 | F | Equipment Failure | Equip Fail-conductor | HDWR | Relayed - 5/28/23, 0854 Copus-Old River 70kV line relayed and tested NG. On the trouble, South Kern Solar separated. Weather clear. Line is not in a tier 2/3 HFTD/HFRA. Protection reports A-C-G fault near STR A019/316. 1146 Copus to Lakeview line section tested OK, restoring South Kern Solar. 1900 Old River to San Emidio JCT line section returned to service after crew repaired two phases of downed conductor between poles 018/312 and 019/313. Line returned normal. | NONE | CENTRAL VALLEY | INT-17391 | 1 | 0 | 0 | 0 | 0 | 0 | 5675418 | A-C-G | A019/316 | AUTO | Single Mode | Non-HFTD | Kern | Kern | 35.1236 | -119.1096 | Copus-Old River 70kV line COND STR 018/312 | Clear | 715 AAC | Lat: 35.12358, Long: -119.10962 |  |  | SN=703;SE=802;WN=972;WE=1039
89 | 20 | Non-HFTD |  | NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | ETL.7970 | 60400 | SMARTVILLE-CAMP FAR WEST | 2023 | 2023-06-08 14:19 | 45085.5965 | No | YES | YES | 0.33889 | 488 | 2023-06-08 22:27 | 22:27 | F | Equipment Failure | Equip Fail-insulator-line | STRU | Relayed - 6/8/23, 1419 Smartville-Camp Far West 60kV line (EPSS) relayed and did not test as directed by Operations. Sustained interruption to Smartville and Camp Far West PH(1). Weather clear. 1558 Smartville restored. 2227 Line returned to service after crew repaired one phase of down wire and replaced NG structure 005/096 and NG insulators, restoring Camp Far West PH. | NONE | NORTH VALLEY AND SIERRA | INT-17424 | 561 | 561 | 42075 | 9.8847e-05 | 0.0074136 | 75 | 5675418 | B-G | 006/114 | AUTO | Single Mode | Non-HFTD | Yuba | Sierra | 39.1422 | -121.3226 | Smartville-Camp Far West 60kV line STR and INSL 005/096 | Clear | 4/0 AAC | Lat: 39.14223, Long: -121.32262 | Smartville-Camp Far West 60kV line STR and INSL 005/096 | Clear | SN=297;SE=345;WN=443;WE=473
MEDS |  | 8.0917 |  |  | Wire down events on MEDs in HFTDs
Formulas:
Durn (hr:min) = [Date In]-[Date Out]
Note on O58: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Changed from non-MED to MED on 5/18 because of storm backlog per Tom Huynh

## 3.3 WD MED HFTD
HFTD | RFW/HWW | REGION | TL Area | kV Cls | kV | SAP FL | LINE NO | FACILITY | YEAR | Date Out | Time Out | MED | ET Wire Down | Auto Reclose Disabled | Durn (hr:min) | Durn (mins) | Date In | Time In | Out Cls | Cause Category | Cause Detail | Secondary Cause | Comments | CAP | REGION | TOTL | Customers Affected | CESO/ Event | CMIN/ Event | SAIFI Contr | SAIDI Contr | CAIDI | System Customer Count | Fault Type | Fault Estimate | AUTO / EFO / SCHD | Outage Mode | HFTD | County | Division | LAT | LONG | Actual Location | Weather | Conductor | ET-GIS Location | Conductor Rating
Tier 2 |  | NORTH COAST | NORTH | 69 | 60 | ETL.7490 | 60145 | MAPLE CREEK-HOOPA | 2023 | 2023-01-04 07:16 | 44930.3028 | YES | YES | No | 1900-01-02 10:43 | 4963 | 2023-01-07 17:59 | 44933.7493 | C | Tree | Tree-failure | NONE | Relayed – 1/4/23, 0716 Maple Creek-Hoopa 60kV line relayed and tested NG. SUS Russ Ranch(1), Willow Creek(CESO=2,483;CMIN=xxxx) and Hoopa(CESO=1,618;CMIN=30,661,100). Weather storm. Protection reports A-C fault near STR 002/006. 0720 Maple Creek to Willow Creek section manually tested NG. 1300 Willow Creek and Hoopa restored by temporary generation. No estimated return. 1/7/23, 1759 Maple Creek-Hoopa 60kV line returned to service after crew repaired conductor down at pole 2/6. This restores transmission service to Russ Ranch, Willow Creek and Hoopa. DO given OK to restore load. INT-16519 | NONE | NORTH COAST | INT-16519 | 4101 | 4101 | 31540082 | 0.00072259 | 5.5573 | 7690.8271 | 5675418 | A-C | 002/006 | AUTO | Single Mode | Tier 2 | Humboldt | Humboldt | 40.7894 | -123.8378 | Maple Creek-Hoopa 60kV Line STR 002/006 | Storm | 4/0 ACAR | Lat: 40.78936, Long: -123.83780 | SN=330;SE=364;WN=432;WE=454
Tier 3 |  | NORTH COAST | NORTH | 69 | 60 | ETL.7550 | 60151 | MENDOCINO-WILLITS-FORT BRAGG | 2023 | 2023-01-04 07:22 | 44930.3069 | YES | YES | No | 0.26389 | 380 | 2023-01-04 13:42 | 44930.5708 | F | Equipment Failure | Equip Fail-conductor | NONE | Relayed – 1/4/23, 0548 Mendocino-Willits-Fort Bragg 60kV line relayed and improperly did not test. No customer interruption. Weather storm. Line is in a tier 2/3 HFTD. Protection reports A-C fault near STR 010/006. 0555 Line manually tested OK. 0556 line returned normal. Patrol found 1 phase of downed conductor between 010/000 and 010/001. 1342 Mendocino-Willits-Fort Bragg 60kV line returned to service after crews repaired 1 phase of down conductor. INT-16521 | NONE | NORTH COAST | INT-16521 | 0 | 0 | 0 | 0 | 0 | 0 | 5675418 | A-C | 010/006 | AUTO | Single Mode | Tier 3 | Mendocino | Humboldt | 39.3471 | -123.3066 | Mendocino-Willits-Fort Bragg 60kV line between 001/000 and 001/001 | Storm | 397.5 AAC | Lat: 39.34714, Long: -123.30664 | SN=440;SE=514;WN=666;WE=711
Tier 2 |  | NORTH COAST | NORTH | 69 | 60 | ETL.6980 | 60430 | FORT ROSS-GUALALA | 2023 | 2023-01-04 10:55 | 44930.4549 | YES | YES | No | 1900-01-04 08:36 | 7716 | 2023-01-09 19:31 | 44935.8132 | C | Tree | Tree-failure | COND | Relayed – 1/4/23, 1055 Fort Ross-Gualala 60kV line relayed and tested NG. MOM Gualala(423). SUS Annapolis(CESO=111;CMIN=1,198,444). Weather storm. Protection reports A-B-C fault near STR 053/008. 1208 Fort Ross to Annapolis section manually tested OK, restoring Annapolis. 1419 Fort Ross to Annapolis section relayed and tested NG. SUS Annapolis. Estimated return 1/8/23 due to safety issues of crew getting to location from adverse weather. 1/9/23, 1931 Fort Ross-Gualala 60kV line manually tested OK, restoring Annapolis, after crews repaired 2 phases of wire down at structure 31/12, repaired single phase of wire down at structures 35/3, 35/4 and 35/6 & replaced structure 35/2 and repaired 2 phases of wire down. INT-16538 | NONE | NORTH COAST | INT-16538 | 111 | 111 | 1198444 | 1.9558e-05 | 0.21116 | 10796.7928 | 5675418 | A-B-C | 053/008 | AUTO | Single Mode | Tier 2 | Sonoma | Sonoma | 38.5909 | -123.3024 | Fort Ross-Gualala 60kV line STRs 031/012, 035/003, 035/004, 035/006, 035/002 | Storm | 715 AAC | Lat: 38.59086, Long: -123.30243 | SN=703;SE=802;WN=972;WE=1039
Tier 3 |  | SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 60 | ETL.7590 | 60156 | MONTA VISTA-BURNS | 2023 | 2023-01-04 13:36 | 44930.5667 | YES | YES | No | 1900-01-01 06:32 | 3272 | 2023-01-06 20:08 | 44932.8389 | F | Tree | Tree-failure | COND | Relayed – 1/4/23, 1336 Monta Vista-Burns 60kV line relayed and tested NG. On the trouble, Burns-Lone Star #1 and #2-60kV lines de-energized. SUS Big Basin(CESO=4,072;CMIN=13,323,584), Point Moretti(CESO=1,060;CMIN=3,476,800), Crusher(1) and Cemex(1). Weather storm. Protection reports A-B-C fault near STR 013/104. 1420 T-line troubleman confirmed three phases of downed conductor one span between poles 011/093 and 011/094 on Monta Vista-Burns 60kV line caused by fallen tree top. 1/5/23, 1359 Crew is continuing with repair at 11/93-11/94. ETOR is now unknown as there is a report of additional wire down at another location (008/073-009/074) -patrol to confirm has been initiated. Helicopter for full line patrols has not been able to get up at this time – there looks to be a window of opportunity from 1500-1600. 2021 Monta Vista-Burns 60kV line (Monta Vista to Big Basin section) cleared for crew to repair three phases of downed conductor one span between poles 11/93 and 11/94 damaged by downed tree top. Estimated return 01/05/23. Multiple locations of wires down on line. 1/6/23, 1951 Monta Vista-Burns 60kV line (Monta Vista-Big Basin section) manually tested OK. 2008 Line restored, restoring Big Basin. 2011 Burns energized, restoring Burns. 2016 Burns-Lone Star #2-60kV line returned to service restoring Point Moretti and Crusher. 2103 Burns-Lone Star #1-60kV line returned to service restoring transmission service to Cemex (1). INT-16543 | NONE | SOUTH BAY AND CENTRAL COAST | INT-16543-1 | 4072 | 4072 | 13323584 | 0.00071748 | 2.3476 | 3272 | 5675418 | A-B-C | 013/104 | AUTO | Common Mode-initiating | Tier 3 | Santa Cruz | Central Coast | 37.1694 | -122.1658 | Monta Vista-Burns 60kV line STRs 008/073-009/074 | Storm | 397.5 AAC | Lat: 37.16936, Long: -122.16582 | SN=440;SE=514;WN=666;WE=711
Tier 2 |  | NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | ETL.8410 | 60244 | ELK-GUALALA | 2023 | 2023-01-04 14:48 | 44930.6167 | YES | YES | No | 1900-01-01 02:18 | 3018 | 2023-01-06 17:06 | 44932.7125 | F | Tree | Tree-failure | COND | Relayed - 1/4/23, 1448 Elk-Gualala 60kV line relayed and tested NG. SUS Point Arena(CESO=909;CMIN=2,743,362), Garcia(CESO=9;CMIN=27,162) and Gualala(CESO=3,782;CMIN=11,414,076). Weather storm. Protection reports A-B-C fault near STR 056/002. Line patrol found tree in the line and 3 phases of down conductor between structure 054/003 and 054/004. No estimated return. 1/6/23, 1706 Elk-Gualala 60kV line, (Point arena to Gualala section) returned to service restoring Garcia (9) and Gualala (3782) after crew removed tree from line and repaired three phases of downed conductor between poles 54/3 and 54/4 on Garcia to Gualala section. INT-16546 | NONE | NORTH VALLEY AND SIERRA | INT-16546 | 4700 | 4700 | 14184600 | 0.00082813 | 2.4993 | 3018 | 5675418 | A-B-C | 056/002 | AUTO | Single Mode | Tier 2 | Mendocino | Humboldt | 38.9078 | -123.6612 | Elk-Gualala 60kV line between STRs 054/003 and 054/004 | Storm | 397.5 AAC | Lat: 38.90775, Long: -123.66117 | SN=440;SE=514;WN=666;WE=711
Tier 2 |  | NORTH COAST | NORTH | 69 | 60 | ETL.2060 | 60389 | FORT BRAGG-ELK | 2023 | 2023-01-04 14:59 | 44930.6243 | YES | YES | No | 1899-12-31 18:59 | 2579 | 2023-01-06 09:58 | 44932.4153 | F | Tree | Tree-failure | COND | Relayed – 1/4/23, 1459 Fort Bragg-Elk 60kV line (Elk to Big River section) relayed and tested NG. On the trouble, Big River 60kV SVC tripped. MOM Big River(2,613). Weather storm. No estimated return. Protection reports A-B-C fault near STR 004/001. 1745, Line patrol found broken pole 004/010 and wire down between pole 004/009 and 004/011. 1/6/23, 0955 Crew replaced pole 4/10 and repaired conductor between poles 4/9 and 4/10. 0955 Fort Bragg-Elk 60kV Line (Big River-Elk section) tested OK. 0958 Fort Bragg-Elk 60kV Line restored normal. INT-16547 | NONE | NORTH COAST | INT-16547 | 2613 | 0 | 0 | 0 | 0 | 0 | 5675418 | A-B-C | 004/001 | AUTO | Single Mode | Tier 2 | Mendocino | Humboldt | 39.1895 | -123.7453 | Fort Bragg-Elk 60kV line STRs 004/009 to 004/011 | Storm | 397.5 AAC | Lat: 39.18950, Long: -123.74527 | SN=440;SE=514;WN=666;WE=711
Tier 2 |  | BAY AREA | NORTH | 69 | 60 | ETL.7180 | 60113 | IGNACIO-BOLINAS #2 | 2023 | 2023-01-04 16:35 | 44930.691 | YES | YES | No | 1899-12-31 21:16 | 2716 | 2023-01-06 13:51 | 44932.5771 | F | Equipment Failure | Equip Fail-structure-line | COND | Relayed - 1/4/23, 1635 Ignacio-Bolinas #2-60kV line relayed and tested NG. SUS Tocaloma(1) and Olema(CESO=2,225;CMIN=). Weather storm. Protection reports A-G fault near STR 025/277. 1646 Ignacio to Tocaloma line section manually tested NG. 1651 Bolinas to Tocaloma line section manually tested OK, restoring Olema. 1957 Bolinas to Tocaloma section relayed and did not test. Sustained interruption to Olema. Estimated return 01/05/23. 1/5/23, Line patrol found downed center phase conductor between STR 013/158 and 013/159 and NG cross arm at pole 023/266 and a blown jumper at pole 023/269. 1/6/23, 1351 Ignacio-Bolinas #2-60kV line (Stafford JCT to Tocaloma JCT section) tested OK after crew repaired downed conductor between 13/158 and 1/159, restoring transmission service to Tocaloma and Olema. Bolimas-Olema JCT will be cleared to repair issues once safe. INT-16549 | NONE | BAY AREA | INT-16549 | 2225 | 2225 | 6043100 | 0.00039204 | 1.0648 | 2716 | 5675418 | A-G | 025/277 | AUTO | Single Mode | Tier 2 | Marin | North Bay | 38.0668 | -122.7174 | Ignacio-Bolinas #2 STRs 013/158 to 013/159 | Storm | 715 AAC | Lat: 38.06682, Long: -122.71738 | SN=703;SE=802;WN=972;WE=1039
Tier 3 |  | NORTH COAST | NORTH | 69 | 60 | ETL.6979 | 60429 | MONTE RIO-FORT ROSS | 2023 | 2023-01-04 19:51 | 44930.8271 | YES | YES | No | 1899-12-31 02:07 | 1567 | 2023-01-05 21:58 | 44931.9153 | F | Tree | Tree-failure | COND | Relayed – 1/4/23, 1951 Monte Rio-Fort Ross 60kV line relayed and tested NG. On the trouble, Salmon Creek 60kV tap de-energized. SUS Fort Ross(CESO=642;CMIN=1,006,014) and Salmon Creek(CESO=1,820;CMIN=2,851,940). Weather storm. No estimated return. Protection reports A-B fault near STR 017/002. 1/5/23, 2158 Monte Rio-Fort Ross 60kV line manually tested OK after crew repaired three phases of downed conductor between poles 17/2 and 17/3. Salmon Creek 60kV tap energized. INT-16562 | NONE | NORTH COAST | INT-16562 | 2462 | 2462 | 3857954 | 0.0004338 | 0.67977 | 1567 | 5675418 | A-B | 017/002 | AUTO | Single Mode | Tier 3 | Sonoma | Sonoma | 38.4784 | -123.0545 | Monte Rio-Fort Ross 60kV line COND between STRs 017/002, 017/003 | Storm | 4/0 AAC | Lat: 38.47839, Long: -123.05445 | SN=328;SE=372;WN=443;WE=473
Tier 2 |  | NORTH COAST | NORTH | 115 | 115 | ETL.1110 | 10018 | BRIDGEVILLE-COTTONWOOD | 2023 | 2023-01-04 23:59 | 44930.9993 | YES | YES | No | 1900-01-01 21:55 | 4195 | 2023-01-07 21:54 | 44933.9125 | F | Tree | Tree-failure | COND | Relayed - 1/4/23, 2359 Bridgeville-Cottonwood 115kV line relayed and tested NG. SUS Wildwood(CESO=139;CMIN=2,085), Forest Glen(1) and Low Gap(1). Weather storm. Protection reports A-C-G fault near STR 059/433. 0107 Cottonwood to Low Gap section manually tested NG. 0110 Cottonwood to Wildwood JCT manually tested OK, restoring Wildwood. 0117 Bridgeville to Low Gap JCT section manually tested OK, restored Low Gap. 1414 Low Gap to Wildwood section cleared for crew to remove tree in the line between structures 059/432 to 059/433 and repair NG insulator at structure 059/432. Estimated return 01/06/23. INT-16576 | NONE | NORTH COAST | INT-16576 | 139 | 139 | 2085 | 2.4492e-05 | 0.00036737 | 15 | 5675418 | A-C-G | 059/433 | AUTO | Single Mode | Tier 2 | Trinity | Humboldt | 40.3716 | -123.3593 | Bridgeville-Cottonwood 60kV line COND between STRs 059/432 and 059/433 | Storm | 397.5 ACSR | Lat: 40.37164, Long: -123.35932 | SN=538;SE=602;WN=712;WE=757
Tier 2 | HWW | NORTH COAST | NORTH | 69 | 60 | ETL.2060 | 60389 | FORT BRAGG-ELK | 2023 | 2023-01-07 06:34 | 44933.2736 | YES | YES | No | 0.3 | 432 | 2023-01-07 13:46 | 44933.5736 | F | Tree | Tree-failure | NONE | Relayed – 1/7/23, 0634 Fort Bragg-Elk 60kV line relayed and tested NG. SUS Big River(CESO=2,542;CMIN=35,588). Weather wind. Protection reports B-G fault near STR 021/001. 1346 Line returned to service after crew repaired downed conductor at pole 21/1. INT-16585 | NONE | NORTH COAST | INT-16585 | 2542 | 2542 | 35588 | 0.0004479 | 0.0062706 | 14 | 5675418 | B-G | 021/001 | AUTO | Single Mode | Tier 2 | Mendocino | Humboldt | 39.3935 | -123.801 | Fort Bragg-Elk 60kV line conductor at pole 021/001 | Wind | 397.5 AAC | Lat: 39.39355, Long: -123.80098 | SN=440;SE=514;WN=666;WE=711
Tier 3 |  | BAY AREA | NORTH | 69 | 60 | ETL.7140 | 60109 | IGNACIO-BOLINAS #1 | 2023 | 2023-01-07 23:45 | 44933.9896 | YES | YES | No | 1900-01-01 19:00 | 4020 | 2023-01-10 18:45 | 44936.7812 | F | Tree | Tree-failure | COND | Relayed – 1/7/23, 2345 Ignacio-Bolinas #1-60kV line relayed and tested NG. SUS Woodacre(CESO=4,154;CMIN=2,546,416) and Bolinas(CESO=3,438;CMIN=939,877). Weather storm. Protection reports A-B fault near STR 003/042. 1/10/23, 1845 Ignacio-Bolinas #1-60kV line (Ignacio to Woodacre section) returned to service after crew replaced NG pole 4/44 damaged by the storm. From trouble on 01/07/23 at 2345. INT-16601 | NONE | BAY AREA | INT-16601 | 7602 | 7602 | 3486293 | 0.0013395 | 0.61428 | 458.6021 | 5675418 | A-B | 003/042 | AUTO | Single Mode | Tier 3 | Marin | North Bay | 38.0483 | -122.5988 | Ignacio-Bolinas #1 STR 004/044 | Storm | 715 AAC | Lat: 38.04832, Long: -122.59881 | SN=802;SE=846;WN=972;WE=1039
Tier 2 |  | NORTH COAST | NORTH | 69 | 60 | ETL.7820 | 60181 | POTTER VALLEY-WILLITS | 2023 | 2023-01-08 04:09 | 44934.1729 | YES | YES | No | 0.54583 | 786 | 2023-01-08 17:15 | 44934.7188 | F | Tree | Tree-failure | NONE | Relayed – 1/8/23, 0409 Potter Valley-Willits 60kV line relayed and tested NG. No customer interruption. Weather storm. Protection reports A-B fault near STR 003/000. 1715 Line returned to service after crews repaired 3 phases of down conductor between 003/002 and 003/003. INT-16620 | NONE | NORTH COAST | INT-16620 | 0 | 0 | 0 | 0 | 0 | 0 | 5675418 | A-B | 003/000 | AUTO | Single Mode | Tier 2 | Mendocino | Humboldt | 39.3829 | -123.2271 | Potter Valley-Willits 60kV line COND between STRs 003/002 and 003/003 | Storm | 1/0 ACSR | Lat: 39.38294, Long: -123.22713 | SN=222;SE=245;WN=287;WE=303
Tier 3 |  | NORTH COAST | NORTH | 69 | 60 | ETL.7490 | 60145 | MAPLE CREEK-HOOPA | 2023 | 2023-01-08 23:06 | 44934.9625 | YES | YES | No | 1900-01-01 13:17 | 3677 | 2023-01-11 12:23 | 44937.516 | F | Tree | Tree-failure | COND | Relayed – 1/8/23, 2306 Maple Creek-Hoopa 60kV line relayed, Maple Creek to Willow Creek section tested OK, Willow Creek to Hoopa tested NG. No customer interruption. Weather storm. Protection reports A-B-C fault near STR 020/014. 1/11/23, 1223 Maple Creek-Hoopa 60kV line returned to service restoring transmission service to Hoopa (2044) after crew repaired (3) phases of downed conductor between poles 21/10 and 22/0. INT-16631 | NONE | NORTH COAST | INT-16631 | 2044 | 2044 | 7515788 | 0.00036015 | 1.3243 | 3677 | 5675418 | B-C-G | 001/026 | AUTO | Single Mode | Tier 3 | Humboldt | Humboldt | 40.9715 | -123.6423 | Maple Creek-Hoopa 60kV Line CONDs 021/010 to 022/000 | Storm | 4/0 ACAR | Lat: 40.97147, Long: -123.64229 | SN=330;SE=364;WN=432;WE=454
Tier 2 | HWW | NORTH COAST | NORTH | 69 | 60 | ETL.6980 | 60430 | FORT ROSS-GUALALA | 2023 | 2023-01-09 00:49 | 44935.034 | YES | YES | No | 0.82083 | 1182 | 2023-01-09 20:31 | 44935.8549 | F | Tree | Tree-failure | NONE | Relayed - 1/9/23, 0049 Elk-Gualala 60kV line relayed and tested NG. On the trouble, Fort Ross-Gualala 60kV line (Annapolis to Gualala section) de-energized. 0052 Elk-Gualala 60kV line manually tested OK. SUS Annapolis(CESO=229;CMIN=270,678). MOM Point Arena(909), Garcia(9) and Gualala(3,782). Weather storm. Protection reports A-C fault near STR 045/009. 1931 Fort Ross-Gualala 60kV line manually tested OK, restoring Annapolis, after crews removed a tree at structure 48/3, repaired 2 phases of wire down at structure 31/12, repaired single phase of wire down at structures 35/3, 35/4 and 35/6 and replaced structure 35/2 and repaired 2 phases of wire down. 2031 Line returned normal. INT-16633 | NONE | NORTH COAST | INT-16633-2 | 229 | 229 | 270678 | 4.0349e-05 | 0.047693 | 1182 | 5675418 | NA | NA | AUTO | Dependent Mode | Tier 2 | Sonoma | Sonoma | 38.5909 | -123.3024 | Fort Ross-Gualala 60kV line CONDs 031/012, 035/003 to 035/006 | Storm | 715 AAC | Lat: 38.59086, Long: -123.30243 | SN=631;SE=742;WN=972;WE=1039
Tier 3 |  | SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 60 | ETL.6240 | 60012 | BURNS-LONE STAR #2 | 2023 | 2023-01-10 01:57 | 44936.0813 | YES | YES | No | 1899-12-31 15:16 | 2356 | 2023-01-11 17:13 | 44937.7174 | F | Tree | Tree-failure | COND | Relayed – 1/10/23, 0157 Burns-Lone Star #2-60kV line relayed and locked out. SUS Crusher(1). Weather storm. Protection reports A-G fault near STR 003/066. 1/11/23, 1713 Burns-Lone Star #2-60kV line returned to service after crew repaired wire down between 2/63 and 2/64, restoring Crusher. From trouble on 01/10/23 at 0157. INT-16647 | NONE | SOUTH BAY AND CENTRAL COAST | INT-16647 | 1 | 0 | 0 | 0 | 0 | 0 | 5675418 | A-G | 003/066 | AUTO | Single Mode | Tier 3 | Santa Cruz | Central Coast | 37.0658 | -122.1545 | Burns-Lone Star #2 60kV line CONDs between STR 002/063 and 002/064 | Storm | 4/0 AAC | Lat: 37.06578, Long: -122.15453 | SN=328;SE=372;WN=443;WE=473
Tier 2 |  | SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 60 | ETL.6710 | 60064 | DEL MONTE-VIEJO | 2023 | 2023-01-10 00:04 | 44936.0028 | YES | YES | No | 1899-12-31 00:44 | 1484 | 2023-01-11 00:48 | 44937.0333 | F | Tree | Tree-failure | STRU | Relayed – 1/10/23, 0204 Del Monte-Viejo 60kV line relayed and tested OK, but tested NG on Viejo end. MOM Navy Lab(1) and Hatton(4,752). Weather storm. Protection reports A-B-C fault near STR 006/041. 1/11/23, 0048 Del Monte-Viejo 60kV line (Hatton to Viejo section) returned to service after crews rehung wire down between pole 5/137 to 5/140 and straighten leaning pole 5/139 and 5/137. Cause found to be tree failed into line. INT-16646 | NONE | SOUTH BAY AND CENTRAL COAST | INT-16646 | 4753 | 0 | 0 | 0 | 0 | 0 | 5675418 | A-B-C | 006/041 | AUTO | Single Mode | Tier 2 | Monterey | Central Coast | 36.563 | -121.9113 | Del Monte-Viejo 60kV line CONDs between STRs 005/137 to 005/140 | Storm | 397.5 AAC | Lat: 36.56303, Long: -121.91128 | SN=440;SE=514;WN=666;WE=711
Tier 2 |  | NORTH COAST | NORTH | 69 | 60 | ETL.7850 | 60184 | RIO DELL JCT-BRIDGEVILLE | 2023 | 2023-01-10 03:58 | 44936.1653 | YES | YES | No | 1899-12-31 15:52 | 2392 | 2023-01-11 19:50 | 44937.8264 | F | Tree | Tree-failure | COND | Relayed – 1/10/23, 0358 Rio Dell JCT-Bridgeville 60kV line relayed and tested NG. SUS Carlotta(CESO=1,133;CMIN=15,862) and Humboldt Redwood Co-generator (offline). Weather storm. Protection reports C-G fault near STR 037/006. 0411 Rio Dell JCT to Carlotta section energized restoring Carlotta and Humboldt Redwood Co-generator. Estimated return 01/11/23. Patrol found fallen tree between structure 038/005 and 038/006, one transmission phase down and two broken distribution arms. 1/11/23, 1950 Rio Dell JCT-Bridgeville 60kV line (Bridgeville to Carlotta section) returned to service after crews removed tree and repaired 1 phase of down conductor between structure 38/5 and 38/6. INT-16661 | NONE | NORTH COAST | INT-16661 | 1133 | 1133 | 15862 | 0.00019963 | 0.0027949 | 14 | 5675418 | C-G | 037/006 | AUTO | Single Mode | Tier 2 | Humboldt | Humboldt | 40.4697 | -123.817 | Rio Dell JCT-Humboldt 60kV line COND STRs 038/005, 038/006 | Storm | 4/0 AAC | Lat: 40.46971, Long: -123.81696 | SN=328;SE=372;WN=443;WE=473
Tier 2 |  | NORTH COAST | NORTH | 69 | 60 | ETL.8170 | 60217 | TRINITY-MAPLE CREEK | 2023 | 2023-01-10 21:37 | 44936.9007 | YES | YES | YES | 1900-01-12 19:25 | 19885 | 2023-01-24 17:02 | 44950.7097 | X | Disaster | Disaster-flood | STRU | Forced – 1/10/23, 2137 Trinity-Maple Creek 60kV line (Trinity to Big Bar section) forced out of service due to leaning pole 8/13, caused by landslide. No customer interruption. No estimated return. 1/24/23, 1702 Trinity-Maple Creek 60kV line (Trinity to Big Bar section) returned to service after crew replaced NG structures 8/12, 8/13, added 2 new poles and repaired downed conductors in between NG structures due to landslide. T23-003316 | NONE | NORTH VALLEY AND SIERRA | T23-003316 | 0 | 0 | 0 | 0 | 0 | 0 | 5675418 | NA | NA | EFO | Emergency Forced Outage | Tier 2 | Trinity | Humboldt | 40.7619 | -123.0691 | Trinity-Maple Creek 60kV line STRs, CONDs 008/012, 008/013 | Storm | 4/0 ACSR | Lat: 40.76193, Long: -123.06914 | SN=303;SE=340;WN=432;WE=454
Tier 3 |  | NORTH COAST | NORTH | 69 | 60 | ETL.6220 | 60010 | BRIDGEVILLE-GARBERVILLE | 2023 | 2023-01-14 07:00 | 44940.2917 | YES | YES | No | 0.57222 | 824 | 2023-01-14 20:44 | 44940.8639 | F | Tree | Tree-failure | COND | Relayed – 1/14/23, 0700 Bridgeville-Garberville 60kV line relayed and tested NG. 0704 Fruitland JCT to Garberville section manually tested OK. MOM Fruitland(335) and Fort Seward(1,143). Weather storm. Protection reports A-G fault near STR 010/000. 2044 Line returned normal after crews repaired one phase of downed transmission conductor and two phases of downed distribution conductor on Bridgeville to Fruitland JCT section between poles 9/17 and 10/0. INT-16716 | NONE | NORTH COAST | INT-16716 | 1478 | 0 | 0 | 0 | 0 | 0 | 5675418 | A-G | 010/000 | AUTO | Single Mode | Tier 3 | Humboldt | Humboldt | 40.3669 | -123.731 | Bridgeville-Garberville 60kV line COND 009/017 and 010/000 | Storm | 4/0 ACSR | Lat: 40.36686, Long: -123.73101 | SN=303;SE=340;WN=432;WE=454
Tier 3 |  | SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 60 | ETL.6710 | 60064 | DEL MONTE-VIEJO | 2023 | 2023-01-14 09:58 | 44940.4153 | YES | YES | No | 0.95347 | 1373 | 2023-01-15 08:51 | 44941.3688 | F | Tree | Tree-failure | STRU | Relayed – 1/14/23, 0958 Del Monte-Viejo 60kV line relayed and tested NG. Hatton to Viejo section tested OK via automatics. MOM Hatton(4,752). SUS Navy Lab(1). Weather storm. Protection reports A-B-C fault near STR 002/045. 1210 Del Monte to Viejo JCT section manually tested OK, restoring Navy Lab. 1427 Viejo JCT to Hatton section cleared to repair downed conductor between structures 2/50 to 2/53 and replace NG pole 2/51. Estimated return 01/15/23. 1/15/23, 0847 Del Monte-Viejo 60kV line (Viejo JCT to Hatton section) returned to service after crews repair downed conductor between structures 2/50 and 2/53, and replace NG pole 2/51. 0851 Line returned normal. Caused by tree failure. INT-16725 | NONE | SOUTH BAY AND CENTRAL COAST | INT-16725 | 4752 | 0 | 0 | 0 | 0 | 0 | 5675418 | C-G | 001/041 | AUTO | Single Mode | Tier 3 | Monterey | Central Coast | 36.5814 | -121.8738 | Del Monte-Viejo 60kV line CONDs between STRs 002/050 and 002/053 | Storm | 715 AAC | Lat: 36.58143, Long: -121.87378 | SN=703;SE=802;WN=972;WE=1039
Tier 2 |  | BAY AREA | NORTH | 69 | 60 | ETL.7140 | 60109 | IGNACIO-BOLINAS #1 | 2023 | 2023-02-21 14:24 | 44978.6 | YES | YES | YES | 0.97083 | 1398 | 2023-02-22 13:42 | 44979.5708 | F | Tree | Tree-failure | COND | Relayed - 2/21/23, 1424 Ignacio-Bolinas #1-60kV line relayed and did not test due to automatic reclosing disabled for wildfire mitigation. 1426 Line manually tested NG. SUS Woodacre(CESO=3,906;CMIN=355,446). Weather wind. Line is in a HFRA and tier 2/3 HFTD. Protection reports A-C fault near STR 014/148, 1431 Ignacio to Woodacre section manually tested OK restoring Woodacre. Estimated return 02/22/23. 2/22/23, 1342 Ignacio-Bolinas 60kV line (Bolinas to Woodacre section) returned to service after crew repaired two phases of downed conductor between poles 13/147 and 13/148. | NONE | BAY AREA | INT-16815 | 3906 | 3906 | 355446 | 0.00068823 | 0.062629 | 91 | 5675418 | A-C | 014/148 | AUTO | Single Mode | Tier 2 | Marin | North Bay | 37.9412 | -122.7057 | Ignacio-Bolinas #1 60kV line COND between 014/147 and 014/148 | Wind | 2 CU | Lat: 37.94121, Long: -122.70569 | SN=201;SE=227;WN=266;WE=284
Tier 2 |  | NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | ETL.7710 | 60168 | NICOLAUS-WILKINS SLOUGH | 2023 | 2023-02-24 01:22 | 44981.0569 | YES | YES | No | 0.61736 | 889 | 2023-02-24 16:11 | 44981.6743 | F | Equipment Failure | Equip Fail-conductor | NONE | Relayed - 2/24/23, 0122 Nicolaus-Wilkins Slough 60kV line relayed and tested NG. SUS Carnac(1) and District 1001 Metering. Weather storm. Line is in a HFRA and tier 2/3 HFTD. Protection reports B-C fault near STR 001/027. 0932 Nicolaus to District 1500 section manually tested OK, restoring District 1001 and District 1500 (Carnack). 1611 DIST 1500 JCT to DIST 2047 JCT section returned to service after crews repair 2 phases of wire down between 019/137 and 019/138. | NONE | NORTH VALLEY AND SIERRA | INT-16864 | 0 | 0 | 0 | 0 | 0 | 0 | 5675418 | B-C | 001/027 | AUTO | Single Mode | Non-HFTD | Yolo | Sacramento | 38.749 | -121.6926 | Nicolaus-Wilkins Slough 60kV line between 019/137 and 019/138. | Storm | 6 CU | Lat: 38.74905, Long: -121.69268 | SN=100;SE=115;WN=144;WE=153
Tier 3 |  | NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | ETL.6310 | 60019 | CASCADE-BENTON-DESCHUTES | 2023 | 2023-02-24 05:35 | 44981.2326 | YES | YES | YES | 0.5125 | 738 | 2023-02-24 17:53 | 44981.7451 | F | Equipment Failure | Equip Fail-conductor | NONE | Relayed - 2/24/23, 0535 Cascade-Benton-Deschutes 60kV line relayed and did not test due to automatic reclosing disabled for wildfire mitigation. SUS Oregon Trail(CESO=3,671;CMIN=851,672) and Wintu pumps(1). Weather storm. Protection reports A-C fault near STR 001/035. Comm issues and indication of 10kV on line, possible Distribution co-mingling with transmission. Line is in a HFRA and tier 2/3 HFTD. 0927 Cascade-Benton-Deschutes 60kV line manually tested OK from Cascade, after Wintu PP SW 65 was opened, restoring Oregon Trail. 1753 Cascade-Benton-Deschutes 60kV line (Wintu tap section) returned to service after crew repaired wire down between 1/23 and 1/24. | NONE | NORTH VALLEY AND SIERRA | INT-16889 | 3672 | 3672 | 851672 | 0.000647 | 0.15006 | 231.9368 | 5675418 | A-C | 001/035 | AUTO | Single Mode | Tier 2 | Shasta | North Valley | 40.6391 | -122.3319 | Cascade-Benton-Deschutes 60kV line COND between 0/23 and 1/24 | Storm | 4/0 AAC | Lat: 40.63909, Long: -122.33186 | SN=356;SE=409;WN=443;WE=473
Tier 2 |  | NORTH COAST | NORTH | 69 | 60 | ETL.6880 | 60082 | FULTON-CALISTOGA | 2023 | 2023-02-24 05:58 | 44981.2486 | YES | YES | YES | 0.49097 | 707 | 2023-02-24 17:45 | 44981.7396 | F | Equipment Failure | Equip Fail-insulator-line | COND | Relayed - 2/24/23, 0558 Fulton-Calistoga 60kV line relayed and did not test due to automatic reclosing disabled for wildfire mitigation. SUS Calistoga(CESO=3,824;CMIN=1,300,160) and Middletown(CESO=4,642;CMIN=190,322). 0609 Line manually tested NG. Weather storm. Line is in a Tier 2/3 HFTD/HFRA. Protection reports B-C fault near :006/006. 0639 Middletown transferred to alternate source. 1138 Fulton to Calistoga JCT section manually tested OK, restoring Calistoga. 1342 to 1745 Cleared Middletown to Calistoga JCT section for crew to repair two phases of downed conductor at structure :7/8. | NONE | NORTH COAST | INT-16892 | 8466 | 8466 | 1490482 | 0.0014917 | 0.26262 | 176.055 | 5675418 | B-C | :006/006 | AUTO | Single Mode | Tier 3 | Lake | Humboldt | 38.6982 | -122.5974 | Fulton-Calistoga 60kV line STR :007/008 | Storm | 4/0 AAC | Lat: 38.69827, Long: -122.59739 | SN=328;SE=372;WN=443;WE=473
Tier 3 |  | NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | ETL.6720 | 60065 | DESABLA-CENTERVILLE | 2023 | 2023-02-24 06:14 | 44981.2597 | YES | YES | YES | 1900-01-03 05:54 | 6114 | 2023-02-28 12:08 | 44985.5056 | C | Tree | Tree-failure | COND | Relayed - 2/24/23, 0614 DeSabla-Centerville 60kV line relayed and did not test due to automatic reclosing disabled for wildfire mitigation. SUS Orofino(CESO=4,733;CMIN= 9,234,173), Toadstown(offline), DeSabla PH(offline) and Forks of the Butte(offline). Weather storm. 0726 Line manually tested NG. Weather storm. Line is in a HFRA and tier 2/3 HFTD. Protection cannot report fault location due to comms failure. Estimated return 02/25/23. 2/28/23, 1208 DeSabla-Centerville 60kV line returned to service after crew repaired downed conductor at poles 1/20-1/21, 2/30-2/31 & 2/34-2/35, restoring transmissioon service to Toadtown PH, Oro Fino, Forks of the Butte and DeSabla. | NONE | NORTH VALLEY AND SIERRA | INT-16903 | 4733 | 4733 | 9234173 | 0.00083395 | 1.627 | 1951.0188 | 5675418 | Unknown | COMM Issues | AUTO | Single Mode | Tier 3 | Butte | North Valley | 39.8571 | -121.6286 | DeSabla-Centerville 60kV line CONDs 001/020-001/021, 002/030-002/031 & 002/034-002/035 | Storm | 350 AAC | Lat: 39.85710, Long: -121.62864 | SN=406;SE=474;WN=613;WE=655
Tier 3 |  | NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | ETL.7300 | 60125 | KILARC-DESCHUTES | 2023 | 2023-02-24 06:34 | 44981.2736 | YES | YES | YES | 0.70069 | 1009 | 2023-02-24 23:23 | 44981.9743 | F | Equipment Failure | Equip Fail-conductor | NONE | Relayed - 2/24/23, 0634 Kilarc-Deschutes 60kV line relayed and did not test due to automatic reclosing disabled for wildfire mitigation. 0638 Line manually tested NG. SUS CAL Creek PH (offline), Cow Creek PH (offline), Bear Creek (offline), Whitmore(CESO=542;CMIN=835,764) and Mega Olsen (offline). Weather storm. Line is in a HFRA and tier 2/3 HFTD. Protection reports B-G fault near 001/028. 1218 TKO JCT to Deschutes section manually tested OK, restoring Cow Creek PH and Bear Creek Hydro. 2321 Kilarc-Deschutes 60kV line (Whitmore to TKO JCT section) manually tested OK after crew repaired wire down between structures 10/215 and 10/216. 2323 Kilarc to Whitmore section energized, restoring Whitmore and Mega Olsen co-generator. | NONE | NORTH VALLEY AND SIERRA | INT-16901 | 542 | 542 | 835764 | 9.55e-05 | 0.14726 | 1542 | 5675418 | B-G | 001/028 | AUTO | Single Mode | Tier 2 | Shasta | North Valley | 40.5812 | -122.0116 | Kilarc-Deschutes 60kV line COND between STRs 010/215 and 010/216 | Storm | 2 ACSR | Lat: 40.58119, Long: -122.01159 | SN=154;SE=173;WN=216;WE=228
Tier 3 |  | CENTRAL VALLEY | CENTRAL | 69 | 70 | ETL.9340 | 70094 | WISHON-SAN JOAQUIN #3 | 2023 | 2023-02-24 19:36 | 44981.8167 | YES | YES | YES | 1900-01-01 15:42 | 3822 | 2023-02-27 11:18 | 44984.4708 | F | Weather | Weather-snow/ ice | COND | Relayed - 2/24/23, 1936 Wishon-San Joaquin #3-70kV line relayed and did not test due automatic reclosing disabled for wildfire mitigation. 1939 Line manually test NG. SUS San Joaquin #2 PH(CESO=1,056;CMIN=4,036,032), Crane Valley PH (offline) and San Joaquin #3 PH (offline). Weather storm. Line is in a HFRA and tier 2/3 HFTD. Protection reports 2/25/23, Update for Wishon-San Joaquin #3-70kV line trouble on 02/24/23 at 1936: 1518 A.G. Wishon PH #3 to San Joaquin PH #2 JCT section manually tested OK restoring San Joaquin #2 PH 70/12kV Distribution transformer and San Joaquin #2 PH (offline). San Joaquin #3 PH to San Joaquin #2 PH JCT section cleared for crew to repair two phases of downed conductor between poles 3/1 and 3/2. Estimated return 02/26/23. 2/27/23, 1118 Wishon-San Joaquin #3-70kV line returned to service normal after crews repaired downed conductor between structures 3/4 to 3/5. Caused by wire being pencilled from being annealled and snow load. DO notified OK to restore San Joaquin #2 PH. | NONE | CENTRAL VALLEY | INT-16938 | 1056 | 1056 | 4036032 | 0.00018607 | 0.71114 | 3822 | 5675418 | A-C | 001/001 | AUTO | Single Mode | Tier 3 | Madera | Yosemite | 37.21 | -119.4968 | Wishon-San Joaquin #3-70kV line COND between STRs 003/004 and 003/005 | Storm | 1 CU | Lat: 37.210005, Long: -119.496794 | SN=243;SE=282;WN=358;WE=382
Tier 2 |  | SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 70 | ETL.9210 | 70081 | TAFT-CUYAMA #2 | 2023 | 2023-02-24 21:27 | 44981.8938 | YES | YES | YES | 1900-01-02 00:27 | 4347 | 2023-02-27 21:54 | 44984.9125 | C | Equipment Failure | Equip Fail-structure-line | COND | Relayed - 2/24/23, 2127 Taft-Cuyama #2-70kV line relayed and did not test due to automatic reclosing disabled for wildfire mitigation. 2129 Line manually tested OK to Open Cuyama SW 35. SUS Cuyama #2-70/12kV transformer(CESO=400;CMIN=856,000). Weather storm. Line is in a HFRA and tier 2/3 HFTD. Protection reports B-G fault near STR 006/069. 2229 Taft-Cuyama #2-70kV line relayed and did not test due to automatic reclosing disabled for wildfire mitigation. 2/26/23, Update to Taft-Cuyama #2-70kV line trouble 02/24/23 at 2127. 0907 Cuyama #2-70/12kV transformer restored from alternate transmission source. 2/27/23, 2154 Taft-Cuyama #2-70kV line returned to service after crew repaired downed conductor between poles 7/73 to 7/74, 9/84 to 9/87, 10/92 to 10/93 and 10/96 to 11/97. Snow and wind in area, poles twisted. From trouble on 02/24/23 at 2229. | NONE | SOUTH BAY AND CENTRAL COAST | INT-16943 | 400 | 400 | 856000 | 7.0479e-05 | 0.15083 | 2140 | 5675418 | B-G | 006/069 | AUTO | Single Mode | Non-HFTD | San Luis Obispo | Kern | 35.0376 | -119.5186 | Taft-Cuyama #2-70kV line COND between STRs 7/73 to 7/74, 9/84 to 9/87, 10/92 to 10/93 and 10/96 to 11/97 | Storm | 2 ACSR | Lat: 35.03759, Long: -119.51861 | SN=154;SE=173;WN=216;WE=228
Tier 2 |  | NORTH COAST | NORTH | 69 | 60 | ETL.7850 | 60184 | RIO DELL JCT-BRIDGEVILLE | 2023 | 2023-02-27 08:04 | 44984.3361 | YES | YES | YES | 1899-12-31 13:11 | 2231 | 2023-02-28 21:15 | 44985.8854 | F | Equipment Failure | Equip Fail-connector/ hardware | COND | Relayed - 2/27/23, 0804 Rio Dell JCT-Bridgeville 60kV line relayed and did not test due to automatic reclosing disabled for wildfire mitigation. 0810 Line manually tested NG. SUS Carlotta(CESO=1,305;CMIN=9,135) and Humboldt Redwood (offline). Weather storm. Line is in a tier 2/3 HFTD/HFRA. Protection reports A-G fault near STR 032/002. 0811 Rio Dell JCT to Carlotta JCT section manually tested OK restoring Carlotta and Humboldt Redwood (offline). Caused by one phase of downed conductor between pole 32/5 and 32/6. Estimated return 02/28/23. 2/28/23, 2115 Rio Dell JCT-Bridgeville 60kV line (Bridgeville to Carlotta section) returned to service after crew repaired one span of wire down between 33/5 and 33/6 | NONE | NORTH COAST | INT-16983 | 1305 | 1305 | 9135 | 0.00022994 | 0.0016096 | 7 | 5675418 | A-G | 032/002 | AUTO | Single Mode | Tier 2 | Humboldt | Humboldt | 40.4865 | -123.8977 | Rio Dell JCT-Bridgeville 60kV line COND between 033/005 and 033/006 | Storm | 4/0 AAC | Lat: 40.48652, Long: -123.89776 | SN=328;SE=372;WN=443;WE=473
Tier 2 |  | NORTH COAST | NORTH | 69 | 60 | ETL.7130 | 60108 | HUMBOLDT-MAPLE CREEK | 2023 | 2023-02-27 09:26 | 44984.3931 | YES | YES | YES | 1900-01-01 05:42 | 3222 | 2023-03-01 15:08 | 44986.6306 | F | Weather | Weather-lightning | HDWR | Relayed - 2/27/23, 0926 Humboldt-Maple Creek 60kV line relayed and did not test due to automatic reclosing disabled for wildfire mitigation. On the trouble, Maple Creek-Hoopa 60kV line de-energized and Trinity-Maple Creek 60kV line open-ended at Maple Creek. 0930 Humboldt-Maple Creek 60kV line manually tested NG. 0934 Trinity-Maple Creek 60kV line returned to service restoring Maple Creek. 0936 Humboldt-Maple Creek 60kV line manually tested NG. On the trouble, the Humboldt-Maple Creek 60kV line de-energized. 0936 Maple Creek to Willow Creek section manually tested OK restoring transmission service to Russ Ranch and Willow Creek. SUS Maple Creek(CESO=147;CMIN=1,176), Russ Ranch(CESO=2;CMIN=20), Willow Creek(CESO=2,373;CMIN=33,222) and Hoopa(CESO=1,413;CMIN=611,829). Weather storm. Line is in a tier 2/3 HFTD/HFRA. Protection reports A-G fault near STR 013/004. Caused by center phase wire down between structures 14/000 and 13/005 on Humboldt-Maple Creek 60kV line. Estimated return 2/28/23. No estimated return for Maple Creek-Hoopa 60kV line (Willow Creek to Hoopa section). 3/1/23, 1508 Humboldt-Maple Creek 60kV line returned to service after crew replaced center phase of conductor between 014/000 and 013/005. 3/2/23, 1254 Maple Creek-Hoopa 60kV line (Willow Creek to Hoopa section) manually tested OK and returned to service, restoring transmission service to Hoopa after crew repaired 3 spans of down conductor between poles 25/4, 25/6, 25/7 and 25/8. Unknown cause of wire down on Humboldt-Maple Creek line. Tree fell through line for Maple Creek-Hoopa WD. | NONE | NORTH COAST | INT-16990-1 | 0 | 0 | 0 | 0 | 0 | 0 | 5675418 | A-G | 013/004 | AUTO | Dependent Mode-initiating | Tier 2 | Humboldt | Humboldt | 40.7679 | -123.8762 | Humboldt-Maple Creek 60kV line COND between 014/000 and 013/005 | Storm | 2/0 CU | Lat: 40.76788, Long: -123.87624 | SN=310;SE=350;WN=415;WE=443
Tier 2 |  | NORTH COAST | NORTH | 69 | 60 | ETL.7490 | 60145 | MAPLE CREEK-HOOPA | 2023 | 2023-02-27 09:26 | 44984.3931 | YES | YES | No | 1900-01-02 03:28 | 4528 | 2023-03-02 12:54 | 44987.5375 | C | Tree | Tree-failure | COND | Relayed - 2/27/23, 0926 Humboldt-Maple Creek 60kV line relayed and did not test due to automatic reclosing disabled for wildfire mitigation. On the trouble, Maple Creek-Hoopa 60kV line de-energized and Trinity-Maple Creek 60kV line open-ended at Maple Creek. 0930 Humboldt-Maple Creek 60kV line manually tested NG. 0934 Trinity-Maple Creek 60kV line returned to service restoring Maple Creek. 0936 Humboldt-Maple Creek 60kV line manually tested NG. On the trouble, the Humboldt-Maple Creek 60kV line de-energized. 0936 Maple Creek to Willow Creek section manually tested OK restoring transmission service to Russ Ranch and Willow Creek. SUS Maple Creek(CESO=;CMIN=), Russ Ranch(CESO=;CMIN=), Willow Creek(CESO=;CMIN=) and Hoopa(CESO=;CMIN=). Weather storm. Line is in a tier 2/3 HFTD/HFRA. Protection reports A-G fault near STR 013/004. Caused by center phase wire down between structures 14/000 and 13/005 on Humboldt-Maple Creek 60kV line. Estimated return 2/28/23. No estimated return for Maple Creek-Hoopa 60kV line (Willow Creek to Hoopa section). 3/1/23, 1508 Humboldt-Maple Creek 60kV line returned to service after crew replaced center phase of conductor between 014/000 and 013/005. 3/2/23, 1254 Maple Creek-Hoopa 60kV line (Willow Creek to Hoopa section) manually tested OK and returned to service, restoring transmission service to Hoopa after crew repaired 3 spans of down conductor between poles 25/4, 25/6, 25/7 and 25/8. Unknown cause of wire down on Humboldt-Maple Creek line. Tree fell through line for Maple Creek-Hoopa WD. | NONE | NORTH COAST | INT-16990-2 | 3788 | 3788 | 645071 | 0.00066744 | 0.11366 | 170.2932 | 5675418 | NA | NA | AUTO | Dependent Mode | Tier 3 | Humboldt | Humboldt | 41.0159 | -123.6469 | Maple Creek-Hoopa 60kV line COND between STRs 025/004 and 025/008 | Storm | 4/0 ACSR | Lat: 41.01590, Long: -123.64689 | SN=303;SE=340;WN=432;WE=454
Tier 3 |  | NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | ETL.6760 | 60070 | DRUM-GRASS VALLEY-WEIMAR | 2023 | 2023-02-27 17:59 | 44984.7493 | YES | YES | YES | 1900-01-03 21:56 | 7076 | 2023-03-04 15:55 | 44989.6632 | C | Tree | Tree-failure | COND | Relayed - 2/27/23, 1759 Drum-Grass Valley-Weimar 60kV line relayed and did not test due to automatic reclosing disabled for wildfire mitigation. 1804 Line manually tested NG. SUS Shady Glen(CESO=2,202;CMIN=17,616), Bonnie Nook(1) and Cape Horn(1). Rollins PH separated on the trouble. Weather storm. Line is in a tier 2/3 HFTD/HFRA. Protection reports A-B-C-G fault near STR B024/552. 1809 Drum-Grass Valley-Weimar 60kV line (Drum to Shady Glen JCT section manually tested OK restoring Shady Glen, Bonnie Nook and Cape Horn. Estimated return 02/28/23. 3/1/23, T-line patrol reports Tree on conductor at the following structures: B21/467, B22/493, B22/502, B23/514, B23/518, B23/530 wire down between structure B23/531 & B23/532. 3/4/23, 1555 Drum-Grass Valley-Weimar 60kV line (Grass Valley to Rollins JCT section) returned to service after crew removed tree from structures B21/467, B22/493, B22/502, B23/514, B23/518, B23/530 and repaired down conductor between structures B23/531 and B23/532. | NONE | NORTH VALLEY AND SIERRA | INT-17004 | 2202 | 2202 | 1716 | 0.00038799 | 0.00030236 | 0.77929 | 5675418 | A-B-C-G | B024/552 | AUTO | Single Mode | Tier 3 | Nevada | Sierra | 39.1919 | -121.0125 | Drum-Grass Valley-Weimar 60kV line CONDs at STRs B021/467, B022/493, B022/502, B023/514, B023/518, B023/530, B023/531 & B023/532 | Storm | 397.5 AAC | Lat: 39.19188, Long: -121.01248 | SN=440;SE=514;WN=666;WE=711
Tier 3 |  | NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | ETL.6480 | 60039 | COLGATE-CHALLENGE | 2023 | 2023-02-28 07:48 | 44985.325 | YES | YES | YES | 1900-01-01 10:29 | 3509 | 2023-03-02 18:17 | 44987.7618 | F | Tree | Tree-failure | COND | Relayed - 2/28/23, 0748 Colgate-Challenge 60kV line relayed and did not test due to automatic reclosing disabled for wildfire mitigation. 0750 Line manually tested NG. 0751 Colgate to Dobbins section manually tested OK. SUS Challenge(CESO=576;CMIN=554,224)and Dobbins(CESO=923;CMIN=17,537). Weather storm. Line is in a tier 2/3 HFTD/HFRA. Protection reports A-C fault near 005/104. 3/2/23, 1817 Colgate-Challenge 60kV line manually tested OK. D.O. given OK to restore customers at Challenge. Work completed by T-line: Repaired slack conductor at poles 5/104, 5/105 and 5/106, (2) phases of downed conductor at poles 005/099 to 005/101 and (8) spans of conductor with trees on line between structures 005/101 to 006/111. | NONE | NORTH VALLEY AND SIERRA | INT-17011 | 1499 | 1499 | 571761 | 0.00026412 | 0.10074 | 381.4283 | 5675418 | A-C | 005/104 | AUTO | Single Mode | Tier 3 | Yuba | Sierra | 39.3975 | -121.1671 | Colgate-Challenge 60kV line CONDs at STR 005/104, 005/105 and 005/106, 005/099 to 005/101 between structures 005/101 to 006/111 | Storm | 4/0 ACSR | Lat: 39.39753, Long: -121.16709 | SN=303;SE=340;WN=432;WE=454
Tier 3 |  | NORTH COAST | NORTH | 69 | 60 | ETL.7820 | 60181 | POTTER VALLEY-WILLITS | 2023 | 2023-02-28 07:57 | 44985.3313 | YES | YES | YES | 1900-01-01 05:20 | 3200 | 2023-03-02 13:17 | 44987.5535 | F | Tree | Tree-failure | COND | Relayed - 2/28/23, 0757 Potter Valley-Willits 60kV line relayed and did not test due to automatic reclosing disabled for wildfire mitigation. 0759 Line manually tested NG. No customer interruption. Weather storm. Line is in a tier 2/3 HFTD/HFRA. Protection reports A-C fault near STR 004/007. 3/2/23, 1317 Line returned to service after crew repaired repaired multiple spans of wire down between poles 5/9 and 6/0. | NONE | NORTH COAST | INT-17012 | 0 | 0 | 0 | 0 | 0 | 0 | 5675418 | A-C | 004/007 | AUTO | Single Mode | Tier 3 | Mendocino | Humboldt | 39.3848 | -123.2221 | Potter Valley-Willits 60kV line COND between poles 005/009 and 006/000 | Storm | 1/0 ACSR | Lat: 39.38483, Long: -123.22212 | SN=222;SE=245;WN=287;WE=303
Tier 3 |  | NORTH COAST | NORTH | 69 | 60 | ETL.6220 | 60010 | BRIDGEVILLE-GARBERVILLE | 2023 | 2023-02-28 11:24 | 44985.475 | YES | YES | YES | 1899-12-31 04:52 | 1732 | 2023-03-01 16:16 | 44986.6778 | F | Equipment Failure | Equip Fail-conductor | NONE | Relayed - 2/28/23, 1124 Bridgeville-Garberville 60kV line relayed and did not test due to automatic reclosing disabled for wildfire mitigation. 1126 Line tested NG. 1128 Bridgeville to Fort Seward section manually tested OK. 1129 Garberville to Fort Seward section manually tested NG. 1130 Fort Seward 60kV tap isolated. 1130 Garberville to Fort Seward JCT manually tested NG. SUS Fort Seward(CESO=335;CMIN=580,220). MOM Fruitland(1,143). Weather storm. Line is in a tier 2/3 HFTD/HFRA. Protection reports B-C fault near STR 026/003. 1544 Bridgeville to Fort Seward JCT section forced out of service to test Fort Seward 60kV tap with CB. 1548 Bridgeville to Fort Seward section manually tested OK, restoring transmission service to Fort Seward. Momentary interruption to Fruitland. Estimated return 03/01/23. 3/1/23, 1616 Bridgeville-Garberville 60kV line (Fort Seward JCT to Garberville section) returned to service after crew spliced one phase of conductor between structures 025/002 and 025/004. | NONE | NORTH COAST | INT-17019 | 1478 | 1732 | 580220 | 0.00030518 | 0.10223 | 335 | 5675418 | B-C | 026/003 | AUTO | Single Mode | Non-HFTD | Humboldt | Humboldt | 40.199 | -123.7078 | Bridgeville-Garberville 60kV line COND between STRs 025/002 and 025/004. | Storm | 4/0 ACSR | Lat: 40.19899, Long: -123.70786 | SN=303;SE=340;WN=432;WE=454
Tier 3 |  | NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | ETL.6760 | 60070 | DRUM-GRASS VALLEY-WEIMAR | 2023 | 2023-02-28 12:40 | 44985.5278 | YES | YES | YES | 1900-01-02 06:29 | 4709 | 2023-03-03 19:09 | 44988.7979 | C | Tree | Tree-failure | COND | Relayed - 2/28/23, 1240 Drum-Grass Valley-Weimar 60kV line (Drum to Shady Glen section) relayed and did not test due to automatic reclosing disabled for wildfire mitigation. 1257 Drum to Cape Horn section manually tested NG. SUS Shady Glen(CESO=2,852;CMIN=82,708), Bonnie Nook(CESO=895;CMIN=22,375) and Cape Horn(1). Weather storm. Line is in a tier 2/3 HFTD/HFRA. 1305 Drum to Bonnie Nook section manually tested OK, restoring Bonnie Nook. 1309 Weimar to Shady Glen to Cape Horn JCT section manually tested OK, restoring Shady Glen. 1312 Cape Horn restored. Estimated return Bonnie Nook to Cape Horn JCT section 03/01/23. 3/3/23, 1909 Drum-Grass Valley-Weimar 60kV line (Bonnie Nook to Cape Horn section) returned to service after crew replaced NG pole 12/279, repaired one phase of downed conductor between poles 11/265 & 11/266, repaired one phase of downed conductor at pole 11/265, one phase of downed conductor at pole 13/298 and removed tree from line at pole 7/175. | NONE | NORTH VALLEY AND SIERRA | INT-17030-2 | 3747 | 3747 | 105083 | 0.00066022 | 0.018515 | 28.0446 | 5675418 | A-C | 012/294 | AUTO | Single Mode | Tier 3 | Placer | Sierra | 39.1511 | -120.8988 | Drum-Grass Valley-Weimar 60kV line COND between poles 011/265 & 011/266, 011/265, 013/298, 007/175 | Storm | 2/0 CU | Lat: 39.15110, Long: -120.89881 | SN=310;SE=350;WN=415;WE=443
Tier 3 |  | NORTH VALLEY AND SIERRA | NORTH | 115 | 115 | ETL.4393 | 10459 | DRUM-HIGGINS | 2023 | 2023-02-28 15:47 | 44985.6576 | YES | YES | YES | 1900-01-02 18:17 | 5417 | 2023-03-04 10:04 | 44989.4194 | C | Tree | Tree-failure | COND | Relayed - 2/28/23, 1547 Drum-Higgins 115kV line relayed and did not test due to automatic reclosing disabled for wildfire mitigation. 1550 Line tested NG. SUS Dutch Flat #1 PH (offline), Dutch Flat #2 PH (offline) and Chicago Park PH (offline). Weather storm. Line is in a tier 2/3 HFTD/HFRA. Protection reports A-B fault near STR 008/081. 3/4/23, 1004 Drum-Higgins 115kV line de-energized during restoration switching to close Dutch Flat #1 JCT 119 and Chicago Park JCT 137 dead. Sustained interruption to Dutch Flat #1 PH (offline), Dutch Flat #2 PH (offline) and Chicago Park PH (offline). 1053 Dutch Flat #1 JCT to Chicago Park JCT section manually tested OK after crew repaired 2 phases of down conductor between towers 7/72 and 7/73 and 1 phase of down conductor between towers 8/78 and 8/80, restoring Dutch Flat #1 PH (offline), Dutch Flat #2 PH (offline) and Chicago Park PH (offline). 1056 Drum-Higgins 115kV line (Dutch Flat #1 JCT to Chicago Park JCT section) returned to service. | NONE | NORTH VALLEY AND SIERRA | INT-17033 | 0 | 0 | 0 | 0 | 0 | 0 | 5675418 | A-B | 008/081 | AUTO | Single Mode | Tier 3 | Placer | Sierra | 39.1897 | -120.8598 | Drum-Higgins 115kV line COND between STRs 007/072 and 007/073 and COND between STRs 008/078 and 008/080 | Storm | 397.5 ACSR | Lat: 39.18972, Long: -120.85975 | SN=538;SE=602;WN=712;WE=757
Tier 3 |  | NORTH VALLEY AND SIERRA | NORTH | 115 | 115 | ETL.1540 | 10068 | EL DORADO-MISSOURI FLAT #2 | 2023 | 2023-02-28 19:23 | 44985.8076 | YES | YES | YES | 1899-12-31 21:34 | 2734 | 2023-03-02 16:57 | 44987.7063 | F | Unknown | Unk-no patrol conducted | NONE | Relayed - 2/28/23, 1923 El Dorado-Missouri Flat #2-115kV line relayed and did not test due to automatic reclosing disabled for wildfire mitigation. 1928 Line manually tested NG. MOM Apple Hill(1,503) and Placerville(7,866). Weather storm. Line is in a tier 2/3 HFTD/HFRA. 2116 Line manually tested NG. Protection reports A-C fault near STR 003/024. 3/2/23, 1646 El Dorado-Missouri Flat #2-115kV line (Missouri Flat to Apple Hill JCT section) forced out of service to close Apple Hill JCT SW 329 dead. No customer interruption. 1650 Line manually tested OK after crew repaired wire down between tower 2/18 and 2/17. 1652 Line returned to service. 1657 Line restored normal. From trouble on 02/28/23 at 1923. | NONE | NORTH VALLEY AND SIERRA | INT-17038 | 9369 | 0 | 0 | 0 | 0 | 0 | 5675418 | B-C | 003/024 | AUTO | Single Mode | Tier 3 | El Dorado | Sierra | 38.7724 | -120.6526 | El Dorado-Missouri Flat #2-115kV line COND between 002/018 and 002/017 | Storm | 3/0 CU | Lat: 38.77237, Long: -120.65261 | SN=325;SE=377;WN=482;WE=515
Tier 2 |  | SOUTH BAY AND CENTRAL COAST | CENTRAL | 69 | 60 | ETL.6710 | 60064 | DEL MONTE-VIEJO | 2023 | 2023-03-09 18:46 | 44994.7819 | YES | YES | YES | 1899-12-31 07:11 | 1871 | 2023-03-11 01:57 | 44996.0813 | F | Tree | Tree-failure | STRU | Relayed - 3/9/23, 1846 Del Monte-Viejo 60kV line relayed and did not test due to automatic reclosing disabled for wildfire mitigation. SUS Navy Lab(1), Hatton(CESO=2,149;CMIN=147,356), Viejo(CESO=3,803;CMIN=7,165,770). Weather storm. Line is in a tier 2/3 HFTD/HFRA. Protection reports A-B-C fault near STR 005/129. 1857 Del Monte to Navy lab section manually tested OK, restoring transmission service to Navy Lab. 1930 Viejo to Hatton section manually tested NG. 1934 Del Monte to Navy Lab section forced out of service to closed Hatton SW 57 dead. 1939 Del Monte to Navy Lab section energized. MOM Navy Lab. 1940 Transmission service to Hatton restored. Estimated return for Viejo to Hatton section 03/10/23. 2146 Del Monte-Viejo 60kV line (Del Monte to Hatton section) relayed and did not test due to automatic reclosing disabled for wildfire mitigation. 2150 Del Monte to Hatton section manually tested OK. Momentary to Navy Lab and Hatton. Weather storm. Line is in a tier 2/3 HFTD/HFRA. 2202 Del Monte-Viejo 60kV line (Del Monte to Hatton section) relayed and did not test due to automatic reclosing disabled for wildfire mitigation. 2203 Del Monte to Hatton section manually tested OK. Momentary to Navy Lab and Hatton. Weather storm. Line is in a tier 2/3 HFTD/HFRA. 2321 Del Monte-Viejo (Del Monte to Hatton section) forced out of service to secure loose guy wires at pole 0/10. Sustained interruption to Navy Lab and Hatton. 2353 Del Monte to Hatton section returned to service restoring Navy Lab and Hatton after crew cut pole 0/10 guy wires in the clear. 3/11/23, 0157 Del Monte-Viejo 60kV line, (Del Monte to Hatton section) forced out of service to close Hatton SW 59 dead. 0200 Line manually tested OK after crew repaired downed conductor between poles 5/136 & 5/137. Momentary interruption to Navy Lab and Hatton. 0357 Line returned normal restoring transmission service to Viejo. From trouble on 03/09/23 at 1846. | NONE | SOUTH BAY AND CENTRAL COAST | INT-17092 | 5952 | 5952 | 7313126 | 0.0010487 | 1.2886 | 1228.6838 | 5675418 | A-B-C | 005/129 | AUTO | Single Mode | Tier 2 | Monterey | Central Coast | 36.5617 | -121.9114 | Del Monte-Viejo 60kV line COND between STRs 005/136, 005/137 | Storm | 397.5 AAC | Lat: 36.56174, Long: -121.91139 | SN=488;SE=554;WN=666;WE=711
Tier 2 |  | NORTH COAST | NORTH | 69 | 60 | ETL.8170 | 60217 | TRINITY-MAPLE CREEK | 2023 | 2023-03-09 20:41 | 44994.8618 | YES | YES | YES | 1899-12-31 20:55 | 2695 | 2023-03-11 17:36 | 44996.7333 | F | Tree | Tree-failure | HDWR | Relayed - 3/9/23, 2041 Trinity-Maple Creek 60kV line relayed and did not test due to automatic reclosing disabled for wildfire mitigation. On the trouble Hyampom 60kV tap de-energized. MOM Big Bar, Grouse Creek, Big Creek, Hyampom and Ridge Cabin. Weather storm. Line is in tier 2/3 HFTD/HFRA. 2045 Line manually tested NG. 2048 Big Bar JCT to Maple Creek section manually tested OK, restoring Big Bar and Ridge Cabin. 2050 Hyampom 60kV tap energized, restoring Grouse Creek, Big Creek and Hyampom. Estimated return for Trinity to Big Bar JCT section 03/10/23. 3/11/23, 1736 Trinity-Maple Creek 60kV line (Trinity to Big Bar JCT section) manually tested OK after crew replaced three phases of NG conductor and removed downed tree between poles 1/10, 1/11 and reframed pole 1/11. From trouble on 03/09/23 at 2041. | NONE | NORTH COAST | INT-17096 | 0 | 0 | 0 | 0 | 0 | 0 | 5675418 | A-C | 001/010 | AUTO | Single Mode | Tier 2 | Trinity | Humboldt | 40.7287 | -122.9583 | Trinity-Maple Creek 60kV line COND between poles 001/010, 001/011 | Storm | 4/0 ACSR | Lat: 40.72866, Long: -122.95825 | SN=303;SE=340;WN=432;WE=454
Tier 2 |  | NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | ETL.7640 | 60161 | MTN GATE JCT-CASCADE | 2023 | 2023-03-09 21:01 | 44994.8757 | YES | YES | YES | 0.81458 | 1173 | 2023-03-10 16:34 | 44995.6903 | F | Equipment Failure | Equip Fail-conductor | NONE | Relayed - 3/9/23, 2101 Mountain Gate JCT-Cascade 60kV line relayed and did not test due to automatic reclosing disabled for wildfire mitigation. On the trouble, Keswick CB 22 and Deschutes CB 12 tripped out of section Delta-Mountain Gate JCT 60kV line de-energized. SUS Mountain Gate(1) and Antler(CESO=879;CMIN=1,208,625). Weather storm. Line is in a tier 2/3 HFTD/HFRA. Protection reports A-C fault near STR 001/010. 2102 Keswick CB 22 closed via automatics. 2102 Deschutes CB 12 closed via automatics. 2110 Line manually tested NG. No estimated return. 3/10/23, 1634 Mountain Gate JCT-Cascade 60kV line manually tested OK restoring transmission service to Mountain Gate after crew repaired center phase wire down between structures 000/001 and 015/187. 1637 Delta-Mountain Gate JCT 60kV line energized restoring transmission service to Antler. From trouble on 03/09/23 at 2101. Burn spots found mid span but no clear vegetation contact. | NONE | NORTH VALLEY AND SIERRA | INT-17098-1 | 879 | 879 | 1208625 | 0.00015488 | 0.21296 | 1375 | 5675418 | A-C | 001/010 | AUTO | Dependent Mode-initiating | Tier 2 | Shasta | North Valley | 40.7442 | -122.3084 | Mountain Gate JCT-Cascade 60kV line COND between STRs 000/001 and 015/187 | Storm | 4/0 AAC | Lat: 40.74416, Long: -122.30840 | SN=297;SE=345;WN=443;WE=473
Tier 2 |  | NORTH COAST | NORTH | 69 | 60 | ETL.7850 | 60184 | RIO DELL JCT-BRIDGEVILLE | 2023 | 2023-03-14 18:08 | 44999.7556 | YES | YES | YES | 0.95694 | 1378 | 2023-03-15 17:06 | 45000.7125 | F | Tree | Tree-failure | COND | Relayed - 3/14/23, 1808 Rio Dell JCT-Bridgeville 60kV line relayed and did not test due to automatic reclosing disabled for wildfire mitigation. 1810 Bridgeville to Carlotta section manually tested NG. 1813 Rio Dell JCT to Carlotta section manually tested OK. MOM Carlotta(1,129) and Humboldt Redwood at Carlotta(1). Weather storm. Line is in tier 2/3 HFTD/HFRA. Protection reports B-G fault near STR 036/001. Estimated return 03/15/23. 3/15/23, 1706 Rio Dell JCT-Bridgeville 60kV line (Bridgeville to Carlotta section) returned to service after crew spliced conductor at poles 36/0 and 35/11. From trouble on 03/14/23 at 1808. | NONE | NORTH COAST | INT-17145 | 1129 | 0 | 0 | 0 | 0 | 0 | 5675418 | B-G | 036/001 | AUTO | Single Mode | Tier 2 | Humboldt | Humboldt | 40.4655 | -123.8585 | Rio Dell JCT-Bridgeville 60kV line COND STRs 036/000 and 035/011 | Storm | 4/0 AAC | Lat: 40.46546, Long: -123.85851 | SN=297;SE=345;WN=443;WE=473
Tier 3 |  | SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 60 | ETL.6230 | 60011 | BURNS-LONE STAR #1 | 2023 | 2023-03-21 12:39 | 45006.5271 | YES | YES | YES | 1900-01-03 10:59 | 6419 | 2023-03-25 23:38 | 45010.9847 | C | Tree | Tree-tree contact | COND | Relayed - 3/21/23, 1239 Burns-Lone Star #1-60kV line relayed and did not test. SUS Point Moretti(CESO=174;CMIN=1,066,910), Crusher(1) and CEMEX(1). Weather storm. Line is in a tier 2/3 HFTD/HFRA. Protection reports B-C fault near STR 013/106. 1243 Line manually tested NG. Estimated return 03/22/23. 3/25/23, 2338 Burns-Lone Star #1 line returned to service after crews repair one phase of downed conductor between poles 000/003 and 000/004 and replace NG insulator at pole 000/003. | NONE | SOUTH BAY AND CENTRAL COAST | INT-17172 | 174 | 174 | 1066910 | 3.0659e-05 | 0.18799 | 6131.6667 | 5675418 | B-C | 013/106 | AUTO | Single Mode | Tier 3 | Santa Cruz | Central Coast | 37.094 | -122.1445 | Burns-Lonestar #1 STRs 000/003, 000/004 | Rain | 4/0 AAC | Lat: 37.09399, Long: -122.14446 | SN=328;SE=372;WN=443;WE=473
Tier 3 |  | SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 60 | ETL.7590 | 60156 | MONTA VISTA-BURNS | 2023 | 2023-03-21 13:05 | 45006.5451 | YES | YES | YES | 1900-01-02 08:40 | 4840 | 2023-03-24 21:45 | 45009.9062 | C | Tree | Tree-tree contact | STRU | Relayed - 3/21/23, 1305 Monta Vista-Burns 60kV line relayed and did not test. On the trouble, Burns 60kV bus and Burns-Lone Star #2-60kV line de-energized. SUS Big Basin(CESO=4,072;CMIN=) and Burns(CESO=35;CMIN=). Weather storm. Line is in a tier 2/3 HFTD/HFRA. Protection reports A-B-C fault near STR 008/067. 1311 Monta Vista to Big Basin section manually tested NG. Estimated return 03/22/23. 3/24/23, 2145 Monta Vista-Burns 60kV line returned to service restoring transmission service to Big Basin after crew replaced NG conductors and hardware between structures 8/69, 8/70 and 8/71. From trouble on 03/21/23 at 1305. 3/25/23, 2331 Burns 60kV bus returned to service restoring transmission service to Burns. 2333 Burns-Lone Star #2-60kV line returned to service. | NONE | SOUTH BAY AND CENTRAL COAST | INT-17172-4 | 4072 | 4072 | 19708480 | 0.00071748 | 3.4726 | 4840 | 5675418 | A-B-C | 008/067 | AUTO | Dependent Mode-initiating | Tier 3 | Santa Cruz | Central Coast | 37.213 | -122.1503 | Monta Vista-Burns 60kV line CONDs, STRs, HDWR 008/069, 008/070 and 008/071 | Storm | 397.5 AAC | Lat: 37.21301, Long: -122.15027 | SN=488;SE=554;WN=666;WE=711
8.0917 |  |  | HFTD Miles: 5437.7

## List of MEDs from Reliability
IEEE-1366 TMED Days
No Planned Outage Classification | [7 empty] | Planned Outage Classification Available
[8 empty] | MED Threshold | 5.033 | MED Threshold
1988 | 1989 | 1990 | 1991 | 1992 | 1993 | 1994 | 1995 |  | 2023
227 | 302 | 216 | 302 | 105 | 101 | 216 | 104 |  | 104
228 | 406 | 217 | 303 | 215 | 113 | 217 | 106 |  | 105
717 | 808 | 218 | 304 | 1029 | 114 | 815 | 107 |  | 107
1113 | 916 | 422 | 325 | 1121 | 121 | 928 | 108 |  | 108
1214 | 1017 | 423 | 1020 | 1206 | 219 | 1004 | 109 |  | 109
1215 | 1018 | 520 | 1025 | 1228 | 1111 | 1015 | 110 |  | 110
1220 | 1023 | 922 | 1026 | 1231 | 1114 | 1109 | 308 |  | 114
1222 |  | 1125 | 1129 |  | 1211 | 1214 | 309 |  | 116
1224 |  |  | 1227 |  |  |  | 310 |  | 219
[7 empty] | 311 |  | 221
[7 empty] | 314 |  | 223
[7 empty] | 322 |  | 224
[7 empty] | 323 |  | 225
[7 empty] | 716 |  | 226
[7 empty] | 717 |  | 227
[7 empty] | 1004 |  | 228
[7 empty] | 1210 |  | 309
[7 empty] | 1211 |  | 314
[7 empty] | 1212 |  | 321
1213
1214
1220
9 | 7 | 8 | 9 | 7 | 8 | 8 | 22
19

## Cause Translation
PG&E Outage Cause Category-Details | ISO Outage Primary Cause Code | ISO Outage Primary Cause Code Description | PG&E and ISO Outage Secondary Cause Code | ISO Outage Secondary Cause Code Description |  | Cause Category (10 categories) | Cause Details | Outage Mode
Animal-bird | ANIM | Animal Contact | ARRS | Arrestor | 1 | Animal | Animal-bird | Common Mode
Animal-ground | ANIM | Animal Contact | AUX | Station auxiliary equip (e.g., CT, PT, CCVT) | 2 | Contamination | Animal-ground | Common Mode-initiating
Contamination-agriculture | CNTM | Contamination | BATT | Battery system | 3 | Disaster | Cntmn-agriculture | Dependent Mode
Contamination-animal waste | CNTM | Contamination | BUSH | Bushing | 4 | Equipment Failure | Cntmn-animal waste | Dependent Mode-initiating
Contamination-environmental | CNTM | Contamination | CB | Circuit breaker/Circuit switch | 5 | External Contact | Cntmn-environmental | Emergency Forced Outage
Contamination-industrial waste | CNTM | Contamination | COMM | Communication facility (no relay) | 6 | Other | Cntmn-industrial waste | Scheduled Outage
Disaster-earthquake | ND | Natural Disaster | COND | Conductor/shield wire/splice | 7 | Tree | Disaster-earthquake | Single Mode
Disaster-fire | FIRE | Fire | DISC | Disconnect | 8 | Unknown | Disaster-fire
Disaster-flood | ND | Natural Disaster | ENCR | Encroachment | 9 | Weather | Disaster-flood
Disaster-other | ND | Natural Disaster | GUYS | Guy/anchor | 10 | Work Procedure Error | Disaster-other
Equipment Failure-arrestor | SEQP | Substation Equipment Problem | HDWR | Hardware, fittings, accessories |  |  | Equip Fail-arrestor
Equipment Failure-bus | SEQP | Substation Equipment Problem | INSL | Insulator (station/line) |  |  | Equip Fail-bus
Equipment Failure-bushing | SEQP | Substation Equipment Problem | LS | Line switch |  |  | Equip Fail-bushing
Equipment Failure-ccvt | SEQP | Substation Equipment Problem | NONE | None |  |  | Equip Fail-ccvt
Equipment Failure-circuit breaker | CB | Circuit Breaker Trouble | REAC | Reactive device (e.g., capacitors, condenser) |  |  | Equip Fail-circuit breaker
Equipment Failure-conductor | LEQP | Line Equipment Problem | REG | Regulator |  |  | Equip Fail-conductor
Equipment Failure-connector/hardware | LEQP | Line Equipment Problem | RELY | Relay/communicatons for relay |  |  | Equip Fail-connector/ hardware
Equipment Failure-CT | SEQP | Substation Equipment Problem | STRU | Structure/foundation |  |  | Equip Fail-CT
Equipment Failure-insulator-line | LEQP | Line Equipment Problem | XFRM | dre56] |  |  | Equip Fail-insulator-line
Equipment Failure-insulator-station | SEQP | Substation Equipment Problem | UG | Underground transmission component |  |  | Equip Fail-insulator-station
Equipment Failure-other-line | LEQP | Line Equipment Problem | PROC | Work Procedure/Human Error |  |  | Equip Fail-other-line
Equipment Failure-other-station | SEQP | Substation Equipment Problem | PSPS | Public Safety Power Shutoff |  |  | Equip Fail-other-station
Equipment Failure-PT | SEQP | Substation Equipment Problem |  |  |  |  | Equip Fail-PT
Equipment Failure-reactive equipment | SEQP | Substation Equipment Problem |  |  |  |  | Equip Fail-reactive equipment
Equipment Failure-regulator/LTC | SEQP | Substation Equipment Problem |  |  |  |  | Equip Fail-regulator/ LTC
Equipment Failure-relay | PROT | Protection |  |  |  |  | Equip Fail-relay
Equipment Failure-structure-line | LEQP | Line Equipment Problem |  |  |  |  | Equip Fail-structure-line
Equipment Failure-structure-station | SEQP | Substation Equipment Problem |  |  |  |  | Equip Fail-structure-station
Equipment Failure-switch-line | LEQP | Line Equipment Problem |  |  |  |  | Equip Fail-switch-line
Equipment Failure-switch-station | SEQP | Substation Equipment Problem |  |  |  |  | Equip Fail-switch-station
Equipment Failure-transformer | SEQP | Substation Equipment Problem |  |  |  |  | Equip Fail-transformer
External Contact-aircraft | AIR | Aircraft |  |  |  |  | Ext Cont-aircraft
External Contact-car pole | VEH | Vehicle Contact |  |  |  |  | Ext Cont-car pole
External Contact-foreign object | OTHR | Other |  |  |  |  | Ext Cont-foreign object
External Contact-system disturbance | DIST | System Disturbance |  |  |  |  | Ext Cont-system disturbance
External Contact-vandalism | OTHR | Other |  |  |  |  | Ext Cont-vandalism
Other-customer/IPP caused | OTHR | Other |  |  |  |  | Other-customer/ IPP caused
Other-distribution caused | UC | Utility Contact |  |  |  |  | Other-distribution caused
Other-generation caused | GEN | Generation Trouble |  |  |  |  | Other-generation caused
Other-overload situation | DIST | System Disturbance |  |  |  |  | Other-load control
Other-safety clearance | OTHR | Other |  |  |  |  | Other-safety clearance
Scheduled-approved | SCHD | Scheduled Outage |  |  |  |  | Other-scheduled-approved
Scheduled-disapproved | LATE | Late Notification |  |  |  |  | Other-scheduled-disapproved
Scheduled-extended | LATE | Late Notification |  |  |  |  | Other-scheduled-extended
Tree-3rd party | OTHR | Other |  |  |  |  | Tree-3rd party
Tree-failure | VEGA | Vegetation |  |  |  |  | Tree-failure
Tree-tree contact | VEGA | Vegetation |  |  |  |  | Tree-tree contact
Unknown-no patrol conducted | UNKN | Unknown |  |  |  |  | Unk-no patrol conducted
Unknown-patrol found nothing | UNKN | Unknown |  |  |  |  | Unk-patrol found nothing
Weather-lightning | LIGT | Lightning |  |  |  |  | Weather-lightning
Weather-rain | WEAT | Weather |  |  |  |  | Weather-rain
Weather-snow/ice | WEAT | Weather |  |  |  |  | Weather-snow/ ice
Weather-wind | WEAT | Weather |  |  |  |  | Weather-wind
Work Procedure-design error | OPER | Operating error |  |  |  |  | Work Procedure-design error
Work Procedure-equipment incorrectly set | OPER | Operating error |  |  |  |  | Work Procedure-equip incorrectly set
Work Procedure-inattention or carelessness | OPER | Operating error |  |  |  |  | Work Procedure-inattention or carelessness
Work Procedure-miscommunications or unclear expectations | OPER | Operating error |  |  |  |  | Work Procedure-miscommunications or unclear expectations
Work Procedure-not following prescribed procedures | OPER | Operating error |  |  |  |  | Work Procedure-not following prescribed procedures
SGS CAUSE CODE CATEGORIES
Description | SGS Category No | Examples
Equipment | 1 | Terminal equipment: breakers, switches, transformers, cap bks, busses, etc. ("inside the fence")
System Protection | 2 | Relay equipment failure, misoperation, incorrect settings or scheme, "over-reaching", communications
Lines | 3 | Failed hardware "outside the fence"; structures, conductors, cable cable hardware, insulators, static wire
Weather, other than lightning | 4 | Severe weather conditions, usually beyond design capabilities of facilities, exclusive of lightning
Lightning Only | 5 | Verified or suspected outages resulting from lightning
Unknown | 6 | Diligent attempts to verify cause were unsuccessful
Vegetation | 7 | Vegetation and trees which directly cause an outage
External | 8 | Causes outside control of ET system (e.g., foreign utilities, customer equip, generation, UF, instability)
Other | 9 | Operating errors, contractors, dig-ins, loggers, birds, animals, public damage, contamination, autos
Excludable Outage, Natural Causes Only | 10 | Major events (extreme), system disturbances associated w/ cascading
Excludable Outage, System Causes Only | 11 | Operational Outage for safety, voltage control or stability, System Disturbances, Unusual Configurations
Human Factors | 12 | WPE/ HPE

## ILIS Causes
Basic Cause Field | Supplemental Cause Field | [13 empty] | Equipment Condition
3rd Party* 00 | Aircraft | Aircraft-Crop Dusting | Contact with High Voltage, 3rd Party | Customer Equipment | Dig In, 3rd Party | Fire, house or bldg | Gun Shot | Kite | Metallic Balloon | Thrown Object | Vandalism | Vehicle | Other | tree - cutting 3rd party | Annealed
Animal* 02 | Bird Found | Other | Squirrel | [11 empty] | Arcing
Company Initiated* 05 | Construction Activity/equip, company | Contact with High Voltage, company | Coordination Failure | Dig in, company | Improper Construction | Insulator washing | Operating error | Other Circuits | Personnel, company | Planned, capital | Planned, customer | Planned, maintenance | Rotating Outage | Return circuit normal | Bent or Twisted
Equipment Failure/Involved* 03 | Electrical Overload | Fire, pole | overhead | Substation | underground | [9 empty] | Blown / exploded
Vegatation* 01 | Other Ground Vegetation | Tree - bark fell into line | Tree - branch fell on line | Tree - cutting PG&E contractor | Tree - fell into line | Tree - grew into line | Tree - palm frond fell into line | [7 empty] | Broken
Unknown 04 | Patrol - Found Nothing | Patrol - Not Conducted | [12 empty] | Broken, wire on ground
(Environmental)External influence * 06 | Earthquake | Fire, forest/grass | Flood/ errosion | Ice or snow | Lightning | water | [8 empty] | Burned Open
Burned / flashed
* These type outages require "Equipment Involved" & "Equipment Condition" field be populated. See available selection below | [14 empty] | Contaminated
Deteriorated
Equipment Involved | Anchor or Guy | Booster | Bus | Bushing | PT/CCVT | CT/PT | Capacitor | Circuit Breaker | Conductor, Overhead | Conductor, Underground | Connector or Splice (OH) | Connector or Splice (UG) | Crossarm, Steel |  | Leaking
See also next tabs | Crossarm, Wood | Customer Equipment | Cutout, Fused, Distribution | Cutout fuse holder | Elbow | Footings, Tower or Pole | Fuse | Insulator | Interrupter | Jumper | Lightning Arrestor | Manhole, primary box | Metering Equipment |  | Malfunctioning
| Other | PGs, Kearneys | Pole - Tower, steel | Pole - Wood | Pothead or Cable Termination | Reactive Equipment | Recloser | Regulator | Regulator, LTC substation | Relay, substation | Riser | Secondary | Sectionalizer |  | Normal
| Service Conductor | Splice Box | Stepdown | Street Light Equipment | Switch | Transformer | Transformer, Station Bank, Power | Woodpin | Generator | SCADA |  |  |  |  | Together
Equipment Condition | Annealed | Arcing | Bent or Twisted | Blown / exploded | Broken | Broken, wire on ground | Burned Open | Burned / flashed | Contaminated | Deteriorated | Leaking | Malfunctioning | Normal
see also next tabs | On Ground | Together |  |  |  | Broken, wire on object
Outage Level | Distribution Circuit | Substation Distribution | Substation Transmission | Transmission Line | Transformer Only | Generation | secondary | service
[7 empty] | FAS only | FAS only