## Slide 1: Selective Overview of R&D to Improve Energy Simulation
Philip Haves
LBNL
CPUC Workshop: Energy Modeling Tools and their Applications in Energy Efficiency
September 18, 2015

## Slide 2
Improve the Reliability of Energy Simulation in Use:
Practitioners: design and operation
Policy and program support – e.g. DEER
Requires:
Accurate, explicit modeling of low energy and conventional buildings and systems
Characterizing and estimating the effects of uncertainty → manage risk of investing in energy efficiency
Goal

## Slide 3: Challenge
Sources of differences:
Uncertainty:
  model algorithms
  input parameters
  modeler decisions
Variability:
  weather
  occupancy
  operation – controls, O&M
Minimize, then quantify
Source: Energy performance of LEED-NC buildings, NBI, 2008
as-built vs. as-designed issue for low-energy buildings

## Slide 4: Goals of Current Research
Validation:
Enable substantial improvements in the energy performance of new construction and major retrofits by increasing the accuracy and credibility of all energy simulation tools.
Uncertainty:
Facilitate the management of risk associated with the procurement of high performance buildings by characterizing the uncertainty of energy performance predictions.

## Slide 5: Doesn’t BESTEST Validate Energy Calculations?
ASHRAE Standard 140 Method of Test for Evaluation of Building Energy Analysis Computer Programs is based on IEA BESTEST procedures:
Standard 140 tests & partially validates energy calculations
  Analytical tests – idealized cases → partial validation
  Comparative tests - no ‘ground truth’
The Standard 140 framework accommodates empirical tests but does not (yet) include any
We now have facilities to make cost-effective empirical testing possible:
  LBNL FLEXLAB
  ORNL FRP
  NREL HVAC

## Slide 6: Model algorithm validation – new DOE project
Generate sets of measured data for simulation model validation:
  Set priorities based on Validation Roadmap and input from TAG
  Conventional systems (↔ existing Standard 140 cases)
  Low energy systems
  Control of multi-zone systems
  HVAC performance maps
  EnergyPlus and commercial programs

## Slide 7: Experimental Facilities - LBNL
LBNL: FLEXLAB
4 matched pairs of 20’x30’ test cells
1 pair of cells rotates
Reconfigurable south façade
Radiant slab and panels

## Slide 8: Experimental Facilities – NREL and ORNL
NREL: HVAC test facility
Performance maps of HVAC components ≤ 10 tons
Uncertainty < 5%
ORNL: Flexible Research Platforms (FRP)
Two buildings:
  Two story, 5 zones per floor
  Single story, large zone

## Slide 9: Uncertainty characterization – DOE
Implement a framework for estimating the uncertainty of simulation results:
Georgia Tech – funded by NSF: probability distributions for 75 common/important input parameters:
  Insulation R-value per inch
  Luminaire power
  …
Develop a representation of ‘model form’ uncertainty driven by validation data
Extend the implementation of the input parameter uncertainty framework in OpenStudio
→ Simulation results: X±Y

## Slide 10: User Variability
Chart: Electric Consumption
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
1 | 1936.019 | 1782.557 | 2083.187 | 1935.305 | 2163.996 | 519.756 | 528.642 | 527.442 | 2168.08 | 2046.357 | 1885.173 | 1909.02
2 | 2595.63 | 2438.99 | 2860.8 | 2659.62 | 2920.64 | 3073.54 | 3037.77 | 3304.21 | 2932.81 | 2815.96 | 2581.9 | 2609.34
3 | 2235.12 | 2047.39 | 2394.31 | 2192.86 | 2423.72 | 2539.77 | 2418.99 | 2721.87 | 2387.36 | 2292.03 | 2151.35 | 2194.62
4 | 1974.186 | 1849.067 | 2207.83 | 2051.963 | 2355.651 | 2544.493 | 2457.864 | 2764.914 | 2370.747 | 2172.118 | 1956.181 | 1961.396
5 | 1464.805 | 1495.24 | 1800.924 | 1782.765 | 2210.581 | 2381.302 | 2297.611 | 2637.003 | 2276.069 | 2021.812 | 1601.814 | 1458.715
6 | 2176.684 | 2149.283 | 2636.623 | 2568.332 | 3175.477 | 3504.928 | 3359.266 | 3821.413 | 3260.302 | 2853.971 | 2281.537 | 2166.933
7 | 1843.713 | 1818.011 | 2199.562 | 2049.304 | 2455.615 | 2621.128 | 2503.802 | 2853.354 | 2438.488 | 2260.581 | 1924.171 | 1837.086
8 | 1935.32 | 1761.14 | 2053.96 | 1878.23 | 2121.92 | 2258.6 | 2220.61 | 2466.88 | 2107.77 | 1970.67 | 1846.08 | 1890.33
9 | 3002.283 | 2974.937 | 3580.65 | 3374.785 | 4094.489 | 4378.325 | 4227.782 | 4769.8 | 4075.676 | 3727.666 | 3141.69 | 2991.927
10 | 1629.117 | 1506.386 | 1785.292 | 1709.787 | 2024.722 | 2281.674 | 2274.05 | 2563.473 | 2161.247 | 1823.449 | 1597.735 | 1602.119
11 | 1973.791 | 1865.754 | 2247.725 | 2017.87 | 2299.607 | 2438.92 | 2386.515 | 2711.177 | 2289.291 | 2159.648 | 1968.354 | 1960.15
12 | 1992.697 | 2026.992 | 2417.808 | 2399.958 | 2984.824 | 3211.321 | 3118.556 | 3488.544 | 3024.447 | 2680.614 | 2147.854 | 1982.771
Chart: Gas Consumption
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
1 | 2626.4 | 993.9 | 654.6 | 446.5 | 400.1 | 25.5 | 25.1 | 24.8 | 334.2 | 356.9 | 716.8 | 1688.3
2 | 19701 | 14501 | 13259 | 10367 | 7082 | 4168 | 3148 | 2750 | 3168 | 6722 | 13976 | 18466
3 | 3969 | 3606 | 4028 | 3852 | 3989 | 3858 | 3928 | 3969 | 3805 | 3944 | 3826 | 3956
4 | 3605.03 | 1705.77 | 1362.96 | 916.09 | 432.13 | 352.9 | 315.46 | 347.18 | 307.29 | 549.29 | 1649.65 | 3111.22
5 | 38655 | 32747 | 36873 | 28071 | 26192 | 22514 | 19254 | 21840 | 19703 | 26904 | 32922 | 37744
6 | 17841 | 14606 | 15632 | 12517 | 11081 | 9765 | 8023 | 9442 | 9001 | 11767 | 14602 | 16930
7 | 28703 | 24113 | 26753 | 20870 | 19404 | 16878 | 14302 | 16135 | 14693 | 19420 | 23686 | 27745
8 | 6851.4 | 3374.9 | 2342.3 | 1416.5 | 642.7 | 604 | 536.4 | 598.6 | 524.4 | 680.2 | 2660.2 | 5509.1
9 | 34202 | 28016 | 30632 | 23561 | 21104 | 17403 | 14272 | 16076 | 15088 | 21747 | 27786 | 32641
10 | 5919.51 | 2971.79 | 2078.1 | 1378.56 | 608.73 | 572.45 | 506.7 | 565.51 | 495.52 | 750.02 | 2608.28 | 5367.15
11 | 9281.4 | 5480.9 | 4696.5 | 3018.4 | 1169.2 | 456.4 | 354.9 | 391.6 | 344.1 | 1072.5 | 4337.4 | 7440.2
12 | 26391 | 21754 | 23911 | 18096 | 16401 | 13925 | 11667 | 13505 | 12491 | 17561 | 21858 | 25519
Experiment on 12 practicing eQuest modelers:
Each given identical plans and schedules for relatively conventional middle school – 3 hours
Input differences: internal gains, HVAC – need for more explicit modeling protocols(?)
Source: Pam Berkeley, Philip Haves and Erik Kolderup. Proc. SimBuild 2014, ASHRAE/IBPSA-USA

## Slide 11: New project: Accuracy of HVAC Load Predictions -Validation of EnergyPlus and DOE-2 using FLEXLAB
    Characterize differences between EnergyPlus and DOE-2.1e and DOE-2.2
  Use FLEXLAB to adjudicate between EnergyPlus and DOE-2
  Start with ASHRAE Standard 140 Tests:
    thermal Mass
    night-set-up/setback
    night ventilation …
  Report problems with DOE-2
  Fix and document any problems with EnergyPlus

## Slide 12: Conclusions
Need for ongoing development – validated models and procedures for:
  High performance new construction
  Deep retrofits
  Building operations
  Policy and program data
Impact of validation and uncertainty characterization:
  Designer confidence: direct energy savings from greater user of advanced low-energy systems and improved integrated design
  Investor confidence: management of risk → scaling up of high performance building projects